## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 02-01-2026 | [28 empty] | Date: | 02-01-2026 | [28 empty] | Date: | 02-01-2026 | [28 empty] | Date: | 02-01-2026 | [28 empty] | Date: | 02-01-2026 | [17 empty] | Date: | 02-01-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [17 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 20 | 710 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 800 | 0 | 0 | 40 | 310 | 357 | 0 | 5 | 49 | 0 | 36 | 0 | 111 | 0 | 0 | 11 | 0 | 74 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 50 | 104 | 0 | 17 | 0 | 42 | 20 | 0 | 0 | 159 | 0 | 19 | 8 | 166 | 0 | 0 | 0 | 4508 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 772 | 0 | 0 | 0 | 827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 140 | 220 | 0 | 270 | 490 | 0 | 4346 | 8854 | 97.6
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 600 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 620 | 0 | 0 | 8 | 325 | 355 | 0 | 5 | 7 | 0 | 36 | 0 | 112 | 0 | 0 | 11 | 0 | 66 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 50 | 85 | 0 | 5 | 0 | 42 | 20 | 0 | 0 | 159 | 0 | 19 | 0 | 162 | 0 | 0 | 0 | 4160 | 727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 778 | 0 | 0 | 0 | 833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 140 | 220 | 0 | 261 | 300 | 0 | 3952 | 8112 | 97.57
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 540 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 610 | 0 | 0 | 8 | 332 | 300 | 0 | 5 | 5 | 0 | 36 | 0 | 50 | 0 | 0 | 11 | 0 | 64 | 0 | 0 | 0 | 305 | 0 | 0 | 41 | 50 | 86 | 0 | 5 | 0 | 42 | 20 | 0 | 0 | 158 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 3844.5 | 705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 784 | 0 | 0 | 0 | 838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 256 | 280 | 0 | 3839 | 7683.5 | 97.57
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 555 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 610 | 0 | 0 | 8 | 317 | 350 | 0 | 5 | 5 | 0 | 36 | 0 | 50 | 0 | 0 | 11 | 0 | 60 | 0 | 0 | 0 | 300 | 0 | 0 | 41 | 50 | 86 | 0 | 5 | 0 | 22 | 20 | 0 | 0 | 158 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 3889.5 | 462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 785 | 0 | 0 | 0 | 839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 261 | 250 | 0 | 3547 | 7436.5 | 97.58
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 526 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 610 | 0 | 0 | 8 | 315 | 335 | 0 | 5 | 5 | 0 | 36 | 0 | 50 | 0 | 0 | 5 | 0 | 60 | 0 | 0 | 0 | 300 | 0 | 0 | 41 | 50 | 82 | 0 | 5 | 0 | 5 | 20 | 0 | 0 | 159 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 3946.5 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 0 | 0 | 0 | 838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 267 | 250 | 0 | 3321 | 7267.5 | 97.58
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 488 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 615 | 0 | 0 | 8 | 230 | 300 | 0 | 5 | 5 | 0 | 10 | 0 | 50 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 280 | 0 | 0 | 41 | 40 | 80 | 0 | 5 | 0 | 5 | 20 | 0 | 0 | 159 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 3689.5 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 0 | 0 | 0 | 836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 267 | 250 | 0 | 3287 | 6976.5 | 97.57
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 35 | 471 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 650 | 0 | 0 | 8 | 320 | 330 | 0 | 5 | 5 | 0 | 17 | 0 | 50 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 285 | 0 | 0 | 41 | 40 | 25 | 0 | 5 | 0 | 5 | 30 | 0 | 0 | 159 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 3880.5 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 795 | 0 | 0 | 0 | 837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 220 | 0 | 258 | 250 | 0 | 3360 | 7240.5 | 97.57
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0.04 | 46 | 0 | 29 | 471 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 652 | 1 | 0 | 8 | 340 | 300 | 0 | 25 | 19 | 0 | 30 | 0 | 50 | 0 | 0 | 0 | 0 | 56 | 0 | 1 | 0 | 300 | 0 | 0 | 41 | 40 | 17 | 0 | 5 | 0 | 32 | 30 | 0 | 0 | 159 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 3894.54 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.94 | 784 | 0 | 0 | 0 | 833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 0 | 0 | 0.02 | 150 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 264 | 250 | 0 | 3423.17 | 7317.71 | 97.56
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 14.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0.39 | 46 | 0 | 29 | 455 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 610 | 3 | 0 | 8 | 320 | 365 | 0 | 44 | 33 | 0 | 36 | 0 | 114 | 0 | 0 | 7 | 0 | 62 | 0 | 7 | 0 | 305 | 0 | 0 | 41 | 40 | 18 | 0 | 17 | 0 | 40 | 30 | 0 | 0 | 159 | 0 | 8 | 0 | 161 | 0 | 0 | 0 | 4053.89 | 705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.87 | 795 | 0 | 0 | 0 | 834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.48 | 10 | 0 | 0 | 2.68 | 160 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0.27 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.9 | 12 | 0.03 | 0 | 171 | 120 | 200 | 0 | 263 | 274 | 0 | 3943.23 | 7997.12 | 97.56
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 475 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 14.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0.85 | 46 | 0 | 29 | 450 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 768 | 7 | 0 | 8 | 300 | 389 | 0 | 44 | 40 | 0 | 36 | 0 | 113 | 0 | 0 | 11 | 0 | 82 | 0 | 12 | 0 | 300 | 0 | 0 | 41 | 30 | 17 | 1 | 17 | 0 | 75 | 30 | 0 | 0 | 159 | 0 | 19 | 0 | 160 | 0 | 0 | 0 | 4421.35 | 798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.23 | 788 | 0 | 0 | 0 | 835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.19 | 30 | 0 | 0 | 6.23 | 154 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.51 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 2.5 | 58 | 0.13 | 0 | 169 | 140 | 205 | 0 | 254 | 280 | 0 | 4181.79 | 8603.14 | 97.55
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 14.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.25 | 46 | 0 | 33 | 450 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 870 | 18 | 0 | 8 | 300 | 390 | 0 | 44 | 45 | 0 | 36 | 0 | 113 | 0 | 0 | 11 | 0 | 86 | 0 | 17 | 0 | 290 | 0 | 0 | 41 | 30 | 17 | 1 | 17 | 0 | 75 | 30 | 0 | 0 | 158 | 0 | 19 | 0 | 164 | 0 | 0 | 0 | 4548.75 | 798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 786 | 0 | 0 | 0 | 838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.74 | 65 | 0 | 0 | 10.87 | 148 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.01 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 34 | 0.25 | 0 | 168 | 140 | 209 | 0 | 269 | 280 | 0 | 4245.87 | 8794.62 | 97.55
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 435 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 14.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 1.77 | 46 | 0 | 34 | 450 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 850 | 20 | 0 | 78 | 300 | 393 | 0 | 44 | 46 | 0 | 36 | 0 | 111 | 0 | 0 | 11 | 0 | 98 | 0 | 16 | 0 | 300 | 0 | 0 | 41 | 30 | 17 | 2 | 17 | 0 | 77 | 30 | 0 | 0 | 159 | 0 | 19 | 0 | 165 | 1 | 0 | 0 | 4589.27 | 798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 775 | 0 | 0 | 0 | 845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.76 | 75 | 0 | 0 | 44.45 | 149 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 3.93 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 4.7 | 65 | 0.46 | 0 | 167 | 140 | 220 | 0 | 261 | 280 | 0 | 4351.3 | 8940.57 | 97.55
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 14.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.35 | 46 | 0 | 34 | 550 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 1010 | 20 | 0 | 130 | 300 | 389 | 0 | 44 | 46 | 0 | 36 | 0 | 110 | 0 | 0 | 11 | 0 | 110 | 0 | 13 | 0 | 315 | 0 | 0 | 41 | 30 | 16 | 1 | 17 | 0 | 81 | 30 | 0 | 0 | 159 | 0 | 19 | 24 | 165 | 1 | 0 | 0 | 4965.85 | 798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 810 | 0 | 0 | 0 | 977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.25 | 83 | 0 | 0 | 49.68 | 165 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.4 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 5.1 | 133 | 0.5 | 0 | 215 | 140 | 220 | 0 | 260 | 283 | 0 | 4698.93 | 9664.78 | 97.54
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 485 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 14.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.04 | 46 | 0 | 39 | 625 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1125 | 19 | 0 | 155 | 295 | 391 | 0 | 44 | 46 | 0 | 39 | 0 | 111 | 0 | 0 | 5 | 0 | 120 | 0 | 17 | 0 | 315 | 0 | 0 | 41 | 30 | 16 | 1 | 17 | 0 | 81 | 30 | 0 | 0 | 159 | 0 | 19 | 56 | 165 | 1 | 11 | 0 | 5300.54 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 1064 | 0 | 0 | 0 | 1191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.53 | 86 | 0 | 0 | 37.48 | 189 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 3.75 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 4.4 | 132 | 0.44 | 0 | 245 | 140 | 220 | 0 | 300 | 350 | 0 | 5392.6 | 10693.14 | 97.54
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 15.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.57 | 46 | 0 | 34 | 520 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 910 | 16 | 0 | 71 | 315 | 300 | 0 | 44 | 47 | 0 | 37 | 0 | 50 | 0 | 0 | 5 | 0 | 92 | 0 | 12 | 0 | 305 | 0 | 0 | 41 | 30 | 16 | 2 | 17 | 0 | 11 | 30 | 0 | 0 | 160 | 0 | 19 | 56 | 164 | 1 | 10.99 | 0 | 4482.06 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 973 | 0 | 0 | 0 | 973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.21 | 70 | 0 | 0 | 27.58 | 181 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 2.56 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 2.5 | 106 | 0.41 | 0 | 173 | 100 | 180 | 0 | 266 | 300 | 0 | 4710.26 | 9192.32 | 97.54
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 1.7 | 46 | 0 | 20 | 510 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 695 | 13 | 0 | 8 | 290 | 280 | 0 | 0 | 45 | 0 | 39 | 0 | 50 | 0 | 0 | 18 | 0 | 90 | 0 | 8 | 0 | 310 | 0 | 0 | 41 | 30 | 16 | 2 | 8 | 0 | 11 | 20 | 0 | 0 | 160 | 0 | 8 | 8 | 164 | 1 | 21.35 | 0 | 3941.05 | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 787 | 0 | 0 | 0 | 828.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.29 | 46 | 0 | 0 | 16.45 | 171 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 1.85 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 2.4 | 73 | 0.33 | 0 | 166 | 100 | 180 | 0 | 255 | 280 | 0 | 3929.51 | 7870.56 | 97.53
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0.86 | 32 | 0 | 0 | 510 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 600 | 7 | 0 | 0 | 330 | 280 | 0 | 0 | 12 | 0 | 25 | 0 | 50 | 0 | 0 | 18 | 0 | 82 | 0 | 6 | 0 | 315 | 0 | 0 | 41 | 30 | 16 | 1 | 0 | 0 | 0 | 20 | 0 | 0 | 160 | 0 | 8 | 0 | 164 | 0 | 8.43 | 0 | 3773.29 | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 782 | 0 | 0 | 0 | 841.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.98 | 22 | 0 | 0 | 5.61 | 202 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0.52 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 1.1 | 33 | 0.14 | 0 | 174 | 100 | 180 | 0 | 256 | 250 | 0 | 3867.75 | 7641.04 | 97.53
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 1 | 17 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0.06 | 32 | 0 | 5 | 510 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 715 | 1 | 0 | 0 | 340 | 310 | 0 | 0 | 10 | 0 | 25 | 0 | 50 | 0 | 0 | 5 | 0 | 78 | 0 | 1 | 0 | 320 | 0 | 0 | 41 | 30 | 16 | 0 | 0 | 0 | 5 | 20 | 0 | 0 | 160 | 3 | 8 | 8 | 164 | 0 | 0.7 | 0 | 4009.76 | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 787 | 0 | 0 | 0 | 956.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.27 | 4 | 0 | 0 | 1.3 | 183 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0.14 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.2 | 3 | 0 | 0 | 177 | 100 | 180 | 0 | 259 | 260 | 0 | 3991.95 | 8001.71 | 97.53
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 25 | 625 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 895 | 0 | 0 | 70 | 360 | 360 | 0 | 23 | 29 | 0 | 39 | 0 | 110 | 0 | 0 | 11 | 0 | 100 | 0 | 0 | 0 | 320 | 0 | 0 | 41 | 50 | 17 | 0 | 17 | 0 | 77 | 30 | 0 | 0 | 160 | 17 | 19 | 26 | 164 | 0 | 0 | 0 | 4859 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 819 | 0 | 0 | 0 | 1031.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 140 | 220 | 0 | 302 | 352 | 0 | 4611.35 | 9470.35 | 97.53
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 21 | 625 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 965 | 0 | 0 | 55 | 350 | 360 | 0 | 44 | 46 | 0 | 39 | 0 | 110 | 0 | 0 | 5 | 0 | 90 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 50 | 16 | 0 | 17 | 0 | 78 | 30 | 0 | 0 | 160 | 0 | 19 | 35 | 165 | 0 | 0 | 0 | 4875 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 861 | 0 | 0 | 0 | 932.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 140 | 220 | 0 | 320 | 438 | 0 | 4686.09 | 9561.09 | 97.52
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 21 | 625 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 950 | 0 | 0 | 12 | 395 | 360 | 0 | 5 | 46 | 0 | 36 | 0 | 111 | 0 | 0 | 11 | 0 | 96 | 0 | 0 | 0 | 320 | 0 | 0 | 41 | 50 | 16 | 0 | 17 | 0 | 81 | 30 | 0 | 0 | 160 | 0 | 19 | 35 | 165 | 0 | 0 | 0 | 4848 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 882 | 0 | 0 | 0 | 909.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 140 | 220 | 0 | 258 | 493 | 0 | 4685.58 | 9533.58
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 29 | 625 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 950 | 0 | 0 | 8 | 393 | 360 | 0 | 5 | 47 | 0 | 36 | 0 | 111 | 0 | 0 | 11 | 0 | 96 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 50 | 16 | 0 | 17 | 0 | 81 | 30 | 0 | 0 | 160 | 0 | 19 | 35 | 166 | 0 | 0 | 0 | 4855 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 933 | 0 | 0 | 0 | 924.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 140 | 220 | 0 | 253 | 502 | 0 | 4750.14 | 9605.14 | 97.52
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 30 | 625 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 950 | 0 | 0 | 8 | 325 | 360 | 0 | 5 | 48 | 0 | 36 | 0 | 112 | 0 | 0 | 11 | 0 | 96 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 50 | 73 | 0 | 17 | 0 | 81 | 30 | 0 | 0 | 160 | 0 | 19 | 8 | 167 | 0 | 0 | 0 | 4786 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 940 | 0 | 0 | 0 | 928.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 140 | 220 | 0 | 260 | 545 | 0 | 4777.05 | 9563.05 | 97.52
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 35 | 625 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 873 | 0 | 0 | 8 | 300 | 360 | 0 | 5 | 49 | 0 | 39 | 0 | 112 | 0 | 0 | 11 | 0 | 98 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 50 | 99 | 0 | 17 | 0 | 81 | 30 | 0 | 0 | 159 | 0 | 19 | 8 | 168 | 0 | 0 | 0 | 4678 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 876 | 0 | 0 | 0 | 855.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 140 | 220 | 0 | 264 | 547 | 0 | 4646.3 | 9324.3 | 97.52
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 37 | 530 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 830 | 0 | 0 | 8 | 310 | 300 | 0 | 5 | 49 | 0 | 35 | 0 | 113 | 0 | 0 | 11 | 0 | 82 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 50 | 88 | 0 | 17 | 0 | 42 | 20 | 0 | 0 | 159 | 0 | 19 | 0 | 168 | 0 | 0 | 0 | 4376 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 776 | 0 | 0 | 0 | 838.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 140 | 220 | 0 | 253 | 500 | 0 | 4349.53 | 8725.53 | 97.52
Total KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8276400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4451100 | 0 | 9476364 | 0 | 0 | 0 | 0 | 0 | 102337 | 27600 | 355800 | 348840 | 0 | 0 | 0 | 0 | 0 | 0 | 237600 | 0 | 0 | 0 | 0 | 0 | 16563 | 1073280 | 0 | 740640 | 12981818.18 | 0 | 0 | 0 | 0 | 0 | 3989769 | 0 | 0 | 0 | 18692725 | 124470 | 0 | 719273 | 7698800 | 8514200 | 0 | 556728 | 718560 | 0 | 804456 | 0 | 2024263 | 0 | 0 | 219990 | 0 | 1948800 | 0 | 113327 | 0 | 7418000 | 0 | 0 | 974000 | 966480 | 1031236 | 12950 | 272496 | 0 | 976320 | 621216 | 0 | 0 | 3431570 | 35280 | 307200 | 264000 | 3655680 | 6300 | 44780 | 0 | 104231211.18 | 17051636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 432720 | 19839997 | 0 | 0 | 0 | 21381818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201372 | 504520 | 0 | 0 | 201744 | 4181818 | 0 | 0 | 0 | 0 | 0 | 9208363 | 0 | 17940 | 0 | 0 | 0 | 131637 | 0 | 0 | 0 | 0 | 25310.16 | 667744 | 2724 | 0 | 4648000 | 2972000 | 5181250 | 0 | 6407272 | 8634181.82 | 0 | 101692046.98 | 205923258.16

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 03-01-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-01-2026 | during | 03-01-2026 | during | 03-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 338 | 353 | 412 | 412 | 392 | 392 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 450 | 450 | 225 | 225 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 7 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 14.5 | 15 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 14 | 14 | 14 | 14 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 21 | 0 | 20 | 0 | 20 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 430 | 415 | 583 | 583 | 450 | 450 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 0 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1042.5 | 1022 | 5006.35 | 4986.35 | 2369.33 | 2349.33
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 16 | 0 | 16 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 | 46 | 46 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 172 | 173 | 150 | 150 | 150 | 150 | Plant availability less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 56 | 72 | 40 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 10 | 10 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 34 | 29 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.35 | 0 | 3.31 | 0 | 3.31 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1010 | 950 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 13 | 0 | 6 | 0 | 6 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 550 | 625 | 520 | 520 | 520 | 520 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1835.35 | 1836 | 3302.17 | 3311.86 | 2803.81 | 2821.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 389 | 360 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 318.81 | 318.81 | 0 | 0 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 300 | 393 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 36 | 36 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 46 | 47 | 55 | 55 | 55 | 55 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 130 | 8 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 5 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 110 | 111 | 163 | 163 | 115 | 115 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 110 | 96 | 84 | 82 | 84 | 82 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 11 | 20.77 | 20.77 | 20.77 | 20.77 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 13 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1189 | 1067 | 2484.83 | 2422.83 | 2014.02 | 1952.02
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-01-2026 | during | 03-01-2026 | during | 03-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 165 | 166 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.4 | 0 | 1.4 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 24 | 35 | 60 | 60 | 60 | 60 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 19 | 20 | 20 | 20 | 20 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 0 | 0 | 25 | 0 | 25 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 209 | 220 | 340.4 | 314 | 330.4 | 304
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 41 | 41 | 41 | 41 | 41 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 50 | 50 | 50 | 50 | 50 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 16 | 16 | 163 | 163 | 100 | 100 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 81 | 81 | 81 | 81 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 159 | 160 | 155 | 155 | 158 | 158 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 690 | 710 | 906 | 906 | 792 | 792
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 798 | 892 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 70 | 0 | 76 | 0 | 76 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 810 | 933 | 0 | 0 | 1108 | 1108 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1678 | 1825 | 2348 | 2272 | 2291.1 | 2215.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 260 | 253 | 0 | 0 | 622 | 622 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 140 | 140 | 136 | 136 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 283 | 502 | 605 | 605 | 575 | 575 | FGMO & # 01 Under maint.
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 215 | 279 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.5 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1118.5 | 1394 | 1529 | 1528 | 1968 | 1967
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 44.25 | 0 | 37.17 | 0 | 37.17 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 165 | 193 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.4 | 0 | 5.1 | 0 | 5.1 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 977 | 924.14 | 1435.88 | 1435.88 | 1356 | 1356 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 49.68 | 0 | 55 | 0 | 55 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 83 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1737.33 | 1531.14 | 3116.14 | 2918.87 | 2503.48 | 2306.21
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.1 | 0 | 3.2 | 0 | 3.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 27 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 133 | 0 | 126.45 | 0 | 126.45 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 165.1 | 0 | 416.65 | 262 | 382.65 | 228
System Total |  |  |  |  | 28823.2 | 28382.248 | 9664.78 | 9605.14 | 19449.54 | 18921.91 | 15454.79 | 14935.16
Forecast Scenario (03-01-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8200 |  | 0 |  | 8200
|  |  |  | 1:00 | 7500 |  | 0 |  | 7500
|  |  |  | 2:00 | 7110 |  | 0 |  | 7110
|  |  |  | 3:00 | 6870 |  | 0 |  | 6870
|  |  |  | 4:00 | 6600 |  | 0 |  | 6600
|  |  |  | 5:00 | 6620 |  | 0 |  | 6620
|  |  |  | 6:00 | 7040 |  | 0 |  | 7040
|  |  |  | 7:00 | 7380 |  | 0 |  | 7380
|  |  |  | 8:00 | 8310 |  | 0 |  | 8310
|  |  |  | 9:00 | 8740 |  | 0 |  | 8740
|  |  |  | 10:00 | 8380 |  | 0 |  | 8380
|  |  |  | 11:00 | 8670 |  | 0 |  | 8670
|  |  |  | 12:00 | 8990 |  | 0 |  | 8990
|  |  |  | 13:00 | 9500 |  | 0 |  | 9500
|  |  |  | 14:00 | 9220 |  | 0 |  | 9220
|  |  |  | 15:00 | 8910 |  | 0 |  | 8910
|  |  |  | 16:00 | 8680 |  | 0 |  | 8680
|  |  |  | 17:00 | 9290 |  | 0 |  | 9290
|  |  |  | 18:00 | 10560 |  | 0 |  | 10560
|  |  |  | 18:30 | 10650 |  | 0 |  | 10650
|  |  |  | 19:00 | 10800 |  | 0 |  | 10800
|  |  |  | 19:30 | 10750 |  | 0 |  | 10750
|  |  |  | 20:00 | 10620 |  | 0 |  | 10620
|  |  |  | 21:00 | 10400 |  | 0 |  | 10400
|  |  |  | 22:00 | 10050 |  | 0 |  | 10050
|  |  |  | 23:00 | 9230 |  | 0 |  | 9230
Probable Maximum Temperature: |  |  | 24.30°C
Probable Maximum Demand at Day Peak: |  |  | 8990.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 10800.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10800.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 207.67 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:27 hrs on 03-01-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 02-01-2026
Power Supply Scenario
| Day Peak Generation |  |  | 9664.78 | MW | 12:00 Hr. | Energy Generated |  |  | 205.9233 |  | MKWHr.
| Day Peak Demand |  |  | 9664.78 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 9605.14 | MW | 20:00 Hr. | Energy Demand |  |  | 205.9233 |  | MKWHr.
| Evening Peak Demand |  |  | 9605.14 | MW | 20:00 Hr. | Maximum Temperature |  |  | 23.6 |  | °C
| Minimum Generation of the Day |  |  | 6976.5 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 656.64 |  | MMCFD
| Maximum Generation of the Day |  |  | 10693.14 | MW | 13:00 Hr. | Production Cost per KWHr |  |  | 5.2718 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 22.9085 | 0 | 0.0276 | 0 | 0 | 0.10234 | 0 | 0 | 23.0384 | Gas | 89.7856 | Gas | 317708139.35
| Chattogram Zone |  |  | 4.7304 | 31.6745 | 0 | 0 | 1.0733 | 0.14103 | 0 | 0.2376 | 37.8569 | Coal | 71.204 | Coal | 473715461.431
| Cumilla Zone |  |  | 21.2563 | 0 | 0 | 0 | 0 | 0.11333 | 1.9488 | 0 | 23.3184 | HFO | 0.63408 | HFO | 11427494.4
| Mymensingh Zone |  |  | 3.6557 | 0 | 0.60648 | 0 | 0 | 0.05108 | 0 | 0 | 4.3132 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 15.6913 | 0 | 0 | 0 | 0 | 0.01295 | 0 | 0 | 15.7043 | Hydro | 1.0733 | Hydro | 107328
| Khulna Zone |  |  | 0 | 19.84 | 0 | 0 | 0 | 0.43272 | 17.0516 | 0 | 37.3244 | Solar | 2.6064 | Solar | 41889867.182
| Barishal Zone |  |  | 8.1532 | 19.6895 | 0 | 0 | 0 | 0.002724 | 0 | 0 | 27.8454 | Import | 40.3823 | Import | 237239549.2
| Rajshahi Zone |  |  | 13.3902 | 0 | 0 | 0 | 0 | 0.92558 | 21.3818 | 0 | 35.6976 | Wind | 0.2376 | Wind | 3495096
| Rangpur Zone |  |  | 0 | 0 | 0 | 0 | 0 | 0.82469 | 0 | 0 | 0.82469
| Total |  |  | 89.7856 | 71.204 | 0.63408 | 0 | 1.0733 | 2.6064 | 40.3823 | 0.2376 | 205.9233
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 317708139.35 |  | Hydro | 107328
|  |  |  | Coal | 473715461.431 |  | Solar | 41889867.182
|  |  |  | HFO | 11427494.4 |  | Import | 237239549.2
|  |  |  | HSD | 0 |  | Wind | 3495096
[5 empty] | Total: | 108,55,82,935 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 2414000 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 17.0516 | Peak Hr Flow | 892.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 29835272.73 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 21.3818 | Peak Hr Flow | 924.14 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1658 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.9488 | Peak Hr Flow | 96.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2059 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 40.3823 | Peak Hr Flow | 1912.14 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3129
|  |  |  | Chattogram |  | 0 |  | 1069
|  |  |  | Cumilla |  | 0 |  | 895
|  |  |  | Mymensingh |  | 0 |  | 801
|  |  |  | Sylhet |  | 0 |  | 374
|  |  |  | Khulna |  | 0 |  | 1146
|  |  |  | Barishal |  | 0 |  | 313
|  |  |  | Rajshahi |  | 0 |  | 919
|  |  |  | Rangpur |  | 0 |  | 622
|  |  |  | Total |  | 0 |  | 9268
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bheramara 410 MW CCPP GT |  |  | 278
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Bheramara 410 MW CCPP ST |  |  | 132
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 410
|  |  |  | Total Unavailable Capacity |  |  |  | 710
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:05 |  | Ghorasal-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Ghorashal
end side work
| 08:20 | 17:15 | Tongi 230/132/33kV S/S T-03 LT Scheduled S/D Due to Annual maintenance
|  | 08:28 | Juldah 132/33kV S/S 133/33 KV T-2 416T HT is restored.
| 08:36 | 17:31 | Gopalganj 400/132kV S/S 400kV Amtoli Ckt-1 Scheduled S/D
| 08:43 | 16:40 | Aminbazar-Meghnaghat 400kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end Due to
Requested by Aminbazar
| 08:45 | 12:42 | Barapukuria-Rangpur 132 kV Ckt-2 Project Work S/D from Saidpur 132/33kV end.
| 08:46 | 12:44 | Barapukuria-Saidpur 132 kV Ckt-2 Project Work S/D from Saidpur 132/33kV end. and from
Barapukuria 230/132/33kV end Due to project work
| 08:47 | 12:41 | Barapukuria-Saidpur 132 kV Ckt-1 Project Work S/D from Barapukuria 230/132/33kV end Due
to project work
| 08:49 | 16:25 | Haripur-Sonargaon 132kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to Annual
Deadline checking. and from Sonargaon 132/33kV end Due to Annual maintenance work.
| 08:50 | 19:30 | Tongi 230/132/33kV S/S 132 kV Bus-1 Scheduled S/D Due to Project (To4 Trans former
Installations Work)
| 08:51 | 15:00 | Kasba 132/33kV S/S Muradnagar-Kasba Ckt-1 Project Work S/D Due to Remove birds net, kites
and others obstacles by Project
| 08:58 | 14:58 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Kosba Ckt-01 Project Work S/D Due to project
work
| 10:40 | 12:16 | Rahanpur 400/132kV S/S AT-01 LT Project Work S/D Due to Maintenance work
| 10:40 | 12:16 | Rahanpur 400/132kV S/S AT-01 HT Project Work S/D Due to Maintenance work
| 12:00 |  | Day Peak Generation is 9662 MW.
|  | 12:07 | Rampura 230/132kV S/S Auto Transformer - 02 HT is restored.
|  | 12:08 | Rampura 230/132kV S/S Auto Transformer - 02 LT is restored.
|  | 12:30 | Mymensingh 132/33kV S/S Bus A is restored.
|  | 12:48 | Mymensingh 132/33kV S/S 50 MW Solar Plant is restored.
| 13:04 | 15:00 | Rahanpur 400/132kV S/S AT-02 LT Project Work S/D Due to Maintenance work
| 13:04 | 15:00 | Rahanpur 400/132kV S/S AT-02 HT Project Work S/D Due to Maintenance work
| 15:44 | 17:17 | Ishurdi 230/132kV S/S 230/132 kV T-01 LT Project Work S/D Due to HT side "B" phase PT
voltage test
| 15:45 | 17:16 | Ishurdi 230/132kV S/S 230/132 kV T-01 HT Project Work S/D Due to HT side "B" phase PT
voltage test
| 16:35 | 18:48 | Chandina 132/33kV S/S TR-3 HT Forced S/D Due to for red hot solution work in pbs
cumilla-1 feeder
| 16:35 | 18:48 | Chandina 132/33kV S/S TR-3 LT Forced S/D Due to for red hot solution work in pbs
cumilla-1 feeder
|  | 18:00 | Ghorasal- Ishwardi 230 kV Ckt-1 is restored.
|  | 18:00 | Ghorasal- Ishwardi 230 kV Ckt-1 is restored.
|  | 18:10 | Khulna (C) S/S Tr-2 415 T HT is restored.
| 18:10 |  | 22 MW interruption occurred under T-3 transformer of Tangail substation from 18:10 hrs to
18:46 hrs due to fire of PBS feeder named "Ghatail". Now, No interruption is occuring.
|  | 18:11 | Khulna (C) S/S Tr-2 415 T LT is restored.
|  | 18:37 | Ghorasal-Joydeb-B 132kV Ckt-2 is restored.
|  | 19:15 | Siddhirganj 230/132kV S/S 335MW EGCB 1 is restored.
|  | 21:11 | Meghnaghat-Shyampur 230kV Ckt-2 is restored.
| 01:17 |  | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 Forced S/D Due to Shutdown
instructed by NLDC due to emergency voltage Control .
| 01:17 |  | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 Forced S/D Due to Shutdown
instructed by NLDC due to emergency voltage Control .
| 05:00 |  | Minimum generation 6686 MW
| 06:36 |  | Ashuganj 230/132 kV OAT-11 transformer scheduled shutdown due to red-hot maintenance
| 07:23 |  | Meghnaghat-Shyampur 230kV Ckt-1 Scheduled S/D from Meghnaghat 400/230kV end Due to
Maintenance purpose
| 07:28 |  | Ghorasal-Joydeb-B 132kV Ckt-2 Scheduled S/D from Joydebpur 132/33kV end Due to OPGW
wire stringing by OFCN.
| 07:31 |  | Rampura 230/132kV S/S Auto Transformer - 02 HT Scheduled S/D Due to Annual Maintenance
| 07:31 |  | Rampura 230/132kV S/S Auto Transformer - 02 LT Scheduled S/D Due to Annual Maintenance
| 07:42 |  | Meghnaghat-Shyampur 230kV Ckt-1 Scheduled S/D from Shyampur 230/132kV end Due to Dead
Line Checking & Disc Cleaning
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 02-01-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 353 | 8276400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4451100 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 15 | 355800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 348840 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 0 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 102337 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 415 | 9476364 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 0 | 27600 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1022 | 23038441
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 124470 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1073280 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 173 | 3989769 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 29 | 740640 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 16563 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 950 | 18692725 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 13 | 237600 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 625 | 12981818.18 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 1836 | 37856865.18
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 0 | 0 | Shutdown
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 360 | 8514200 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 7698800 | FGMO
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 36 | 804456 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 47 | 718560 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 719273 | Transformer overload
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 5 | 556728 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 111 | 2024263 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 96 | 1948800 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 11 | 219990 | Machine Schedule Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 113327 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1067 | 23318397
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 166 | 3655680 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 6300 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 35 | 264000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 307200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 44780 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 35280 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 220 | 4313240
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 12950 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 974000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 50 | 966480 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 16 | 1031236 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 621216 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 976320 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 160 | 3431570 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 272496 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7418000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 710 | 15704268
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 892 | 17051636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 432720 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 933 | 19839997 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1825 | 37324353
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 253 | 6407272 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 140 | 2972000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 502 | 8634181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5181250 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 279 | 4648000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2724 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1394 | 27845427.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 201372 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 193 | 4181818 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9208363 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 17940 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 924.14 | 21381818 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 201744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 504520 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1531.14 | 35697575
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 25310.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 0 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 131637 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 667744 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 0 | 824691.16
Eastern Grid Total |  |  |  |  | 17398.245 | 4855 | 104231211.18
Western Grid Total |  |  |  |  | 10984.003 | 4750.14 | 101692046.98
National Grid Total |  |  |  |  | 28382.248 | 9605.14 | 205923258.16
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 02-01-2026
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6267.96 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 2999.5 | MW
i) Dhaka area |  |  | 3128.66 |  | MW | i) Khulna area |  |  |  | 1145.5 | MW
ii) Chattogram area |  |  | 1069.3 |  | MW | ii) Barishal area |  |  |  | 313 | MW
iii) Cumilla area |  |  | 895 |  | MW | iii) Rajshahi area |  |  |  | 919 | MW
iv) Mymensingh area |  |  | 801 |  | MW | iv) Rangpur area |  |  |  | 622 | MW
v) Sylhet area |  |  | 374 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 9267.46 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 90 | 12:00 | 133 | Netrakona | 109 | 18:30
2 | AKSML | 131.3 | 04:00 | 68 | Hathazari | 60 | 13:00 | 134 | New | 50 | 12:00
3 | Aftabnagar | 28 | 13:00 | 69 | Hatirjheel | 24 | 13:00 | 135 | Niamatpur | 52 | 08:00
4 | Agargaon | 88 | 13:00 | 70 | Ishurdi | 51 | 19:30 | 136 | Noapara | 30 | 18:00
5 | Agrabad | 34 | 12:00 | 71 | Jaldhaka | 58 | 09:00 | 137 | PHP | 8 | 08:00
6 | Amnura | 22 | 09:00 | 72 | Jamalpur | 95 | 18:30 | 138 | Pabna | 61 | 13:00
7 | Ashuganj | 52 | 13:00 | 73 | Jashore | 109 | 13:00 | 139 | Palashbari | 78 | 18:30
8 | BSRM | 197 | 18:00 | 74 | Jhenaidah | 96 | 18:00 | 140 | Panchagarh | 42 | 18:00
9 | Bagerhat | 63 | 18:00 | 75 | Joydebpur | 80 | 12:00 | 141 | Patiya | 6.5 | 13:00
10 | Bajitpur | 63 | 13:00 | 76 | Joypurhat | 42 | 20:00 | 142 | Patuakhali | 38 | 20:00
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 12 | 19:00 | 143 | Payra | 28 | 13:00
12 | Bakulia | 54 | 12:00 | 78 | KSRM | 21 | 07:00 | 144 | Postogola | 35 | 13:00
13 | Banani | 15.6 | 13:00 | 79 | Kabirpur | 132 | 12:00 | 145 | Purbachal | 19 | 12:00
14 | Bangabhaban | 4 | 11:00 | 80 | Kachua | 60 | 13:00 | 146 | Purbasadipur | 109 | 13:00
15 | Barapukuria | 43 | 19:30 | 81 | Kallyanpur | 72 | 12:00 | 147 | Rahanpur | 24 | 18:30
16 | Barguna | 14 | 13:00 | 82 | Kalurghat | 22 | 12:00 | 148 | Rahim | 26 | 02:00
17 | Barishal | 95 | 13:00 | 83 | Kamrangirchar | 46 | 01:00 | 149 | Rajbari | 54 | 18:30
18 | Barishal-230 | 68 | 13:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 104 | 09:00
19 | Baroaulia | 53 | 12:00 | 85 | Kasba | 25 | 13:00 | 151 | Rajshahi | 68 | 13:00
20 | Baroirhat | 56 | 13:00 | 86 | Kazla | 75 | 13:00 | 152 | Rajshahi-230 | 78 | 13:00
21 | Bashundhara | 134 | 13:00 | 87 | Keranigonj | 38 | 13:00 | 153 | Ramganj | 74 | 12:00
22 | BashundharaCement | 7 | 00:00 | 88 | Khagrachori | 24 | 18:00 | 154 | Rampur | 25 | 13:00
23 | Beanibazar | 48 | 13:00 | 89 | Khulna | 46 | 13:00 | 155 | Rangamati | 13 | 18:00
24 | Benapole | 54 | 09:00 | 90 | Khulshi | 155 | 12:00 | 156 | Rangpur | 110 | 12:00
25 | Bhaluka | 113 | 13:00 | 91 | Kishoreganj | 85 | 19:00 | 157 | Ruppur | 1.4 | 11:00
26 | Bhandaria | 36 | 20:00 | 92 | Kodda | 165 | 00:00 | 158 | SSM | 0 | 00:00
27 | Bhangura | 24 | 13:00 | 93 | Kulaura | 31 | 13:00 | 159 | Saidpur | 75 | 13:00
28 | Bheramara(GK) | 38 | 18:00 | 94 | Kurigram | 44 | 18:00 | 160 | Satkhira | 88 | 18:30
29 | Bhulta | 157 | 11:00 | 95 | Kushtia | 102 | 13:00 | 161 | Satmasjid | 78 | 13:00
30 | Bog-Sherpur | 52 | 18:00 | 96 | Laksam | 23 | 13:00 | 162 | Savar | 124 | 12:00
31 | Bogura | 103 | 19:30 | 97 | Lakshmipur | 25 | 13:00 | 163 | SevenRings | 14.19 | 01:00
32 | Borhanuddin | 63 | 13:00 | 98 | Lalbag | 46 | 00:00 | 164 | ShahCement | 18 | 02:00
33 | Brahmanbaria | 96 | 13:00 | 99 | Lalmonirhat | 40 | 18:00 | 165 | Shahjadpur | 46 | 13:00
34 | Cantonment | 82 | 12:00 | 100 | MI_Cement | 15.8 | 02:00 | 166 | Shahjibazar | 78 | 21:00
35 | Chandina | 15 | 19:30 | 101 | Madanganj | 38 | 12:00 | 167 | Shahmirpur | 28 | 00:00
36 | Chandpur | 58 | 13:00 | 102 | Madaripur | 74 | 13:00 | 168 | Shariatpur | 62 | 13:00
37 | Chandraghona | 27 | 18:00 | 103 | Madartek | 64 | 13:00 | 169 | Sherpur | 104 | 13:00
38 | Chapai | 47 | 19:30 | 104 | Madunaghat | 44 | 13:00 | 170 | Shikalbaha | 15 | 12:00
39 | Charsaidpur | 44 | 00:00 | 105 | Magura | 46 | 18:00 | 171 | Shitalakhya | 45.6 | 12:00
40 | Chauddagram | 59 | 13:00 | 106 | Mahasthangarh | 44 | 09:00 | 172 | Sholosohor | 28 | 12:00
41 | Chhatak | 25 | 18:30 | 107 | Maijdee | 25 | 19:00 | 173 | Shyampur | 128 | 01:00
42 | Chowmuhani | 128 | 13:00 | 108 | Manikganj | 86 | 18:00 | 174 | Siddhirganj | 77 | 13:00
43 | Chuadanga | 83 | 13:00 | 109 | Maniknagar | 52 | 13:00 | 175 | Sirajganj | 62 | 19:00
44 | Coxsbazar | 103 | 13:00 | 110 | Matarbari | 38 | 13:00 | 176 | Sonargaon | 103 | 00:00
45 | Cumilla(N) | 84 | 18:00 | 111 | Matuail | 32 | 00:00 | 177 | Sreemongol | 53 | 13:00
46 | Cumilla(S) | 120 | 13:00 | 112 | Metrorail_Motijheel | 24 | 18:00 | 178 | Sreepur | 69 | 18:30
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 3 | 18:00 | 179 | Srinagar | 36.4 | 13:00
48 | Daudkandi | 102 | 19:30 | 114 | Millgate | 56 | 11:00 | 180 | Sunamganj | 37 | 13:00
49 | DhakaUniversity | 30 | 12:00 | 115 | Mirpur | 112 | 13:00 | 181 | Sylhet | 35 | 12:00
50 | Dhamrai | 102 | 19:30 | 116 | Mirsorai | 7 | 18:30 | 182 | Sylhet-132 | 79 | 13:00
51 | Dhanmondi | 63 | 13:00 | 117 | Mirzapur | 31 | 13:00 | 183 | TK | 17 | 13:00
52 | Dohazari | 64 | 20:00 | 118 | Mithapukur | 42 | 18:00 | 184 | Tangail | 122 | 13:00
53 | Faridpur | 101 | 19:00 | 119 | Modern | N/A | N/A | 185 | Taraganj | 14 | 18:00
54 | Fatullah | 76 | 00:00 | 120 | Mogbazar | 32.4 | 10:00 | 186 | Tasnim | 23 | 01:00
55 | Fenchuganj | 29 | 13:00 | 121 | Mongla | 23 | 18:00 | 187 | Thakurgaon | 76 | 18:30
56 | Feni | 77 | 13:00 | 122 | Motijheel | 27 | 13:00 | 188 | Tongi | 88 | 12:00
57 | GPH | 79 | 00:00 | 123 | Muktagacha | 30 | 18:00 | 189 | Ullahpara | 23 | 18:00
58 | Ghatail | 58 | 19:00 | 124 | Munshiganj | 84 | 13:00 | 190 | Ullon | 59 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 25 | 13:00 | 191 | Uttara | 59 | 13:00
60 | Ghorashal-230 | 66 | 00:00 | 126 | Mymensingh | 142 | 12:00 | 192 | UttaraNew | 38 | 14:00
61 | Goalpara | 27 | 12:00 | 127 | Naogaon | 79 | 13:00 | 193 | Zigatola | 76 | 13:00
62 | Gollamari | 76 | 13:00 | 128 | Narail | 41.5 | 18:30
63 | Gopalganj | 77 | 18:30 | 129 | Narinda | 42 | 13:00
64 | Gulshan | 58 | 13:00 | 130 | Narshingdi | 127 | 19:00
65 | Halishahar | 29 | 19:00 | 131 | Natore | 99 | 13:00
66 | HaripurSBU | 85 | 03:00 | 132 | Nawabganj | 34.6 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 02-01-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 8854 | 0 |  | 8854
1:00 | 8112 | 0 |  | 8112
2:00 | 7683.5 | 0 |  | 7683.5
3:00 | 7436.5 | 0 |  | 7436.5
4:00 | 7267.5 | 0 |  | 7267.5
5:00 | 6976.5 | 0 |  | 6976.5
6:00 | 7240.5 | 0 |  | 7240.5
7:00 | 7317.71 | 0 |  | 7317.71
8:00 | 7997.12 | 0 |  | 7997.12
9:00 | 8603.14 | 0 |  | 8603.14
10:00 | 8794.62 | 0 |  | 8794.62
11:00 | 8940.57 | 0 |  | 8940.57
12:00 | 9664.78 | 0 |  | 9664.78
13:00 | 10693.14 | 0 |  | 10693.14
14:00 | 9192.32 | 0 |  | 9192.32
15:00 | 7870.56 | 0 |  | 7870.56
16:00 | 7641.04 | 0 |  | 7641.04
17:00 | 8001.71 | 0 |  | 8001.71
18:00 | 9470.35 | 0 |  | 9470.35
19:00 | 9561.09 | 0 |  | 9561.09
19:30 | 9533.58 | 0 |  | 9533.58
20:00 | 9605.14 | 0 |  | 9605.14
21:00 | 9563.05 | 0 |  | 9563.05
22:00 | 9324.3 | 0 |  | 9324.3
23:00 | 8725.53 | 0 |  | 8725.53
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 02-01-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4508 | 4346 | 8854 | DAILY GENERATION CURVE
00:30 | 4334 | 4149 | 8483
01:00 | 4160 | 3952 | 8112 | 02-01-2026
01:30 | 4002.25 | 3895.5 | 7897.75
02:00 | 3844.5 | 3839 | 7683.5
02:30 | 3867 | 3693 | 7560
03:00 | 3889.5 | 3547 | 7436.5
03:30 | 3918 | 3434 | 7352
04:00 | 3946.5 | 3321 | 7267.5
04:30 | 3818 | 3304 | 7122
05:00 | 3689.5 | 3287 | 6976.5
05:30 | 3785 | 3323.5 | 7108.5
06:00 | 3880.5 | 3360 | 7240.5
06:30 | 3887.52 | 3391.585 | 7279.105
07:00 | 3894.54 | 3423.17 | 7317.71
07:30 | 3974.215 | 3683.2 | 7657.415
08:00 | 4053.89 | 3943.23 | 7997.12
08:30 | 4237.62 | 4062.51 | 8300.13
09:00 | 4421.35 | 4181.79 | 8603.14
09:30 | 4485.05 | 4213.83 | 8698.88
10:00 | 4548.75 | 4245.87 | 8794.62
10:30 | 4569.01 | 4298.585 | 8867.595
11:00 | 4589.27 | 4351.3 | 8940.57
11:30 | 4777.56 | 4525.115 | 9302.675
12:00 | 4965.85 | 4698.93 | 9664.78
12:30 | 5133.195 | 5045.765 | 10178.96
13:00 | 5300.54 | 5392.6 | 10693.14
13:30 | 4891.3 | 5051.43 | 9942.73
14:00 | 4482.06 | 4710.26 | 9192.32
14:30 | 4211.555 | 4319.885 | 8531.44
15:00 | 3941.05 | 3929.51 | 7870.56
15:30 | 3857.17 | 3898.63 | 7755.8
16:00 | 3773.29 | 3867.75 | 7641.04
16:30 | 3891.525 | 3929.85 | 7821.375
17:00 | 4009.76 | 3991.95 | 8001.71
17:30 | 4434.38 | 4301.65 | 8736.03
18:00 | 4859 | 4611.35 | 9470.35
18:30 | 4867 | 4648.72 | 9515.72
19:00 | 4875 | 4686.09 | 9561.09
19:30 | 4848 | 4685.58 | 9533.58
20:00 | 4855 | 4750.14 | 9605.14
20:30 | 4820.5 | 4763.595 | 9584.095 |  | Executive Engineer
21:00 | 4786 | 4777.05 | 9563.05 |  | Network Operation Division
21:30 | 4732 | 4711.675 | 9443.675
22:00 | 4678 | 4646.3 | 9324.3
22:30 | 4527 | 4497.915 | 9024.915
23:00 | 4376 | 4349.53 | 8725.53

## En-Curve
QF-LDC-12
Date | 02-01-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2434 | 1291 | 892 | 0 | 74 | 827 | 46 | 3242 | 0 | 0 | 27 | 0 | 0 | 21 | 0 | DAILY ENERGY CURVE
00:30 | 2451.5 | 1258 | 809.5 | 0 | 70 | 830 | 46 | 2970.5 | 0 | 0 | 23 | 0 | 0 | 24.5 | 0 | 02-01-2026
01:00 | 2469 | 1225 | 727 | 0 | 66 | 833 | 46 | 2699 | 0 | 0 | 19 | 0 | 0 | 28 | 0
01:30 | 2377 | 1169.25 | 716 | 0 | 65 | 835.5 | 46 | 2654.5 | 0 | 0 | 9.5 | 0 | 0 | 25 | 0 | Energy Generated | 205.9233 |  | MKWHr
02:00 | 2285 | 1113.5 | 705 | 0 | 64 | 838 | 46 | 2610 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2289.5 | 1110 | 583.5 | 0 | 62 | 838.5 | 46 | 2605.5 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | Total Energy Requirement | 205.9233 |  | MKWHr
03:00 | 2294 | 1106.5 | 462 | 0 | 60 | 839 | 46 | 2601 | 0 | 0 | 0 | 0 | 0 | 28 | 0
03:30 | 2279 | 1167.5 | 350.5 | 0 | 60 | 838.5 | 46 | 2587 | 0 | 0 | 0 | 0 | 0 | 23.5 | 0
04:00 | 2264 | 1228.5 | 239 | 0 | 60 | 838 | 46 | 2573 | 0 | 0 | 0 | 0 | 0 | 19 | 0
04:30 | 2165.5 | 1201 | 239 | 0 | 59 | 837 | 46 | 2556.5 | 0 | 0 | 0 | 0 | 0 | 18 | 0
05:00 | 2067 | 1173.5 | 239 | 0 | 58 | 836 | 46 | 2540 | 0 | 0 | 0 | 0 | 0 | 17 | 0
05:30 | 2176 | 1188.5 | 239 | 0 | 59 | 836.5 | 46 | 2552 | 0 | 0 | 0 | 0 | 0 | 11.5 | 0
06:00 | 2285 | 1203.5 | 239 | 0 | 60 | 837 | 46 | 2564 | 0 | 0 | 0 | 0 | 0 | 6 | 0
06:30 | 2266.5 | 1207.5 | 294.5 | 0 | 58 | 835 | 46 | 2562.5 | 2.105 | 0 | 0 | 0 | 0 | 7 | 0
07:00 | 2248 | 1211.5 | 350 | 0 | 56 | 833 | 46 | 2561 | 4.21 | 0 | 0 | 0 | 0 | 8 | 0
07:30 | 2333.5 | 1251.5 | 527.5 | 0 | 59 | 833.5 | 46 | 2564.5 | 32.915 | 0 | 4 | 0 | 0 | 5 | 0
08:00 | 2419 | 1291.5 | 705 | 0 | 62 | 834 | 46 | 2568 | 61.62 | 0 | 8 | 0 | 0 | 2 | 0
08:30 | 2443.5 | 1383 | 751.5 | 0 | 72 | 834.5 | 46 | 2638.5 | 115.63 | 0 | 13.5 | 0 | 0 | 2 | 0
09:00 | 2468 | 1474.5 | 798 | 0 | 82 | 835 | 46 | 2709 | 169.64 | 0 | 19 | 0 | 0 | 2 | 0
09:30 | 2465.5 | 1478.5 | 798 | 0 | 84 | 836.5 | 46 | 2766 | 204.38 | 0 | 19 | 0 | 0 | 1 | 0
10:00 | 2463 | 1482.5 | 798 | 0 | 86 | 838 | 46 | 2823 | 239.12 | 0 | 19 | 0 | 0 | 0 | 0
10:30 | 2456.5 | 1507.5 | 798 | 0 | 92 | 841.5 | 46 | 2803 | 302.095 | 0 | 19 | 0 | 0 | 2 | 0
11:00 | 2450 | 1532.5 | 798 | 0 | 98 | 845 | 46 | 2783 | 365.07 | 0 | 19 | 0 | 0 | 4 | 0
11:30 | 2469.5 | 1565 | 798 | 0 | 104 | 911 | 46 | 2955.5 | 420.675 | 0 | 31 | 0 | 0 | 2 | 0
12:00 | 2489 | 1597.5 | 798 | 0 | 110 | 977 | 46 | 3128 | 476.28 | 0 | 43 | 0 | 0 | 0 | 0
12:30 | 2499.5 | 1637 | 845 | 0 | 115 | 1084 | 46 | 3418.5 | 474.96 | 0 | 59 | 0 | 0 | 0 | 0
13:00 | 2510 | 1676.5 | 892 | 0 | 120 | 1191 | 46 | 3709 | 473.64 | 0 | 75 | 0 | 0 | 0 | 0
13:30 | 2388 | 1505.5 | 892 | 0 | 106 | 1082 | 46 | 3425.5 | 422.73 | 0 | 75 | 0 | 0 | 0 | 0
14:00 | 2266 | 1334.5 | 892 | 0 | 92 | 973 | 46 | 3142 | 371.82 | 0 | 75 | 0 | 0 | 0 | 0
14:30 | 2179.5 | 1229.75 | 798 | 0 | 91 | 900.595 | 46 | 2917.5 | 320.095 | 0 | 45.5 | 0 | 0 | 3.5 | 0
15:00 | 2093 | 1125 | 704 | 0 | 90 | 828.19 | 46 | 2693 | 268.37 | 0 | 16 | 0 | 0 | 7 | 0
15:30 | 2147.5 | 1095 | 704 | 0 | 86 | 834.795 | 39 | 2632.5 | 198.005 | 0 | 12 | 0 | 0 | 7 | 0
16:00 | 2202 | 1065 | 704 | 0 | 82 | 841.4 | 32 | 2572 | 127.64 | 0 | 8 | 0 | 0 | 7 | 0
16:30 | 2261.5 | 1105 | 704 | 0 | 80 | 898.72 | 32 | 2640 | 72.655 | 8.5 | 13.5 | 0 | 0 | 5.5 | 0
17:00 | 2321 | 1145 | 704 | 0 | 78 | 956.04 | 32 | 2708 | 17.67 | 17 | 19 | 0 | 0 | 4 | 0
17:30 | 2454.5 | 1314 | 798 | 0 | 89 | 993.695 | 39 | 2975.5 | 8.835 | 17 | 40.5 | 0 | 0 | 6 | 0
18:00 | 2588 | 1483 | 892 | 0 | 100 | 1031.35 | 46 | 3243 | 0 | 17 | 62 | 0 | 0 | 8 | 0
18:30 | 2575.5 | 1482 | 892 | 0 | 95 | 981.72 | 46 | 3366 | 0 | 8.5 | 58 | 0 | 0 | 11 | 0
19:00 | 2563 | 1481 | 892 | 0 | 90 | 932.09 | 46 | 3489 | 0 | 0 | 54 | 0 | 0 | 14 | 0
19:30 | 2623 | 1413 | 892 | 0 | 96 | 909.58 | 46 | 3489 | 0 | 0 | 54 | 0 | 0 | 11 | 0
20:00 | 2620 | 1418 | 892 | 0 | 96 | 924.14 | 46 | 3542 | 0 | 0 | 54 | 0 | 0 | 13 | 0
20:30 | 2565.5 | 1437.5 | 892 | 0 | 96 | 926.095 | 46 | 3568.5 | 0 | 0 | 40.5 | 0 | 0 | 12 | 0
21:00 | 2511 | 1457 | 892 | 0 | 96 | 928.05 | 46 | 3595 | 0 | 0 | 27 | 0 | 0 | 11 | 0
21:30 | 2494.5 | 1454.5 | 892 | 0 | 97 | 891.675 | 46 | 3528 | 0 | 0 | 27 | 0 | 0 | 13 | 0
22:00 | 2478 | 1452 | 892 | 0 | 98 | 855.3 | 46 | 3461 | 0 | 0 | 27 | 0 | 0 | 15 | 0
22:30 | 2419.5 | 1418.5 | 892 | 0 | 90 | 846.915 | 46 | 3274.5 | 0 | 0 | 23 | 0 | 0 | 14.5 | 0
23:00 | 2361 | 1385 | 892 | 0 | 82 | 838.53 | 46 | 3088 | 0 | 0 | 19 | 0 | 0 | 14 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 02-01-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 421 | 03:00 | 400 | 12:00 | Meghnaghat | 429 | 03:00 | 412 | 13:00
Ashuganj | 414 | 3:00 | 400 | 12:00 | Payra | 424 | 04:00 | 416 | 13:00
Bhulta | 407 | 04:00 | 392 | 12:00 | Rahanpur | 421 | 04:00 | 406 | 13:00
Bibiana | 420 | 05:00 | 408 | 12:00 | Rampal | 418 | 04:00 | 399 | 13:00
BIPTC | 409 | 03:00 | 393 | 13:00
Bogura | 418 | 04:00 | 396 | 13:00
Gopalganj | 422 | 04:00 | 404 | 13:00
Kaliakoir | 418 | 03:00 | 400 | 12:00
Korerhat | 423 | 03:00 | 408 | 13:00
Madunaghat | 416 | 04:00 | 406 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 246 | 04:00 | 233 | 12:00 | Kachua | 242 | 03:00 | 230 | 13:00
AKSML | 243.1 | 06:00 | 234.2 | 13:00 | Kaliakoir | 245 | 03:00 | 233 | 12:00
Aminbazar | 246 | 04:00 | 231 | 12:00 | Keranigonj | 244 | 03:00 | 231 | 13:00
Ashuganj | 240 | 04:00 | 231 | 12:00 | Khulna(S) | 246 | 04:00 | 231 | 13:00
Ashuganj-400 | 240 | 04:00 | 231 | 12:00 | Korerhat | 246 | 04:00 | 236 | 13:00
Baghabari | 241 | 05:00 | 232 | 18:00 | Madunaghat | 240 | 03:00 | 234 | 13:00
Barapukuria | 233 | 06:00 | 216 | 18:00 | Madunaghat-400 | 241 | 03:00 | 234 | 13:00
Barapukuria-230 | 233 | 06:00 | 216 | 18:00 | Maniknagar | 244 | 05:00 | 233 | 13:00
Barishal | 239 | 03:00 | 231 | 13:00 | Meghnaghat | 246 | 03:00 | 240 | 12:00
Bheramara | 241 | 04:00 | 223 | 18:00 | Meghnaghat-400 | 244 | 04:00 | 234 | 12:00
Bhulta | 245 | 03:00 | 235 | 12:00 | Mirsorai | 246 | 04:00 | 235 | 13:00
Bibiana | 248 | 03:00 | 239 | 12:00 | Rajshahi | 242 | 05:00 | 222 | 18:00
BIPTC | 241 | 05:00 | 223 | 18:00 | Rampal | 243 | 04:00 | 228 | 13:00
Bogura | 244 | 04:00 | 232 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 245 | 05:00 | 230 | 13:00 | Rampura | 244 | 05:00 | 235 | 12:00
Borhanuddin | 242 | 02:00 | 236 | 11:00 | Shikalbaha | 238 | 01:00 | 233 | 11:00
BSRM | 244 | 03:00 | 235 | 13:00 | Shyampur | 243 | 03:00 | 231 | 13:00
Cumilla(N) | 242 | 04:00 | 234 | 12:00 | Siddhirganj | 245 | 04:00 | 235 | 12:00
Faridpur | 240 | 02:00 | 229 | 13:00 | Sirajgonj | 247 | 04:00 | 239 | 13:00
Fenchuganj | 246 | 03:00 | 239 | 13:00 | Sreepur | 238 | 03:00 | 229 | 13:00
Feni | 244 | 03:00 | 234 | 13:00 | Tongi | 241 | 04:00 | 230 | 12:00
Ghorashal | 243 | 03:00 | 240 | 00:00
Ghorashal-230 | 237 | 04:00 | 219 | 13:00
Gopalganj | 238 | 05:00 | 227 | 13:00
GPH | 242 | 03:00 | 234 | 13:00
Haripur | 244 | 03:00 | 234 | 13:00
Hasnabad | 244 | 02:00 | 231 | 15:00
Hathazari | 238 | 03:00 | 234 | 13:00
Ishurdi | 242 | 04:00 | 226 | 18:00
Jhenaidah | 243 | 05:00 | 224 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 04:00 | 129 | 12:00 | Laksam | 143 | 03:00 | 135 | 13:00 | UttaraNew | 139 | 02:00 | 133 | 11:00
Agargaon | 140 | 03:00 | 131 | 13:00 | Lakshmipur | 138 | 03:00 | 132 | 13:00 | Zigatola | 138 | 04:00 | 130 | 13:00
Agrabad | 140 | 03:00 | 134 | 13:00 | Lalbag | 137 | 23:00 | 130 | 13:00
AKS | 137 | 01:00 | 134 | 12:00 | Lalmonirhat | 132 | 00:00 | 121 | 18:00
Aminbazar | 140 | 03:00 | 130 | 01:00 | Madanganj | 140 | 06:00 | 134 | 00:00
Amnura | 139 | 01:00 | 131 | 12:00 | Madaripur | 143 | 04:00 | 136 | 13:00
Ashuganj | 144 | 04:00 | 138 | 12:00 | Madartek | 134 | 04:00 | 128 | 12:00
Bagerhat | 136 | 06:00 | 127 | 13:00 | Madunaghat | 140 | 00:00 | 136 | 13:00
Bajitpur | 138 | 03:00 | 132 | 13:00 | Magura | 140 | 04:00 | 125 | 13:00
Bakerganj | 138.3 | 16:00 | 136 | 07:00 | Mahasthangarh | 138 | 03:00 | 129 | 18:00
Bakulia | 139 | 04:00 | 136 | 12:00 | Maijdee | 138 | 03:00 | 132 | 13:00
Banani | 135 | 03:00 | 128 | 12:00 | Manikganj | 136 | 06:00 | 130 | 13:00
Bangabhaban | 142 | 06:00 | 135 | 12:00 | Maniknagar | 142 | 05:00 | 135 | 12:00
Barapukuria | 140 | 06:00 | 129 | 18:00 | Matarbari | 131 | 03:00 | 120 | 16:00
Barguna | 139 | 06:00 | 136 | 13:00 | Matuail | 141 | 05:00 | 135.6 | 12:00
Barishal | 141 | 04:00 | 134 | 13:00 | Metrorail_Motijheel | 142 | 05:00 | 135 | 12:00
Barishal-230 | 141 | 04:00 | 133 | 13:00 | Metrorail_Uttara | 140 | 04:00 | 133 | 11:00
Baroaulia | 140 | 04:00 | 135 | 13:00 | Millgate | 139 | 02:00 | 130 | 12:00
Baroirhat | 140 | 04:00 | 134 | 13:00 | Mirpur | 139 | 05:00 | 130 | 13:00
Bashundhara | 135 | 03:00 | 128 | 13:00 | Mirzapur | 138 | 05:00 | 130 | 12:00
BashundharaCement | 139 | 04:00 | 134 | 00:00 | Mithapukur | 137 | 04:00 | 126 | 09:00
Beanibazar | 138 | 03:00 | 134 | 13:00 | MI_Cement | 138 | 04:00 | 130 | 12:00
Benapole | 137 | 03:00 | 117 | 13:00 | Modern | N/A | N/A | N/A | N/A
Bhaluka | 136 | 04:00 | 129 | 13:00 | Mogbazar | 139 | 04:00 | 130 | 12:00
Bhandaria | 140 | 03:00 | 133 | 13:00 | Mongla | 137 | 06:00 | 127 | 13:00
Bhangura | 140 | 05:00 | 134 | 08:00 | Motijheel | 142 | 06:00 | 135 | 12:00
Bheramara | 141 | 05:00 | 130 | 18:00 | Muktagacha | 136 | 06:00 | 129 | 09:00
Bheramara(GK) | 140 | 04:00 | 129 | 18:00 | Munshiganj | 140 | 06:00 | 134 | 12:00
Bhulta | 132 | 03:00 | 128 | 12:00 | Muradnagar | 141 | 02:00 | 133 | 12:00
Bog-Sherpur | 140 | 04:00 | 132 | 18:00 | Mymensingh | 136 | 15:00 | 127 | 09:00
Bogura | 139 | 05:00 | 132 | 18:00 | Naogaon | 136 | 05:00 | 126 | 13:00
Bogura-230 | 139 | 03:00 | 132 | 13:00 | Narail | 139 | 03:00 | 127 | 18:00
Brahmanbaria | 137 | 04:00 | 133 | 09:00 | Narinda | 142 | 05:00 | 135 | 12:00
Cantonment | 139 | 02:00 | 131 | 12:00 | Narshingdi | 139 | 06:00 | 131 | 19:30
Chandina | 143 | 03:00 | 136 | 13:00 | Natore | 139 | 05:00 | 129 | 13:00
Chandpur | 142 | 03:00 | 135 | 13:00 | Nawabganj | 138 | 03:00 | 130 | 13:00
Chandraghona | 141 | 04:00 | 136 | 13:00 | Netrakona | 131 | 15:00 | 123 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 139 | 01:00 | 134 | 13:00 | New | 140 | 03:00 | 132 | 12:00
Charsaidpur | 140 | 03:00 | 134 | 13:00 | Niamatpur | 140 | 06:00 | 135 | 12:00
Chauddagram | 141 | 03:00 | 135 | 12:00 | Noapara | 137 | 04:00 | 119 | 13:00
Chhatak | 136 | 00:00 | 132 | 13:00 | Pabna | 140 | 04:00 | 131 | 18:00
Chowmuhani | 138 | 05:00 | 132 | 13:00 | Palashbari | 135 | 05:00 | 126 | 18:30
Chuadanga | 139 | 06:00 | 124 | 13:00 | Panchagarh | 139 | 03:00 | 127 | 18:00
Coxsbazar | 131 | 02:00 | 124 | 13:00 | Patiya | 140 | 03:00 | 134 | 13:00
Cumilla(N) | 143 | 06:00 | 137 | 12:00 | Patuakhali | 138 | 03:00 | 134 | 18:00
Cumilla(S) | 143 | 03:00 | 127 | 09:00 | Payra | 139 | 01:00 | 137 | 13:00
Daganbhuiyan | 139 | 05:00 | 135 | 13:00 | PHP | 139 | 03:00 | 133 | 13:00
Daudkandi | 139 | 03:00 | 132 | 13:00 | Postogola | 139 | 05:00 | 131 | 13:00
DhakaUniversity | 134 | 01:00 | 128 | 12:00 | Purbachal | 136 | 03:00 | 127 | 12:00
Dhamrai | 140 | 06:00 | 135 | 10:00 | Purbasadipur | 135 | 04:00 | 121 | 12:00
Dhanmondi | 142 | 05:00 | 136 | 12:00 | Rahanpur | 141 | 04:00 | 136 | 13:00
Dohazari | 137 | 05:00 | 131 | 13:00 | Rahanpur-400 | 142 | 04:00 | 136 | 13:00
Faridpur | 138 | 03:00 | 133 | 13:00 | Rahim | 140 | 03:00 | 136 | 12:00
Fatullah | 141 | 04:00 | 130 | 12:00 | Rajbari | 139 | 03:00 | 132 | 13:00
Fenchuganj | 142 | 03:00 | 138 | 13:00 | Rajendrapur | 136 | 04:00 | 132 | 09:00
Feni | 138 | 04:00 | 132 | 13:00 | Rajshahi | 139 | 03:00 | 130 | 18:00
Feni-230 | 139 | 02:00 | 133 | 13:00 | Rajshahi-230 | 139 | 04:00 | 128 | 13:00
Ghatail | 135 | 06:00 | 127 | 13:00 | Ramganj | 139 | 01:00 | 134 | 12:00
Ghorashal | 138 | 02:00 | 131 | 13:00 | Rampur | 140 | 02:00 | 134 | 13:00
Goalpara | 139 | 03:00 | 130 | 13:00 | Rampura | 135 | 03:00 | 128 | 12:00
Gollamari | 139 | 04:00 | 131 | 12:00 | Rangamati | 140 | 06:00 | 130 | 07:00
Gopalganj | 141 | 04:00 | 133 | 13:00 | Rangpur | 135 | 01:00 | 126 | 12:00
Gopalganj-400 | 143 | 03:00 | 137 | 13:00 | Ruppur | 140 | 04:00 | 131 | 18:00
Gulshan | 134 | 04:00 | 128 | 12:00 | Saidpur | 136 | 04:00 | 124 | 09:00
Halishahar | 141 | 03:00 | 135 | 13:00 | Satkhira | 137 | 03:00 | 126 | 13:00
Haripur | 140 | 03:00 | 135 | 12:00 | Satmasjid | 139 | 03:00 | 130 | 13:00
HaripurSBU | 140 | 04:00 | 135 | 13:00 | Savar | 138 | 05:00 | 129 | 12:00
Hasnabad | 138 | 03:00 | 129 | 12:00 | SevenRings | 138 | 03:00 | 131 | 13:00
Hathazari | 140 | 03:00 | 136 | 12:00 | ShahCement | 140 | 03:00 | 134 | 13:00
Hatirjheel | 135 | 03:00 | 128 | 13:00 | Shahjadpur | 140 | 00:00 | 136 | 18:30
Ishurdi | 142 | 04:00 | 132 | 18:00 | Shahjibazar | 137 | 04:00 | 134 | 12:00
Jaldhaka | 134 | 05:00 | 121 | 09:00 | Shahmirpur | 140 | 05:00 | 135 | 13:00
Jamalpur | 135 | 14:00 | 124 | 09:00 | Shariatpur | 142 | 04:00 | 135 | 13:00
Jashore | 138 | 05:00 | 120 | 13:00 | Sherpur | 131 | 14:00 | 120 | 09:00
Jhenaidah | 138 | 02:00 | 114 | 13:00 | Shikalbaha | 130 | 03:00 | 124 | 13:00
Jhenaidah-230 | 141 | 04:00 | 127 | 13:00 | Shikalbaha-230 | 141 | 01:00 | 137 | 11:00
Joydebpur | 137 | 05:00 | 128 | 10:00 | Shitalakhya | 138 | 04:00 | 130 | 12:00
Joypurhat | 136 | 04:00 | 128 | 13:00 | Sholosohor | 140 | 03:00 | 136 | 12:00
Juldah | 139 | 00:00 | 135 | 13:00 | Shyampur | 138 | 06:00 | 132 | 13:00
Kabirpur | 138 | 05:00 | 129 | 12:00 | Shyampur-230 | 141 | 03:00 | 134 | 12:00
Kachua | 143 | 03:00 | 136 | 13:00 | Siddhirganj | 141 | 06:00 | 136 | 12:00
Kaliakoir | 142 | 04:00 | 134 | 12:00 | Sirajganj | 138 | 01:00 | 131 | 18:00
Kallyanpur | 140 | 06:00 | 132 | 12:00 | Sonargaon | 140 | 03:00 | 134 | 12:00
Kalurghat | 140 | 15:00 | 135 | 13:00 | Sreemongol | 138 | 02:00 | 134 | 13:00
Kamrangirchar | 138 | 05:00 | 130 | 12:00 | Sreepur | 139 | 03:00 | 134 | 09:00
Kaptai | 142 | 3:00 | 137 | 13:00 | Srinagar | 138 | 04:00 | 128 | 13:00
Kasba | 141 | 03:00 | 133 | 13:00 | SSM | 142 | 00:00 | 140 | 10:00
Kazla | 140 | 03:00 | 134 | 13:00 | Sunamganj | 135 | 01:00 | 132 | 12:00
Keranigonj | 138 | 03:00 | 130 | 13:00 | Sylhet | 138 | 03:00 | 134 | 13:00
Khagrachori | 140 | 03:00 | 134 | 13:00 | Sylhet-132 | 137 | 01:00 | 135 | 12:00
Khulna | 136 | 06:00 | 128 | 13:00 | Tangail | 135 | 05:00 | 127 | 12:00
Khulna(S) | 138 | 03:00 | 129 | 13:00 | Taraganj | 134 | 05:00 | 124 | 12:00
Khulshi | 138 | 03:00 | 133 | 13:00 | Tasnim | 140 | 04:00 | 134 | 12:00
Kishoreganj | 136 | 05:00 | 130 | 12:00 | Thakurgaon | 137 | 03:00 | 124 | 18:00
Kodda | 136 | 05:00 | 129 | 12:00 | TK | 140 | 06:00 | 136 | 13:00
KSRM | 140 | 06:00 | 134 | 18:30 | Tongi | 141 | 04:00 | 132 | 12:00
Kulaura | 141 | 01:00 | 138 | 12:00 | Ullahpara | 140 | 03:00 | 132 | 18:00
Kurigram | 131 | 14:00 | 122 | 18:00 | Ullon | 136 | 04:00 | 128 | 12:00
Kushtia | 136 | 06:00 | 123 | 18:00 | Uttara | 139 | 03:00 | 132 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division