## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 03-01-2026 | [28 empty] | Date: | 03-01-2026 | [28 empty] | Date: | 03-01-2026 | [28 empty] | Date: | 03-01-2026 | [28 empty] | Date: | 03-01-2026 | [17 empty] | Date: | 03-01-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 31 | 455 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 720 | 0 | 0 | 8 | 320 | 300 | 0 | 5 | 27 | 0 | 38 | 0 | 112 | 0 | 0 | 11 | 0 | 76 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 50 | 89 | 0 | 17 | 0 | 5 | 20 | 0 | 0 | 159 | 0 | 19 | 0 | 168 | 0 | 0 | 0 | 4160 | 798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 778 | 0 | 0 | 0 | 832.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 140 | 220 | 0 | 257 | 310 | 0 | 4050.56 | 8210.56 | 97.52
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 455 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 609 | 0 | 0 | 0 | 330 | 300 | 0 | 0 | 5 | 0 | 10 | 0 | 50 | 0 | 0 | 10 | 0 | 76 | 0 | 0 | 0 | 315 | 0 | 0 | 34 | 30 | 88 | 0 | 0 | 0 | 5 | 20 | 0 | 0 | 159 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 3841 | 718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 776 | 0 | 0 | 0 | 840.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 256 | 250 | 0 | 3812.55 | 7653.55 | 97.51
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 455 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 610 | 0 | 0 | 0 | 220 | 280 | 0 | 0 | 5 | 0 | 10 | 0 | 50 | 0 | 0 | 10 | 0 | 76 | 0 | 0 | 0 | 305 | 0 | 0 | 34 | 30 | 85 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 159 | 0 | 0 | 0 | 116 | 0 | 0 | 0 | 3552 | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 775 | 0 | 0 | 0 | 840.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 251 | 250 | 0 | 3730.82 | 7282.82 | 97.51
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 455 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 610 | 0 | 0 | 0 | 220 | 280 | 0 | 0 | 5 | 0 | 10 | 0 | 50 | 0 | 0 | 10 | 0 | 70 | 0 | 0 | 0 | 315 | 0 | 0 | 34 | 30 | 86 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 159 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 3583 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 0 | 0 | 0 | 831.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 261 | 250 | 0 | 3362.32 | 6945.32 | 97.5
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 455 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 610 | 0 | 0 | 0 | 220 | 280 | 0 | 0 | 5 | 0 | 10 | 0 | 50 | 0 | 0 | 10 | 0 | 72 | 0 | 0 | 0 | 310 | 0 | 0 | 34 | 30 | 80 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 158 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 3584 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 766 | 0 | 0 | 0 | 830.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 257 | 250 | 0 | 3143.05 | 6727.05 | 97.5
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 455 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 610 | 0 | 0 | 0 | 220 | 280 | 0 | 0 | 5 | 0 | 10 | 0 | 50 | 0 | 0 | 10 | 0 | 70 | 0 | 0 | 0 | 300 | 0 | 0 | 34 | 30 | 72 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 158 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 3544 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 765 | 0 | 0 | 0 | 834.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 253 | 250 | 0 | 3142.32 | 6686.32 | 97.5
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 455 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 609 | 0 | 0 | 0 | 315 | 330 | 0 | 0 | 9 | 0 | 38 | 0 | 50 | 0 | 0 | 10 | 0 | 78 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 50 | 21 | 0 | 0 | 0 | 76 | 30 | 0 | 0 | 159 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 3844 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 768 | 0 | 0 | 0 | 831.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 100 | 180 | 0 | 258 | 275 | 0 | 3349.38 | 7193.38 | 97.5
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0.07 | 46 | 0 | 0 | 455 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 610 | 1 | 0 | 0 | 310 | 405 | 0 | 0 | 41 | 0 | 24 | 0 | 50 | 0 | 0 | 10 | 0 | 72 | 0 | 1 | 0 | 310 | 0 | 0 | 41 | 50 | 15 | 0 | 17 | 0 | 74 | 30 | 0 | 0 | 159 | 0 | 0 | 0 | 163 | 0 | 0.04 | 0 | 3942.11 | 493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.43 | 766 | 0 | 0 | 0 | 830.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55 | 0 | 0 | 0 | 0.47 | 164 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 172 | 100 | 180 | 0 | 249 | 275 | 0 | 3579.57 | 7521.68 | 97.49
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0.57 | 46 | 0 | 20 | 455 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 629 | 7 | 0 | 25 | 340 | 396 | 0 | 18 | 48 | 0 | 30 | 0 | 115 | 0 | 0 | 10 | 0 | 84 | 0 | 5 | 0 | 325 | 0 | 0 | 41 | 50 | 17 | 2 | 17 | 0 | 75 | 30 | 0 | 0 | 159 | 6 | 10 | 22 | 162 | 0 | 1.44 | 0 | 4235.01 | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 784 | 0 | 0 | 0 | 849.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.65 | 14 | 0 | 0 | 7.13 | 170 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.42 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.6 | 22 | 0.05 | 0 | 181 | 140 | 220 | 0 | 258 | 280 | 0 | 4066.5 | 8301.51 | 97.49
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 10 | 28 | 31.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 1.72 | 46 | 0 | 16 | 500 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 730 | 0 | 0 | 60 | 300 | 396 | 0 | 44 | 49 | 0 | 33 | 0 | 114 | 0 | 0 | 10 | 0 | 68 | 0 | 11 | 0 | 305 | 0 | 0 | 41 | 50 | 16 | 5 | 17 | 0 | 78 | 30 | 0 | 0 | 158 | 17 | 19 | 56 | 163 | 0 | 2.21 | 1 | 4621.43 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 802 | 0 | 0 | 0 | 864.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.29 | 31 | 0 | 0 | 9.1 | 173 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 25 | 0.14 | 0 | 220 | 140 | 180 | 0 | 304 | 315 | 0 | 4391.96 | 9013.39 | 97.49
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 15 | 52 | 31.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 2.48 | 46 | 0 | 18 | 500 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 725 | 16 | 0 | 63 | 295 | 399 | 0 | 44 | 49 | 0 | 35 | 0 | 114 | 0 | 0 | 10 | 0 | 82 | 0 | 14 | 0 | 305 | 0 | 0 | 41 | 50 | 16 | 7 | 17 | 0 | 78 | 30 | 0 | 0 | 158 | 17 | 19 | 56 | 166 | 1 | 4.41 | 12 | 4619.39 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 790 | 0 | 0 | 0 | 835.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.47 | 54 | 0 | 0 | 15.45 | 151 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 47 | 0.31 | 0 | 177 | 140 | 180 | 0 | 264 | 300 | 0 | 4312.71 | 8932.1 | 97.48
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 19 | 35 | 31.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 2.95 | 46 | 0 | 17 | 500 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 718 | 19 | 0 | 63 | 300 | 405 | 0 | 44 | 48 | 0 | 36 | 0 | 112 | 0 | 0 | 10 | 0 | 84 | 0 | 19 | 0 | 300 | 0 | 0 | 41 | 50 | 16 | 5 | 17 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 19 | 58 | 166 | 0 | 6.84 | 12 | 4578.29 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 771 | 0 | 0 | 0 | 836.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.43 | 80 | 0 | 0 | 19.15 | 148 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 1.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7 | 87 | 0.39 | 0 | 179 | 100 | 180 | 0 | 260 | 290 | 0 | 4286.67 | 8864.96 | 97.48
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 21 | 35 | 31.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 3.03 | 46 | 0 | 20 | 520 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 902 | 19 | 0 | 88 | 345 | 394 | 0 | 44 | 46 | 0 | 29 | 0 | 110 | 0 | 0 | 10 | 0 | 90 | 0 | 19 | 0 | 315 | 0 | 0 | 41 | 50 | 17 | 6 | 17 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 19 | 58 | 164 | 1 | 6.48 | 12 | 4949.01 | 893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 821 | 0 | 0 | 0 | 925.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.23 | 83 | 0 | 0 | 36.99 | 162 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 4.9 | 102 | 0.43 | 0 | 182 | 100 | 180 | 0 | 250 | 300 | 0 | 4573.75 | 9522.76 | 97.48
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 13 | 30 | 0 | 225 | 0 | 470 | 0 | 17 | 0 | 0 | 0 | 20 | 52 | 31.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 12 | 2.75 | 46 | 0 | 23 | 520 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1033 | 18 | 0 | 140 | 320 | 393 | 0 | 44 | 46 | 0 | 34 | 0 | 110 | 4 | 0 | 11 | 0 | 84 | 0 | 42 | 0 | 315 | 0 | 0 | 41 | 50 | 15 | 6 | 17 | 0 | 78 | 30 | 0 | 0 | 159 | 17 | 19 | 58 | 164 | 1 | 5.66 | 12 | 5277.91 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.08 | 812 | 0 | 0 | 0 | 1057.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.16 | 84 | 0 | 0 | 37.98 | 184 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 3.39 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 4.8 | 109 | 0.41 | 0 | 177 | 140 | 220 | 0 | 260 | 300 | 0 | 4741.18 | 10019.09 | 97.48
14:00 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 32.9 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 225 | 0 | 430 | 0 | 17 | 0 | 0 | 0 | 18 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 12 | 2.26 | 46 | 0 | 18 | 520 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 966 | 14 | 0 | 145 | 325 | 393 | 0 | 44 | 46 | 0 | 35 | 0 | 110 | 0 | 0 | 11 | 0 | 90 | 0 | 39 | 0 | 305 | 0 | 0 | 41 | 50 | 15 | 9 | 17 | 0 | 78 | 30 | 0 | 0 | 159 | 17 | 19 | 58 | 164 | 1 | 10.33 | 12 | 5117.49 | 893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 794 | 0 | 0 | 0 | 953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.43 | 68 | 0 | 0 | 29.91 | 176 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 2.79 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 3.9 | 88 | 0.33 | 0 | 178 | 140 | 220 | 0 | 258 | 295 | 0 | 4535.36 | 9652.85 | 97.48
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 32.9 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 160 | 0 | 360 | 0 | 17 | 0 | 0 | 0 | 13 | 35 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 1.51 | 46 | 0 | 20 | 520 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 825 | 9 | 0 | 145 | 295 | 392 | 0 | 10 | 49 | 0 | 36 | 0 | 109 | 0 | 0 | 5 | 0 | 80 | 0 | 27 | 0 | 305 | 0 | 0 | 41 | 50 | 38 | 5 | 17 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 19 | 58 | 164 | 1 | 7.06 | 12 | 4735.47 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.78 | 787 | 0 | 0 | 0 | 850 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.22 | 47 | 0 | 0 | 16.61 | 166 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 1.72 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 2.4 | 62 | 0.22 | 0 | 179 | 100 | 180 | 0 | 260 | 295 | 0 | 4248.95 | 8984.42 | 97.47
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 33.1 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 160 | 0 | 300 | 0 | 17 | 0 | 0 | 0 | 7 | 17 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0.62 | 46 | 0 | 20 | 520 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 855 | 4 | 0 | 88 | 330 | 385 | 0 | 10 | 47 | 0 | 36 | 0 | 108 | 0 | 0 | 11 | 0 | 106 | 0 | 12 | 0 | 310 | 0 | 0 | 41 | 50 | 60 | 2 | 17 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 19 | 58 | 164 | 0 | 7.16 | 6 | 4686.88 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.07 | 780 | 0 | 0 | 0 | 844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.32 | 20 | 0 | 0 | 8.19 | 169 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0.7 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 32 | 0.1 | 0 | 182 | 100 | 180 | 0 | 263 | 300 | 0 | 4178.38 | 8865.26 | 97.47
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 34.9 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 160 | 0 | 345 | 0 | 17 | 0 | 0 | 0 | 1 | 17 | 30 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0.06 | 46 | 0 | 25 | 520 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1000 | 1 | 0 | 90 | 330 | 386 | 0 | 10 | 47 | 0 | 36 | 0 | 109 | 0 | 0 | 11 | 0 | 102 | 0 | 1 | 0 | 325 | 0 | 0 | 41 | 50 | 100 | 0 | 17 | 0 | 78 | 30 | 0 | 0 | 159 | 0 | 19 | 35 | 164 | 0 | 0.72 | 6 | 4908.68 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 860 | 0 | 0 | 0 | 987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.44 | 3 | 0 | 0 | 1.19 | 177 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.13 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.2 | 4 | 0 | 0 | 184 | 100 | 220 | 0 | 260 | 300 | 0 | 4408.26 | 9316.94 | 97.47
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 34.9 | 0 | 2 | 0 | 0 | 0 | 17 | 52 | 0 | 225 | 0 | 440 | 0 | 17 | 0 | 0 | 0 | 0 | 90 | 30 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 22 | 0 | 46 | 0 | 28 | 520 | 0 | 0 | 0 | 0 | 15 | 173 | 0 | 0 | 0 | 1160 | 0 | 0 | 90 | 325 | 392 | 0 | 20 | 49 | 0 | 36 | 0 | 110 | 21 | 0 | 11 | 0 | 114 | 0 | 0 | 0 | 320 | 0 | 0 | 41 | 50 | 141 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 159 | 0 | 19 | 55 | 164 | 0 | 0 | 6 | 5497.9 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 0 | 0 | 0 | 1270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 140 | 220 | 0 | 337 | 345 | 0 | 5129 | 10626.9 | 97.47
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 225 | 0 | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 26.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 31 | 520 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1150 | 0 | 0 | 26 | 393 | 390 | 0 | 44 | 17 | 0 | 30 | 0 | 110 | 17 | 0 | 17 | 0 | 106 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 50 | 145 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 159 | 0 | 19 | 35 | 164 | 0 | 0 | 0 | 5331.5 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1102 | 0 | 0 | 0 | 1268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 140 | 220 | 0 | 443 | 460 | 0 | 5405 | 10736.5 | 97.46
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 225 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 26.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 31 | 520 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1155 | 0 | 0 | 26 | 365 | 387 | 0 | 44 | 49 | 0 | 36 | 0 | 110 | 0 | 0 | 15 | 0 | 106 | 0 | 0 | 0 | 320 | 0 | 0 | 41 | 50 | 162 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 159 | 0 | 19 | 35 | 165 | 0 | 0 | 0 | 5397.5 | 892 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1109 | 0 | 0 | 0 | 1172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 140 | 220 | 0 | 505 | 520 | 0 | 5409 | 10806.5
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 445 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 26.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 31 | 520 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1143 | 0 | 0 | 26 | 340 | 394 | 0 | 44 | 47 | 0 | 33 | 0 | 111 | 0 | 0 | 15 | 0 | 114 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 50 | 158 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 159 | 0 | 19 | 35 | 165 | 0 | 0 | 0 | 5306.5 | 891 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 0 | 0 | 0 | 1152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 140 | 220 | 0 | 481 | 537 | 0 | 5365 | 10671.5 | 97.46
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 26.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 34 | 520 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1155 | 0 | 0 | 26 | 320 | 395 | 0 | 44 | 49 | 0 | 33 | 0 | 112 | 0 | 0 | 15 | 0 | 114 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 50 | 157 | 0 | 17 | 0 | 78 | 30 | 0 | 0 | 159 | 0 | 19 | 35 | 166 | 0 | 0 | 0 | 5305.5 | 892 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1035 | 0 | 0 | 0 | 1016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 140 | 220 | 0 | 504 | 550 | 0 | 5195 | 10500.5 | 97.46
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 35 | 520 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1007 | 0 | 0 | 0 | 230 | 360 | 0 | 44 | 50 | 50 | 36 | 0 | 111 | 0 | 0 | 15 | 0 | 102 | 0 | 0 | 0 | 320 | 0 | 0 | 41 | 50 | 159 | 0 | 17 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 35 | 166 | 0 | 0 | 0 | 5008 | 892 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 894 | 0 | 0 | 0 | 926.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 140 | 220 | 0 | 400 | 555 | 0 | 4921.1 | 9929.1 | 97.46
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 37 | 520 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 956 | 0 | 0 | 0 | 230 | 360 | 0 | 44 | 50 | 60 | 33 | 0 | 111 | 0 | 0 | 15 | 0 | 104 | 0 | 0 | 0 | 305 | 0 | 0 | 41 | 50 | 148 | 0 | 17 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 16 | 166 | 0 | 0 | 0 | 4674 | 892 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 0 | 0 | 918.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 140 | 180 | 0 | 310 | 545 | 0 | 4605.83 | 9279.83 | 97.45
Total KWH | 0 | 0 | 9821 | 0 | 0 | 0 | 0 | 0 | 8146800 | 0 | 0 | 300960 | 0 | 15552 | 0 | 0 | 0 | 42040 | 197280 | 0 | 4883600 | 0 | 9356591 | 0 | 115376 | 0 | 0 | 0 | 128293 | 926400 | 516600 | 231120 | 0 | 0 | 0 | 0 | 0 | 0 | 408000 | 0 | 0 | 0 | 0 | 49920 | 17645 | 1100940 | 0 | 439200 | 12000000 | 0 | 0 | 0 | 0 | 50181 | 3998608 | 0 | 0 | 0 | 19936361 | 108675 | 0 | 1087273 | 7233100 | 9008300 | 0 | 639786 | 862080 | 140000 | 679464 | 0 | 2243413 | 94560 | 0 | 274330 | 0 | 2125440 | 0 | 190691 | 0 | 7573500 | 0 | 0 | 931000 | 708840 | 1838536.36 | 51527 | 315240 | 0 | 1390080 | 640320 | 0 | 0 | 4423870 | 164520 | 313200 | 748800 | 3637440 | 4900 | 56060 | 100560 | 110456793.36 | 18092363 | 190368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411120 | 20116365 | 0 | 0 | 0 | 22231243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235880 | 498550 | 0 | 0 | 181504 | 4045909 | 0 | 0 | 0 | 0 | 0 | 8703200 | 0 | 14340 | 0 | 0 | 59905 | 66828 | 0 | 0 | 0 | 0 | 24987.6 | 576000 | 2364 | 0 | 4865000 | 2913000 | 5004910 | 0 | 7381818 | 8616727.27 | 0 | 104232381.87 | 214689175.23

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 04-01-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-01-2026 | during | 04-01-2026 | during | 04-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 341 | 353 | 412 | 412 | 392 | 392 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 450 | 450 | 225 | 225 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 7 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 35 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 31.5 | 26.5 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 14 | 14 | 14 | 14 | 14 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 5 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 21 | 0 | 25 | 0 | 25 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 405 | 480 | 583 | 583 | 424.7 | 424.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 142 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1093.5 | 1245.5 | 5011.35 | 4986.35 | 2349.03 | 2324.03
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 | 46 | 46 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 167 | 173 | 150 | 150 | 150 | 150 | Plant availability less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 56 | 56 | 40 | 56 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 10 | 10 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 20 | 31 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.03 | 0 | 3.34 | 0 | 3.34 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 20 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 902 | 1155 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 12 | 9 | 8 | 20 | 8 | 20 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 520 | 520 | 770 | 830 | 770 | 830 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1689.03 | 1934 | 3562.2 | 3616.86 | 3063.84 | 3214.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 394 | 387 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 318.81 | 318.81 | 0 | 0 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 345 | 365 | 393 | 393 | 393 | 393 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 29 | 36 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 46 | 49 | 55 | 55 | 55 | 55 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 88 | 26 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 51 | 51 | Machine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 110 | 110 | 163 | 163 | 115 | 115 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 90 | 106 | 84 | 84 | 84 | 84 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 10 | 15 | 20.77 | 20.77 | 20.77 | 20.77 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 19 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1175 | 1138 | 2474.83 | 2424.83 | 2004.02 | 1954.02
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-01-2026 | during | 04-01-2026 | during | 04-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 164 | 165 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.5 | 0 | 1.5 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 35 | 60 | 60 | 60 | 60 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 19 | 20 | 20 | 20 | 20 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 6.48 | 0 | 15 | 0 | 15 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 0 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 277.48 | 219 | 330.5 | 314 | 320.5 | 304
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 41 | 41 | 41 | 41 | 41 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 50 | 50 | 50 | 50 | 50 | 50 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 17 | 162 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 78 | 81 | 81 | 81 | 81 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 160 | 159 | 158 | 158 | 158 | 158 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 320 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | under maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 714 | 861 | 889 | 889 | 839 | 839
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 893 | 892 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 15 | 410 | 410 | 350 | 350 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 68 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 821 | 1109 | 1148.28 | 1148.28 | 1108 | 1108 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1782 | 2016 | 3495.28 | 3420.28 | 2640.1 | 2565.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 250 | 505 | 622 | 622 | 622 | 622 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 100 | 140 | 136 | 136 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 300 | 520 | 605 | 605 | 575 | 575 | FGMO & #01 under maint.
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 182 | 279 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.43 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1012.43 | 1664 | 2151 | 2151 | 1968 | 1968
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 39.23 | 0 | 40 | 0 | 40 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 162 | 178 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 406 | 379 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0 | 0 | 5 | 0 | 5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 925.2 | 1172 | 1435.88 | 1435.88 | 1356 | 1356 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 36.99 | 0 | 40 | 0 | 40 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 83 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1652.42 | 1729 | 3103.87 | 2918.87 | 2491.21 | 2306.21
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.9 | 0 | 3.2 | 0 | 3.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 20 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 102 | 0 | 126.45 | 0 | 126.45 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 126.9 | 0 | 416.65 | 262 | 382.65 | 228
System Total |  |  |  |  | 28823.2 | 28382.248 | 9522.76 | 10806.5 | 21434.68 | 20983.19 | 16058.35 | 15702.86
Forecast Scenario (04-01-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8270 |  | 0 |  | 8270
|  |  |  | 1:00 | 7710 |  | 0 |  | 7710
|  |  |  | 2:00 | 7240 |  | 0 |  | 7240
|  |  |  | 3:00 | 6880 |  | 0 |  | 6880
|  |  |  | 4:00 | 6620 |  | 0 |  | 6620
|  |  |  | 5:00 | 6600 |  | 0 |  | 6600
|  |  |  | 6:00 | 6940 |  | 0 |  | 6940
|  |  |  | 7:00 | 7670 |  | 0 |  | 7670
|  |  |  | 8:00 | 8630 |  | 0 |  | 8630
|  |  |  | 9:00 | 9450 |  | 0 |  | 9450
|  |  |  | 10:00 | 9110 |  | 0 |  | 9110
|  |  |  | 11:00 | 9290 |  | 0 |  | 9290
|  |  |  | 12:00 | 9680 |  | 0 |  | 9680
|  |  |  | 13:00 | 10330 |  | 0 |  | 10330
|  |  |  | 14:00 | 10150 |  | 0 |  | 10150
|  |  |  | 15:00 | 9240 |  | 0 |  | 9240
|  |  |  | 16:00 | 8850 |  | 0 |  | 8850
|  |  |  | 17:00 | 9340 |  | 0 |  | 9340
|  |  |  | 18:00 | 10590 |  | 0 |  | 10590
|  |  |  | 18:30 | 10560 |  | 0 |  | 10560
|  |  |  | 19:00 | 10560 |  | 0 |  | 10560
|  |  |  | 19:30 | 10550 |  | 0 |  | 10550
|  |  |  | 20:00 | 10470 |  | 0 |  | 10470
|  |  |  | 21:00 | 10260 |  | 0 |  | 10260
|  |  |  | 22:00 | 9890 |  | 0 |  | 9890
|  |  |  | 23:00 | 9300 |  | 0 |  | 9300
Probable Maximum Temperature: |  |  | 23.60°C
Probable Maximum Demand at Day Peak: |  |  | 9680.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 10590.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10590.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 213.07 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:43 hrs on 04-01-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 03-01-2026
Power Supply Scenario
| Day Peak Generation |  |  | 9522.76 | MW | 12:00 Hr. | Energy Generated |  |  | 214.6892 |  | MKWHr.
| Day Peak Demand |  |  | 9522.76 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 10806.5 | MW | 19:30 Hr. | Energy Demand |  |  | 214.6892 |  | MKWHr.
| Evening Peak Demand |  |  | 10806.5 | MW | 19:30 Hr. | Maximum Temperature |  |  | 23.7 |  | °C
| Minimum Generation of the Day |  |  | 6686.32 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 695.02 |  | MMCFD
| Maximum Generation of the Day |  |  | 10806.5 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 5.4273 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 23.1347 | 0 | 1.6074 | 0 | 0 | 0.12829 | 0 | 0 | 24.8704 | Gas | 92.0565 | Gas | 326546253.8276
| Chattogram Zone |  |  | 4.4378 | 31.9364 | 0.1001 | 0 | 1.1009 | 0.12632 | 0 | 0.408 | 38.1095 | Coal | 72.9163 | Coal | 485659107.4766
| Cumilla Zone |  |  | 22.1677 | 0 | 0.09456 | 0 | 0 | 0.19069 | 2.1254 | 0 | 24.5784 | HFO | 3.1891 | HFO | 57903736.27
| Mymensingh Zone |  |  | 3.6374 | 0 | 1.3271 | 0 | 0 | 0.06096 | 0 | 0 | 5.0255 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 17.8214 | 0 | 0 | 0 | 0 | 0.051527 | 0 | 0 | 17.8729 | Hydro | 1.1009 | Hydro | 110094
| Khulna Zone |  |  | 0.19037 | 20.1164 | 0 | 0 | 0 | 0.41112 | 18.0924 | 0 | 38.8102 | Solar | 2.5694 | Solar | 39815072.84
| Barishal Zone |  |  | 7.9179 | 20.8635 | 0 | 0 | 0 | 0.002364 | 0 | 0 | 28.7838 | Import | 42.449 | Import | 249136081.36
| Rajshahi Zone |  |  | 12.7491 | 0 | 0 | 0 | 0 | 0.93027 | 22.2312 | 0 | 35.9106 | Wind | 0.408 | Wind | 6001680
| Rangpur Zone |  |  | 0 | 0 | 0.059905 | 0 | 0 | 0.66782 | 0 | 0 | 0.72772
| Total |  |  | 92.0565 | 72.9163 | 3.1891 | 0 | 1.1009 | 2.5694 | 42.449 | 0.408 | 214.6892
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 326546253.8276 |  | Hydro | 110094
|  |  |  | Coal | 485659107.4766 |  | Solar | 39815072.84
|  |  |  | HFO | 57903736.27 |  | Import | 249136081.36
|  |  |  | HSD | 0 |  | Wind | 6001680
[5 empty] | Total: | 116,51,72,025 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 18.0924 | Peak Hr Flow | 892.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 33721381.83 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 22.2312 | Peak Hr Flow | 1172.00 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1982 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.1254 | Peak Hr Flow | 106.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1996 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 42.449 | Peak Hr Flow | 2170.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3768
|  |  |  | Chattogram |  | 0 |  | 1147
|  |  |  | Cumilla |  | 0 |  | 941
|  |  |  | Mymensingh |  | 0 |  | 869
|  |  |  | Sylhet |  | 0 |  | 401
|  |  |  | Khulna |  | 0 |  | 1260
|  |  |  | Barishal |  | 0 |  | 329
|  |  |  | Rajshahi |  | 0 |  | 980
|  |  |  | Rangpur |  | 0 |  | 698
|  |  |  | Total |  | 0 |  | 10393
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:18 | 14:46 | Benapole 132/33kV S/S Transformer-1(406T) LT Scheduled S/D Due to PBS Annual Maintenance | [7 empty] | 45.0MW load
interrup.
| 08:18 | 14:47 | Benapole 132/33kV S/S Transformer-2(416T) LT Scheduled S/D Due to PBS Annual Maintenance | [7 empty] | 45.0MW load
interrup.
| 08:19 | 14:45 | Benapole 132/33kV S/S Transformer-1(406T) HT Scheduled S/D Due to PBS Annual Maintenance | [7 empty] | 45.0MW load
interrup.
| 08:19 | 14:45 | Benapole 132/33kV S/S Transformer-2(416T) HT Scheduled S/D Due to PBS Annual Maintenance | [7 empty] | 45.0MW load
interrup.
| 08:29 | 16:36 | Rajshahi 230/132/33kV S/S 230 Kv BIPTC Ckt-01 Scheduled S/D Due to A/M
| 08:31 | 16:06 | Mymensingh 132/33kV S/S Bus B Scheduled S/D Due to Project work.
| 08:33 | 16:54 | Jamalpur United(20MW)-Sherpur 132kV Ckt-1 Scheduled S/D from Sherpur 132/33kV end Due to
Deadline checking.
| 08:36 | 15:03 | Mirzapur 132/33kV S/S Transformer-01(E05) LT Project Work S/D Due to Existing LILO | [7 empty] | 16.0MW load
|  |  | lINEMirzapur grid Re-conducting | [7 empty] | interrup.
| 08:36 | 15:15 | Mirzapur 132/33kV S/S Transformer-02(E07) LT Project Work S/D Due to Existing LILO lINE | [7 empty] | 9.0MW load
|  |  | Mirzapur grid Re-conducting | [7 empty] | interrup.
| 08:37 | 15:33 | Jhenaidah-Khulna 230kV Ckt-1 Scheduled S/D from Jhenaidah 230/132kV end Due to A/M and
from Khulna(S) 230/132kV end Due to Annual Maintenance Work
| 08:38 | 14:39 | Mirzapur 132/33kV S/S Mirzapur-Tangail-ckt-2B(E03) Project Work S/D Due to Existing LILO | [7 empty] | 25.0MW load
|  |  | lINEMirzapur grid Re-conducting | [7 empty] | interrup.
| 08:38 | 14:39 | Mirzapur 132/33kV S/S Mirzapur-Tangail-ckt-2A(E04) Project Work S/D Due to Existing LILO | [7 empty] | 25.0MW load
|  |  | lINEMirzapur grid Re-conducting | [7 empty] | interrup.
| 08:39 | 17:25 | Pabna- Shahjadpur 132kV Ckt-1 Scheduled S/D from Shahjadpur 132/33kV end Due to annual
maintenance and from Pabna 132/33kVend.
| 08:39 | 15:38 | Mirzapur 132/33kV S/S Mirzapur-Kaliakair-ckt-2A(E08) Project Work S/D Due to Existing | [7 empty] | 25.0MW load
|  |  | LILO lINEMirzapur grid Re-conducting | [7 empty] | interrup.
| 08:39 | 15:38 | Mirzapur 132/33kV S/S Mirzapur-Kaliakoir ckt-2B(E-09) Project Work S/D Due to Existing | [7 empty] | 25.0MW load
|  |  | LILO lINEMirzapur grid Re-conducting | [7 empty] | interrup.
| 08:40 | 16:58 | Kallyanpur-Lalbag 132kV Ckt-2 Scheduled S/D from Kallyanpur 132/33kV end Due to Deadline
Check
| 08:42 | 17:18 | Gopalganj 400/132kV S/S 400kV Amtoli Ckt-2 Scheduled S/D
| 08:43 | 14:38 | Tangail 132/33kV S/S Kaliakair-2 Scheduled S/D Due to Maintenance.
| 08:43 | 16:38 | HVDC Bheramera- Rajshahi 230kV Ckt-1 Scheduled S/D from BIPTC end Due to Annual
maintenance
| 08:47 | 16:43 | Jamalpur-Mymensingh 132kV Ckt-2 Scheduled S/D from Jamalpur 132/33kV end Due to 132kv
bus Maintenance work purpose of Mymensingh grid substation. and from Mymensingh 132/33kV
end Due to Project work.
| 08:56 | 15:02 | Mirzapur 132/33kV S/S Transformer-01(E05) HT Project Work S/D Due to Existing LILO | [7 empty] | 16.0MW load
|  |  | lINEMirzapur grid Re-conducting | [7 empty] | interrup.
| 08:56 | 14:43 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Kosba Ckt-02 Project Work S/D Due to Remove
bird nest and other obstacles
| 08:56 | 17:00 | Agargaon 230/132kV S/S 132kV Transformer-1 (405T1) LT Scheduled S/D Due to Annual
maintenance
| 08:57 | 16:54 | Agargaon 230/132kV S/S 132kV Transformer-1 (405T1) HT Scheduled S/D Due to Annual
maintenance
| 08:57 | 16:28 | Bogura 132/33kV S/S Transformer-4 LT Scheduled S/D Due to Annual Maintenance
| 08:57 | 16:28 | Bogura 132/33kV S/S Transformer-4 HT Scheduled S/D Due to Annual Maintenance
| 08:57 | 16:11 | Chattak-Sylhet 132 kV Ckt-1 Scheduled S/D from Chhatak 132/33kV end Due to dead line
cheacking and from Sylhet 132/33kV end Due to Dead line checking
| 08:57 | 15:13 | Mirzapur 132/33kV S/S Transformer-02(E07) HT Project Work S/D Due to Existing LILO | [7 empty] | 9.0MW load
|  |  | lINEMirzapur grid Re-conducting | [7 empty] | interrup.
| 09:00 | 16:35 | Cox'sbazar-Dohazari 132 kV Ckt-1 Scheduled S/D from Coxsbazar 132/33kV end Due to | [7 empty] | and 10.0MW load
|  |  | Maintenance and from Dohazari 132/33kV end Due to Annual Maintenance | [7 empty] | interrup. Dohazari
132/33kV end
| 09:00 | 14:44 | Kasba 132/33kV S/S Muradnagar-Kasba Ckt-2 Project Work S/D Due to Remove bird nest kites
and other obstacles
| 09:00 | 16:28 | Chowmuhani-Feni 132 kV Ckt-1 Scheduled S/D from Chowmuhani 132/33kV end Due to Annual
Maintenance. and from Daganbhuiyan 132/33kV end Due to Deadline Check
| 09:01 | 16:10 | Bagerhat 132/33kV S/S Transformer-1 (403T) LT Scheduled S/D Due to Yearly Maintenance
work.
| 09:01 | 13:40 | Bogura 230/132kV S/S T-04 HT Scheduled S/D Due to Annual Maintenance
| 09:01 | 13:40 | Bogura 230/132kV S/S T-04 LT Scheduled S/D Due to Annual Maintenance
| 09:02 | 16:09 | Bagerhat 132/33kV S/S Transformer-1 (403T) HT Scheduled S/D Due to Yearly Maintenance
work.
| 09:04 | 16:48 | Ruppur 132/11kV S/S TR-01 LT Scheduled S/D
| 09:06 | 16:43 | Ruppur 132/11kV S/S TR-01 HT Scheduled S/D
| 09:07 | 17:05 | Fenchuganj -Sylhet 132kV Ckt-1 Scheduled S/D from Beanibazar 132/33kV end Due to 33kv | [7 empty] | 44.0MW load
|  |  | bus 1 & 2 maintenance | [7 empty] | interrup.
Beanibazar 132/33kV
end
| 09:08 | 17:10 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Scheduled S/D from Beanibazar 132/33kV
end Due to 33kv bus 1 & 2 maintenance and from Fenchuganj 230/132/33kV end Due to Annual
Maintenance
| 09:10 | 14:03 | Kachua 230/132/33kV S/S Main Bus-2 (132 kV) Scheduled S/D Due to Annual maintenance
| 09:12 | 16:13 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Scheduled S/D from Brahmanbaria 132/33kV end. and
from Shahjibazar 132/33kV end Due to Shutdown for annual maintenance
| 09:12 | 17:02 | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-1 Scheduled S/D Due to For Fenchugonj
grid schedule shutdown.
| 09:13 | 17:02 | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-2 Scheduled S/D Due to For Fenchugonj
grid schedule shutdown.
| 09:18 | 16:40 | Dhamrai 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Annual maintenance
| 09:19 | 16:37 | Dhamrai 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Annual maintenance
| 09:22 | 17:09 | Aminbazar 400/230/132kV S/S Gopalganj-1 Scheduled S/D Due to Scheduled shutdown
| 09:22 | 16:30 | BIPTC S/S 20DF24 Forced S/D Due to Corrective maintenance due to trip
| 09:23 | 17:07 | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-1 Scheduled S/D
| 09:29 | 16:05 | Maniknagar-Narinda 132kV Ckt-1 Scheduled S/D from Maniknagar 132/33kV end Due to PT oil
leakage repair (Blue phase)
| 09:38 | 16:43 | Tongi 230/132/33kV S/S T-02 LT Scheduled S/D Due to Annual Maintenance Work.
| 09:38 | 16:43 | Tongi 230/132/33kV S/S T-02 HT Scheduled S/D Due to Annual Maintenance Work
| 09:39 | 13:49 | Cumilla(N) 230/132/33kV S/S 230KV ATR-03 LT Scheduled S/D Due to Annual Maintenance work
| 09:39 | 13:49 | Cumilla(N) 230/132/33kV S/S 230KV ATR-03 HT Scheduled S/D Due to Annual Maintenance works
| 09:42 | 17:18 | Dhamrai-Kaliakoir 132 kV Ckt-1 Scheduled S/D from Dhamrai 132/33kV end Due to Annual
maintenance
| 10:09 | 14:57 | Goalpara- Khulna (C) 132kV Ckt-1 Scheduled S/D from Goalpara 132/33kV end Due to Annual
Maintenance and from Khulna (C) end Due to Annual maintenance
| 10:16 | 16:47 | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to PBS REB-1, REB-2 feeder & 33kv bus | [7 empty] | 18.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 10:16 | 16:53 | Haripur-Madanganj 132kV Ckt-1 Scheduled S/D from Madanganj 132/33kV end Due to Annual
maintenance and from Haripur 230/132kV end Due to Annual Maintenance
| 10:17 | 16:46 | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to PBS REB-1, REB-2 feeder & 33kv bus | [7 empty] | 18.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 10:25 |  | Kodda-Rajendrapur 132kV Ckt-1 Scheduled S/D from Rajendrapur 132/33kV end Due to For
yearly maintenance work.
| 10:41 |  | Joydebpur 132/33kV S/S 132kV Bus Forced S/D Due to Annual Maintenance
| 10:47 |  | Kodda 132/33kV S/S Summit 149 MW PS Scheduled S/D Due to Dead line check
| 11:01 | 11:11 | Ashuganj-Kishoreganj 132kV Ckt-2 Forced S/D from Kishoreganj 132/33kV end Due to By NLDC
| 11:01 | 11:11 | Ashuganj-Kishoreganj 132kV Ckt-1 Forced S/D from Kishoreganj 132/33kV end Due to By NLDC
| 11:55 | 15:26 | Keranigonj 230/132/33kV S/S 132 kV Lalbagh Ckt. 3 Project Work S/D Due to Line material
checking for project work.
| 12:00 |  | Day Peak Generation: 9519 MW.
| 13:20 | 14:48 | Kaliakoir 400/230/132kV S/S 132kV Bus 2 Scheduled S/D Due to Maintenance.
| 14:00 |  | Kushiara 163MW CCPP ST was sync.
| 14:55 | 16:35 | Cox'sbazar-Dohazari 132 kV Ckt-1 Scheduled S/D from Coxsbazar 132/33kV end Due to
Maintenance
|  | 16:50 | Meghnaghat-Shyampur 230kV Ckt-1 is restored.
|  | 16:50 | Meghnaghat-Shyampur 230kV Ckt-1 is restored.
|  | 17:38 | Rampura 230/132kV S/S Auto Transformer - 02 HT is restored.
|  | 17:40 | Rampura 230/132kV S/S Auto Transformer - 02 LT is restored.
|  | 18:52 | Ghorasal-Joydeb-B 132kV Ckt-2 is restored.
| 19:26 |  | Bheramara 410 MW CCPP GT was syn.
| 19:26 |  | Bheramara 410 MW CCPP Synchronized with remarks:- GT
| 19:26 |  | Bheramara 410 MW CCPP GT Synchronized with remarks:- GTG has been synchronized with grid
as per NLDC demand and ST start up process is on going
| 19:30 |  | Evening Peak Generation is 10806 MW
| 21:29 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- GT
| 21:29 |  | Ashuganj 225 MW CCPP GT was sync.
| 02:48 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- ST
| 03:45 |  | Bheramara 410 MW CCPP ST Synchronized with remarks:- STG has been synchronized with grid
at 03:45 hrs on 04.01.2026 as per NLDC demand
| 03:45 |  | Bheramara 410 MW CCPP Synchronized with remarks:- ST
| 04:38 | 04:45 | Chowmuhani 132/33kV S/S TR3-435T LT Tripped showing O/C relays Due to 33kv kabirhat | [7 empty] | 23.0MW load
|  |  | feeser fault | [7 empty] | interrup.
| 04:38 | 04:45 | Chowmuhani 132/33kV S/S TR2-425T HT Tripped showing E/F ,O/C relays Due to 33kv kabirhat | [7 empty] | 23.0MW load
|  |  | feeder fault | [7 empty] | interrup.
| 04:38 | 04:45 | Chowmuhani 132/33kV S/S TR2-425T LT Tripped showing E/F,O/C relays Due to 33 kv kabirhat | [7 empty] | 23.0MW load
|  |  | fault | [7 empty] | interrup.
| 05:00 |  | Minimum generation 6985 MW
| 06:34 |  | Bheramara 410 MW CCPP, FGMO is ON with remarks:- FGMO on at 06:22 hrs
| 07:43 |  | Aminbazar 400/230/132kV S/S Gopalganj-1 Scheduled S/D Due to Schedule shutdown
| 07:43 |  | Ghorasal-Joydeb-B 132kV Ckt-2 Scheduled S/D from Joydebpur 132/33kV end.
| 07:45 |  | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-1 Scheduled S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 03-01-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 353 | 8146800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4883600 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 300960 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 42040 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 115376 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 26.5 | 516600 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 231120 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 9821 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 15552 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 5 | 197280 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 128293 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 480 | 9356591 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 926400 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1245.5 | 24870433
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 108675 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1100940 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 173 | 3998608 | Plant availability less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 50181 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 31 | 439200 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 17645 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 49920 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1155 | 19936361 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 9 | 408000 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 520 | 12000000 | Machine Problem
Chattogram Area Total |  |  |  |  | 4898.863 | 1934 | 38109530
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 0 | 140000 | Shutdown
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 387 | 9008300 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 365 | 7233100 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 36 | 679464 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 49 | 862080 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 26 | 1087273 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 639786 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 110 | 2243413 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 94560 | -
| Import (Tripura) |  | Import | 0 | 160 | 106 | 2125440 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 15 | 274330 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 190691 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1138 | 24578437
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 165 | 3637440 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 4900 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 35 | 748800 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 313200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 56060 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 100560 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 164520 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 219 | 5025480
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 51527 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 931000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 50 | 708840 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 162 | 1838536.36 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 640320 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1390080 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 159 | 4423870 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 315240 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7573500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 861 | 17872913.36
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 892 | 18092363 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 15 | 190368 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 411120 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1109 | 20116365 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2016 | 38810216
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 505 | 7381818 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 140 | 2913000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 520 | 8616727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5004910 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 279 | 4865000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2364 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1664 | 28783819.27
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 235880 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 178 | 4045909 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 379 | 8703200 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 14340 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1172 | 22231243 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 181504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 498550 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1729 | 35910626
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 24987.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 59905 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 66828 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 576000 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 0 | 727720.6
Eastern Grid Total |  |  |  |  | 17398.245 | 5397.5 | 110456793.36
Western Grid Total |  |  |  |  | 10984.003 | 5409 | 104232381.87
National Grid Total |  |  |  |  | 28382.248 | 10806.5 | 214689175.23
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 03-01-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7126.12 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3266.6 | MW
i) Dhaka area |  |  | 3767.92 |  | MW | i) Khulna area |  |  |  | 1259.6 | MW
ii) Chattogram area |  |  | 1147.2 |  | MW | ii) Barishal area |  |  |  | 329 | MW
iii) Cumilla area |  |  | 941 |  | MW | iii) Rajshahi area |  |  |  | 980 | MW
iv) Mymensingh area |  |  | 869 |  | MW | iv) Rangpur area |  |  |  | 698 | MW
v) Sylhet area |  |  | 401 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10392.72 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 90 | 13:00 | 133 | Netrakona | 104 | 19:30
2 | AKSML | 96.5 | 04:00 | 68 | Hathazari | 54 | 13:00 | 134 | New | 66.6 | 12:00
3 | Aftabnagar | 26 | 13:00 | 69 | Hatirjheel | 24 | 15:00 | 135 | Niamatpur | 51 | 13:00
4 | Agargaon | 80 | 13:00 | 70 | Ishurdi | 60 | 18:00 | 136 | Noapara | 38 | 19:00
5 | Agrabad | 38 | 12:00 | 71 | Jaldhaka | 57 | 18:00 | 137 | PHP | 7 | 02:00
6 | Amnura | 25 | 13:00 | 72 | Jamalpur | 97 | 19:30 | 138 | Pabna | 67 | 18:30
7 | Ashuganj | 55 | 20:00 | 73 | Jashore | 122 | 13:00 | 139 | Palashbari | 94 | 18:00
8 | BSRM | 200 | 04:00 | 74 | Jhenaidah | 104 | 18:00 | 140 | Panchagarh | 45 | 19:30
9 | Bagerhat | 64 | 18:00 | 75 | Joydebpur | 90 | 19:00 | 141 | Patiya | 6.71 | 20:00
10 | Bajitpur | 56 | 20:00 | 76 | Joypurhat | 43 | 21:00 | 142 | Patuakhali | 39 | 18:00
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 14 | 12:00 | 143 | Payra | 28 | 18:00
12 | Bakulia | 59 | 14:00 | 78 | KSRM | 28 | 13:00 | 144 | Postogola | 40 | 13:00
13 | Banani | 18 | 18:00 | 79 | Kabirpur | 174 | 12:00 | 145 | Purbachal | 19 | 12:00
14 | Bangabhaban | 5 | 11:00 | 80 | Kachua | 55 | 19:30 | 146 | Purbasadipur | 110 | 18:00
15 | Barapukuria | 51 | 18:00 | 81 | Kallyanpur | 72 | 13:00 | 147 | Rahanpur | 23 | 13:00
16 | Barguna | 14 | 19:00 | 82 | Kalurghat | 28 | 10:00 | 148 | Rahim | 24 | 11:00
17 | Barishal | 80 | 20:00 | 83 | Kamrangirchar | 60 | 13:00 | 149 | Rajbari | 60 | 18:00
18 | Barishal-230 | 70 | 18:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 117 | 14:00
19 | Baroaulia | 54 | 13:00 | 85 | Kasba | 23 | 20:00 | 151 | Rajshahi | 71 | 20:00
20 | Baroirhat | 40 | 18:00 | 86 | Kazla | 85 | 13:00 | 152 | Rajshahi-230 | 72 | 13:00
21 | Bashundhara | 127 | 13:00 | 87 | Keranigonj | 43 | 13:00 | 153 | Ramganj | 70 | 13:00
22 | BashundharaCement | 9 | 15:00 | 88 | Khagrachori | 24 | 18:00 | 154 | Rampur | 26 | 18:00
23 | Beanibazar | 66 | 18:00 | 89 | Khulna | 48 | 13:00 | 155 | Rangamati | 12 | 18:00
24 | Benapole | 52 | 07:00 | 90 | Khulshi | 159 | 16:00 | 156 | Rangpur | 104 | 18:00
25 | Bhaluka | 123 | 18:30 | 91 | Kishoreganj | 89 | 19:30 | 157 | Ruppur | 1.2 | 09:00
26 | Bhandaria | 38 | 18:00 | 92 | Kodda | 231 | 10:00 | 158 | SSM | 0 | 00:00
27 | Bhangura | 23 | 18:00 | 93 | Kulaura | 37 | 18:00 | 159 | Saidpur | 90 | 18:00
28 | Bheramara(GK) | 41 | 18:00 | 94 | Kurigram | 48 | 18:00 | 160 | Satkhira | 96 | 18:00
29 | Bhulta | 183 | 19:30 | 95 | Kushtia | 112 | 13:00 | 161 | Satmasjid | 77 | 14:00
30 | Bog-Sherpur | 54 | 18:00 | 96 | Laksam | 23 | 13:00 | 162 | Savar | 180 | 14:00
31 | Bogura | 111 | 20:00 | 97 | Lakshmipur | 24 | 20:00 | 163 | SevenRings | 19.42 | 07:00
32 | Borhanuddin | 68 | 19:00 | 98 | Lalbag | 54 | 13:00 | 164 | ShahCement | 16 | 23:00
33 | Brahmanbaria | 94 | 13:00 | 99 | Lalmonirhat | 46 | 18:00 | 165 | Shahjadpur | 52 | 18:00
34 | Cantonment | 82 | 13:00 | 100 | MI_Cement | 14.3 | 11:00 | 166 | Shahjibazar | 86 | 18:30
35 | Chandina | 13 | 15:00 | 101 | Madanganj | 27 | 00:00 | 167 | Shahmirpur | 36.5 | 18:00
36 | Chandpur | 50 | 13:00 | 102 | Madaripur | 72 | 19:30 | 168 | Shariatpur | 58 | 19:30
37 | Chandraghona | 26 | 18:00 | 103 | Madartek | 56 | 13:00 | 169 | Sherpur | 114 | 18:00
38 | Chapai | 48 | 08:00 | 104 | Madunaghat | 38 | 18:00 | 170 | Shikalbaha | 21.5 | 12:00
39 | Charsaidpur | 39 | 12:00 | 105 | Magura | 49 | 18:00 | 171 | Shitalakhya | 63.7 | 12:00
40 | Chauddagram | 54 | 13:00 | 106 | Mahasthangarh | 48 | 18:30 | 172 | Sholosohor | 32 | 10:00
41 | Chhatak | 26 | 18:00 | 107 | Maijdee | 26 | 18:00 | 173 | Shyampur | 148 | 12:00
42 | Chowmuhani | 110 | 21:00 | 108 | Manikganj | 94 | 19:00 | 174 | Siddhirganj | 92 | 12:00
43 | Chuadanga | 78 | 18:00 | 109 | Maniknagar | 52 | 13:00 | 175 | Sirajganj | 72 | 19:00
44 | Coxsbazar | 108 | 18:00 | 110 | Matarbari | 42 | 18:00 | 176 | Sonargaon | 92 | 22:00
45 | Cumilla(N) | 97 | 13:00 | 111 | Matuail | 44 | 13:00 | 177 | Sreemongol | 53 | 12:00
46 | Cumilla(S) | 115 | 18:00 | 112 | Metrorail_Motijheel | 14 | 13:00 | 178 | Sreepur | 99 | 11:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 4 | 10:00 | 179 | Srinagar | 30.76 | 20:00
48 | Daudkandi | 106 | 18:00 | 114 | Millgate | 74 | 12:00 | 180 | Sunamganj | 40 | 18:00
49 | DhakaUniversity | 44 | 13:00 | 115 | Mirpur | 106 | 13:00 | 181 | Sylhet | 36 | 18:00
50 | Dhamrai | 84 | 09:00 | 116 | Mirsorai | 8 | 09:00 | 182 | Sylhet-132 | 77 | 18:00
51 | Dhanmondi | 69 | 18:00 | 117 | Mirzapur | 39 | 18:00 | 183 | TK | 16 | 18:00
52 | Dohazari | 67 | 20:00 | 118 | Mithapukur | 44 | 18:00 | 184 | Tangail | 116 | 18:30
53 | Faridpur | 115 | 19:30 | 119 | Modern | N/A | N/A | 185 | Taraganj | 16 | 18:00
54 | Fatullah | 90 | 12:00 | 120 | Mogbazar | 32.8 | 13:00 | 186 | Tasnim | 22 | 11:00
55 | Fenchuganj | 25 | 18:00 | 121 | Mongla | 33 | 18:00 | 187 | Thakurgaon | 80 | 18:30
56 | Feni | 78 | 13:00 | 122 | Motijheel | 26 | 13:00 | 188 | Tongi | 81 | 12:00
57 | GPH | 81 | 06:00 | 123 | Muktagacha | 28 | 13:00 | 189 | Ullahpara | 28 | 13:00
58 | Ghatail | 64 | 18:00 | 124 | Munshiganj | 68 | 19:30 | 190 | Ullon | 50 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 24 | 18:00 | 191 | Uttara | 58 | 13:00
60 | Ghorashal-230 | 84 | 13:00 | 126 | Mymensingh | 142 | 13:00 | 192 | UttaraNew | 44 | 13:00
61 | Goalpara | 30 | 13:00 | 127 | Naogaon | 88 | 13:00 | 193 | Zigatola | 72 | 13:00
62 | Gollamari | 70 | 13:00 | 128 | Narail | 44.5 | 18:00
63 | Gopalganj | 74.6 | 18:30 | 129 | Narinda | 52 | 17:00
64 | Gulshan | 60 | 13:00 | 130 | Narshingdi | 145 | 18:30
65 | Halishahar | 59 | 15:00 | 131 | Natore | 101 | 18:00
66 | HaripurSBU | 86 | 03:00 | 132 | Nawabganj | 30.2 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 03-01-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 8210.56 | 0 |  | 8210.56
1:00 | 7653.55 | 0 |  | 7653.55
2:00 | 7282.82 | 0 |  | 7282.82
3:00 | 6945.32 | 0 |  | 6945.32
4:00 | 6727.05 | 0 |  | 6727.05
5:00 | 6686.32 | 0 |  | 6686.32
6:00 | 7193.38 | 0 |  | 7193.38
7:00 | 7521.68 | 0 |  | 7521.68
8:00 | 8301.51 | 0 |  | 8301.51
9:00 | 9013.39 | 0 |  | 9013.39
10:00 | 8932.1 | 0 |  | 8932.1
11:00 | 8864.96 | 0 |  | 8864.96
12:00 | 9522.76 | 0 |  | 9522.76
13:00 | 10019.09 | 0 |  | 10019.09
14:00 | 9652.85 | 0 |  | 9652.85
15:00 | 8984.42 | 0 |  | 8984.42
16:00 | 8865.26 | 0 |  | 8865.26
17:00 | 9316.94 | 0 |  | 9316.94
18:00 | 10626.9 | 0 |  | 10626.9
19:00 | 10736.5 | 0 |  | 10736.5
19:30 | 10806.5 | 0 |  | 10806.5
20:00 | 10671.5 | 0 |  | 10671.5
21:00 | 10500.5 | 0 |  | 10500.5
22:00 | 9929.1 | 0 |  | 9929.1
23:00 | 9279.83 | 0 |  | 9279.83
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 03-01-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4160 | 4050.56 | 8210.56 | DAILY GENERATION CURVE
00:30 | 4000.5 | 3931.555 | 7932.055
01:00 | 3841 | 3812.55 | 7653.55 | 03-01-2026
01:30 | 3696.5 | 3771.685 | 7468.185
02:00 | 3552 | 3730.82 | 7282.82
02:30 | 3567.5 | 3546.57 | 7114.07
03:00 | 3583 | 3362.32 | 6945.32
03:30 | 3583.5 | 3252.685 | 6836.185
04:00 | 3584 | 3143.05 | 6727.05
04:30 | 3564 | 3142.685 | 6706.685
05:00 | 3544 | 3142.32 | 6686.32
05:30 | 3694 | 3245.85 | 6939.85
06:00 | 3844 | 3349.38 | 7193.38
06:30 | 3893.055 | 3464.475 | 7357.53
07:00 | 3942.11 | 3579.57 | 7521.68
07:30 | 4088.56 | 3823.035 | 7911.595
08:00 | 4235.01 | 4066.5 | 8301.51
08:30 | 4428.22 | 4229.23 | 8657.45
09:00 | 4621.43 | 4391.96 | 9013.39
09:30 | 4620.41 | 4352.335 | 8972.745
10:00 | 4619.39 | 4312.71 | 8932.1
10:30 | 4598.84 | 4299.69 | 8898.53
11:00 | 4578.29 | 4286.67 | 8864.96
11:30 | 4763.65 | 4430.21 | 9193.86
12:00 | 4949.01 | 4573.75 | 9522.76
12:30 | 5113.46 | 4657.465 | 9770.925
13:00 | 5277.91 | 4741.18 | 10019.09
13:30 | 5197.7 | 4638.27 | 9835.97
14:00 | 5117.49 | 4535.36 | 9652.85
14:30 | 4926.48 | 4392.155 | 9318.635
15:00 | 4735.47 | 4248.95 | 8984.42
15:30 | 4711.175 | 4213.665 | 8924.84
16:00 | 4686.88 | 4178.38 | 8865.26
16:30 | 4797.78 | 4293.32 | 9091.1
17:00 | 4908.68 | 4408.26 | 9316.94
17:30 | 5203.29 | 4768.63 | 9971.92
18:00 | 5497.9 | 5129 | 10626.9
18:30 | 5414.7 | 5267 | 10681.7
19:00 | 5331.5 | 5405 | 10736.5
19:30 | 5397.5 | 5409 | 10806.5
20:00 | 5306.5 | 5365 | 10671.5
20:30 | 5306 | 5280 | 10586 |  | Executive Engineer
21:00 | 5305.5 | 5195 | 10500.5 |  | Network Operation Division
21:30 | 5156.75 | 5058.05 | 10214.8
22:00 | 5008 | 4921.1 | 9929.1
22:30 | 4841 | 4763.465 | 9604.465
23:00 | 4674 | 4605.83 | 9279.83

## En-Curve
QF-LDC-12
Date | 03-01-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2397 | 1338 | 798 | 0 | 76 | 832.56 | 46 | 2692 | 0 | 0 | 19 | 0 | 0 | 12 | 0 | DAILY ENERGY CURVE
00:30 | 2328 | 1277 | 758 | 0 | 76 | 836.555 | 46 | 2589 | 0 | 0 | 9.5 | 0 | 0 | 12 | 0 | 03-01-2026
01:00 | 2259 | 1216 | 718 | 0 | 76 | 840.55 | 46 | 2486 | 0 | 0 | 0 | 0 | 0 | 12 | 0
01:30 | 2127.5 | 1166 | 711 | 0 | 76 | 840.685 | 46 | 2483.5 | 0 | 0 | 0 | 0 | 0 | 17.5 | 0 | Energy Generated | 214.6892 |  | MKWHr
02:00 | 1996 | 1116 | 704 | 0 | 76 | 840.82 | 46 | 2481 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 1954.5 | 1134 | 557 | 0 | 73 | 836.07 | 46 | 2488.5 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | Total Energy Requirement | 214.6892 |  | MKWHr
03:00 | 1913 | 1152 | 410 | 0 | 70 | 831.32 | 46 | 2496 | 0 | 0 | 0 | 0 | 0 | 27 | 0
03:30 | 1891.5 | 1163 | 325 | 0 | 71 | 830.685 | 46 | 2487 | 0 | 0 | 0 | 0 | 0 | 22 | 0
04:00 | 1870 | 1174 | 240 | 0 | 72 | 830.05 | 46 | 2478 | 0 | 0 | 0 | 0 | 0 | 17 | 0
04:30 | 1871 | 1148.5 | 240 | 0 | 71 | 832.185 | 46 | 2475.5 | 0 | 0 | 0 | 0 | 0 | 22.5 | 0
05:00 | 1872 | 1123 | 240 | 0 | 70 | 834.32 | 46 | 2473 | 0 | 0 | 0 | 0 | 0 | 28 | 0
05:30 | 2084.5 | 1128 | 239.5 | 0 | 74 | 832.85 | 46 | 2504.5 | 0 | 0 | 0 | 0 | 0 | 30.5 | 0
06:00 | 2297 | 1133 | 239 | 0 | 78 | 831.38 | 46 | 2536 | 0 | 0 | 0 | 0 | 0 | 33 | 0
06:30 | 2317 | 1152.5 | 366 | 0 | 75 | 830.725 | 46 | 2531.5 | 3.305 | 0 | 0 | 0 | 0 | 35.5 | 0
07:00 | 2337 | 1172 | 493 | 0 | 72 | 830.07 | 46 | 2527 | 6.61 | 0 | 0 | 0 | 0 | 38 | 0
07:30 | 2445 | 1248.5 | 598.5 | 0 | 78 | 839.86 | 46 | 2557 | 46.235 | 0 | 19 | 0 | 0 | 33.5 | 0
08:00 | 2553 | 1325 | 704 | 0 | 84 | 849.65 | 46 | 2587 | 85.86 | 0 | 38 | 0 | 0 | 29 | 0
08:30 | 2520.5 | 1410.25 | 798 | 0 | 76 | 856.83 | 46 | 2729 | 115.87 | 14 | 65.5 | 0 | 0 | 25.5 | 0
09:00 | 2488 | 1495.5 | 892 | 0 | 68 | 864.01 | 46 | 2871 | 145.88 | 28 | 93 | 0 | 0 | 22 | 0
09:30 | 2464.5 | 1463.5 | 892 | 0 | 75 | 849.9 | 46 | 2813.5 | 202.845 | 40 | 104.5 | 0 | 0 | 21 | 0
10:00 | 2441 | 1431.5 | 892 | 0 | 82 | 835.79 | 46 | 2756 | 259.81 | 52 | 116 | 0 | 0 | 20 | 0
10:30 | 2400 | 1408 | 892 | 0 | 83 | 835.97 | 46 | 2737 | 311.06 | 43.5 | 126 | 0 | 0 | 16 | 0
11:00 | 2359 | 1384.5 | 892 | 0 | 84 | 836.15 | 46 | 2718 | 362.31 | 35 | 136 | 0 | 0 | 12 | 0
11:30 | 2429 | 1430.5 | 892.5 | 0 | 87 | 880.675 | 46 | 2846.5 | 396.185 | 35 | 138.5 | 0 | 0 | 12 | 0
12:00 | 2499 | 1476.5 | 893 | 0 | 90 | 925.2 | 46 | 2975 | 430.06 | 35 | 141 | 0 | 0 | 12 | 0
12:30 | 2482 | 1556 | 892.5 | 0 | 87 | 991.28 | 46 | 3038.5 | 444.145 | 43.5 | 178.5 | 0 | 0 | 11.5 | 0
13:00 | 2465 | 1635.5 | 892 | 0 | 84 | 1057.36 | 46 | 3102 | 458.23 | 52 | 216 | 0 | 0 | 11 | 0
13:30 | 2457 | 1606.75 | 892.5 | 0 | 87 | 1005.18 | 46 | 3056.5 | 424.09 | 53 | 200.45 | 0 | 0 | 7.5 | 0
14:00 | 2449 | 1578 | 893 | 0 | 90 | 953 | 46 | 3011 | 389.95 | 54 | 184.9 | 0 | 0 | 4 | 0
14:30 | 2409 | 1487.5 | 892.5 | 0 | 85 | 901.5 | 46 | 2938.5 | 329.235 | 44.5 | 178.4 | 0 | 0 | 6.5 | 0
15:00 | 2369 | 1397 | 892 | 0 | 80 | 850 | 46 | 2866 | 268.52 | 35 | 171.9 | 0 | 0 | 9 | 0
15:30 | 2407.5 | 1354 | 892 | 0 | 93 | 847 | 46 | 2883 | 197.84 | 26 | 170 | 0 | 0 | 8.5 | 0
16:00 | 2446 | 1311 | 892 | 0 | 106 | 844 | 46 | 2900 | 127.16 | 17 | 168.1 | 0 | 0 | 8 | 0
16:30 | 2487.5 | 1387 | 892 | 0 | 104 | 915.5 | 46 | 3012 | 72.6 | 17 | 149 | 0 | 0 | 8.5 | 0
17:00 | 2529 | 1463 | 892 | 0 | 102 | 987 | 46 | 3124 | 18.04 | 17 | 129.9 | 0 | 0 | 9 | 0
17:30 | 2554 | 1571.5 | 892 | 0 | 108 | 1128.5 | 46 | 3384.5 | 9.02 | 53.5 | 212.9 | 0 | 0 | 12 | 0
18:00 | 2579 | 1680 | 892 | 0 | 114 | 1270 | 46 | 3645 | 0 | 90 | 295.9 | 0 | 0 | 15 | 0
18:30 | 2581 | 1644.75 | 892 | 0 | 110 | 1269 | 46 | 3799 | 0 | 116 | 209.45 | 0 | 0 | 14.5 | 0
19:00 | 2583 | 1609.5 | 892 | 0 | 106 | 1268 | 46 | 3953 | 0 | 142 | 123 | 0 | 0 | 14 | 0
19:30 | 2581 | 1711.5 | 892 | 0 | 106 | 1172 | 46 | 4088 | 0 | 142 | 59 | 0 | 0 | 9 | 0
20:00 | 2533 | 1665.5 | 891 | 0 | 114 | 1152 | 46 | 4068 | 0 | 142 | 54 | 0 | 0 | 6 | 0
20:30 | 2524 | 1673 | 891.5 | 0 | 114 | 1084 | 46 | 4054.5 | 0 | 133.5 | 54 | 0 | 0 | 11.5 | 0
21:00 | 2515 | 1680.5 | 892 | 0 | 114 | 1016 | 46 | 4041 | 0 | 125 | 54 | 0 | 0 | 17 | 0
21:30 | 2505 | 1671.25 | 892 | 0 | 108 | 971.05 | 46 | 3849 | 0 | 97.5 | 54 | 0 | 0 | 21 | 0
22:00 | 2495 | 1662 | 892 | 0 | 102 | 926.1 | 46 | 3657 | 0 | 70 | 54 | 0 | 0 | 25 | 0
22:30 | 2453 | 1555 | 892 | 0 | 103 | 922.465 | 46 | 3531.5 | 0 | 35 | 44.5 | 0 | 0 | 22 | 0
23:00 | 2411 | 1448 | 892 | 0 | 104 | 918.83 | 46 | 3406 | 0 | 0 | 35 | 0 | 0 | 19 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 03-01-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 426 | 03:00 | 397 | 12:00 | Meghnaghat | 430 | 03:00 | 404 | 12:00
Ashuganj | 416 | 7:00 | 396 | 12:00 | Payra | 425 | 00:00 | 416 | 18:00
Bhulta | 406 | 04:00 | 386 | 12:00 | Rahanpur | 418 | 00:00 | 402 | 18:00
Bibiana | 422 | 04:00 | 402 | 12:00 | Rampal | 418 | 04:00 | 402 | 12:00
BIPTC | 407 | 01:00 | 393 | 18:30
Bogura | 415 | 05:00 | 395 | 18:00
Gopalganj | 424 | 03:00 | 405 | 12:00
Kaliakoir | 420 | 04:00 | 380 | 14:00
Korerhat | 424 | 04:00 | 407 | 12:00
Madunaghat | 416 | 04:00 | 403 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 248 | 03:00 | 228 | 12:00 | Kachua | 240 | 06:00 | 237 | 00:00
AKSML | 243 | 05:00 | 233 | 13:00 | Kaliakoir | 247 | 04:00 | 228 | 12:00
Aminbazar | 247 | 05:00 | 227 | 12:00 | Keranigonj | 246 | 04:00 | 227 | 12:00
Ashuganj | 240 | 05:00 | 232 | 19:30 | Khulna(S) | 247 | 04:00 | 233 | 12:00
Ashuganj-400 | 240 | 05:00 | 232 | 19:30 | Korerhat | 246 | 03:00 | 236 | 12:00
Baghabari | 242 | 01:00 | 231 | 18:00 | Madunaghat | 241 | 06:00 | 233 | 12:00
Barapukuria | 232 | 05:00 | 210 | 18:00 | Madunaghat-400 | 241 | 03:00 | 233 | 13:00
Barapukuria-230 | 232 | 05:00 | 210 | 18:00 | Maniknagar | 244 | 03:00 | 228 | 12:00
Barishal | 242 | 03:00 | 232 | 12:00 | Meghnaghat | 247 | 02:00 | 235 | 12:00
Bheramara | 243 | 04:00 | 221 | 12:00 | Meghnaghat-400 | 244 | 03:00 | 230 | 12:00
Bhulta | 246 | 04:00 | 230 | 12:00 | Mirsorai | 246 | 04:00 | 235 | 13:00
Bibiana | 246 | 04:00 | 236 | 12:00 | Rajshahi | 243 | 05:00 | 220 | 13:00
BIPTC | 242 | 04:00 | 223 | 12:00 | Rampal | 243 | 04:00 | 229 | 18:00
Bogura | 243 | 04:00 | 229 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 242 | 04:00 | 230 | 18:00 | Rampura | 245 | 03:00 | 230 | 12:00
Borhanuddin | 242 | 02:00 | 236 | 18:30 | Shikalbaha | 238 | 00:00 | 231 | 12:00
BSRM | 245 | 03:00 | 235 | 12:00 | Shyampur | 245 | 03:00 | 227 | 12:00
Cumilla(N) | 242 | 05:00 | 230 | 13:00 | Siddhirganj | 245 | 05:00 | 233 | 13:00
Faridpur | 241 | 03:00 | 229 | 12:00 | Sirajgonj | 244 | 00:00 | 238 | 18:00
Fenchuganj | 247 | 04:00 | 240 | 12:00 | Sreepur | 239 | 03:00 | 230 | 12:00
Feni | 246 | 03:00 | 235 | 12:00 | Tongi | 242 | 04:00 | 227 | 12:00
Ghorashal | 247 | 06:00 | 235 | 12:00
Ghorashal-230 | 242 | 04:00 | 219 | 12:00
Gopalganj | 239 | 03:00 | 228 | 12:00
GPH | 243 | 03:00 | 234 | 12:00
Haripur | 245 | 03:00 | 231 | 12:00
Hasnabad | 246 | 06:00 | 227 | 12:00
Hathazari | 240 | 04:00 | 229 | 17:00
Ishurdi | 244 | 04:00 | 226 | 12:00
Jhenaidah | 244 | 04:00 | 221 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 03:00 | 126 | 12:00 | Laksam | 141 | 03:00 | 135 | 12:00 | UttaraNew | 141 | 03:00 | 126 | 12:00
Agargaon | 141 | 03:00 | 129 | 12:00 | Lakshmipur | 138 | 03:00 | 132 | 12:00 | Zigatola | 140 | 04:00 | 127 | 12:00
Agrabad | 140 | 02:00 | 134 | 17:00 | Lalbag | 140 | 05:00 | 124 | 12:00
AKS | 136 | 00:00 | 133 | 04:00 | Lalmonirhat | 131 | 01:00 | 118 | 18:00
Aminbazar | 140 | 04:00 | 127 | 12:00 | Madanganj | 139 | 05:00 | 135 | 17:00
Amnura | 139 | 00:00 | 128 | 13:00 | Madaripur | 140 | 02:00 | 137 | 12:00
Ashuganj | 144 | 04:00 | 135 | 19:30 | Madartek | 135 | 03:00 | 125 | 12:00
Bagerhat | 137 | 05:00 | 126 | 18:00 | Madunaghat | 141 | 04:00 | 136 | 12:00
Bajitpur | 139 | 11:00 | 129 | 19:00 | Magura | 139 | 03:00 | 126 | 13:00
Bakerganj | 138.8 | 06:00 | 136 | 17:00 | Mahasthangarh | 138 | 04:00 | 127 | 18:00
Bakulia | 139 | 04:00 | 135 | 17:00 | Maijdee | 138 | 03:00 | 132 | 12:00
Banani | 135 | 02:00 | 126 | 12:00 | Manikganj | 137 | 02:00 | 126 | 12:00
Bangabhaban | 142 | 02:00 | 132 | 12:00 | Maniknagar | 142 | 03:00 | 132 | 12:00
Barapukuria | 139 | 03:00 | 125 | 18:00 | Matarbari | 133 | 03:00 | 114 | 12:00
Barguna | 140 | 04:00 | 135 | 19:00 | Matuail | 141.31 | 06:00 | 133.5 | 13:00
Barishal | 142 | 05:00 | 135 | 19:30 | Metrorail_Motijheel | 142 | 03:00 | 132 | 12:00
Barishal-230 | 142 | 04:00 | 135 | 13:00 | Metrorail_Uttara | 141 | 03:00 | 126 | 12:00
Baroaulia | 140 | 03:00 | 135 | 12:00 | Millgate | 141 | 04:00 | 127 | 12:00
Baroirhat | 136 | 00:00 | 132 | 12:00 | Mirpur | 140 | 03:00 | 126 | 12:00
Bashundhara | 135 | 02:00 | 125 | 12:00 | Mirzapur | 138 | 02:00 | 130 | 19:00
BashundharaCement | 139 | 05:00 | 135 | 17:00 | Mithapukur | 137 | 02:00 | 122 | 18:00
Beanibazar | 137 | 00:00 | 133 | 18:00 | MI_Cement | 139.3 | 05:00 | 124 | 12:00
Benapole | 136 | 04:00 | 120 | 18:00 | Modern | N/A | N/A | N/A | N/A
Bhaluka | 137 | 05:00 | 132 | 14:00 | Mogbazar | 139 | 05:00 | 129 | 13:00
Bhandaria | 140 | 05:00 | 134 | 18:00 | Mongla | 138 | 03:00 | 126 | 18:00
Bhangura | 139 | 00:00 | 130 | 18:30 | Motijheel | 142 | 02:00 | 132 | 12:00
Bheramara | 141 | 04:00 | 129 | 12:00 | Muktagacha | 135 | 04:00 | 129 | 19:30
Bheramara(GK) | 141 | 04:00 | 129 | 13:00 | Munshiganj | 140 | 04:00 | 132 | 12:00
Bhulta | 132 | 05:00 | 125 | 12:00 | Muradnagar | 141 | 03:00 | 132 | 12:00
Bog-Sherpur | 139 | 01:00 | 130 | 18:00 | Mymensingh | 136 | 08:00 | 127 | 19:00
Bogura | 138 | 01:00 | 130 | 18:00 | Naogaon | 135 | 01:00 | 125 | 18:00
Bogura-230 | 139 | 03:00 | 129 | 18:00 | Narail | 140 | 03:00 | 126 | 13:00
Brahmanbaria | 139 | 18:00 | 133 | 12:00 | Narinda | 142 | 03:00 | 132 | 12:00
Cantonment | 140 | 03:00 | 128 | 12:00 | Narshingdi | 140 | 22:00 | 128 | 19:00
Chandina | 143 | 07:00 | 134 | 12:00 | Natore | 138 | 03:00 | 128 | 18:30
Chandpur | 140 | 00:00 | 135 | 12:00 | Nawabganj | 140 | 04:00 | 128 | 12:00
Chandraghona | 141 | 04:00 | 136 | 12:00 | Netrakona | 131 | 15:00 | 124 | 19:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 138 | 00:00 | 134 | 18:00 | New | 140 | 03:00 | 127 | 12:00
Charsaidpur | 141 | 06:00 | 133 | 12:00 | Niamatpur | 140 | 00:00 | 134 | 18:00
Chauddagram | 140 | 03:00 | 132 | 12:00 | Noapara | 138 | 04:00 | 122 | 13:00
Chhatak | 137 | 02:00 | 130 | 18:00 | Pabna | 141 | 03:00 | 128 | 18:00
Chowmuhani | 135 | 00:00 | 130 | 13:00 | Palashbari | 136 | 04:00 | 122 | 18:00
Chuadanga | 142 | 04:00 | 125 | 13:00 | Panchagarh | 138 | 03:00 | 127 | 18:00
Coxsbazar | 132 | 02:00 | 118 | 12:00 | Patiya | 140 | 03:00 | 134 | 17:00
Cumilla(N) | 142 | 04:00 | 134 | 13:00 | Patuakhali | 138 | 03:00 | 135 | 12:00
Cumilla(S) | 142 | 07:00 | 126 | 16:00 | Payra | 140 | 03:00 | 137 | 12:00
Daganbhuiyan | 139 | 03:00 | 132 | 12:00 | PHP | 138 | 02:00 | 132 | 12:00
Daudkandi | 138 | 00:00 | 130 | 12:00 | Postogola | 140 | 05:00 | 126 | 12:00
DhakaUniversity | 135 | 04:00 | 126 | 12:00 | Purbachal | 135 | 03:00 | 126 | 12:00
Dhamrai | 139 | 00:00 | 129 | 12:00 | Purbasadipur | 134 | 04:00 | 121 | 18:00
Dhanmondi | 141.5 | 06:00 | 133.5 | 12:00 | Rahanpur | 140 | 00:00 | 135 | 18:00
Dohazari | 137 | 03:00 | 131 | 17:00 | Rahanpur-400 | 141 | 01:00 | 135 | 18:00
Faridpur | 140 | 03:00 | 132 | 12:00 | Rahim | 140 | 02:00 | 133 | 12:00
Fatullah | 142 | 04:00 | 125 | 12:00 | Rajbari | 140 | 05:00 | 132 | 12:00
Fenchuganj | 142 | 00:00 | 140 | 12:00 | Rajendrapur | 139 | 05:00 | 131 | 11:00
Feni | 137 | 03:00 | 130 | 13:00 | Rajshahi | 139 | 05:00 | 128 | 13:00
Feni-230 | 138 | 02:00 | 132 | 12:00 | Rajshahi-230 | 140 | 05:00 | 127 | 13:00
Ghatail | 135 | 05:00 | 128 | 12:00 | Ramganj | 137 | 00:00 | 132 | 11:00
Ghorashal | 139 | 06:00 | 128 | 18:30 | Rampur | 140 | 04:00 | 133 | 17:00
Goalpara | 140 | 03:00 | 130 | 13:00 | Rampura | 135 | 03:00 | 126 | 12:00
Gollamari | 138 | 00:00 | 130 | 12:00 | Rangamati | 140 | 04:00 | 135 | 12:00
Gopalganj | 141 | 02:00 | 134 | 12:00 | Rangpur | 136 | 02:00 | 126 | 18:00
Gopalganj-400 | 144 | 02:00 | 137 | 12:00 | Ruppur | 142 | 03:00 | 131 | 13:00
Gulshan | 135 | 04:00 | 126 | 12:00 | Saidpur | 135 | 15:00 | 123 | 18:00
Halishahar | 140 | 02:00 | 134 | 17:00 | Satkhira | 137 | 03:00 | 125 | 18:00
Haripur | 140 | 03:00 | 133 | 12:00 | Satmasjid | 140 | 03:00 | 130 | 12:00
HaripurSBU | 140 | 03:00 | 133 | 12:00 | Savar | 139 | 04:00 | 125 | 12:00
Hasnabad | 139 | 03:00 | 127 | 11:00 | SevenRings | 138 | 03:00 | 127 | 19:30
Hathazari | 141 | 05:00 | 135 | 12:00 | ShahCement | 141 | 06:00 | 133 | 12:00
Hatirjheel | 135 | 03:00 | 126 | 12:00 | Shahjadpur | 142 | 03:00 | 135 | 10:00
Ishurdi | 143 | 04:00 | 132 | 18:00 | Shahjibazar | 139 | 06:00 | 135 | 17:00
Jaldhaka | 134 | 05:00 | 120 | 18:00 | Shahmirpur | 141 | 06:00 | 135 | 17:00
Jamalpur | 136 | 08:00 | 124 | 19:30 | Shariatpur | 143 | 02:00 | 136 | 11:00
Jashore | 137 | 02:00 | 122 | 13:00 | Sherpur | 131 | 17:00 | 121 | 09:00
Jhenaidah | 142 | 04:00 | 111 | 18:00 | Shikalbaha | 130 | 04:00 | 124 | 12:00
Jhenaidah-230 | 141 | 02:00 | 129 | 12:00 | Shikalbaha-230 | 141 | 01:00 | 136 | 16:00
Joydebpur | 136 | 04:00 | 124 | 19:00 | Shitalakhya | 139.3 | 05:00 | 124 | 12:00
Joypurhat | 135 | 01:00 | 126 | 18:00 | Sholosohor | 141 | 03:00 | 135 | 12:00
Juldah | 139 | 03:00 | 134 | 17:00 | Shyampur | 138 | 07:00 | 128 | 12:00
Kabirpur | 141 | 04:00 | 125 | 12:00 | Shyampur-230 | 142 | 03:00 | 131 | 12:00
Kachua | 142 | 06:00 | 136 | 12:00 | Siddhirganj | 141 | 03:00 | 132 | 12:00
Kaliakoir | 143 | 04:00 | 132 | 12:00 | Sirajganj | 139 | 04:00 | 129 | 18:00
Kallyanpur | 141 | 03:00 | 128 | 12:00 | Sonargaon | 140 | 04:00 | 133 | 13:00
Kalurghat | 141 | 03:00 | 136 | 12:00 | Sreemongol | 139 | 02:00 | 136 | 11:00
Kamrangirchar | 138 | 04:00 | 124 | 12:00 | Sreepur | 140 | 03:00 | 134 | 19:00
Kaptai | 142 | 7:00 | 137 | 20:00 | Srinagar | 140 | 03:00 | 128 | 12:00
Kasba | 141 | 03:00 | 132 | 12:00 | SSM | 142 | 00:00 | 140 | 12:00
Kazla | 142 | 04:00 | 131 | 13:00 | Sunamganj | 135 | 05:00 | 131 | 18:00
Keranigonj | 140 | 04:00 | 128 | 12:00 | Sylhet | 138 | 02:00 | 133 | 13:00
Khagrachori | 140 | 02:00 | 134 | 12:00 | Sylhet-132 | 137 | 00:00 | 134 | 14:00
Khulna | 137 | 05:00 | 128 | 18:00 | Tangail | 135 | 04:00 | 126 | 12:00
Khulna(S) | 139 | 04:00 | 130 | 18:00 | Taraganj | 135 | 03:00 | 123 | 18:00
Khulshi | 139 | 07:00 | 134 | 12:00 | Tasnim | 140 | 03:00 | 133 | 13:00
Kishoreganj | 135 | 03:00 | 127 | 19:30 | Thakurgaon | 136 | 03:00 | 125 | 18:00
Kodda | 137 | 05:00 | 125 | 12:00 | TK | 141 | 05:00 | 136 | 12:00
KSRM | 140 | 07:00 | 134 | 13:00 | Tongi | 142 | 04:00 | 130 | 12:00
Kulaura | 142 | 01:00 | 138 | 18:00 | Ullahpara | 140 | 02:00 | 131 | 18:00
Kurigram | 133 | 03:00 | 121 | 18:00 | Ullon | 135 | 06:00 | 125 | 13:00
Kushtia | 137 | 00:00 | 121 | 18:00 | Uttara | 141 | 04:00 | 127 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division