## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 05-01-2026 | [28 empty] | Date: | 05-01-2026 | [28 empty] | Date: | 05-01-2026 | [28 empty] | Date: | 05-01-2026 | [28 empty] | Date: | 05-01-2026 | [17 empty] | Date: | 05-01-2026
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [17 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 37 | 668 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 300 | 320 | 0 | 0 | 0 | 194 | 0 | 0 | 80 | 0 | 0 | 15 | 0 | 96 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 50 | 156 | 0 | 5 | 0 | 0 | 30 | 0 | 0 | 158 | 0 | 19 | 0 | 167 | 0 | 0 | 0 | 4831 | 892 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 0 | 834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 140 | 220 | 0 | 256 | 280 | 0 | 4093 | 8924 | 97.39
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 650 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 230 | 280 | 0 | 0 | 0 | 198 | 0 | 0 | 50 | 0 | 0 | 10 | 0 | 82 | 0 | 0 | 0 | 305 | 0 | 0 | 29 | 20 | 149 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 158 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 4359 | 751 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 0 | 831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 140 | 220 | 0 | 256 | 300 | 0 | 3929 | 8288 | 97.38
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 650 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 230 | 280 | 0 | 0 | 0 | 198 | 0 | 0 | 50 | 0 | 0 | 10 | 0 | 86 | 0 | 0 | 0 | 315 | 0 | 0 | 29 | 20 | 138 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 160 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 4213 | 704 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 0 | 0 | 830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 100 | 180 | 0 | 252 | 285 | 0 | 3650 | 7863 | 97.38
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 650 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 230 | 280 | 0 | 0 | 0 | 193 | 0 | 0 | 50 | 0 | 0 | 10 | 0 | 80 | 0 | 0 | 0 | 305 | 0 | 0 | 29 | 20 | 136 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 158 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 4159 | 424 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 100 | 180 | 0 | 252 | 280 | 0 | 3356 | 7515 | 97.38
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 570 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 828 | 0 | 0 | 0 | 230 | 280 | 0 | 0 | 0 | 192 | 0 | 0 | 50 | 0 | 0 | 10 | 0 | 80 | 0 | 0 | 0 | 320 | 0 | 0 | 29 | 20 | 139 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 157 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 4093 | 239 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 0 | 837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 100 | 180 | 0 | 261 | 270 | 0 | 3125 | 7218 | 97.38
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 570 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 731 | 0 | 0 | 0 | 230 | 280 | 0 | 0 | 0 | 191 | 0 | 0 | 50 | 0 | 0 | 10 | 0 | 74 | 0 | 0 | 0 | 315 | 0 | 0 | 29 | 20 | 143 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 158 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 3984 | 239 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 100 | 180 | 0 | 254 | 250 | 0 | 3219 | 7203 | 97.37
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 570 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 773 | 0 | 0 | 0 | 325 | 280 | 0 | 0 | 0 | 198 | 0 | 0 | 50 | 0 | 0 | 5 | 0 | 84 | 0 | 0 | 0 | 320 | 0 | 0 | 32 | 20 | 143 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 158 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 4334 | 321 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 140 | 220 | 0 | 258 | 255 | 0 | 3438 | 7772 | 97.37
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 22 | 615 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 845 | 1 | 0 | 0 | 315 | 280 | 0 | 0 | 0 | 202 | 0 | 0 | 112 | 0 | 0 | 10 | 0 | 82 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 50 | 144 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 158 | 0 | 2 | 0 | 167 | 0 | 0 | 0 | 4654 | 518 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 385 | 0 | 0 | 0 | 835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0 | 0 | 0 | 0.07 | 145 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 140 | 220 | 0 | 250 | 275 | 0 | 3645.21 | 8299.21 | 97.37
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 475 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 22 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0.1 | 46 | 0 | 12 | 720 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1110 | 5 | 0 | 0 | 320 | 280 | 0 | 24 | 0 | 201 | 0 | 0 | 114 | 0 | 0 | 11 | 0 | 100 | 0 | 2 | 0 | 310 | 0 | 0 | 41 | 50 | 156 | 0 | 17 | 0 | 74 | 30 | 0 | 0 | 158 | 0 | 19 | 45 | 166 | 0 | 0.65 | 0 | 5274.75 | 471 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 438 | 0 | 0 | 0 | 1074.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.38 | 16 | 0 | 0 | 3.55 | 138 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0.35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.3 | 3 | 0.04 | 0 | 280 | 140 | 220 | 0 | 266 | 320 | 0 | 4130.3 | 9405.05 | 97.37
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 3 | 11 | 30 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0.16 | 46 | 0 | 6 | 830 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1160 | 9 | 0 | 0 | 295 | 360 | 0 | 27 | 0 | 190 | 10 | 0 | 114 | 0 | 0 | 11 | 0 | 106 | 0 | 4 | 0 | 320 | 0 | 0 | 41 | 50 | 161 | 1 | 17 | 0 | 75 | 30 | 0 | 0 | 158 | 0 | 19 | 56 | 165 | 0 | 2.29 | 0 | 5553.95 | 422 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 580 | 0 | 0 | 0 | 1170.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.49 | 16 | 0 | 0 | 8.84 | 133 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0.75 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.8 | 8 | 0.11 | 0 | 277 | 140 | 220 | 0 | 288 | 440 | 0 | 4463.58 | 10017.53 | 97.36
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 3 | 108 | 30 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0.31 | 46 | 0 | 6 | 750 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1160 | 17 | 0 | 0 | 315 | 360 | 0 | 26 | 0 | 198 | 10 | 0 | 112 | 0 | 0 | 11 | 0 | 104 | 0 | 8 | 0 | 305 | 0 | 0 | 41 | 50 | 133 | 1 | 17 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 56 | 165 | 0 | 4.3 | 3 | 5479.61 | 423 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 556 | 0 | 0 | 0 | 1023.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.17 | 12 | 0 | 0 | 16.96 | 141 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 1.35 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 1.3 | 11 | 0.19 | 0 | 236 | 100 | 180 | 0 | 266 | 508 | 0 | 4223 | 9702.61 | 97.36
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 7 | 90 | 30 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0.63 | 46 | 0 | 6 | 830 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1160 | 19 | 0 | 0 | 315 | 335 | 0 | 26 | 0 | 199 | 26 | 0 | 111 | 0 | 0 | 12 | 0 | 112 | 0 | 9 | 0 | 315 | 0 | 0 | 41 | 50 | 142 | 1 | 17 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 56 | 165 | 0 | 7.15 | 15 | 5644.78 | 423 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 472 | 0 | 0 | 0 | 988.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.43 | 18 | 0 | 0 | 11.63 | 168 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0.98 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 1.5 | 21 | 0.46 | 0 | 239 | 110 | 220 | 0 | 256 | 514 | 0 | 4218.89 | 9863.67 | 97.36
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 50.5 | 55 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 225 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 6 | 90 | 30 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0.57 | 46 | 0 | 9 | 830 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1163 | 20 | 0 | 15 | 350 | 340 | 0 | 35 | 0 | 203 | 30 | 0 | 111 | 7 | 0 | 13 | 0 | 124 | 0 | 12 | 0 | 310 | 0 | 0 | 41 | 50 | 142 | 2 | 17 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 56 | 165 | 0 | 5.45 | 18 | 5866.52 | 423 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 480 | 0 | 0 | 0 | 1080.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.85 | 18 | 0 | 0 | 10.62 | 168 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0.95 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 1.8 | 19 | 0.48 | 0 | 278 | 140 | 220 | 0 | 254 | 540 | 0 | 4430.56 | 10297.08 | 97.36
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 41.5 | 55 | 3 | 0 | 15 | 0 | 4 | 30 | 0 | 225 | 0 | 485 | 0 | 0 | 0 | 0 | 0 | 5 | 108 | 23 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 4 | 0 | 0 | 0 | 0 | 0.6 | 46 | 0 | 17 | 830 | 0 | 0 | 0 | 0 | 1 | 172 | 0 | 0 | 0 | 1160 | 18 | 0 | 35 | 305 | 295 | 0 | 35 | 0 | 195 | 36 | 0 | 108 | 17 | 0 | 17 | 0 | 128 | 0 | 11 | 0 | 310 | 0 | 0 | 41 | 50 | 152 | 1 | 17 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 56 | 165 | 0 | 7.8 | 18 | 5900.9 | 434 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 592 | 0 | 0 | 0 | 1259.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.43 | 20 | 0 | 0 | 9.39 | 182 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0.89 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 1.8 | 20 | 0.46 | 0 | 278 | 140 | 220 | 0 | 303 | 552 | 0 | 4838.18 | 10739.08 | 97.35
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 54 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 475 | 0 | 0 | 0 | 0 | 0 | 6 | 108 | 25 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 10 | 0 | 0 | 0 | 0 | 0.53 | 46 | 0 | 11 | 835 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1160 | 16 | 0 | 35 | 315 | 310 | 0 | 35 | 0 | 197 | 34 | 0 | 108 | 0 | 0 | 15 | 0 | 118 | 0 | 13 | 0 | 315 | 0 | 0 | 41 | 50 | 137 | 1 | 17 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 56 | 158 | 0 | 6.43 | 18 | 5820.96 | 434 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 607 | 0 | 0 | 0 | 1154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.52 | 19 | 0 | 0 | 6.61 | 167 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0.64 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 1.5 | 14 | 0.38 | 0 | 250 | 100 | 180 | 0 | 250 | 520 | 0 | 4474.65 | 10295.61 | 97.35
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 54 | 55 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 225 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 3 | 108 | 31 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 6 | 0 | 0 | 0 | 0 | 0.35 | 46 | 0 | 8 | 832 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1120 | 12 | 0 | 35 | 300 | 305 | 0 | 35 | 0 | 198 | 37 | 0 | 110 | 0 | 0 | 17 | 0 | 116 | 0 | 7 | 0 | 315 | 0 | 0 | 41 | 50 | 142 | 1 | 17 | 0 | 75 | 30 | 0 | 0 | 158 | 0 | 19 | 35 | 148 | 0 | 3.61 | 18 | 5661.96 | 434 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 558 | 0 | 0 | 0 | 1020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.98 | 14 | 0 | 0 | 3.78 | 168 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0.38 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 1.3 | 10 | 0.26 | 0 | 171 | 100 | 180 | 0 | 264 | 450 | 0 | 4148.7 | 9810.66 | 97.35
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 54 | 55 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 225 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 2 | 108 | 31 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14 | 0 | 0 | 0 | 0 | 0.11 | 46 | 0 | 8 | 770 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1042 | 7 | 0 | 8 | 300 | 280 | 0 | 44 | 0 | 211 | 0 | 0 | 111 | 0 | 0 | 11 | 0 | 110 | 0 | 13 | 0 | 310 | 0 | 0 | 41 | 50 | 144 | 0 | 17 | 0 | 75 | 30 | 0 | 0 | 158 | 0 | 19 | 24 | 148 | 0 | 1.38 | 14 | 5450.49 | 434 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 438 | 0 | 0 | 0 | 1037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.65 | 11 | 0 | 0 | 1.42 | 170 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0.15 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1.1 | 5 | 0.12 | 0 | 178 | 100 | 180 | 0 | 254 | 450 | 0 | 4058.44 | 9508.93 | 97.35
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 54 | 55 | 0 | 0 | 0 | 15 | 0 | 25 | 0 | 225 | 0 | 470 | 0 | 5 | 0 | 0 | 0 | 0 | 108 | 28 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 2 | 0 | 0 | 0 | 5 | 0 | 46 | 0 | 13 | 770 | 0 | 0 | 0 | 0 | 2 | 173 | 0 | 0 | 0 | 1048 | 1 | 0 | 0 | 300 | 280 | 0 | 44 | 0 | 202 | 0 | 0 | 112 | 3 | 0 | 11 | 0 | 108 | 0 | 2 | 0 | 320 | 0 | 0 | 41 | 50 | 160 | 0 | 17 | 0 | 77 | 30 | 0 | 0 | 158 | 0 | 19 | 28 | 141 | 0 | 0 | 18 | 5558 | 434 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 459 | 0 | 0 | 0 | 1158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37 | 1 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.01 | 0 | 0 | 11 | 0 | 5 | 0 | 0 | 0 | 0.2 | 2 | 0.01 | 0 | 222 | 140 | 220 | 0 | 284 | 478 | 0 | 4425.59 | 9983.59 | 97.34
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 54 | 55 | 24 | 32 | 45 | 15 | 38 | 47 | 0 | 225 | 0 | 460 | 0 | 35 | 0 | 0 | 0 | 0 | 142 | 25 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 14 | 0 | 0 | 0 | 36 | 0 | 46 | 0 | 20 | 830 | 0 | 0 | 0 | 0 | 25 | 173 | 0 | 0 | 0 | 1160 | 0 | 50 | 0 | 300 | 280 | 0 | 44 | 0 | 201 | 0 | 0 | 111 | 51 | 0 | 11 | 0 | 120 | 0 | 0 | 0 | 320 | 0 | 0 | 41 | 50 | 163 | 0 | 17 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 56 | 138 | 0 | 0 | 18 | 6141 | 434 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 482 | 0 | 0 | 0 | 1451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 50 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 140 | 220 | 0 | 308 | 510 | 0 | 4917 | 11058 | 97.34
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 47.9 | 0 | 45 | 0 | 0 | 0 | 35 | 35 | 0 | 225 | 0 | 455 | 0 | 35 | 0 | 0 | 0 | 0 | 142 | 25 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 17 | 0 | 0 | 0 | 36 | 0 | 46 | 0 | 27 | 830 | 0 | 0 | 0 | 0 | 34 | 173 | 0 | 0 | 0 | 1170 | 0 | 0 | 0 | 300 | 315 | 0 | 44 | 0 | 200 | 0 | 0 | 112 | 34 | 0 | 19 | 0 | 120 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 50 | 159 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 56 | 139 | 0 | 0 | 0 | 5982.9 | 434 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 597 | 0 | 0 | 0 | 1442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 140 | 220 | 0 | 305 | 558 | 0 | 4996 | 10978.9 | 97.34
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 35 | 33 | 0 | 225 | 0 | 498 | 0 | 35 | 0 | 0 | 0 | 0 | 142 | 25 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 17 | 0 | 0 | 0 | 36 | 0 | 46 | 0 | 29 | 830 | 0 | 0 | 0 | 0 | 34 | 173 | 0 | 0 | 0 | 1172 | 0 | 0 | 0 | 275 | 320 | 0 | 44 | 0 | 202 | 0 | 0 | 112 | 33 | 0 | 13 | 0 | 112 | 0 | 0 | 0 | 325 | 0 | 0 | 41 | 50 | 152 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 56 | 139 | 0 | 0 | 0 | 5980 | 434 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 1443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 140 | 220 | 0 | 304 | 555 | 0 | 5013 | 10993
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 34.2 | 0 | 34 | 0 | 0 | 0 | 35 | 32 | 0 | 225 | 0 | 485 | 0 | 35 | 0 | 0 | 0 | 0 | 142 | 25 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 17 | 0 | 0 | 0 | 36 | 0 | 46 | 0 | 25 | 830 | 0 | 0 | 0 | 0 | 34 | 173 | 0 | 0 | 0 | 1162 | 0 | 0 | 0 | 275 | 305 | 0 | 44 | 0 | 193 | 0 | 0 | 112 | 34 | 0 | 19 | 0 | 116 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 50 | 155 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 56 | 143 | 0 | 0 | 0 | 5921.2 | 434 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 613 | 0 | 0 | 0 | 1445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 140 | 220 | 0 | 309 | 553 | 0 | 5011 | 10932.2 | 97.34
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 31.4 | 0 | 34 | 0 | 0 | 0 | 35 | 30 | 0 | 225 | 0 | 475 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 24 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 36 | 0 | 46 | 0 | 31 | 830 | 0 | 0 | 0 | 0 | 34 | 173 | 0 | 0 | 0 | 1163 | 0 | 0 | 0 | 285 | 305 | 0 | 44 | 0 | 193 | 0 | 0 | 112 | 32 | 0 | 19 | 0 | 112 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 50 | 153 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 45 | 143 | 0 | 0 | 0 | 5716.4 | 434 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607 | 0 | 0 | 0 | 1457.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 140 | 220 | 0 | 309 | 548 | 0 | 4966.44 | 10682.84 | 97.33
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 34 | 750 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1117 | 0 | 0 | 0 | 310 | 305 | 0 | 44 | 0 | 194 | 0 | 0 | 112 | 0 | 0 | 19 | 0 | 96 | 0 | 0 | 0 | 305 | 0 | 0 | 41 | 50 | 149 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 35 | 138 | 0 | 0 | 0 | 5311 | 434 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 591 | 0 | 0 | 0 | 1380.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 140 | 220 | 0 | 295 | 500 | 0 | 4729.17 | 10040.17 | 97.33
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 35 | 654 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 285 | 305 | 0 | 44 | 0 | 190 | 0 | 0 | 111 | 0 | 0 | 11 | 0 | 100 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 50 | 155 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 157 | 0 | 19 | 24 | 138 | 0 | 0 | 0 | 5091 | 434 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483 | 0 | 0 | 0 | 1221.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 140 | 220 | 0 | 255 | 400 | 0 | 4320.84 | 9411.84 | 97.33
Total KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8316000 | 0 | 0 | 573120 | 423000 | 166176 | 54240 | 71007 | 54471 | 156805 | 243360 | 0 | 5020800 | 0 | 10242403 | 0 | 128188 | 0 | 0 | 0 | 35835 | 1244400 | 537600 | 325800 | 0 | 0 | 0 | 0 | 0 | 0 | 536640 | 86898 | 0 | 0 | 0 | 168000 | 3480 | 1097100 | 0 | 490080 | 17803636.36 | 0 | 0 | 0 | 0 | 171454 | 4176475 | 0 | 0 | 0 | 24725452 | 126360 | 95345 | 117091 | 7061500 | 7577800 | 0 | 639594 | 0 | 4903000 | 180000 | 0 | 2241217 | 243360 | 0 | 314160 | 0 | 2439360 | 0 | 87400 | 0 | 7608500 | 0 | 0 | 897000 | 1023000 | 3556636.36 | 10048 | 308184 | 0 | 1253760 | 569664 | 0 | 0 | 3427140 | 0 | 326400 | 760800 | 3421440 | 1750 | 38690 | 150960 | 126232579.72 | 10859636 | 8800128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179280 | 11694544 | 0 | 0 | 0 | 26277659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57672 | 150340 | 0 | 0 | 73504 | 3926727 | 0 | 0 | 0 | 0 | 0 | 8885527 | 0 | 6720 | 0 | 0 | 166656 | 34234 | 177340 | 0 | 0 | 0 | 12266.16 | 113040 | 2533 | 0 | 5542000 | 2986000 | 5226800 | 0 | 6516363 | 10660363.64 | 0 | 102349332.8 | 228581912.52

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 06-01-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-01-2026 | during | 06-01-2026 | during | 06-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 346 | 343 | 412 | 412 | 392 | 392 | FGMO, Gas Shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 450 | 450 | 240 | 240 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 50.5 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 32 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 38 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 30 | 25 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 15 | 15.1 | 15.1 | 15.1 | 15.1 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 45 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 24 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 15 | 47 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 6 | 0 | 10 | 0 | 10 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 460 | 460 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 90 | 142 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1292.5 | 1555 | 5332.45 | 5322.45 | 2443.13 | 2433.13
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 | 46 | 46 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 160 | 173 | 150 | 150 | 150 | 150 | Plant availability less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 25 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 56 | 56 | 56 | 56 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 14 | 50 | 50 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 10 | 10 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 9 | 20 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0.57 | 0 | 3.11 | 0 | 3.11 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 36 | 100 | 100 | 20 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1163 | 1160 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 14 | 26 | 15 | 29 | 15 | 29 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 830 | 830 | 720 | 720 | 830 | 830 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2242.57 | 2330 | 3519.97 | 3515.86 | 3147.61 | 3223.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 203 | 201 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 340 | 280 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 318.81 | 318.81 | 0 | 0 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 350 | 300 | 393 | 393 | 363 | 363 | FGMO, Gas Shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 30 | 0 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 15 | 0 | 195 | 195 | 80 | 80 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 35 | 44 | 51 | 51 | 51 | 51 | Machine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 50 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 111 | 111 | 163 | 163 | 115 | 115 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 7 | 51 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 124 | 120 | 84 | 84 | 128 | 128 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 11 | 24.5 | 24.5 | 24.5 | 24.5 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 12 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1240 | 1168 | 2699.56 | 2649.56 | 2111.75 | 2061.75
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-01-2026 | during | 06-01-2026 | during | 06-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 165 | 138 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0 | 0 | 1.5 | 0 | 1.5 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 56 | 56 | 60 | 60 | 60 | 60 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 19 | 20 | 20 | 20 | 20 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 5.45 | 0 | 25 | 0 | 25 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 18 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 263.45 | 231 | 340.5 | 314 | 330.5 | 304
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 41 | 41 | 41 | 41 | 41 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 50 | 50 | 60 | 60 | 60 | 60 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 142 | 163 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 78 | 81 | 81 | 81 | 81 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 158 | 158 | 158 | 158 | 158 | 158 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 320 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 828 | 857 | 899 | 899 | 849 | 849
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 423 | 434 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 390 | 396 | 410 | 410 | 369 | 369 | FGMO
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 21 | 0 | 63 | 0 | 63 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 480 | 482 | 617.1 | 617.1 | 617.1 | 617.1 | U-2 Under Maintenance
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1314 | 1312 | 2952.1 | 2889.1 | 2156.2 | 2093.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 254 | 308 | 622 | 622 | 622 | 622 | Machine Problem
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 140 | 140 | 136 | 136 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 540 | 510 | 605 | 605 | 575 | 575 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 278 | 279 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.48 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1432.48 | 1457 | 2151 | 2151 | 1968 | 1968
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 9.85 | 0 | 20 | 0 | 20 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 168 | 185 | 214 | 214 | 192.6 | 192.6 | Foggy Weather
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 369 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0.95 | 0 | 2.4 | 0 | 2.4 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1080.86 | 1451 | 1435.88 | 1435.88 | 1356 | 1356 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 10.62 | 0 | 40 | 1 | 40 | 1 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 18 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1657.28 | 2050 | 3051.27 | 2889.87 | 2468.61 | 2307.21
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 48 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 1.8 | 0 | 3.2 | 0 | 3.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 6 | 0 | 24 | 0 | 24 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 19 | 0 | 85 | 0 | 85 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 26.8 | 98 | 374.2 | 262 | 340.2 | 228
System Total |  |  |  |  | 28823.2 | 28382.248 | 10297.08 | 11058 | 21320.05 | 20892.84 | 15815 | 15467.79
Forecast Scenario (06-01-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14152.42 |  | 23748.5389 |  | 39020
|  |  |  | 1:00 | 8380 |  | 0 |  | 8380
|  |  |  | 2:00 | 7960 |  | 0 |  | 7960
|  |  |  | 3:00 | 7610 |  | 0 |  | 7610
|  |  |  | 4:00 | 7310 |  | 0 |  | 7310
|  |  |  | 5:00 | 7300 |  | 0 |  | 7300
|  |  |  | 6:00 | 7870 |  | 0 |  | 7870
|  |  |  | 7:00 | 8390 |  | 0 |  | 8390
|  |  |  | 8:00 | 9500 |  | 0 |  | 9500
|  |  |  | 9:00 | 10110 |  | 0 |  | 10110
|  |  |  | 10:00 | 9800 |  | 0 |  | 9800
|  |  |  | 11:00 | 9960 |  | 0 |  | 9960
|  |  |  | 12:00 | 10390 |  | 0 |  | 10390
|  |  |  | 13:00 | 10830 |  | 0 |  | 10830
|  |  |  | 14:00 | 10390 |  | 0 |  | 10390
|  |  |  | 15:00 | 9910 |  | 0 |  | 9910
|  |  |  | 16:00 | 9600 |  | 0 |  | 9600
|  |  |  | 17:00 | 10080 |  | 0 |  | 10080
|  |  |  | 18:00 | 11150 |  | 0 |  | 11150
|  |  |  | 18:30 | 11110 |  | 0 |  | 11110
|  |  |  | 19:00 | 11070 |  | 0 |  | 11070
|  |  |  | 19:30 | 11090 |  | 0 |  | 11090
|  |  |  | 20:00 | 11030 |  | 0 |  | 11030
|  |  |  | 21:00 | 10780 |  | 0 |  | 10780
|  |  |  | 22:00 | 10200 |  | 0 |  | 10200
|  |  |  | 23:00 | 9300 |  | 0 |  | 9300
Probable Maximum Temperature: |  |  | 20.00°C
Probable Maximum Demand at Day Peak: |  |  | 10390.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11150.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11150.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 233.07242 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:49 hrs on 06-01-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 05-01-2026
Power Supply Scenario
| Day Peak Generation |  |  | 10297.08 | MW | 12:00 Hr. | Energy Generated |  |  | 228.5819 |  | MKWHr.
| Day Peak Demand |  |  | 10297.08 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11058 | MW | 18:00 Hr. | Energy Demand |  |  | 228.5819 |  | MKWHr.
| Evening Peak Demand |  |  | 11058 | MW | 18:00 Hr. | Maximum Temperature |  |  | 18.8 |  | °C
| Minimum Generation of the Day |  |  | 7203 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 764.52 |  | MMCFD
| Maximum Generation of the Day |  |  | 11058 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.4175 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 24.4426 | 0 | 3.1148 | 0 | 0 | 0.035835 | 0 | 0 | 27.5932 | Gas | 104.034 | Gas | 365058018.4076
| Chattogram Zone |  |  | 4.6666 | 42.5291 | 0.42635 | 0 | 1.0971 | 0.12984 | 0 | 0.53664 | 49.3856 | Coal | 76.9424 | Coal | 505182985.792
| Cumilla Zone |  |  | 23.0344 | 0 | 0.3387 | 0 | 0 | 0.0874 | 2.4394 | 0 | 25.8998 | HFO | 5.462 | HFO | 96753263.13
| Mymensingh Zone |  |  | 3.4214 | 0 | 1.2382 | 0 | 0 | 0.04044 | 0 | 0 | 4.7 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 18.6439 | 0 | 0 | 0 | 0 | 0.010048 | 0 | 0 | 18.6539 | Hydro | 1.0971 | Hydro | 109710
| Khulna Zone |  |  | 8.8001 | 11.6945 | 0 | 0 | 0 | 0.17928 | 10.8596 | 0 | 31.5336 | Solar | 0.93315 | Solar | 14594954.312
| Barishal Zone |  |  | 8.2128 | 22.7187 | 0 | 0 | 0 | 0.002533 | 0 | 0 | 30.9341 | Import | 39.5767 | Import | 248758116.04
| Rajshahi Zone |  |  | 12.8123 | 0 | 0 | 0 | 0 | 0.28824 | 26.2777 | 0 | 39.3781 | Wind | 0.53664 | Wind | 7893974.4
| Rangpur Zone |  |  | 0 | 0 | 0.344 | 0 | 0 | 0.15954 | 0 | 0 | 0.50354
| Total |  |  | 104.034 | 76.9424 | 5.462 | 0 | 1.0971 | 0.93315 | 39.5767 | 0.53664 | 228.5819
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 365058018.4076 |  | Hydro | 109710
|  |  |  | Coal | 505182985.792 |  | Solar | 14594954.312
|  |  |  | HFO | 96753263.13 |  | Import | 248758116.04
|  |  |  | HSD | 0 |  | Wind | 7893974.4
[5 empty] | Total: | 123,83,51,022 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 10.8596 | Peak Hr Flow | 434.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 27196363.64 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.2777 | Peak Hr Flow | 1451.00 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1390 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.4394 | Peak Hr Flow | 120.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1572 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 39.5767 | Peak Hr Flow | 2005.00 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4063
|  |  |  | Chattogram |  | 0 |  | 1072
|  |  |  | Cumilla |  | 0 |  | 966
|  |  |  | Mymensingh |  | 0 |  | 911
|  |  |  | Sylhet |  | 0 |  | 394
|  |  |  | Khulna |  | 0 |  | 1319
|  |  |  | Barishal |  | 0 |  | 314
|  |  |  | Rajshahi |  | 0 |  | 1022
|  |  |  | Rangpur |  | 0 |  | 780
|  |  |  | Total |  | 0 |  | 10841
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:16 | 16:22 | Rajshahi 230/132/33kV S/S 230 Kv BIPTC Ckt-01 Scheduled S/D Due to Annual Maintenance.
| 08:19 | 17:01 | Gopalganj 400/132kV S/S 400kV Amtoli Ckt-2 Scheduled S/D Due to Annual Maintenance
| 08:22 | 10:43 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 Project Work S/D from Thakurgaon 132/33kV end
Due to EPVTL-Thakurgaon 01 Ckt. Reconductoring under KEC International Limited, India.
| 08:22 | 17:16 | Dhamrai-Kaliakoir 132 kV Ckt-1 Scheduled S/D from Dhamrai 132/33kV end Due to Annual
maintenance
| 08:24 | 10:42 | Sylhet-Sylhet (South) 132KV Ckt-2 Scheduled S/D from Sylhet 132/33kV end Due to GIS
Project work Purpose.
| 08:40 | 16:39 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 Scheduled S/D Due to Annual
Maintenance work
| 08:40 | 16:39 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 Scheduled S/D Due to Annual
Maintenance work
| 08:43 | 16:42 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Scheduled S/D from Shahjibazar 132/33kV end Due to
Annual Maintenance and from Brahmanbaria 132/33kVend.
| 08:51 | 16:37 | Aminbazar 400/230/132kV S/S Gopalganj-1 Scheduled S/D Due to Annual maintenance
| 08:52 | 16:35 | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-1 Scheduled S/D Due to Annual
| 08:52 | 16:21 | HVDC Bheramera- Rajshahi 230kV Ckt-1 Scheduled S/D from BIPTC end Due to Shutdown is
taken from Rajshahi end
| 08:55 |  | Bheramara HVDC Pole-2 was shutdown due to annual maintenance purpose
| 08:55 | 13:55 | Jhenaidah-Khulna 230kV Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end. and from
Jhenaidah 230/132kV end Due to Annual Maintenance
| 08:56 | 17:02 | Cox'sbazar-Dohazari 132 kV Ckt-1 Scheduled S/D from Coxsbazar 132/33kV end Due to Annual
Maintenance of Doh- Cox Ckt-1 Dohazari Side. and from Dohazari 132/33kV end Due to Annual
maintenance.
| 09:01 | 16:50 | Kallyanpur-Lalbag 132kV Ckt-2 Scheduled S/D from Kallyanpur 132/33kV end Due to Annual
Maintenance.
| 09:04 |  | Kurigram-Lalmonirhat 132kV Ckt-1 Project Work S/D from Kurigram 132/33kV end.
| 09:04 | 15:13 | Ruppur 132/11kV S/S TR-02 LT Scheduled S/D
| 09:05 | 17:03 | Dhamrai 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Annual maintenance
| 09:05 | 17:02 | Dhamrai 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Annual maintenance.
| 09:05 |  | Kurigram-Rangpur 132kV Ckt-1 Scheduled S/D from Rangpur 132/33kV end Due to gantry
piling work
| 09:06 | 15:08 | Ruppur 132/11kV S/S TR-02 HT Scheduled S/D Due to Annual maintenance work
| 09:25 | 16:41 | Tangail 132/33kV S/S Kaliakair-1 Scheduled S/D Due to Schedule S/D for Deadline Checking.
| 09:26 | 16:18 | Chowmuhani-Feni 132 kV Ckt-1 Scheduled S/D from Feni 132/33kV end Due to S/D Taken for
AMS=2025-26 (Bay)
| 09:27 | 15:50 | Goalpara 132/33kV S/S Goalpara-NWPGCL Scheduled S/D Due to Annual Maintenance.
| 09:33 | 16:27 | Madanganj 132/33kV S/S Madanganj -Haripur 132 kv Ckt-2 Scheduled S/D Due to Annual
maintenance
| 09:33 | 16:32 | Tongi 230/132/33kV S/S T-01 LT Scheduled S/D Due to Annual maintenance
| 09:34 | 16:32 | Tongi 230/132/33kV S/S T-01 HT Scheduled S/D Due to Annual maintenace
| 09:35 | 12:57 | Shyampur-Shyampur(New) 132kV Ckt-2 Scheduled S/D from Shyampur 230/132kV end Due to
Annual maintenance at 132kV Shyampur SS DPDC end.
| 09:40 | 16:27 | Haripur 230/132kV S/S Madanganj-2 Scheduled S/D Due to Annual Maintenace
| 09:49 | 15:50 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Forced S/D Due to order by NLDC
| 09:51 | 19:03 | Chowmuhani-Feni 132 kV Ckt-1 Forced S/D from Daganbhuiyan 132/33kV end Due to shutdown
for Chowmuhoni Grid Work and from Chowmuhani 132/33kV end Due to Chowmuhani -
Daganbhuiyan ckt-1 OPGW replacement .
| 09:55 | 17:37 | Siddhirganj 230/132kV S/S 335MW EGCB 1 Scheduled S/D Due to EMERGENCY MAINTENANCE WORK
| 09:57 | 11:39 | Agargaon 230/132kV S/S 230kV Transformer-2 ( 715T2) LT Scheduled S/D Due to Relay Testing
| 09:58 | 11:36 | Agargaon 230/132kV S/S 230kV Transformer-2 ( 715T2) HT Scheduled S/D Due to Relay Testing
| 10:04 | 17:40 | Bhaluka-Mymensingh 132 kV Ckt-1 Scheduled S/D from Mymensingh 132/33kV end Due to Dead
line checking by Bhaluka Grid. and from Bhaluka 132/33kV end Due to Annual maintenance
| 10:05 | 16:05 | Bog-Sherpur 132/33kV S/S Transformer-3 (424T) LT Scheduled S/D Due to Annual Maintenance
| 10:06 | 16:04 | Bog-Sherpur 132/33kV S/S Transformer-3 (424T) HT Scheduled S/D Due to Annual Maintenance
| 10:21 | 20:07 | Bhaluka 132/33kV S/S Sreepur Ckt- 01 Scheduled S/D
| 10:22 | 20:05 | Sreepur 230/132/33kV S/S Sreepur-Valuka Ckt-1 Scheduled S/D Due to Annual Maintenance.
| 10:33 | 13:46 | Keranigonj 230/132/33kV S/S 132 kV Hasnabad Ckt. 1 Forced S/D Due to The rope falls on
the 132kV line.
| 11:08 | 14:18 | Satkhira 132/33kV S/S Transformer-1 (T-1) HT Scheduled S/D Due to Due to annual
maintenance work
| 11:08 | 14:20 | Satkhira 132/33kV S/S Transformer-1 (T-1) LT Scheduled S/D Due to Due to annual | [7 empty] | 5.0MW load
|  |  | maintenance work | [7 empty] | interrup.
| 11:19 |  | Muradnagar 132/33kV S/S 132KV Transformar-01 LT Forced S/D Due to PBS newly constructed
33 KV ss commissioning work.
| 11:20 |  | Muradnagar 132/33kV S/S 132KV Transformar-01 HT Forced S/D Due to PBS newly constructed
33 KV ss commissioning work
| 11:35 |  | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 Project Work S/D from Thakurgaon 132/33kV end
Due to Reconductoring works
| 11:59 | 12:32 | Agargaon 230/132kV S/S 132kV Transformer-2 (415T2) LT Scheduled S/D Due to Relay test
| 12:00 | 12:31 | Agargaon 230/132kV S/S 132kV Transformer-2 (415T2) HT Scheduled S/D Due to Relay test
| 12:00 |  | Day peak generation 10291 MW
| 12:32 | 13:21 | Agargaon 230/132kV S/S 132kV Transformer-1 (405T1) HT Scheduled S/D Due to Relay test
| 12:33 | 13:22 | Agargaon 230/132kV S/S 132kV Transformer-1 (405T1) LT Scheduled S/D Due to Relay test
| 13:48 | 15:10 | Agargaon 230/132kV S/S 230kV Transformer-1 ( 705T1) HT Scheduled S/D Due to Relay Testing
| 13:49 | 15:11 | Agargaon 230/132kV S/S 230kV Transformer-1 ( 705T1) LT Scheduled S/D Due to Relay Testing
|  | 14:35 | Sholosohor 132/33kV S/S Sholoshahar-Khulshi Ckt-1 is restored.
| 15:05 | 16:38 | Satkhira 132/33kV S/S Transformer-2 (T-2) HT Scheduled S/D
| 15:05 | 16:39 | Satkhira 132/33kV S/S Transformer-2 (T-2) LT Scheduled S/D
| 15:12 | 17:03 | Cox'sbazar-Dohazari 132 kV Ckt-1 Scheduled S/D from Coxsbazar 132/33kV end Due to Annual
maintenance
| 15:57 | 17:20 | Bogura 230/132kV S/S 230KV Main 2 Forced S/D Due to 230kv sirajganj ckt-01 main CB
problem.
|  | 16:40 | Mirpur 132/33kV S/S T2 HT is restored.
|  | 16:40 | Mirpur 132/33kV S/S T2 LT is restored.
|  | 17:20 | Bogura-Sirajganj 230 kV Ckt-1 is restored.
| 17:45 | 19:29 | Siddhirganj 230/132kV S/S 335MW EGCB 2 Scheduled S/D Due to emergency maintence
maintenance work
|  | 17:50 | Bibiyana-Fenchuganj 230 kV Ckt-1 is restored.
| 18:00 |  | Evening Peak Generation is 11058 MW.
| 18:08 | 19:14 | Bibiyana-Fenchuganj 230 kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
maintenace work of Bibiyana grid end
|  | 18:39 | Ghorasal-Joydeb-B 132kV Ckt-2 is restored.
| 23:20 |  | BIPTC S/S 10CF11 Tripped showing 87.1 (Differential Relay). relays Due to Impedance 21R
Trip.
| 01:58 |  | Bheramara 410 MW CCPP, FGMO is OFF with remarks:- FGMO Off @ 01:56 AM
| 07:13 |  | Bheramara 410 MW CCPP, FGMO is ON with remarks:-
| 07:33 |  | Ghorasal-Joydeb-B 132kV Ckt-2 Scheduled S/D from Joydebpur 132/33kV end Due to OPGW
wire stringing work by OFCN.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 05-01-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 343 | 8316000 | FGMO, Gas Shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5020800 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 54471 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 573120 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 32 | 54240 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 38 | 156805 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 128188 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 25 | 537600 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 325800 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 45 | 71007 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 24 | 166176 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 47 | 243360 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 35835 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 423000 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 460 | 10242403 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1244400 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1555 | 27593205
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 126360 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1097100 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 173 | 4176475 | Plant availability less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 25 | 171454 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 14 | 86898 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 490080 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 3480 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 36 | 168000 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1160 | 24725452 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 26 | 536640 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 830 | 17803636.36 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 2330 | 49385575.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 201 | 4903000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 280 | 7577800 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 300 | 7061500 | FGMO, Gas Shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 180000 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 117091 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 639594 | Machine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 50 | 95345 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 111 | 2241217 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 243360 | -
| Import (Tripura) |  | Import | 0 | 160 | 120 | 2439360 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 11 | 314160 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 87400 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1168 | 25899827
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 138 | 3421440 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 1750 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 56 | 760800 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 326400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 38690 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 150960 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 231 | 4700040
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 10048 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 897000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 50 | 1023000 | machine problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3556636.36 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 569664 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1253760 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 158 | 3427140 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 308184 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7608500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 857 | 18653932.36
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 434 | 10859636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 396 | 8800128 | FGMO
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 179280 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 482 | 11694544 | U-2 Under Maintenance
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1312 | 31533588
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 308 | 6516363 | Machine Problem
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 140 | 2986000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 510 | 10660363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5226800 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 279 | 5542000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2533 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1457 | 30934059.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 57672 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 185 | 3926727 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8885527 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 6720 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1451 | 26277659 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 73504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 150340 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2050 | 39378149
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 48 | 177340 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 12266.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 166656 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 34234 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 113040 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 98 | 503536.16
Eastern Grid Total |  |  |  |  | 17398.245 | 6141 | 126232579.72
Western Grid Total |  |  |  |  | 10984.003 | 4917 | 102349332.8
National Grid Total |  |  |  |  | 28382.248 | 11058 | 228581912.52
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 05-01-2026
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7405.63 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3435.4 | MW
i) Dhaka area |  |  | 4062.83 |  | MW | i) Khulna area |  |  |  | 1319.2 | MW
ii) Chattogram area |  |  | 1071.8 |  | MW | ii) Barishal area |  |  |  | 314.4 | MW
iii) Cumilla area |  |  | 966 |  | MW | iii) Rajshahi area |  |  |  | 1021.8 | MW
iv) Mymensingh area |  |  | 911 |  | MW | iv) Rangpur area |  |  |  | 780 | MW
v) Sylhet area |  |  | 394 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10841.03 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 84 | 12:00 | 133 | Netrakona | 108 | 17:00
2 | AKSML | 118.5 | 00:00 | 68 | Hathazari | 54 | 13:00 | 134 | New | 64 | 18:00
3 | Aftabnagar | 26 | 14:00 | 69 | Hatirjheel | 27 | 15:00 | 135 | Niamatpur | 51 | 18:00
4 | Agargaon | 81 | 13:00 | 70 | Ishurdi | 51 | 18:30 | 136 | Noapara | 39 | 18:30
5 | Agrabad | 32 | 18:00 | 71 | Jaldhaka | 52 | 18:00 | 137 | PHP | 4 | 10:00
6 | Amnura | 24 | 12:00 | 72 | Jamalpur | 96 | 18:00 | 138 | Pabna | 77 | 18:30
7 | Ashuganj | 56 | 12:00 | 73 | Jashore | 108 | 13:00 | 139 | Palashbari | 84 | 18:00
8 | BSRM | 191 | 02:00 | 74 | Jhenaidah | 103 | 18:00 | 140 | Panchagarh | 45 | 18:00
9 | Bagerhat | 67 | 18:30 | 75 | Joydebpur | 107 | 18:30 | 141 | Patiya | 6.5 | 14:00
10 | Bajitpur | 68 | 18:30 | 76 | Joypurhat | 40 | 20:00 | 142 | Patuakhali | 40.1 | 19:30
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 12 | 10:00 | 143 | Payra | 28 | 18:00
12 | Bakulia | 62 | 13:00 | 78 | KSRM | 25 | 06:00 | 144 | Postogola | 42 | 13:00
13 | Banani | 20 | 13:00 | 79 | Kabirpur | 170 | 12:00 | 145 | Purbachal | 21 | 13:00
14 | Bangabhaban | 9 | 12:00 | 80 | Kachua | 48 | 20:00 | 146 | Purbasadipur | 114 | 18:00
15 | Barapukuria | 52 | 18:00 | 81 | Kallyanpur | 72 | 13:00 | 147 | Rahanpur | 23 | 19:30
16 | Barguna | 14 | 19:00 | 82 | Kalurghat | 30 | 12:00 | 148 | Rahim | 23 | 17:00
17 | Barishal | 76 | 13:00 | 83 | Kamrangirchar | 65 | 13:00 | 149 | Rajbari | 60 | 18:00
18 | Barishal-230 | 76 | 18:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 125 | 18:00
19 | Baroaulia | 58 | 17:00 | 85 | Kasba | 23 | 19:30 | 151 | Rajshahi | 74 | 19:30
20 | Baroirhat | 40 | 19:30 | 86 | Kazla | 95 | 12:00 | 152 | Rajshahi-230 | 74 | 13:00
21 | Bashundhara | 134 | 13:00 | 87 | Keranigonj | 70 | 19:30 | 153 | Ramganj | 84 | 13:00
22 | BashundharaCement | 9 | 17:00 | 88 | Khagrachori | 26 | 18:00 | 154 | Rampur | 25 | 12:00
23 | Beanibazar | 46 | 19:00 | 89 | Khulna | 52 | 13:00 | 155 | Rangamati | 13 | 18:00
24 | Benapole | 66 | 08:00 | 90 | Khulshi | 154 | 18:00 | 156 | Rangpur | 112 | 13:00
25 | Bhaluka | 130 | 18:30 | 91 | Kishoreganj | 92 | 19:00 | 157 | Ruppur | 2.4 | 10:00
26 | Bhandaria | 37 | 19:30 | 92 | Kodda | 233 | 09:00 | 158 | SSM | 2 | 00:00
27 | Bhangura | 24 | 18:00 | 93 | Kulaura | 28 | 18:00 | 159 | Saidpur | 94 | 18:30
28 | Bheramara(GK) | 44 | 18:00 | 94 | Kurigram | 49 | 08:00 | 160 | Satkhira | 93 | 18:00
29 | Bhulta | 198 | 12:00 | 95 | Kushtia | 117 | 18:00 | 161 | Satmasjid | 72 | 13:00
30 | Bog-Sherpur | 54 | 18:00 | 96 | Laksam | 23 | 13:00 | 162 | Savar | 182 | 12:00
31 | Bogura | 111 | 19:00 | 97 | Lakshmipur | 24 | 18:00 | 163 | SevenRings | 11.62 | 01:00
32 | Borhanuddin | 66 | 20:00 | 98 | Lalbag | 56 | 17:00 | 164 | ShahCement | 34 | 23:00
33 | Brahmanbaria | 90 | 18:00 | 99 | Lalmonirhat | 44 | 18:00 | 165 | Shahjadpur | 54 | 12:00
34 | Cantonment | 92 | 13:00 | 100 | MI_Cement | 13 | 00:00 | 166 | Shahjibazar | 83 | 21:00
35 | Chandina | 12 | 06:00 | 101 | Madanganj | 40 | 18:30 | 167 | Shahmirpur | 39 | 18:30
36 | Chandpur | 50 | 18:30 | 102 | Madaripur | 75 | 20:00 | 168 | Shariatpur | 60 | 20:00
37 | Chandraghona | 26 | 18:00 | 103 | Madartek | 56 | 13:00 | 169 | Sherpur | 120 | 18:00
38 | Chapai | 54 | 12:00 | 104 | Madunaghat | 39 | 18:00 | 170 | Shikalbaha | 17 | 00:00
39 | Charsaidpur | 39 | 15:00 | 105 | Magura | 51 | 18:00 | 171 | Shitalakhya | 63.6 | 13:00
40 | Chauddagram | 44 | 19:30 | 106 | Mahasthangarh | 52 | 18:30 | 172 | Sholosohor | 35 | 12:00
41 | Chhatak | 25 | 18:30 | 107 | Maijdee | 26 | 19:00 | 173 | Shyampur | 124 | 01:00
42 | Chowmuhani | 116 | 19:00 | 108 | Manikganj | 102 | 18:00 | 174 | Siddhirganj | 93 | 12:00
43 | Chuadanga | 78 | 18:00 | 109 | Maniknagar | 48 | 13:00 | 175 | Sirajganj | 88 | 19:00
44 | Coxsbazar | 105 | 20:00 | 110 | Matarbari | 48 | 18:00 | 176 | Sonargaon | 124 | 18:00
45 | Cumilla(N) | 98 | 18:00 | 111 | Matuail | 46 | 11:00 | 177 | Sreemongol | 53 | 21:00
46 | Cumilla(S) | 129 | 13:00 | 112 | Metrorail_Motijheel | 25 | 16:00 | 178 | Sreepur | 99 | 11:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 5 | 11:00 | 179 | Srinagar | 30.8 | 20:00
48 | Daudkandi | 106 | 18:00 | 114 | Millgate | 74 | 11:00 | 180 | Sunamganj | 39 | 18:00
49 | DhakaUniversity | 52 | 13:00 | 115 | Mirpur | 110 | 14:00 | 181 | Sylhet | 29 | 00:00
50 | Dhamrai | 98 | 18:00 | 116 | Mirsorai | 9 | 09:00 | 182 | Sylhet-132 | 86 | 13:00
51 | Dhanmondi | 77 | 13:00 | 117 | Mirzapur | 38 | 18:00 | 183 | TK | 18.5 | 18:00
52 | Dohazari | 68 | 18:00 | 118 | Mithapukur | 43 | 18:00 | 184 | Tangail | 115 | 18:00
53 | Faridpur | 117 | 18:00 | 119 | Modern | N/A | N/A | 185 | Taraganj | 16 | 18:00
54 | Fatullah | 91 | 12:00 | 120 | Mogbazar | 46.9 | 15:00 | 186 | Tasnim | 33 | 08:00
55 | Fenchuganj | 23 | 18:00 | 121 | Mongla | 31 | 23:00 | 187 | Thakurgaon | 81 | 18:00
56 | Feni | 77 | 18:00 | 122 | Motijheel | 30 | 13:00 | 188 | Tongi | 99 | 11:00
57 | GPH | 76 | 05:00 | 123 | Muktagacha | 27 | 08:00 | 189 | Ullahpara | 32 | 13:00
58 | Ghatail | 66 | 18:00 | 124 | Munshiganj | 76 | 12:00 | 190 | Ullon | 37 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 18 | 00:00 | 191 | Uttara | 60 | 14:00
60 | Ghorashal-230 | 77 | 12:00 | 126 | Mymensingh | 138 | 13:00 | 192 | UttaraNew | 31 | 09:00
61 | Goalpara | 30 | 13:00 | 127 | Naogaon | 95 | 13:00 | 193 | Zigatola | 71 | 14:00
62 | Gollamari | 82 | 13:00 | 128 | Narail | 43 | 18:00
63 | Gopalganj | 81.2 | 18:00 | 129 | Narinda | 48 | 13:00
64 | Gulshan | 72 | 13:00 | 130 | Narshingdi | 138 | 20:00
65 | Halishahar | 54 | 18:00 | 131 | Natore | 106 | 18:00
66 | HaripurSBU | 85 | 06:00 | 132 | Nawabganj | 31.8 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 05-01-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 8924 | 0 |  | 8924
1:00 | 8288 | 0 |  | 8288
2:00 | 7863 | 0 |  | 7863
3:00 | 7515 | 0 |  | 7515
4:00 | 7218 | 0 |  | 7218
5:00 | 7203 | 0 |  | 7203
6:00 | 7772 | 0 |  | 7772
7:00 | 8299.21 | 0 |  | 8299.21
8:00 | 9405.05 | 0 |  | 9405.05
9:00 | 10017.53 | 0 |  | 10017.53
10:00 | 9702.61 | 0 |  | 9702.61
11:00 | 9863.67 | 0 |  | 9863.67
12:00 | 10297.08 | 0 |  | 10297.08
13:00 | 10739.08 | 0 |  | 10739.08
14:00 | 10295.61 | 0 |  | 10295.61
15:00 | 9810.66 | 0 |  | 9810.66
16:00 | 9508.93 | 0 |  | 9508.93
17:00 | 9983.59 | 0 |  | 9983.59
18:00 | 11058 | 0 |  | 11058
19:00 | 10978.9 | 0 |  | 10978.9
19:30 | 10993 | 0 |  | 10993
20:00 | 10932.2 | 0 |  | 10932.2
21:00 | 10682.84 | 0 |  | 10682.84
22:00 | 10040.17 | 0 |  | 10040.17
23:00 | 9411.84 | 0 |  | 9411.84
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 05-01-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4831 | 4093 | 8924 | DAILY GENERATION CURVE
00:30 | 4595 | 4011 | 8606
01:00 | 4359 | 3929 | 8288 | 05-01-2026
01:30 | 4286 | 3789.5 | 8075.5
02:00 | 4213 | 3650 | 7863
02:30 | 4186 | 3503 | 7689
03:00 | 4159 | 3356 | 7515
03:30 | 4126 | 3240.5 | 7366.5
04:00 | 4093 | 3125 | 7218
04:30 | 4038.5 | 3172 | 7210.5
05:00 | 3984 | 3219 | 7203
05:30 | 4159 | 3328.5 | 7487.5
06:00 | 4334 | 3438 | 7772
06:30 | 4494 | 3541.605 | 8035.605
07:00 | 4654 | 3645.21 | 8299.21
07:30 | 4964.375 | 3887.755 | 8852.13
08:00 | 5274.75 | 4130.3 | 9405.05
08:30 | 5414.35 | 4296.94 | 9711.29
09:00 | 5553.95 | 4463.58 | 10017.53
09:30 | 5516.78 | 4343.29 | 9860.07
10:00 | 5479.61 | 4223 | 9702.61
10:30 | 5562.195 | 4220.945 | 9783.14
11:00 | 5644.78 | 4218.89 | 9863.67
11:30 | 5755.65 | 4324.725 | 10080.375
12:00 | 5866.52 | 4430.56 | 10297.08
12:30 | 5883.71 | 4634.37 | 10518.08
13:00 | 5900.9 | 4838.18 | 10739.08
13:30 | 5860.93 | 4656.415 | 10517.345
14:00 | 5820.96 | 4474.65 | 10295.61
14:30 | 5741.46 | 4311.675 | 10053.135
15:00 | 5661.96 | 4148.7 | 9810.66
15:30 | 5556.225 | 4103.57 | 9659.795
16:00 | 5450.49 | 4058.44 | 9508.93
16:30 | 5504.245 | 4242.015 | 9746.26
17:00 | 5558 | 4425.59 | 9983.59
17:30 | 5849.5 | 4671.295 | 10520.795
18:00 | 6141 | 4917 | 11058
18:30 | 6061.95 | 4956.5 | 11018.45
19:00 | 5982.9 | 4996 | 10978.9
19:30 | 5980 | 5013 | 10993
20:00 | 5921.2 | 5011 | 10932.2
20:30 | 5818.8 | 4988.72 | 10807.52 |  | Executive Engineer
21:00 | 5716.4 | 4966.44 | 10682.84 |  | Network Operation Division
21:30 | 5513.7 | 4847.805 | 10361.505
22:00 | 5311 | 4729.17 | 10040.17
22:30 | 5201 | 4525.005 | 9726.005
23:00 | 5091 | 4320.84 | 9411.84

## En-Curve
QF-LDC-12
Date | 05-01-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2917 | 1472 | 892 | 0 | 96 | 834 | 46 | 2600 | 0 | 0 | 19 | 0 | 0 | 48 | 0 | DAILY ENERGY CURVE
00:30 | 2791.5 | 1376.5 | 821.5 | 0 | 89 | 832.5 | 46 | 2601.5 | 0 | 0 | 9.5 | 0 | 0 | 38 | 0 | 05-01-2026
01:00 | 2666 | 1281 | 751 | 0 | 82 | 831 | 46 | 2603 | 0 | 0 | 0 | 0 | 0 | 28 | 0
01:30 | 2546 | 1219.5 | 727.5 | 0 | 84 | 830.5 | 46 | 2595.5 | 0 | 0 | 0 | 0 | 0 | 26.5 | 0 | Energy Generated | 228.5819 |  | MKWHr
02:00 | 2426 | 1158 | 704 | 0 | 86 | 830 | 46 | 2588 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2414.5 | 1139.5 | 564 | 0 | 83 | 835.5 | 46 | 2582 | 0 | 0 | 0 | 0 | 0 | 24.5 | 0 | Total Energy Requirement | 228.5819 |  | MKWHr
03:00 | 2403 | 1121 | 424 | 0 | 80 | 841 | 46 | 2576 | 0 | 0 | 0 | 0 | 0 | 24 | 0
03:30 | 2375 | 1131.5 | 331.5 | 0 | 80 | 839 | 46 | 2533.5 | 0 | 0 | 0 | 0 | 0 | 30 | 0
04:00 | 2347 | 1142 | 239 | 0 | 80 | 837 | 46 | 2491 | 0 | 0 | 0 | 0 | 0 | 36 | 0
04:30 | 2409 | 1139 | 239 | 0 | 77 | 839.5 | 46 | 2429.5 | 0 | 0 | 0 | 0 | 0 | 31.5 | 0
05:00 | 2471 | 1136 | 239 | 0 | 74 | 842 | 46 | 2368 | 0 | 0 | 0 | 0 | 0 | 27 | 0
05:30 | 2602.5 | 1221 | 280 | 0 | 79 | 841 | 46 | 2391 | 0 | 0 | 0 | 0 | 0 | 27 | 0
06:00 | 2734 | 1306 | 321 | 0 | 84 | 840 | 46 | 2414 | 0 | 0 | 0 | 0 | 0 | 27 | 0
06:30 | 2791 | 1351 | 419.5 | 0 | 83 | 837.5 | 46 | 2482.5 | 1.105 | 0 | 1 | 0 | 0 | 23 | 0
07:00 | 2848 | 1396 | 518 | 0 | 82 | 835 | 46 | 2551 | 2.21 | 0 | 2 | 0 | 0 | 19 | 0
07:30 | 2870.5 | 1478.5 | 494.5 | 0 | 91 | 954.84 | 46 | 2842.5 | 22.29 | 0 | 33 | 0 | 0 | 19 | 0
08:00 | 2893 | 1561 | 471 | 0 | 100 | 1074.68 | 46 | 3134 | 42.37 | 0 | 64 | 0 | 0 | 19 | 0
08:30 | 2918.5 | 1564 | 446.5 | 0 | 103 | 1122.635 | 46 | 3354.5 | 56.405 | 5.5 | 78.25 | 0 | 0 | 16 | 0
09:00 | 2944 | 1567 | 422 | 0 | 106 | 1170.59 | 46 | 3575 | 70.44 | 11 | 92.5 | 0 | 0 | 13 | 0
09:30 | 2910.5 | 1491.5 | 422.5 | 0 | 105 | 1096.81 | 46 | 3525.5 | 89.01 | 59.5 | 102.75 | 0 | 0 | 11 | 0
10:00 | 2877 | 1416 | 423 | 0 | 104 | 1023.03 | 46 | 3476 | 107.58 | 108 | 113 | 0 | 0 | 9 | 0
10:30 | 2909 | 1458.5 | 423 | 0 | 108 | 1005.96 | 46 | 3473.5 | 121.68 | 99 | 128.5 | 0 | 0 | 10 | 0
11:00 | 2941 | 1501 | 423 | 0 | 112 | 988.89 | 46 | 3471 | 135.78 | 90 | 144 | 0 | 0 | 11 | 0
11:30 | 2996 | 1535 | 423 | 0 | 118 | 1034.875 | 46 | 3508 | 134.75 | 90 | 182.25 | 0 | 0 | 12.5 | 0
12:00 | 3051 | 1569 | 423 | 0 | 124 | 1080.86 | 46 | 3545 | 133.72 | 90 | 220.5 | 0 | 0 | 14 | 0
12:30 | 3035 | 1599 | 428.5 | 0 | 126 | 1170.035 | 46 | 3630 | 131.545 | 101 | 240 | 0 | 0 | 11 | 0
13:00 | 3019 | 1629 | 434 | 0 | 128 | 1259.21 | 46 | 3715 | 129.37 | 112 | 259.5 | 0 | 0 | 8 | 0
13:30 | 2957 | 1596 | 434 | 0 | 123 | 1206.605 | 46 | 3668.5 | 130.99 | 115 | 230.75 | 0 | 0 | 9.5 | 0
14:00 | 2895 | 1563 | 434 | 0 | 118 | 1154 | 46 | 3622 | 132.61 | 118 | 202 | 0 | 0 | 11 | 0
14:30 | 2897.5 | 1531.5 | 434 | 0 | 117 | 1087 | 46 | 3508.5 | 110.635 | 116 | 193.5 | 0 | 0 | 11.5 | 0
15:00 | 2900 | 1500 | 434 | 0 | 116 | 1020 | 46 | 3395 | 88.66 | 114 | 185 | 0 | 0 | 12 | 0
15:30 | 2900.5 | 1489 | 434 | 0 | 113 | 1028.5 | 46 | 3263.5 | 72.295 | 118 | 183 | 0 | 0 | 12 | 0
16:00 | 2901 | 1478 | 434 | 0 | 110 | 1037 | 46 | 3132 | 55.93 | 122 | 181 | 0 | 0 | 12 | 0
16:30 | 2950.5 | 1539 | 434 | 0 | 109 | 1097.5 | 46 | 3196.5 | 31.76 | 116 | 213 | 0 | 0 | 13 | 0
17:00 | 3000 | 1600 | 434 | 0 | 108 | 1158 | 46 | 3261 | 7.59 | 110 | 245 | 0 | 0 | 14 | 0
17:30 | 2980 | 1599 | 434 | 0 | 114 | 1304.5 | 46 | 3415 | 3.795 | 149 | 455.5 | 0 | 0 | 20 | 0
18:00 | 2960 | 1598 | 434 | 0 | 120 | 1451 | 46 | 3569 | 0 | 188 | 666 | 0 | 0 | 26 | 0
18:30 | 2959.5 | 1600.5 | 434 | 0 | 120 | 1446.5 | 46 | 3654.5 | 0 | 173.5 | 556.45 | 0 | 0 | 27.5 | 0
19:00 | 2959 | 1603 | 434 | 0 | 120 | 1442 | 46 | 3740 | 0 | 159 | 446.9 | 0 | 0 | 29 | 0
19:30 | 2949 | 1645 | 434 | 0 | 112 | 1443 | 46 | 3753 | 0 | 159 | 420 | 0 | 0 | 32 | 0
20:00 | 2916 | 1627 | 434 | 0 | 116 | 1445 | 46 | 3745 | 0 | 159 | 419.2 | 0 | 0 | 25 | 0
20:30 | 2898 | 1621 | 434 | 0 | 114 | 1451.22 | 46 | 3740 | 0 | 79.5 | 401.3 | 0 | 0 | 22.5 | 0
21:00 | 2880 | 1615 | 434 | 0 | 112 | 1457.44 | 46 | 3735 | 0 | 0 | 383.4 | 0 | 0 | 20 | 0
21:30 | 2876.5 | 1609.5 | 434 | 0 | 104 | 1418.805 | 46 | 3629 | 0 | 0 | 218.7 | 0 | 0 | 25 | 0
22:00 | 2873 | 1604 | 434 | 0 | 96 | 1380.17 | 46 | 3523 | 0 | 0 | 54 | 0 | 0 | 30 | 0
22:30 | 2872.5 | 1609 | 434 | 0 | 98 | 1301.005 | 46 | 3282.5 | 0 | 0 | 48.5 | 0 | 0 | 34.5 | 0
23:00 | 2872 | 1614 | 434 | 0 | 100 | 1221.84 | 46 | 3042 | 0 | 0 | 43 | 0 | 0 | 39 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 05-01-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 425 | 05:00 | 395 | 12:00 | Meghnaghat | 427 | 05:00 | 400 | 12:00
Ashuganj | 415 | 5:00 | 391 | 13:00 | Payra | 425 | 03:00 | 416 | 09:00
Bhulta | 407 | 05:00 | 382 | 12:00 | Rahanpur | 423 | 04:00 | 399 | 13:00
Bibiana | 421 | 03:00 | 402 | 12:00 | Rampal | 421 | 04:00 | 400 | 14:00
BIPTC | 408 | 04:00 | 398 | 09:00
Bogura | 419 | 03:00 | 387 | 13:00
Gopalganj | 425 | 04:00 | 400 | 13:00
Kaliakoir | 413 | 23:00 | 397 | 14:00
Korerhat | 422 | 05:00 | 404 | 12:00
Madunaghat | 416 | 06:00 | 401 | 14:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 246 | 04:00 | 226 | 12:00 | Kachua | 244 | 04:00 | 233 | 11:00
AKSML | 243.1 | 05:00 | 230.3 | 12:00 | Kaliakoir | 237 | 23:00 | 225 | 14:00
Aminbazar | 244 | 05:00 | 227 | 12:00 | Keranigonj | 244 | 05:00 | 225 | 12:00
Ashuganj | 241 | 05:00 | 228 | 12:00 | Khulna(S) | 249 | 05:00 | 230 | 12:00
Ashuganj-400 | 241 | 05:00 | 228 | 12:00 | Korerhat | 243 | 03:00 | 229 | 12:00
Baghabari | 243 | 04:00 | 230 | 13:00 | Madunaghat | 240 | 03:00 | 230 | 12:00
Barapukuria | 233 | 05:00 | 212 | 08:00 | Madunaghat-400 | 240 | 03:00 | 230 | 13:00
Barapukuria-230 | 233 | 05:00 | 212 | 08:00 | Maniknagar | 243 | 03:00 | 226 | 12:00
Barishal | 241 | 05:00 | 231 | 12:00 | Meghnaghat | 247 | 04:00 | 234 | 11:00
Bheramara | 244 | 04:00 | 223 | 13:00 | Meghnaghat-400 | 243 | 04:00 | 227 | 12:00
Bhulta | 244 | 03:00 | 228 | 12:00 | Mirsorai | 245 | 05:00 | 230 | 12:00
Bibiana | 246 | 02:00 | 237 | 12:00 | Rajshahi | 242 | 03:00 | 221 | 13:00
BIPTC | 245 | 04:00 | 223 | 13:00 | Rampal | 243 | 04:00 | 228 | 12:00
Bogura | 246 | 05:00 | 225 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 245 | 04:00 | 225 | 13:00 | Rampura | 244 | 04:00 | 227 | 12:00
Borhanuddin | 243 | 05:00 | 236 | 12:00 | Shikalbaha | 238 | 03:00 | 229 | 12:00
BSRM | 245 | 05:00 | 229 | 12:00 | Shyampur | 243 | 04:00 | 225 | 12:00
Cumilla(N) | 240 | 01:00 | 228 | 12:00 | Siddhirganj | 244 | 02:00 | 228 | 12:00
Faridpur | 241 | 04:00 | 227 | 12:00 | Sirajgonj | 247 | 02:00 | 237 | 13:00
Fenchuganj | 249 | 05:00 | 240 | 12:00 | Sreepur | 240 | 04:00 | 227 | 09:00
Feni | 245 | 04:00 | 229 | 12:00 | Tongi | 240 | 04:00 | 222 | 11:00
Ghorashal | 246 | 02:00 | 230 | 11:00
Ghorashal-230 | 244 | 04:00 | 222 | 13:00
Gopalganj | 239 | 04:00 | 225 | 13:00
GPH | 242 | 04:00 | 230 | 12:00
Haripur | 244 | 05:00 | 228 | 12:00
Hasnabad | 243 | 02:00 | 225 | 12:00
Hathazari | 238 | 00:00 | 231 | 11:00
Ishurdi | 246 | 04:00 | 226 | 13:00
Jhenaidah | 246 | 05:00 | 220 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 03:00 | 124 | 12:00 | Laksam | 140 | 07:00 | 130 | 13:00 | UttaraNew | 139 | 02:00 | 126 | 12:00
Agargaon | 140 | 03:00 | 128 | 12:00 | Lakshmipur | 137 | 04:00 | 128 | 12:00 | Zigatola | 138 | 05:00 | 17 | 14:00
Agrabad | 140 | 02:00 | 133 | 12:00 | Lalbag | 136 | 04:00 | 125 | 12:00
AKS | 137 | 03:00 | 131 | 12:00 | Lalmonirhat | 131 | 03:00 | 121 | 12:00
Aminbazar | 139 | 05:00 | 127 | 12:00 | Madanganj | 136 | 00:00 | 132 | 11:00
Amnura | 140 | 03:00 | 129 | 12:00 | Madaripur | 142 | 04:00 | 135 | 12:00
Ashuganj | 141 | 01:00 | 136 | 12:00 | Madartek | 135 | 06:00 | 124 | 12:00
Bagerhat | 136 | 01:00 | 126 | 12:00 | Madunaghat | 140 | 03:00 | 133 | 16:00
Bajitpur | 135 | 03:00 | 128 | 09:00 | Magura | 140 | 02:00 | 125 | 12:00
Bakerganj | 139 | 00:00 | 135 | 18:00 | Mahasthangarh | 139 | 04:00 | 127 | 13:00
Bakulia | 140 | 00:00 | 134 | 12:00 | Maijdee | 137 | 03:00 | 128 | 12:00
Banani | 134 | 01:00 | 124 | 12:00 | Manikganj | 135 | 01:00 | 119 | 12:00
Bangabhaban | 142 | 05:00 | 130 | 12:00 | Maniknagar | 140 | 01:00 | 130 | 12:00
Barapukuria | 140 | 05:00 | 126 | 13:00 | Matarbari | 133 | 03:00 | 114 | 12:00
Barguna | 139 | 03:00 | 135 | 12:00 | Matuail | 140 | 04:00 | 131.5 | 12:00
Barishal | 141 | 04:00 | 134 | 12:00 | Metrorail_Motijheel | 140 | 02:00 | 130 | 12:00
Barishal-230 | 142 | 04:00 | 134 | 12:00 | Metrorail_Uttara | 139 | 01:00 | 126 | 12:00
Baroaulia | 141 | 03:00 | 133 | 13:00 | Millgate | 138 | 01:00 | 121 | 12:00
Baroirhat | 138 | 03:00 | 130 | 12:00 | Mirpur | 138 | 03:00 | 126 | 12:00
Bashundhara | 134 | 03:00 | 124 | 12:00 | Mirzapur | 139 | 04:00 | 129 | 12:00
BashundharaCement | 137 | 10:00 | 132 | 11:00 | Mithapukur | 138 | 04:00 | 124 | 13:00
Beanibazar | 136 | 01:00 | 133 | 12:00 | MI_Cement | 138 | 05:00 | 123 | 13:00
Benapole | 138 | 03:00 | 113 | 13:00 | Modern | N/A | N/A | N/A | N/A
Bhaluka | 135 | 00:00 | 127 | 09:00 | Mogbazar | 136 | 02:00 | 126 | 12:00
Bhandaria | 139 | 03:00 | 134 | 12:00 | Mongla | 137 | 05:00 | 126 | 13:00
Bhangura | 141 | 04:00 | 132 | 11:00 | Motijheel | 142 | 05:00 | 130 | 12:00
Bheramara | 143 | 04:00 | 135 | 09:00 | Muktagacha | 135 | 07:00 | 129 | 18:30
Bheramara(GK) | 143 | 04:00 | 134 | 13:00 | Munshiganj | 138 | 04:00 | 130 | 12:00
Bhulta | 129 | 07:00 | 124 | 12:00 | Muradnagar | 141 | 04:00 | 131 | 12:00
Bog-Sherpur | 140 | 03:00 | 128 | 13:00 | Mymensingh | 137 | 10:00 | 121 | 09:00
Bogura | 139 | 05:00 | 128 | 13:00 | Naogaon | 136 | 04:00 | 125 | 13:00
Bogura-230 | 140 | 03:00 | 128 | 13:00 | Narail | 140 | 06:00 | 123 | 13:00
Brahmanbaria | 137 | 04:00 | 129 | 12:00 | Narinda | 140 | 01:00 | 130 | 12:00
Cantonment | 140 | 04:00 | 127 | 12:00 | Narshingdi | 135 | 03:00 | 127 | 12:00
Chandina | 142 | 03:00 | 132 | 13:00 | Natore | 139 | 05:00 | 129 | 13:00
Chandpur | 139 | 06:00 | 130 | 13:00 | Nawabganj | 138 | 03:00 | 125 | 13:00
Chandraghona | 141 | 02:00 | 134 | 12:00 | Netrakona | 129 | 06:00 | 120 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 141 | 05:00 | 132 | 13:00 | New | 139 | 04:00 | 122 | 12:00
Charsaidpur | 140 | 05:00 | 130 | 12:00 | Niamatpur | 141 | 01:00 | 132 | 13:00
Chauddagram | 139 | 03:00 | 130 | 12:00 | Noapara | 138 | 04:00 | 116 | 13:00
Chhatak | 137 | 06:00 | 131 | 12:00 | Pabna | 142 | 04:00 | 133 | 12:00
Chowmuhani | 135 | 03:00 | 128 | 12:00 | Palashbari | 135 | 05:00 | 123 | 09:00
Chuadanga | 141 | 05:00 | 122 | 13:00 | Panchagarh | 140 | 02:00 | 126 | 08:00
Coxsbazar | 130 | 00:00 | 119 | 12:00 | Patiya | 138 | 00:00 | 133 | 12:00
Cumilla(N) | 140 | 01:00 | 132 | 12:00 | Patuakhali | 138 | 00:00 | 134 | 12:00
Cumilla(S) | 140 | 00:00 | 126 | 08:00 | Payra | 140 | 01:00 | 136 | 13:00
Daganbhuiyan | 138 | 04:00 | 129 | 12:00 | PHP | 138 | 04:00 | 129 | 13:00
Daudkandi | 139 | 04:00 | 129 | 12:00 | Postogola | 139 | 04:00 | 126 | 12:00
DhakaUniversity | 134 | 01:00 | 124 | 12:00 | Purbachal | 134 | 01:00 | 124 | 12:00
Dhamrai | 139 | 03:00 | 131 | 12:00 | Purbasadipur | 133 | 05:00 | 119 | 13:00
Dhanmondi | 141 | 05:00 | 131 | 12:00 | Rahanpur | 141 | 03:00 | 134 | 13:00
Dohazari | 136 | 00:00 | 131 | 11:00 | Rahanpur-400 | 142 | 03:00 | 134 | 13:00
Faridpur | 141 | 04:00 | 131 | 13:00 | Rahim | 139 | 04:00 | 133 | 10:00
Fatullah | 140 | 02:00 | 124 | 12:00 | Rajbari | 140 | 04:00 | 130 | 13:00
Fenchuganj | 140 | 00:00 | 136 | 12:00 | Rajendrapur | 139 | 04:00 | 129 | 08:00
Feni | 135 | 00:00 | 129 | 13:00 | Rajshahi | 138 | 01:00 | 128 | 13:00
Feni-230 | 138 | 04:00 | 129 | 12:00 | Rajshahi-230 | 140 | 05:00 | 127 | 13:00
Ghatail | 133 | 04:00 | 126 | 18:30 | Ramganj | 137 | 05:00 | 128 | 13:00
Ghorashal | 135 | 16:00 | 121 | 11:00 | Rampur | 140 | 03:00 | 133 | 11:00
Goalpara | 140 | 04:00 | 128 | 13:00 | Rampura | 134 | 03:00 | 124 | 12:00
Gollamari | 139 | 02:00 | 129 | 12:00 | Rangamati | 138 | 00:00 | 134 | 12:00
Gopalganj | 142 | 04:00 | 132 | 12:00 | Rangpur | 137 | 05:00 | 124 | 09:00
Gopalganj-400 | 144 | 02:00 | 135 | 13:00 | Ruppur | 143 | 05:00 | 134 | 12:00
Gulshan | 134 | 04:00 | 124 | 12:00 | Saidpur | 136 | 03:00 | 122 | 13:00
Halishahar | 140 | 03:00 | 133 | 12:00 | Satkhira | 138 | 05:00 | 126 | 13:00
Haripur | 139 | 04:00 | 131 | 12:00 | Satmasjid | 139 | 02:00 | 127 | 13:00
HaripurSBU | 140 | 04:00 | 131 | 13:00 | Savar | 137 | 02:00 | 126 | 12:00
Hasnabad | 139 | 05:00 | 128 | 11:00 | SevenRings | 135 | 04:00 | 120 | 12:00
Hathazari | 140 | 05:00 | 135 | 15:00 | ShahCement | 140 | 05:00 | 130 | 12:00
Hatirjheel | 135 | 04:00 | 124 | 12:00 | Shahjadpur | 145 | 04:00 | 134 | 13:00
Ishurdi | 144 | 04:00 | 134 | 13:00 | Shahjibazar | 136 | 04:00 | 131 | 12:00
Jaldhaka | 134 | 04:00 | 120 | 08:00 | Shahmirpur | 140 | 05:00 | 133 | 15:00
Jamalpur | 137 | 10:00 | 126 | 18:00 | Shariatpur | 143 | 04:00 | 134 | 12:00
Jashore | 138 | 23:00 | 117 | 13:00 | Sherpur | 134 | 09:00 | 121 | 18:00
Jhenaidah | 141 | 01:00 | 122 | 08:00 | Shikalbaha | 128 | 02:00 | 124 | 00:00
Jhenaidah-230 | 143 | 04:00 | 125 | 13:00 | Shikalbaha-230 | 141 | 02:00 | 134 | 12:00
Joydebpur | 132 | 03:00 | 115 | 12:00 | Shitalakhya | 138 | 05:00 | 123 | 13:00
Joypurhat | 137 | 02:00 | 126 | 13:00 | Sholosohor | 140 | 03:00 | 134 | 12:00
Juldah | 138 | 00:00 | 133 | 11:00 | Shyampur | 139 | 06:00 | 130 | 11:00
Kabirpur | 137 | 00:00 | 118 | 12:00 | Shyampur-230 | 141 | 05:00 | 130 | 12:00
Kachua | 141 | 04:00 | 130 | 13:00 | Siddhirganj | 140 | 05:00 | 131 | 12:00
Kaliakoir | 140 | 23:00 | 134 | 14:00 | Sirajganj | 139 | 01:00 | 129 | 13:00
Kallyanpur | 141 | 02:00 | 127 | 11:00 | Sonargaon | 138 | 01:00 | 130 | 12:00
Kalurghat | 141 | 05:00 | 133 | 18:00 | Sreemongol | 137 | 04:00 | 132 | 12:00
Kamrangirchar | 138 | 03:00 | 125 | 12:00 | Sreepur | 140 | 03:00 | 131 | 09:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 137 | 06:00 | 125 | 12:00
Kasba | 140 | 04:00 | 131 | 12:00 | SSM | 142 | 00:00 | 140 | 07:00
Kazla | 141 | 04:00 | 130 | 13:00 | Sunamganj | 133 | 00:00 | 131 | 09:00
Keranigonj | 138 | 04:00 | 125 | 13:00 | Sylhet | 137 | 04:00 | 133 | 12:00
Khagrachori | 140 | 05:00 | 133 | 12:00 | Sylhet-132 | 136 | 01:00 | 134 | 09:00
Khulna | 138 | 04:00 | 128 | 09:00 | Tangail | 135 | 02:00 | 127 | 12:00
Khulna(S) | 140 | 04:00 | 128 | 13:00 | Taraganj | 136 | 05:00 | 121 | 08:00
Khulshi | 139 | 05:00 | 131 | 12:00 | Tasnim | 139 | 05:00 | 130 | 12:00
Kishoreganj | 134 | 04:00 | 126 | 13:00 | Thakurgaon | 137 | 04:00 | 123 | 08:00
Kodda | 137 | 02:00 | 127 | 12:00 | TK | 140 | 05:00 | 134 | 12:00
KSRM | 140 | 03:00 | 133 | 14:00 | Tongi | 157 | 13:00 | 126 | 11:00
Kulaura | 140 | 03:00 | 136 | 12:00 | Ullahpara | 141 | 04:00 | 131 | 11:00
Kurigram | 132 | 04:00 | 117 | 12:00 | Ullon | 135 | 04:00 | 124 | 12:00
Kushtia | 138 | 01:00 | 127 | 13:00 | Uttara | 139 | 02:00 | 128 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division