## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 07-01-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-01-2026 | during | 07-01-2026 | during | 07-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 374 | 335 | 412 | 412 | 392 | 392 | FGMO, Gas Shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 450 | 450 | 240 | 240 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 110 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 35 | 41.8 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 150 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 54 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 50 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 30 | 29.5 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 15 | 15.1 | 15.1 | 15.1 | 15.1 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 55 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 64 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 145 | 54 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 5 | 0 | 11 | 0 | 11 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 470 | 495 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 0 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1608 | 1369.3 | 5333.45 | 5322.45 | 2444.13 | 2471.13
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 | 46 | 46 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 173 | 173 | 150 | 150 | 150 | 150 | Plant availability less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 29 | 64 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 24 | 0 | 40 | 64 | 40 | 64 | temp problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 10 | 10 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 10 | 19 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.38 | 0 | 3.34 | 0 | 3.34 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 36 | 100 | 100 | 20 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1100 | 1165 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 3 | 16 | 25 | 38 | 25 | 38 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 720 | 720 | 720 | 720 | 720 | 720 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2140.38 | 2239 | 3513.2 | 3535.86 | 3030.84 | 3133.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 200 | 219 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 325 | 300 | 353.35 | 353.35 | 353.35 | 353.35 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 260 | 210 | 393 | 393 | 363 | 363 | FGMO, Gas Shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 80 | 80 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 51 | 51 | 51 | 51 | 51 | Machine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 50 | 30 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 110 | 114 | 163 | 163 | 115 | 115 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 59 | 51 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 118 | 104 | 84 | 82 | 128 | 128 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 19 | 24.5 | 24.5 | 24.5 | 24.5 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 3 | 0 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 65 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1257 | 1098 | 2385.75 | 2328.75 | 2116.75 | 2061.75
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-01-2026 | during | 07-01-2026 | during | 07-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 109 | 71 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.2 | 0 | 1.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 56 | 58 | 60 | 60 | 60 | 60 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 19 | 20 | 20 | 20 | 20 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 15.88 | 0 | 5.45 | 0 | 5.45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 2 | 22 | 22 | 12 | 12 | To be dispatched 18 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 200.88 | 150 | 320.65 | 314 | 310.65 | 304
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 41 | 41 | 41 | 41 | 41 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 50 | 50 | 60 | 60 | 60 | 60 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 155 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 78 | 81 | 81 | 81 | 81 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 159 | 157 | 160 | 160 | 158 | 158 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 310 | 341 | 341 | 0 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 863 | 842 | 901 | 901 | 542 | 849
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 408 | 407 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 366 | 340 | 410 | 410 | 369 | 369 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 19 | 0 | 68 | 0 | 68 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 460 | 1101 | 1148.28 | 1148.28 | 617.1 | 617.1 | U-2 Under Maintenance
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1253 | 1848 | 3488.28 | 3420.28 | 2161.2 | 2093.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 310 | 307 | 622 | 622 | 622 | 622 | Machine Problem
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 140 | 140 | 136 | 136 | 70 | 70 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 450 | 483 | 605 | 605 | 575 | 575 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 236 | 278 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.39 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1356.39 | 1428 | 2150 | 2150 | 1901 | 1901
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 6.65 | 0 | 16.35 | 0 | 16.35 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 174 | 179 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 380 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.38 | 0 | 2 | 0 | 2 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1185.85 | 1456.97 | 1435.88 | 1435.88 | 1356 | 1356 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 12.93 | 0 | 30 | 0 | 30 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 26 | 0 | 75 | 0 | 75 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1786.81 | 2049.97 | 3012.22 | 2888.87 | 2429.56 | 2306.21
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 49 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 1.6 | 0 | 3.2 | 0 | 3.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 27 | 0 | 24 | 0 | 24 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 57 | 0 | 85 | 0 | 85 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 85.6 | 99 | 340.2 | 228 | 340.2 | 228
System Total |  |  |  |  | 28823.2 | 28382.248 | 10551.06 | 11123.27 | 21444.75 | 21089.21 | 15276.33 | 15347.79
Forecast Scenario (07-01-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8980 |  | 0 |  | 8980
|  |  |  | 1:00 | 8250 |  | 0 |  | 8250
|  |  |  | 2:00 | 7800 |  | 0 |  | 7800
|  |  |  | 3:00 | 7510 |  | 0 |  | 7510
|  |  |  | 4:00 | 7420 |  | 0 |  | 7420
|  |  |  | 5:00 | 7350 |  | 0 |  | 7350
|  |  |  | 6:00 | 7830 |  | 0 |  | 7830
|  |  |  | 7:00 | 8500 |  | 0 |  | 8500
|  |  |  | 8:00 | 9610 |  | 0 |  | 9610
|  |  |  | 9:00 | 10250 |  | 0 |  | 10250
|  |  |  | 10:00 | 10010 |  | 0 |  | 10010
|  |  |  | 11:00 | 10160 |  | 0 |  | 10160
|  |  |  | 12:00 | 10650 |  | 0 |  | 10650
|  |  |  | 13:00 | 11160 |  | 0 |  | 11160
|  |  |  | 14:00 | 10500 |  | 0 |  | 10500
|  |  |  | 15:00 | 9870 |  | 0 |  | 9870
|  |  |  | 16:00 | 9620 |  | 0 |  | 9620
|  |  |  | 17:00 | 9780 |  | 0 |  | 9780
|  |  |  | 18:00 | 10870 |  | 0 |  | 10870
|  |  |  | 18:30 | 11000 |  | 0 |  | 11000
|  |  |  | 19:00 | 11220 |  | 0 |  | 11220
|  |  |  | 19:30 | 11090 |  | 0 |  | 11090
|  |  |  | 20:00 | 11040 |  | 0 |  | 11040
|  |  |  | 21:00 | 10760 |  | 0 |  | 10760
|  |  |  | 22:00 | 10260 |  | 0 |  | 10260
|  |  |  | 23:00 | 9600 |  | 0 |  | 9600
Probable Maximum Temperature: |  |  | 18.80°C
Probable Maximum Demand at Day Peak: |  |  | 10650.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11220.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11220.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 229.00 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:46 hrs on 07-01-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 06-01-2026 | [28 empty] | Date: | 06-01-2026 | [28 empty] | Date: | 06-01-2026 | [28 empty] | Date: | 06-01-2026 | [28 empty] | Date: | 06-01-2026 | [17 empty] | Date: | 06-01-2026
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [17 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 37 | 630 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 980 | 0 | 0 | 0 | 285 | 295 | 0 | 44 | 0 | 189 | 0 | 0 | 112 | 0 | 0 | 11 | 0 | 98 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 50 | 150 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 0 | 150 | 0 | 0 | 0 | 5006 | 433 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 1031.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224 | 140 | 180 | 0 | 257 | 320 | 0 | 3877.8 | 8883.8 | 97.33
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 6 | 37 | 570 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 803 | 0 | 0 | 0 | 285 | 315 | 0 | 0 | 0 | 201 | 0 | 0 | 112 | 0 | 0 | 11 | 0 | 78 | 0 | 0 | 0 | 300 | 0 | 0 | 41 | 50 | 156 | 0 | 0 | 0 | 22 | 20 | 0 | 0 | 158 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 4523 | 434 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 835.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 100 | 180 | 0 | 258 | 324 | 0 | 3633.12 | 8156.12 | 97.32
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 570 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 738 | 0 | 0 | 0 | 270 | 305 | 0 | 0 | 0 | 195 | 0 | 0 | 50 | 0 | 0 | 13 | 0 | 78 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 50 | 147 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 157 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 4248 | 434 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 0 | 0 | 837.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 100 | 180 | 0 | 259 | 280 | 0 | 3458.19 | 7706.19 | 97.32
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 570 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 650 | 0 | 0 | 0 | 230 | 320 | 0 | 0 | 0 | 204 | 0 | 0 | 50 | 0 | 0 | 13 | 0 | 76 | 0 | 0 | 0 | 310 | 0 | 0 | 29 | 40 | 143 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 157 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 4121 | 300 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 839.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 100 | 180 | 0 | 260 | 280 | 0 | 3297.93 | 7418.93 | 97.32
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 570 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 605 | 0 | 0 | 0 | 230 | 310 | 0 | 0 | 0 | 201 | 0 | 0 | 50 | 0 | 0 | 13 | 0 | 78 | 0 | 0 | 0 | 320 | 0 | 0 | 29 | 40 | 145 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 157 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 4063 | 295 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 841.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 100 | 180 | 0 | 261 | 280 | 0 | 3257.9 | 7320.9 | 97.32
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 570 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 606 | 0 | 0 | 0 | 230 | 315 | 0 | 0 | 0 | 200 | 0 | 0 | 50 | 0 | 0 | 13 | 0 | 82 | 0 | 0 | 0 | 325 | 0 | 0 | 29 | 40 | 143 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 157 | 0 | 0 | 0 | 111 | 0 | 0 | 0 | 4024 | 295 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 834.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 100 | 180 | 0 | 252 | 280 | 0 | 3231.55 | 7255.55 | 97.31
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 570 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 651 | 0 | 0 | 0 | 230 | 330 | 0 | 0 | 0 | 208 | 0 | 0 | 50 | 0 | 0 | 13 | 0 | 78 | 0 | 0 | 0 | 320 | 0 | 0 | 29 | 40 | 146 | 0 | 0 | 0 | 41 | 20 | 0 | 0 | 157 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 4206 | 269 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417 | 0 | 0 | 0 | 835.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239 | 100 | 220 | 0 | 262 | 295 | 0 | 3525.5 | 7731.5 | 97.31
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0.1 | 46 | 0 | 2 | 570 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 720 | 0 | 0 | 0 | 340 | 325 | 0 | 15 | 0 | 207 | 0 | 0 | 112 | 0 | 0 | 13 | 0 | 78 | 0 | 1 | 0 | 325 | 0 | 0 | 29 | 40 | 147 | 0 | 17 | 0 | 60 | 20 | 0 | 0 | 157 | 0 | 0 | 0 | 166 | 0 | 0.34 | 0 | 4613.44 | 268 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 420 | 0 | 0 | 0 | 922.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258 | 120 | 220 | 0 | 290 | 380 | 0 | 3787.34 | 8400.78 | 97.31
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 22 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0.71 | 46 | 0 | 3 | 720 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 880 | 2 | 0 | 0 | 340 | 330 | 0 | 44 | 0 | 206 | 0 | 0 | 112 | 0 | 0 | 13 | 0 | 96 | 0 | 12 | 0 | 320 | 0 | 0 | 41 | 50 | 146 | 1 | 17 | 0 | 75 | 30 | 0 | 0 | 156 | 0 | 19 | 35 | 166 | 0 | 3.59 | 0 | 5120.3 | 408 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 478 | 0 | 0 | 0 | 1111.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.41 | 3 | 0 | 0 | 0.96 | 170 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.08 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.2 | 6 | 0.03 | 0 | 284 | 140 | 220 | 0 | 307 | 465 | 0 | 4395.94 | 9516.24 | 97.31
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 27 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 1.4 | 46 | 0 | 2 | 775 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 1150 | 0 | 0 | 0 | 275 | 295 | 0 | 44 | 0 | 190 | 0 | 0 | 114 | 0 | 0 | 13 | 0 | 106 | 0 | 35 | 0 | 320 | 0 | 0 | 41 | 50 | 153 | 2 | 17 | 0 | 75 | 30 | 0 | 0 | 158 | 0 | 19 | 56 | 144 | 0 | 6.09 | 0 | 5420.49 | 407 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 572 | 0 | 0 | 0 | 1323.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.94 | 8 | 0 | 0 | 2.83 | 184 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0.28 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0.8 | 20 | 0.06 | 0 | 268 | 140 | 180 | 0 | 307 | 535 | 0 | 4736.98 | 10157.47 | 97.3
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 455 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 30 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 2.01 | 46 | 0 | 7 | 775 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 985 | 11 | 0 | 0 | 265 | 315 | 0 | 44 | 0 | 200 | 0 | 0 | 112 | 0 | 0 | 6 | 0 | 110 | 0 | 40 | 0 | 310 | 0 | 0 | 41 | 50 | 149 | 3 | 8 | 0 | 75 | 30 | 0 | 0 | 158 | 0 | 19 | 56 | 111 | 0 | 9 | 0 | 5293.01 | 408 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 540 | 0 | 0 | 0 | 1331.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.97 | 10 | 0 | 0 | 5.79 | 172 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0.59 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 1.2 | 50 | 0.09 | 0 | 230 | 100 | 180 | 0 | 309 | 500 | 0 | 4616.97 | 9909.98 | 97.3
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 15 | 0 | 0 | 150 | 40 | 0 | 36 | 66 | 0 | 225 | 0 | 490 | 0 | 20 | 0 | 0 | 0 | 3 | 0 | 30 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 4 | 0 | 0 | 0 | 3.48 | 46 | 0 | 7 | 720 | 0 | 0 | 0 | 0 | 5 | 172 | 0 | 0 | 0 | 960 | 20 | 10 | 0 | 260 | 295 | 0 | 44 | 0 | 190 | 0 | 0 | 111 | 21 | 1 | 7 | 0 | 112 | 0 | 58 | 0 | 310 | 0 | 0 | 41 | 50 | 155 | 7 | 17 | 0 | 75 | 30 | 0 | 0 | 159 | 0 | 19 | 56 | 109 | 0 | 11.68 | 0 | 5539.16 | 407 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 492 | 0 | 0 | 0 | 1232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 15 | 0 | 0 | 8.83 | 168 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 1.08 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 1.5 | 51 | 0.19 | 0 | 230 | 140 | 220 | 0 | 310 | 489 | 0 | 4529.6 | 10068.76 | 97.3
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 35 | 0 | 0 | 150 | 55 | 0 | 54 | 145 | 0 | 225 | 0 | 470 | 0 | 50 | 0 | 0 | 0 | 5 | 0 | 30 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 24 | 0 | 0 | 12 | 3.38 | 46 | 0 | 10 | 720 | 0 | 0 | 0 | 0 | 29 | 173 | 0 | 0 | 0 | 1100 | 20 | 50 | 0 | 260 | 325 | 0 | 44 | 0 | 200 | 0 | 3 | 110 | 59 | 9 | 14 | 0 | 118 | 0 | 65 | 0 | 320 | 0 | 0 | 41 | 50 | 163 | 5 | 17 | 0 | 78 | 30 | 0 | 0 | 159 | 0 | 19 | 56 | 109 | 1 | 15.88 | 0 | 6069.26 | 408 | 366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 460 | 0 | 0 | 0 | 1185.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.65 | 26 | 0 | 0 | 12.93 | 174 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 1.38 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 1.6 | 57 | 0.39 | 0 | 236 | 140 | 220 | 0 | 310 | 450 | 0 | 4481.8 | 10551.06 | 97.29
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 36.2 | 17 | 0 | 150 | 145 | 0 | 55 | 144 | 0 | 225 | 0 | 510 | 0 | 55 | 0 | 0 | 0 | 4 | 0 | 30 | 15 | 0 | 0 | 0 | 16 | 0 | 0 | 5 | 0 | 24 | 0 | 12 | 25 | 3.15 | 46 | 6 | 16 | 720 | 0 | 0 | 13 | 0 | 56 | 173 | 0 | 0 | 0 | 1160 | 19 | 102 | 0 | 235 | 295 | 0 | 44 | 0 | 188 | 0 | 30 | 110 | 128 | 9 | 8 | 0 | 120 | 0 | 62 | 0 | 320 | 0 | 0 | 41 | 50 | 163 | 8 | 17 | 0 | 78 | 30 | 0 | 0 | 159 | 0 | 19 | 56 | 107 | 1 | 17.8 | 0 | 6452.15 | 408 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 490 | 0 | 0 | 0 | 1161.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 10.43 | 27 | 0 | 0 | 13.69 | 181 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 1.33 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 1.8 | 77 | 0.51 | 0 | 278 | 140 | 220 | 0 | 309 | 478 | 0 | 4614.16 | 11066.31 | 97.29
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 32 | 0 | 0 | 150 | 160 | 0 | 17 | 126 | 0 | 180 | 0 | 380 | 0 | 17 | 0 | 0 | 0 | 7 | 0 | 27.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 24 | 0 | 0 | 25 | 2.64 | 46 | 15 | 10 | 720 | 0 | 0 | 2 | 0 | 85 | 173 | 0 | 0 | 0 | 1160 | 17 | 50 | 0 | 240 | 310 | 0 | 44 | 0 | 196 | 0 | 20 | 110 | 100 | 0 | 13 | 0 | 122 | 0 | 52 | 0 | 305 | 0 | 0 | 41 | 50 | 134 | 4 | 17 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 45 | 100 | 1 | 27.95 | 0 | 5985.09 | 408 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 657 | 0 | 0 | 0 | 1115.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 9.86 | 42 | 0 | 0 | 16.32 | 168 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 1.61 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 2.5 | 85 | 0.43 | 0 | 200 | 100 | 180 | 0 | 319 | 450 | 0 | 4418.86 | 10403.95 | 97.29
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 15.4 | 0 | 0 | 150 | 95 | 0 | 17 | 120 | 0 | 180 | 0 | 295 | 0 | 17 | 0 | 0 | 0 | 7 | 0 | 30 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 25 | 1.84 | 46 | 0 | 5 | 720 | 0 | 0 | 0 | 0 | 78 | 173 | 0 | 0 | 0 | 1145 | 11 | 18 | 0 | 240 | 295 | 0 | 51 | 0 | 190 | 0 | 0 | 109 | 96 | 0 | 13 | 0 | 112 | 0 | 34 | 0 | 310 | 0 | 0 | 41 | 50 | 135 | 5 | 17 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 49 | 67 | 1 | 22.69 | 0 | 5639.93 | 408 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 763 | 0 | 0 | 0 | 948.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.06 | 52 | 0 | 0 | 26.74 | 165 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 2.88 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 2 | 57 | 0.28 | 0 | 180 | 100 | 180 | 0 | 309 | 300 | 0 | 4131.19 | 9771.12 | 97.28
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 15.4 | 0 | 0 | 150 | 30 | 0 | 17 | 118 | 0 | 225 | 0 | 260 | 0 | 17 | 0 | 0 | 0 | 5 | 0 | 30 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 25 | 0.9 | 46 | 0 | 7 | 720 | 0 | 0 | 0 | 0 | 17 | 173 | 0 | 0 | 0 | 1150 | 7 | 10 | 0 | 245 | 345 | 0 | 51 | 0 | 202 | 0 | 0 | 111 | 17 | 0 | 13 | 0 | 102 | 0 | 17 | 0 | 305 | 0 | 0 | 41 | 50 | 141 | 2 | 17 | 0 | 75 | 30 | 0 | 0 | 158 | 0 | 19 | 58 | 68 | 0 | 9.28 | 0 | 5456.58 | 408 | 257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 790 | 0 | 0 | 0 | 818.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.84 | 26 | 0 | 0 | 11.28 | 169 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0.97 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 1.3 | 29 | 0.14 | 0 | 184 | 100 | 180 | 0 | 309 | 350 | 0 | 4064.88 | 9521.46 | 97.28
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 34.3 | 0 | 25 | 150 | 30 | 0 | 52 | 148 | 0 | 225 | 0 | 123 | 0 | 17 | 0 | 0 | 0 | 1 | 0 | 30 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 25 | 0.08 | 46 | 0 | 6 | 720 | 0 | 0 | 0 | 0 | 14 | 173 | 0 | 0 | 0 | 1130 | 1 | 10 | 0 | 300 | 295 | 0 | 51 | 0 | 190 | 0 | 0 | 111 | 17 | 0 | 13 | 0 | 98 | 0 | 2 | 0 | 310 | 0 | 0 | 41 | 50 | 140 | 0 | 17 | 0 | 78 | 30 | 0 | 0 | 157 | 0 | 19 | 58 | 71 | 0 | 1.2 | 0 | 5374.58 | 408 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 834 | 0 | 0 | 0 | 955.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.95 | 5 | 0 | 0 | 1.73 | 189 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0.18 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.2 | 5 | 0.02 | 0 | 180 | 140 | 220 | 0 | 308 | 375 | 0 | 4310.33 | 9684.91 | 97.28
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 50.4 | 0 | 60 | 16 | 145 | 0 | 55 | 152 | 0 | 225 | 0 | 275 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 30 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 36 | 0 | 46 | 0 | 9 | 720 | 0 | 0 | 0 | 0 | 40 | 173 | 0 | 0 | 0 | 1165 | 0 | 30 | 0 | 220 | 340 | 0 | 51 | 0 | 200 | 0 | 0 | 112 | 92 | 0 | 18 | 0 | 110 | 0 | 0 | 0 | 320 | 0 | 0 | 41 | 50 | 155 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 157 | 0 | 19 | 58 | 70 | 0 | 0 | 0 | 5785.4 | 408 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 974 | 0 | 0 | 0 | 1229.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 284 | 140 | 220 | 0 | 309 | 427 | 0 | 4993.22 | 10778.62 | 97.27
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 41.8 | 0 | 64 | 0 | 0 | 0 | 0 | 54 | 0 | 225 | 0 | 495 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 29.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 36 | 0 | 46 | 0 | 19 | 720 | 0 | 0 | 0 | 0 | 64 | 173 | 0 | 0 | 0 | 1165 | 0 | 30 | 0 | 210 | 300 | 0 | 51 | 0 | 219 | 0 | 0 | 114 | 51 | 0 | 19 | 0 | 104 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 50 | 155 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 157 | 0 | 19 | 58 | 71 | 0 | 0 | 2 | 5698.3 | 407 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1101 | 0 | 0 | 0 | 1456.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 140 | 220 | 0 | 307 | 483 | 0 | 5424.97 | 11123.27 | 97.27
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 17 | 0 | 79 | 0 | 0 | 0 | 0 | 16 | 0 | 225 | 0 | 510 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 30 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 12 | 0 | 46 | 0 | 19 | 720 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 215 | 315 | 0 | 51 | 0 | 219 | 0 | 0 | 114 | 17 | 0 | 19 | 0 | 102 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 50 | 157 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 157 | 0 | 19 | 58 | 71 | 0 | 0 | 0 | 5537 | 408 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 0 | 0 | 0 | 1452.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 140 | 220 | 0 | 308 | 540 | 0 | 5460.42 | 10997.42
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 16.2 | 0 | 81 | 0 | 0 | 0 | 0 | 17 | 0 | 225 | 0 | 500 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 29.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 12 | 0 | 46 | 0 | 23 | 720 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1161 | 0 | 0 | 0 | 215 | 305 | 0 | 51 | 0 | 216 | 0 | 0 | 114 | 17 | 0 | 19 | 0 | 108 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 50 | 158 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 157 | 0 | 19 | 58 | 71 | 0 | 0 | 0 | 5454.7 | 407 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1118 | 0 | 0 | 0 | 1451.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 140 | 220 | 0 | 306 | 546 | 0 | 5492.36 | 10947.06 | 97.27
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 450 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 29.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 26 | 720 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1161 | 0 | 0 | 0 | 215 | 305 | 0 | 51 | 0 | 204 | 0 | 0 | 115 | 0 | 0 | 19 | 0 | 104 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 50 | 158 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 157 | 0 | 19 | 58 | 71 | 0 | 0 | 0 | 5316.5 | 408 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1117 | 0 | 0 | 0 | 1319.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 140 | 220 | 0 | 312 | 589 | 0 | 5351.61 | 10668.11 | 97.26
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 30 | 720 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1098 | 0 | 0 | 0 | 215 | 280 | 0 | 51 | 0 | 180 | 0 | 0 | 114 | 0 | 0 | 19 | 0 | 110 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 50 | 151 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 157 | 0 | 19 | 25 | 71 | 0 | 0 | 0 | 5095.5 | 408 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1091 | 0 | 0 | 0 | 1175.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 140 | 220 | 0 | 274 | 550 | 0 | 5068.56 | 10164.06 | 97.26
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 36 | 675 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 980 | 0 | 0 | 0 | 230 | 280 | 0 | 51 | 0 | 180 | 0 | 0 | 112 | 0 | 0 | 19 | 0 | 102 | 0 | 0 | 0 | 305 | 0 | 0 | 41 | 50 | 150 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 156 | 0 | 19 | 25 | 71 | 0 | 0 | 0 | 4893.5 | 408 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 960 | 0 | 0 | 0 | 965.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 140 | 220 | 0 | 269 | 500 | 0 | 4584.39 | 9477.89 | 97.26
Total KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8424000 | 0 | 0 | 282600 | 41400 | 368352 | 1145760 | 740684 | 0 | 311189 | 1131840 | 0 | 4969000 | 0 | 9802871 | 0 | 209321 | 0 | 244000 | 0 | 40416 | 0 | 553200 | 336240 | 0 | 0 | 0 | 15305 | 0 | 0 | 487200 | 0 | 97344 | 0 | 16320 | 212160 | 18840 | 1107480 | 55200 | 335520 | 16290909.09 | 0 | 0 | 38880 | 0 | 419018 | 3917759 | 0 | 0 | 0 | 23350907 | 110970 | 398109 | 0 | 6131500 | 7714100 | 0 | 876831 | 0 | 4916000 | 0 | 79680 | 2421453 | 762720 | 35280 | 342010 | 0 | 2375040 | 0 | 393300 | 0 | 7646000 | 0 | 0 | 902000 | 1133880 | 3605564 | 35900 | 325080 | 0 | 1353600 | 649440 | 0 | 0 | 3416170 | 0 | 327600 | 799200 | 2450880 | 4000 | 121840 | 3360 | 124295222.09 | 9439272 | 8034048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162720 | 16109088 | 0 | 0 | 0 | 25793938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16235 | 0 | 60880 | 208030 | 0 | 0 | 109488 | 4135818 | 0 | 0 | 0 | 0 | 0 | 9220073 | 0 | 9300 | 0 | 0 | 106796 | 124275 | 116572 | 0 | 0 | 0 | 14064 | 427680 | 2188 | 0 | 5629000 | 2901000 | 5230150 | 0 | 6974545 | 10622545.45 | 0 | 105447705.45 | 229742927.54

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 06-01-2026
Power Supply Scenario
| Day Peak Generation |  |  | 10551.06 | MW | 12:00 Hr. | Energy Generated |  |  | 229.7429 |  | MKWHr.
| Day Peak Demand |  |  | 10551.06 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11123.27 | MW | 19:00 Hr. | Energy Demand |  |  | 229.7429 |  | MKWHr.
| Evening Peak Demand |  |  | 11123.27 | MW | 19:00 Hr. | Maximum Temperature |  |  | 20.2 |  | °C
| Minimum Generation of the Day |  |  | 7255.55 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 736.73 |  | MMCFD
| Maximum Generation of the Day |  |  | 11123.27 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.601 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 24.3293 | 0 | 4.2311 | 0 | 0 | 0.040416 | 0 | 0 | 28.6009 | Gas | 101.9882 | Gas | 358567196.12
| Chattogram Zone |  |  | 4.2533 | 39.6418 | 0.85423 | 0 | 1.1075 | 0.12981 | 0 | 0.4872 | 46.4738 | Coal | 78.977 | Coal | 521573446.1587
| Cumilla Zone |  |  | 22.4019 | 0 | 1.2758 | 0 | 0 | 0.3933 | 2.375 | 0 | 26.446 | HFO | 7.7309 | HFO | 132227039.64
| Mymensingh Zone |  |  | 2.4509 | 0 | 1.1302 | 0 | 0 | 0.12584 | 0 | 0 | 3.7069 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 19.0317 | 0 | 0 | 0 | 0 | 0.0359 | 0 | 0 | 19.0676 | Hydro | 1.1075 | Hydro | 110748
| Khulna Zone |  |  | 8.034 | 16.1091 | 0 | 0 | 0 | 0.16272 | 9.4393 | 0 | 33.7451 | Solar | 1.8439 | Solar | 28373325.21
| Barishal Zone |  |  | 8.1311 | 23.2261 | 0 | 0 | 0 | 0.002188 | 0 | 0 | 31.3594 | Import | 37.6082 | Import | 238775989.68
| Rajshahi Zone |  |  | 13.3559 | 0 | 0.016235 | 0 | 0 | 0.3877 | 25.7939 | 0 | 39.5538 | Wind | 0.4872 | Wind | 7166712
| Rangpur Zone |  |  | 0 | 0 | 0.22337 | 0 | 0 | 0.56602 | 0 | 0 | 0.78939
| Total |  |  | 101.9882 | 78.977 | 7.7309 | 0 | 1.1075 | 1.8439 | 37.6082 | 0.4872 | 229.7429
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 358567196.12 |  | Hydro | 110748
|  |  |  | Coal | 521573446.1587 |  | Solar | 28373325.21
|  |  |  | HFO | 132227039.64 |  | Import | 238775989.68
|  |  |  | HSD | 0 |  | Wind | 7166712
[5 empty] | Total: | 128,67,94,456 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 9.4393 | Peak Hr Flow | 407.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 6818909.1 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 25.7939 | Peak Hr Flow | 1456.97 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1879 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.375 | Peak Hr Flow | 104.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1968 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 37.6082 | Peak Hr Flow | 1967.97 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3961
|  |  |  | Chattogram |  | 0 |  | 1108
|  |  |  | Cumilla |  | 0 |  | 902
|  |  |  | Mymensingh |  | 0 |  | 902
|  |  |  | Sylhet |  | 0 |  | 396
|  |  |  | Khulna |  | 0 |  | 1323
|  |  |  | Barishal |  | 0 |  | 321
|  |  |  | Rajshahi |  | 0 |  | 1037
|  |  |  | Rangpur |  | 0 |  | 743
|  |  |  | Total |  | 0 |  | 10693
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:15 | 17:58 | Rampura 230/132kV S/S Aux Transformer-01 LT Scheduled S/D Due to Annual Maintenance on
ATR-04
| 08:18 | 17:58 | Rampura 230/132kV S/S Auto Transformer - 04 LT Scheduled S/D Due to Annual Maintenance
| 08:18 | 17:58 | Rampura 230/132kV S/S Auto Transformer - 04 HT Scheduled S/D Due to Annual Maintenance
| 08:18 | 18:04 | Rampura 230/132kV S/S NLDC Trafo LT Scheduled S/D Due to Annual Maintenance on ATR-04
| 08:18 | 18:04 | Rampura 230/132kV S/S NLDC Trafo HT Scheduled S/D Due to Annual Maintenance on ATR-04
| 08:24 | 18:08 | Hasnabad-Shyampur 230kV Ckt-1 Scheduled S/D from Shyampur 230/132kV end Due to Deadline
checking and annual maintenance and from Hasnabad 230/132kV end Due to Annual maintenance
| 08:28 | 16:20 | Halishahar 132/33kV S/S 415T(TR-2) HT Project Work S/D Due to Due to Transformer painting
and maintenance work by ESPNER Project.
| 08:29 | 15:50 | Aminbazar 400/230/132kV S/S Gopalganj-2 Scheduled S/D Due to Annual maintenance
| 08:34 | 16:06 | Magura-Narail 132kV Ckt-1 Scheduled S/D from Narail 132/33kV end Due to Annual
maintenance and from Magura 132/33kV end Due to For Annual Maintenance.
| 08:35 | 17:58 | Rampura 230/132kV S/S Aux Transformer-01 HT Scheduled S/D Due to Annual Maintenance on
ATR-04
| 08:38 | 17:47 | Jhenaidah-Khulna 230kV Ckt-2 Scheduled S/D from Jhenaidah 230/132kV end Due to Annual
Maintenance. and from Khulna(S) 230/132kVend.
| 08:41 | 17:55 | Bibiyana-Fenchuganj 230 kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
deadline cheaking
| 08:42 | 17:31 | Aminbazar-Kaliakoir 230kV Ckt-1 Scheduled S/D from Kaliakoir 400/230/132kV end Due to
Deadline checking .
| 08:50 | 16:44 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Scheduled S/D from Shahjibazar 132/33kV end Due to
Annaul Maintenance. and from Brahmanbaria 132/33kVend.
| 08:54 | 15:47 | Siddhirganj 132/33kV S/S 132kV MTR 2 Scheduled S/D Due to Annual Maintenance Works
| 08:56 | 17:56 | Aminbazar-Airport(Old) 230kV Ckt-1 Scheduled S/D from Agargaon 230/132kV end Due to
Annual Maintenance ( Deep Cleaning of Insulator)
| 09:02 | 16:27 | Bagerhat 132/33kV S/S Transformer-2 (413 T) LT Scheduled S/D Due to Yearly maintenance
| 09:05 | 19:28 | Bogura-Sirajganj 230 kV Ckt-1 Scheduled S/D from Bogura 230/132kV end Due to Annual
Maintenance
| 09:05 | 15:30 | Chowmuhani-Feni 132 kV Ckt-2 Scheduled S/D from Feni 132/33kV end Due to for annual
maintenance. and from Feni 230/132kV end Due to Feni 132kv end annual maintenance.
| 09:08 | 17:40 | Bhaluka 132/33kV S/S BR Powergen Ckt- 01 Scheduled S/D Due to Annual maintenance
| 09:09 | 17:45 | Bhaluka 132/33kV S/S BR Powergen Ckt- 02 Scheduled S/D Due to Annual Maintenance
| 09:12 | 16:27 | Bagerhat 132/33kV S/S Transformer-2 (413 T) HT Scheduled S/D Due to Yearly maintenance
| 09:13 | 17:15 | Mirpur 132/33kV S/S T1 HT Scheduled S/D Due to Annual Maintenance
| 09:13 | 17:22 | Mirpur 132/33kV S/S T1 LT Scheduled S/D Due to Annual Maintenance
| 09:18 | 16:25 | Sylhet 132/33kV S/S T1 LT Scheduled S/D Due to Due to Ten delta Test
| 09:18 | 16:42 | Jhenaidah 132/33kV S/S Transformer T-2 LT Scheduled S/D Due to Annual maintenance
| 09:19 | 16:41 | Jhenaidah 132/33kV S/S Transformer T-2 HT Scheduled S/D Due to Annual maintenance
| 09:20 | 16:25 | Sylhet 132/33kV S/S T1 HT Scheduled S/D Due to Due to Ten delta Test
| 09:23 | 18:12 | Siddhirganj-Ullon (T at Maniknagar) 132kV Ckt-1 Scheduled S/D from Siddhirganj 132/33kV
end Due to Maintenance work by NLDC
| 09:24 | 12:38 | Chhatak 132/33kV S/S T-3 LT Scheduled S/D Due to H.Oil Leakage Repare of T-3 132 kv GCB
| 09:24 | 12:37 | Chhatak 132/33kV S/S T-3 HT Scheduled S/D Due to H.Oil Leakage Repare of T-3 132 kv GCB
| 09:28 | 17:06 | Gopalganj 400/132kV S/S 400kV Amtoli Ckt-2 Scheduled S/D Due to Annual Maintenance
| 09:28 | 17:06 | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-2 Scheduled S/D
| 09:30 | 15:42 | Cox'sbazar-Dohazari 132 kV Ckt-1 Scheduled S/D from Coxsbazar 132/33kV end Due to Annual
maintenance and from Dohazari 132/33kV end Due to Annual maintenance.
| 09:30 | 16:03 | Dhamrai-Kaliakoir 132 kV Ckt-1 Scheduled S/D from Dhamrai 132/33kV end Due to Annual
Maintenance and from Kaliakoir 400/230/132kV end Due to Deadline checking by Dhamrai End.
| 09:35 | 21:11 | Shahjadpur-Ullahpara 132kV Ckt-1 Scheduled S/D from Ullahpara 132/33kV end Due to Annual
Maintenance work to Shahjadpur end. and from Shahjadpur 132/33kV end Due to Annual
Maintenance
| 09:36 | 16:50 | Tongi 230/132/33kV S/S T-01 HT Scheduled S/D Due to Annual maintenance work
| 09:36 | 16:52 | Tongi 230/132/33kV S/S T-01 LT Scheduled S/D Due to Annual maintenance work
| 09:38 |  | Kabirpur 132/33kV S/S XFR, T-2 LT Scheduled S/D Due to Annual maintenance
| 09:39 |  | Kabirpur 132/33kV S/S XFR, T-2 HT Scheduled S/D Due to Annual maintenance
| 09:44 | 17:06 | Mymensingh RPCL-Tangail 132kV Ckt-1 Scheduled S/D from Ghatail 132/33kV end Due to dead
line checking and from Muktagacha 132/33kV end Due to S/D by Ghatail S/S
| 09:44 |  | Bheramara 410 MW CCPP, FGMO is OFF with remarks:-
| 09:47 | 17:14 | Mirpur 132/33kV S/S Main Bus Scheduled S/D Due to Annual Maintenance
| 10:09 | 19:41 | Fatullah-Shyampur(New) 132 kV Ckt-1 Scheduled S/D from Fatullah 132/33kV end Due to
Maintenance work
| 10:13 | 15:03 | Maijdee 132/33kV S/S TR-01 HT Project Work S/D Due to Line parameter test for project
work.
| 10:14 | 15:05 | Maijdee 132/33kV S/S Tr-02 HT Project Work S/D Due to Line parameter test for project
work.
| 10:14 | 11:27 | BIPTC S/S 10CF11 Forced S/D Due to Shutdown is taken for emergency maintenance work
| 10:15 | 14:54 | Maijdee 132/33kV S/S Chowmuhoni-Maijdee ckt -01 Project Work S/D Due to Line parameter
test for project work.
| 10:37 | 14:58 | Maijdee 132/33kV S/S Chowmuhoni-Maijdee ckt -02 Project Work S/D Due to Line parameter
test for project work.
| 10:51 | 14:35 | Lakshmipur 132/33kV S/S Lakshmipur-Chowmuhani Circuit 1 Project Work S/D Due to Line
Parameter Measurement
| 10:52 | 15:33 | Gopalganj 400/132kV S/S ATR-03 LT Project Work S/D Due to Fire Fitting testing &
Commissioning.
| 10:53 | 16:49 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 Scheduled S/D Due to Kaliakoir
ckt-01 shutdown due to annual maintenance
| 11:12 | 15:32 | Gopalganj 400/132kV S/S ATR-03 HT Project Work S/D Due to Fire Fitting testing &
Commissioning.
| 11:29 | 16:43 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Forced S/D Due to Maintenance Works EGCB ends
| 12:00 |  | Day Peak Generation: 10546 MW.
| 12:10 |  | Ghorasal- Ishwardi 230 kV Ckt-2 Scheduled S/D from Ghorashal 230kV end Due to
Maintenance and from Ishurdi 230/132kVend.
| 12:26 | 19:15 | Naogaon-Niyamatpur 132kV Ckt-1 Project Work S/D from Niamatpur 132/33kV end Due to
(Project Work) As per the instruction of Bogura ALDC. and from Naogaon 132/33kV end Due
to Project work.
| 12:33 | 14:40 | Nawabganj 132/33kV S/S TR-1 LT Forced S/D Due to Oil REFILLING
| 12:34 | 14:39 | Nawabganj 132/33kV S/S TR-1 HT Forced S/D Due to OIL REFILLING
| 13:00 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U2
|  | 14:00 | Rajendrapur 132/33kV S/S 132 kV BUS-1 is restored.
| 14:21 | 15:40 | Cox'sbazar-Dohazari 132 kV Ckt-1 Scheduled S/D from Dohazari 132/33kV end Due to Annual
maintenance.
| 14:22 | 14:35 | Keranigonj 230/132/33kV S/S TR-1 LT Tripped showing Siprotec 7UT612 relays Due to 33kV | [7 empty] | 31.0MW load
|  |  | feeder fault | [7 empty] | interrup.
| 14:32 |  | Rajendrapur 132/33kV S/S 132 kV BUS-2 Project Work S/D Due to Bus-1 shutdown restored and
Bus-2 shutdown taken for Bus-2 extention part maintenance work.
| 14:40 |  | Chandpur 132/33kV S/S 422T(T-5) LT Forced S/D Due to PT MCB Trip
|  | 14:40 | Chandpur 132/33kV S/S 402T (T-01) LT is restored.
| 17:16 | 17:24 | Chhatak 132/33kV S/S Bus-B Forced S/D Due to Emergency shutdown required BUS-B due to
kite stuck in BUS-B PT.
|  | 17:18 | Kurigram-Lalmonirhat 132kV Ckt-1 is restored.
|  | 17:22 | Mirpur 132/33kV S/S T1 LT is restored.
|  | 18:10 | Ghorasal-Joydeb-B 132kV Ckt-2 is restored.
| 19:00 |  | Evening peak generation 11121 MW
| 05:00 |  | Minimum Generation is 7120 MW
| 07:31 |  | Shyampur 230/132kV S/S 230 kV APR (D04) Scheduled S/D Due to for Dead Line checking
| 07:31 |  | APR-Hasnabad 230kV Ckt-2 Scheduled S/D from Hasnabad 230/132kV end Due to Annual
Maintenance
| 07:48 |  | Bibiyana-Fenchuganj 230 kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Deadline Checking
| 07:58 |  | Khulshi-Madunaghat 132kV Ckt-2 Scheduled S/D from Khulshi 132/33kV end.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 06-01-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 335 | 8424000 | FGMO, Gas Shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4969000 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 110 | 244000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 41.8 | 282600 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 1145760 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 311189 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 209321 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 29.5 | 553200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 336240 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 740684 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 64 | 368352 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 1131840 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 40416 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 41400 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 495 | 9802871 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 0 | 0 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1369.3 | 28600873
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 110970 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 38880 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1107480 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 173 | 3917759 | Plant availability less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 64 | 419018 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 97344 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 16320 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 19 | 335520 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 18840 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 15305 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 55200 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 36 | 212160 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1165 | 23350907 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 16 | 487200 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 720 | 16290909.09 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 2239 | 46473812.09
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 219 | 4916000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 300 | 7714100 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 210 | 6131500 | FGMO, Gas Shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 876831 | Machine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 30 | 398109 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 114 | 2421453 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 762720 | -
| Import (Tripura) |  | Import | 0 | 160 | 104 | 2375040 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 342010 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 35280 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 79680 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 393300 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1098 | 26446023
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 71 | 2450880 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 4000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 799200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 327600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 121840 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 2 | 3360 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 150 | 3706880
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 35900 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 902000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 50 | 1133880 | machine problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3605564 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 649440 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1353600 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 157 | 3416170 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 325080 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7646000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2325 | 842 | 19067634
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 407 | 9439272 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 340 | 8034048 | FGMO
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 162720 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1101 | 16109088 | U-2 Under Maintenance
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1848 | 33745128
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 307 | 6974545 | Machine Problem
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 140 | 2901000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 483 | 10622545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5230150 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 278 | 5629000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2188 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1428 | 31359428.45
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 60880 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 16235 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 179 | 4135818 | Foggy Weather
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9220073 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 9300 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1456.97 | 25793938 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 109488 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 208030 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2049.97 | 39553762
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 116572 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 14064 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 106796 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 124275 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 427680 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 99 | 789387
Eastern Grid Total |  |  |  |  | 17398.245 | 5698.3 | 124295222.09
Western Grid Total |  |  |  |  | 10984.003 | 5424.97 | 105447705.45
National Grid Total |  |  |  |  | 28382.248 | 11123.27 | 229742927.54
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 06-01-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7268.6 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3424.4 | MW
i) Dhaka area |  |  | 3960.6 |  | MW | i) Khulna area |  |  |  | 1323 | MW
ii) Chattogram area |  |  | 1108 |  | MW | ii) Barishal area |  |  |  | 321 | MW
iii) Cumilla area |  |  | 902 |  | MW | iii) Rajshahi area |  |  |  | 1037.4 | MW
iv) Mymensingh area |  |  | 902 |  | MW | iv) Rangpur area |  |  |  | 743 | MW
v) Sylhet area |  |  | 396 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10693 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 71 | 12:00 | 133 | Netrakona | 116 | 18:00
2 | AKSML | 107.5 | 07:00 | 68 | Hathazari | 58 | 18:30 | 134 | New | 70.2 | 12:00
3 | Aftabnagar | 26 | 13:00 | 69 | Hatirjheel | 21 | 15:00 | 135 | Niamatpur | 51 | 13:00
4 | Agargaon | 85 | 13:00 | 70 | Ishurdi | 55 | 18:30 | 136 | Noapara | 41 | 18:30
5 | Agrabad | 32 | 12:00 | 71 | Jaldhaka | 60 | 18:00 | 137 | PHP | 5 | 16:00
6 | Amnura | 25 | 12:00 | 72 | Jamalpur | 96 | 18:00 | 138 | Pabna | 81 | 18:00
7 | Ashuganj | 62 | 13:00 | 73 | Jashore | 110 | 13:00 | 139 | Palashbari | 84 | 18:00
8 | BSRM | 201 | 15:00 | 74 | Jhenaidah | 106 | 18:00 | 140 | Panchagarh | 41 | 18:30
9 | Bagerhat | 64 | 18:00 | 75 | Joydebpur | 108 | 12:00 | 141 | Patiya | 7 | 18:00
10 | Bajitpur | 69 | 19:00 | 76 | Joypurhat | 38 | 18:30 | 142 | Patuakhali | 39.6 | 21:00
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 13 | 11:00 | 143 | Payra | 28 | 18:00
12 | Bakulia | 61 | 18:00 | 78 | KSRM | 25 | 16:00 | 144 | Postogola | 41 | 13:00
13 | Banani | 23.8 | 13:00 | 79 | Kabirpur | 180 | 17:00 | 145 | Purbachal | 20 | 13:00
14 | Bangabhaban | 8 | 10:00 | 80 | Kachua | 49 | 18:00 | 146 | Purbasadipur | 110 | 19:30
15 | Barapukuria | 50 | 18:00 | 81 | Kallyanpur | 75 | 18:00 | 147 | Rahanpur | 22 | 20:00
16 | Barguna | 16 | 20:00 | 82 | Kalurghat | 28 | 09:00 | 148 | Rahim | 21 | 10:00
17 | Barishal | 79 | 13:00 | 83 | Kamrangirchar | 62 | 13:00 | 149 | Rajbari | 64 | 18:00
18 | Barishal-230 | 80 | 18:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 122 | 08:00
19 | Baroaulia | 66 | 18:00 | 85 | Kasba | 23 | 13:00 | 151 | Rajshahi | 75 | 21:00
20 | Baroirhat | 49 | 13:00 | 86 | Kazla | 95 | 13:00 | 152 | Rajshahi-230 | 81 | 13:00
21 | Bashundhara | 134 | 14:00 | 87 | Keranigonj | 75 | 13:00 | 153 | Ramganj | 100 | 13:00
22 | BashundharaCement | 7 | 00:00 | 88 | Khagrachori | 26 | 18:00 | 154 | Rampur | 26 | 13:00
23 | Beanibazar | 46 | 18:00 | 89 | Khulna | 53 | 13:00 | 155 | Rangamati | 13 | 18:00
24 | Benapole | 64 | 08:00 | 90 | Khulshi | 153 | 18:00 | 156 | Rangpur | 114 | 18:00
25 | Bhaluka | 119 | 18:30 | 91 | Kishoreganj | 88 | 18:30 | 157 | Ruppur | 2.2 | 09:00
26 | Bhandaria | 37 | 20:00 | 92 | Kodda | 239 | 09:00 | 158 | SSM | 5 | 00:00
27 | Bhangura | 24 | 18:00 | 93 | Kulaura | 29 | 18:00 | 159 | Saidpur | 96 | 18:00
28 | Bheramara(GK) | 43 | 18:00 | 94 | Kurigram | 49 | 18:00 | 160 | Satkhira | 93 | 08:00
29 | Bhulta | 197 | 08:00 | 95 | Kushtia | 122 | 13:00 | 161 | Satmasjid | 77 | 13:00
30 | Bog-Sherpur | 54 | 18:00 | 96 | Laksam | 23 | 12:00 | 162 | Savar | 180 | 11:00
31 | Bogura | 111 | 18:30 | 97 | Lakshmipur | 20 | 00:00 | 163 | SevenRings | 2.98 | 17:00
32 | Borhanuddin | 64 | 21:00 | 98 | Lalbag | 54 | 12:00 | 164 | ShahCement | 33 | 04:00
33 | Brahmanbaria | 90 | 18:00 | 99 | Lalmonirhat | 48 | 18:30 | 165 | Shahjadpur | 57 | 18:30
34 | Cantonment | 86 | 13:00 | 100 | MI_Cement | 18.7 | 03:00 | 166 | Shahjibazar | 82 | 18:00
35 | Chandina | 10 | 13:00 | 101 | Madanganj | 43 | 12:00 | 167 | Shahmirpur | 36 | 17:00
36 | Chandpur | 50 | 18:00 | 102 | Madaripur | 76 | 19:30 | 168 | Shariatpur | 57 | 19:30
37 | Chandraghona | 26 | 18:00 | 103 | Madartek | 54 | 13:00 | 169 | Sherpur | 120 | 18:00
38 | Chapai | 51 | 13:00 | 104 | Madunaghat | 95 | 00:00 | 170 | Shikalbaha | 21 | 14:00
39 | Charsaidpur | 37 | 07:00 | 105 | Magura | 50 | 18:00 | 171 | Shitalakhya | 67 | 13:00
40 | Chauddagram | 47 | 11:00 | 106 | Mahasthangarh | 52 | 18:30 | 172 | Sholosohor | 33 | 12:00
41 | Chhatak | 21 | 01:00 | 107 | Maijdee | 27 | 19:30 | 173 | Shyampur | 132 | 12:00
42 | Chowmuhani | 129 | 13:00 | 108 | Manikganj | 101 | 18:00 | 174 | Siddhirganj | 93 | 12:00
43 | Chuadanga | 81 | 18:00 | 109 | Maniknagar | 52 | 13:00 | 175 | Sirajganj | 86 | 18:30
44 | Coxsbazar | 108 | 18:00 | 110 | Matarbari | 39 | 18:00 | 176 | Sonargaon | 117 | 19:30
45 | Cumilla(N) | 106 | 18:30 | 111 | Matuail | 44 | 17:00 | 177 | Sreemongol | 55 | 18:00
46 | Cumilla(S) | 123 | 14:00 | 112 | Metrorail_Motijheel | 21 | 18:30 | 178 | Sreepur | 93 | 11:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 5 | 15:00 | 179 | Srinagar | 31.8 | 13:00
48 | Daudkandi | 88 | 00:00 | 114 | Millgate | 74 | 11:00 | 180 | Sunamganj | 40 | 18:30
49 | DhakaUniversity | 48 | 13:00 | 115 | Mirpur | 112 | 12:00 | 181 | Sylhet | 39 | 19:00
50 | Dhamrai | 90 | 08:00 | 116 | Mirsorai | 10 | 09:00 | 182 | Sylhet-132 | 99 | 13:00
51 | Dhanmondi | 63.4 | 13:00 | 117 | Mirzapur | 38 | 08:00 | 183 | TK | 16 | 18:30
52 | Dohazari | 68 | 19:30 | 118 | Mithapukur | 44 | 18:00 | 184 | Tangail | 122 | 18:30
53 | Faridpur | 121 | 18:30 | 119 | Modern | N/A | N/A | 185 | Taraganj | 16 | 18:00
54 | Fatullah | 82 | 18:00 | 120 | Mogbazar | 49.3 | 15:00 | 186 | Tasnim | 23 | 04:00
55 | Fenchuganj | 24 | 13:00 | 121 | Mongla | 41 | 18:00 | 187 | Thakurgaon | 83 | 18:30
56 | Feni | 79 | 14:00 | 122 | Motijheel | 28 | 13:00 | 188 | Tongi | 99 | 11:00
57 | GPH | 7 | 01:00 | 123 | Muktagacha | 28 | 08:00 | 189 | Ullahpara | 25 | 18:00
58 | Ghatail | 66 | 08:00 | 124 | Munshiganj | 75 | 13:00 | 190 | Ullon | 39 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 7 | 13:00 | 191 | Uttara | 70 | 12:00
60 | Ghorashal-230 | 80 | 11:00 | 126 | Mymensingh | 153 | 18:00 | 192 | UttaraNew | 65 | 23:00
61 | Goalpara | 30 | 13:00 | 127 | Naogaon | 97 | 13:00 | 193 | Zigatola | 74 | 13:00
62 | Gollamari | 86 | 13:00 | 128 | Narail | 45 | 18:30
63 | Gopalganj | 84.2 | 18:00 | 129 | Narinda | 57 | 13:00
64 | Gulshan | 70 | 13:00 | 130 | Narshingdi | 134 | 21:00
65 | Halishahar | 52.5 | 18:00 | 131 | Natore | 108 | 18:00
66 | HaripurSBU | 87 | 12:00 | 132 | Nawabganj | 30.4 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 06-01-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 8883.8 | 0 |  | 8883.8
1:00 | 8156.12 | 0 |  | 8156.12
2:00 | 7706.19 | 0 |  | 7706.19
3:00 | 7418.93 | 0 |  | 7418.93
4:00 | 7320.9 | 0 |  | 7320.9
5:00 | 7255.55 | 0 |  | 7255.55
6:00 | 7731.5 | 0 |  | 7731.5
7:00 | 8400.78 | 0 |  | 8400.78
8:00 | 9516.24 | 0 |  | 9516.24
9:00 | 10157.47 | 0 |  | 10157.47
10:00 | 9909.98 | 0 |  | 9909.98
11:00 | 10068.76 | 0 |  | 10068.76
12:00 | 10551.06 | 0 |  | 10551.06
13:00 | 11066.31 | 0 |  | 11066.31
14:00 | 10403.95 | 0 |  | 10403.95
15:00 | 9771.12 | 0 |  | 9771.12
16:00 | 9521.46 | 0 |  | 9521.46
17:00 | 9684.91 | 0 |  | 9684.91
18:00 | 10778.62 | 0 |  | 10778.62
19:00 | 11123.27 | 0 |  | 11123.27
19:30 | 10997.42 | 0 |  | 10997.42
20:00 | 10947.06 | 0 |  | 10947.06
21:00 | 10668.11 | 0 |  | 10668.11
22:00 | 10164.06 | 0 |  | 10164.06
23:00 | 9477.89 | 0 |  | 9477.89
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 06-01-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5006 | 3877.8 | 8883.8 | DAILY GENERATION CURVE
00:30 | 4764.5 | 3755.46 | 8519.96
01:00 | 4523 | 3633.12 | 8156.12 | 06-01-2026
01:30 | 4385.5 | 3545.655 | 7931.155
02:00 | 4248 | 3458.19 | 7706.19
02:30 | 4184.5 | 3378.06 | 7562.56
03:00 | 4121 | 3297.93 | 7418.93
03:30 | 4092 | 3277.915 | 7369.915
04:00 | 4063 | 3257.9 | 7320.9
04:30 | 4043.5 | 3244.725 | 7288.225
05:00 | 4024 | 3231.55 | 7255.55
05:30 | 4115 | 3378.525 | 7493.525
06:00 | 4206 | 3525.5 | 7731.5
06:30 | 4409.72 | 3656.42 | 8066.14
07:00 | 4613.44 | 3787.34 | 8400.78
07:30 | 4866.87 | 4091.64 | 8958.51
08:00 | 5120.3 | 4395.94 | 9516.24
08:30 | 5270.395 | 4566.46 | 9836.855
09:00 | 5420.49 | 4736.98 | 10157.47
09:30 | 5356.75 | 4676.975 | 10033.725
10:00 | 5293.01 | 4616.97 | 9909.98
10:30 | 5416.085 | 4573.285 | 9989.37
11:00 | 5539.16 | 4529.6 | 10068.76
11:30 | 5804.21 | 4505.7 | 10309.91
12:00 | 6069.26 | 4481.8 | 10551.06
12:30 | 6260.705 | 4547.98 | 10808.685
13:00 | 6452.15 | 4614.16 | 11066.31
13:30 | 6218.62 | 4516.51 | 10735.13
14:00 | 5985.09 | 4418.86 | 10403.95
14:30 | 5812.51 | 4275.025 | 10087.535
15:00 | 5639.93 | 4131.19 | 9771.12
15:30 | 5548.255 | 4098.035 | 9646.29
16:00 | 5456.58 | 4064.88 | 9521.46
16:30 | 5415.58 | 4187.605 | 9603.185
17:00 | 5374.58 | 4310.33 | 9684.91
17:30 | 5579.99 | 4651.775 | 10231.765
18:00 | 5785.4 | 4993.22 | 10778.62
18:30 | 5741.85 | 5209.095 | 10950.945
19:00 | 5698.3 | 5424.97 | 11123.27
19:30 | 5537 | 5460.42 | 10997.42
20:00 | 5454.7 | 5492.36 | 10947.06
20:30 | 5385.6 | 5421.985 | 10807.585 |  | Executive Engineer
21:00 | 5316.5 | 5351.61 | 10668.11 |  | Network Operation Division
21:30 | 5206 | 5210.085 | 10416.085
22:00 | 5095.5 | 5068.56 | 10164.06
22:30 | 4994.5 | 4826.475 | 9820.975
23:00 | 4893.5 | 4584.39 | 9477.89

## En-Curve
QF-LDC-12
Date | 06-01-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2837 | 1551 | 433 | 0 | 98 | 1031.8 | 46 | 2815 | 0 | 0 | 19 | 0 | 0 | 53 | 0 | DAILY ENERGY CURVE
00:30 | 2849 | 1433 | 433.5 | 0 | 88 | 933.46 | 46 | 2677 | 0 | 0 | 12.5 | 0 | 0 | 47.5 | 0 | 06-01-2026
01:00 | 2861 | 1315 | 434 | 0 | 78 | 835.12 | 46 | 2539 | 0 | 0 | 6 | 0 | 0 | 42 | 0
01:30 | 2725.5 | 1284.5 | 434 | 0 | 78 | 836.155 | 46 | 2483 | 0 | 0 | 3 | 0 | 0 | 41 | 0 | Energy Generated | 229.7429 |  | MKWHr
02:00 | 2590 | 1254 | 434 | 0 | 78 | 837.19 | 46 | 2427 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2562.5 | 1247 | 367 | 0 | 77 | 838.56 | 46 | 2383.5 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | Total Energy Requirement | 229.7429 |  | MKWHr
03:00 | 2535 | 1240 | 300 | 0 | 76 | 839.93 | 46 | 2340 | 0 | 0 | 0 | 0 | 0 | 42 | 0
03:30 | 2503 | 1238 | 297.5 | 0 | 77 | 840.915 | 46 | 2326 | 0 | 0 | 0 | 0 | 0 | 41.5 | 0
04:00 | 2471 | 1236 | 295 | 0 | 78 | 841.9 | 46 | 2312 | 0 | 0 | 0 | 0 | 0 | 41 | 0
04:30 | 2467.5 | 1220 | 295 | 0 | 80 | 838.225 | 46 | 2306.5 | 0 | 0 | 0 | 0 | 0 | 35 | 0
05:00 | 2464 | 1204 | 295 | 0 | 82 | 834.55 | 46 | 2301 | 0 | 0 | 0 | 0 | 0 | 29 | 0
05:30 | 2603 | 1251 | 282 | 0 | 80 | 835.025 | 46 | 2367.5 | 0 | 0 | 0 | 0 | 0 | 29 | 0
06:00 | 2742 | 1298 | 269 | 0 | 78 | 835.5 | 46 | 2434 | 0 | 0 | 0 | 0 | 0 | 29 | 0
06:30 | 2848 | 1382.5 | 268.5 | 0 | 78 | 878.92 | 46 | 2536 | 1.22 | 0 | 0 | 0 | 0 | 27 | 0
07:00 | 2954 | 1467 | 268 | 0 | 78 | 922.34 | 46 | 2638 | 2.44 | 0 | 0 | 0 | 0 | 25 | 0
07:30 | 3005 | 1513.5 | 338 | 0 | 87 | 1016.8 | 46 | 2886 | 20.71 | 0 | 27 | 0 | 0 | 18.5 | 0
08:00 | 3056 | 1560 | 408 | 0 | 96 | 1111.26 | 46 | 3134 | 38.98 | 0 | 54 | 0 | 0 | 12 | 0
08:30 | 2982 | 1560.5 | 407.5 | 0 | 101 | 1217.165 | 46 | 3370.5 | 67.19 | 8 | 64.5 | 0 | 0 | 12.5 | 0
09:00 | 2908 | 1561 | 407 | 0 | 106 | 1323.07 | 46 | 3607 | 95.4 | 16 | 75 | 0 | 0 | 13 | 0
09:30 | 2870.5 | 1532.5 | 407.5 | 0 | 108 | 1327.2 | 46 | 3473 | 130.525 | 51.5 | 75 | 0 | 0 | 12 | 0
10:00 | 2833 | 1504 | 408 | 0 | 110 | 1331.33 | 46 | 3339 | 165.65 | 87 | 75 | 0 | 0 | 11 | 0
10:30 | 2816.5 | 1549.5 | 407.5 | 0 | 111 | 1281.665 | 46 | 3270 | 197.705 | 120.5 | 182 | 0 | 0 | 7 | 0
11:00 | 2800 | 1595 | 407 | 0 | 112 | 1232 | 46 | 3201 | 229.76 | 154 | 289 | 0 | 0 | 3 | 0
11:30 | 2845.5 | 1600.5 | 407.5 | 0 | 115 | 1208.925 | 46 | 3238.5 | 248.485 | 164 | 432.5 | 0 | 0 | 3 | 0
12:00 | 2891 | 1606 | 408 | 0 | 118 | 1185.85 | 46 | 3276 | 267.21 | 174 | 576 | 0 | 0 | 3 | 0
12:30 | 2870 | 1626 | 408 | 0 | 119 | 1173.625 | 46 | 3355.5 | 279.46 | 177 | 750.1 | 0 | 0 | 4 | 0
13:00 | 2849 | 1646 | 408 | 0 | 120 | 1161.4 | 46 | 3435 | 291.71 | 180 | 924.2 | 0 | 0 | 5 | 0
13:30 | 2730 | 1514.75 | 408 | 0 | 121 | 1138.27 | 46 | 3470.5 | 302.01 | 182 | 818.6 | 0 | 0 | 4 | 0
14:00 | 2611 | 1383.5 | 408 | 0 | 122 | 1115.14 | 46 | 3506 | 312.31 | 184 | 713 | 0 | 0 | 3 | 0
14:30 | 2570.5 | 1346.25 | 408 | 0 | 117 | 1031.685 | 46 | 3461.5 | 292.4 | 181.5 | 631.2 | 0 | 0 | 1.5 | 0
15:00 | 2530 | 1309 | 408 | 0 | 112 | 948.23 | 46 | 3417 | 272.49 | 179 | 549.4 | 0 | 0 | 0 | 0
15:30 | 2610.5 | 1314 | 408 | 0 | 107 | 883.29 | 46 | 3460 | 205.1 | 164.5 | 446.4 | 0 | 0 | 1.5 | 0
16:00 | 2691 | 1319 | 408 | 0 | 102 | 818.35 | 46 | 3503 | 137.71 | 150 | 343.4 | 0 | 0 | 3 | 0
16:30 | 2734 | 1273.5 | 408 | 0 | 100 | 886.8 | 46 | 3525 | 80.535 | 150 | 396.35 | 0 | 0 | 3 | 0
17:00 | 2777 | 1228 | 408 | 0 | 98 | 955.25 | 46 | 3547 | 23.36 | 150 | 449.3 | 0 | 0 | 3 | 0
17:30 | 2807.5 | 1322.5 | 408 | 0 | 104 | 1092.235 | 46 | 3713 | 11.68 | 83 | 636.85 | 0 | 0 | 7 | 0
18:00 | 2838 | 1417 | 408 | 0 | 110 | 1229.22 | 46 | 3879 | 0 | 16 | 824.4 | 0 | 0 | 11 | 0
18:30 | 2860.5 | 1527.25 | 407.5 | 0 | 107 | 1343.095 | 46 | 3966.5 | 0 | 8 | 671.6 | 0 | 0 | 13.5 | 0
19:00 | 2883 | 1637.5 | 407 | 0 | 104 | 1456.97 | 46 | 4054 | 0 | 0 | 518.8 | 0 | 0 | 16 | 0
19:30 | 2915 | 1655 | 408 | 0 | 102 | 1452.42 | 46 | 4112 | 0 | 0 | 288 | 0 | 0 | 19 | 0
20:00 | 2828 | 1649.5 | 407 | 0 | 108 | 1451.36 | 46 | 4147 | 0 | 0 | 290.2 | 0 | 0 | 20 | 0
20:30 | 2823.5 | 1621 | 407.5 | 0 | 106 | 1385.485 | 46 | 4176.5 | 0 | 0 | 224.1 | 0 | 0 | 17.5 | 0
21:00 | 2819 | 1592.5 | 408 | 0 | 104 | 1319.61 | 46 | 4206 | 0 | 0 | 158 | 0 | 0 | 15 | 0
21:30 | 2767.5 | 1592 | 408 | 0 | 107 | 1247.585 | 46 | 4108.5 | 0 | 0 | 121 | 0 | 0 | 18.5 | 0
22:00 | 2716 | 1591.5 | 408 | 0 | 110 | 1175.56 | 46 | 4011 | 0 | 0 | 84 | 0 | 0 | 22 | 0
22:30 | 2696.5 | 1585 | 408 | 0 | 106 | 1070.475 | 46 | 3812.5 | 0 | 0 | 64 | 0 | 0 | 32.5 | 0
23:00 | 2677 | 1578.5 | 408 | 0 | 102 | 965.39 | 46 | 3614 | 0 | 0 | 44 | 0 | 0 | 43 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 06-01-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 426 | 05:00 | 399 | 10:00 | Meghnaghat | 429 | 04:00 | 405 | 16:00
Ashuganj | 414 | 5:00 | 391 | 12:00 | Payra | 425 | 03:00 | 411 | 13:00
Bhulta | 407 | 04:00 | 384 | 10:00 | Rahanpur | 423 | 05:00 | 402 | 11:00
Bibiana | 423 | 04:00 | 405 | 10:00 | Rampal | 421 | 04:00 | 401 | 12:00
BIPTC | 407 | 01:00 | 396 | 10:00
Bogura | 419 | 03:00 | 388 | 13:00
Gopalganj | 426 | 05:00 | 403 | 12:00
Kaliakoir | 422 | 05:00 | 395 | 10:00
Korerhat | 427 | 05:00 | 408 | 10:00
Madunaghat | 417 | 04:00 | 402 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 246 | 04:00 | 229 | 10:00 | Kachua | 243 | 05:00 | 233 | 10:00
AKSML | 242.9 | 04:00 | 232 | 10:00 | Kaliakoir | 244 | 04:00 | 226 | 10:00
Aminbazar | 245 | 04:00 | 231 | 10:00 | Keranigonj | 245 | 05:00 | 228 | 10:00
Ashuganj | 240 | 02:00 | 229 | 10:00 | Khulna(S) | 248 | 03:00 | 229 | 13:00
Ashuganj-400 | 240 | 02:00 | 229 | 10:00 | Korerhat | 242 | 02:00 | 232 | 10:00
Baghabari | 242 | 04:00 | 229 | 11:00 | Madunaghat | 240 | 03:00 | 233 | 09:00
Barapukuria | 235 | 04:00 | 213 | 12:00 | Madunaghat-400 | 241 | 04:00 | 233 | 10:00
Barapukuria-230 | 235 | 04:00 | 213 | 12:00 | Maniknagar | 242 | 02:00 | 228 | 10:00
Barishal | 241 | 04:00 | 231 | 12:00 | Meghnaghat | 247 | 05:00 | 232 | 10:00
Bheramara | 242 | 03:00 | 223 | 11:00 | Meghnaghat-400 | 244 | 05:00 | 230 | 10:00
Bhulta | 245 | 04:00 | 229 | 10:00 | Mirsorai | 243 | 05:00 | 233 | 10:00
Bibiana | 250 | 03:00 | 238 | 10:00 | Rajshahi | 242 | 04:00 | 222 | 11:00
BIPTC | 243 | 05:00 | 222 | 11:00 | Rampal | 249 | 02:00 | 230 | 11:00
Bogura | 246 | 03:00 | 227 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 245 | 04:00 | 226 | 13:00 | Rampura | 245 | 05:00 | 228 | 12:00
Borhanuddin | 242 | 02:00 | 236 | 12:00 | Shikalbaha | 237 | 05:00 | 230 | 12:00
BSRM | 242 | 03:00 | 232 | 10:00 | Shyampur | 243 | 04:00 | 228 | 10:00
Cumilla(N) | 242 | 03:00 | 229 | 13:00 | Siddhirganj | 243 | 06:00 | 232 | 13:00
Faridpur | 241 | 03:00 | 227 | 13:00 | Sirajgonj | 246 | 04:00 | 235 | 11:00
Fenchuganj | 246 | 04:00 | 240 | 08:00 | Sreepur | 240 | 04:00 | 225 | 12:00
Feni | 244 | 05:00 | 232 | 10:00 | Tongi | 236 | 04:00 | 225 | 19:00
Ghorashal | 245 | 07:00 | 232 | 10:00
Ghorashal-230 | 243 | 05:00 | 220 | 11:00
Gopalganj | 240 | 02:00 | 227 | 12:00
GPH | 241 | 04:00 | 232 | 10:00
Haripur | 244 | 04:00 | 229 | 12:00
Hasnabad | 242 | 01:00 | 228 | 10:00
Hathazari | 239 | 05:00 | 228 | 16:00
Ishurdi | 244 | 03:00 | 226 | 11:00
Jhenaidah | 244 | 05:00 | 220 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 04:00 | 125 | 11:00 | Laksam | 140 | 04:00 | 134 | 10:00
Agargaon | 140 | 03:00 | 130 | 10:00 | Lakshmipur | 136 | 03:00 | 130 | 10:00
Agrabad | 140 | 03:00 | 134 | 12:00 | Lalbag | 137 | 02:00 | 127 | 12:00
AKS | 136 | 07:00 | 132 | 12:00 | Lalmonirhat | 131 | 00:00 | 120 | 08:00
Aminbazar | 140 | 05:00 | 131 | 10:00 | Madanganj | 136 | 00:00 | 130 | 10:00
Amnura | 140 | 06:00 | 128 | 12:00 | Madaripur | 143 | 05:00 | 134 | 13:00
Ashuganj | 141 | 03:00 | 135 | 12:00 | Madartek | 134 | 02:00 | 125 | 12:00
Bagerhat | 137 | 05:00 | 125 | 12:00 | Madunaghat | 140 | 04:00 | 136 | 07:00
Bajitpur | 134 | 03:00 | 127 | 11:00 | Magura | 141 | 05:00 | 125 | 09:00
Bakerganj | 139 | 04:00 | 134.8 | 13:00 | Mahasthangarh | 138 | 03:00 | 127 | 12:00
Bakulia | 140 | 04:00 | 135 | 10:00 | Maijdee | 137 | 05:00 | 131 | 16:00
Banani | 135 | 03:00 | 124 | 12:00 | Manikganj | 134 | 02:00 | 123 | 10:00
Bangabhaban | 142 | 04:00 | 131 | 12:00 | Maniknagar | 141 | 02:00 | 130 | 13:00
Barapukuria | 141 | 04:00 | 127 | 13:00 | Matarbari | 133 | 03:00 | 124 | 18:00
Barguna | 139 | 00:00 | 135 | 11:00 | Matuail | 140 | 03:00 | 131 | 10:00
Barishal | 141 | 02:00 | 134 | 13:00 | Metrorail_Motijheel | 141 | 02:00 | 130 | 13:00
Barishal-230 | 142 | 04:00 | 134 | 12:00 | Metrorail_Uttara | 139 | 03:00 | 129 | 10:00
Baroaulia | 138 | 23:00 | 135 | 14:00 | Millgate | 139 | 03:00 | 125 | 10:00
Baroirhat | 138 | 03:00 | 131 | 10:00 | Mirpur | 139 | 02:00 | 129 | 10:00
Bashundhara | 135 | 03:00 | 125 | 10:00 | Mirzapur | 139 | 04:00 | 127 | 16:00
BashundharaCement | 136 | 00:00 | 130 | 10:00 | Mithapukur | 138 | 05:00 | 126 | 12:00
Beanibazar | 137 | 02:00 | 133 | 10:00 | MI_Cement | 138 | 03:00 | 127 | 10:00
Benapole | 138 | 04:00 | 114 | 12:00 | Modern | N/A | N/A | N/A | N/A
Bhaluka | 136 | 04:00 | 121 | 20:00 | Mogbazar | 136 | 02:00 | 126 | 12:00
Bhandaria | 141 | 03:00 | 135 | 10:00 | Mongla | 134 | 00:00 | 125 | 12:00
Bhangura | 142 | 05:00 | 132 | 10:00 | Motijheel | 142 | 04:00 | 131 | 12:00
Bheramara | 142 | 03:00 | 135 | 09:00 | Muktagacha | 138 | 10:00 | 127 | 18:00
Bheramara(GK) | 142 | 04:00 | 135 | 10:00 | Munshiganj | 138 | 03:00 | 129 | 10:00
Bhulta | 129 | 00:00 | 123 | 11:00 | Muradnagar | 140 | 02:00 | 132 | 10:00
Bog-Sherpur | 140 | 03:00 | 127 | 12:00 | Mymensingh | 138 | 10:00 | 122 | 19:00
Bogura | 140 | 04:00 | 129 | 12:00 | Naogaon | 136 | 04:00 | 123 | 12:00
Bogura-230 | 141 | 05:00 | 128 | 12:00 | Narail | 140 | 03:00 | 123 | 12:00
Brahmanbaria | 136 | 04:00 | 129 | 10:00 | Narinda | 141 | 02:00 | 130 | 13:00
Cantonment | 140 | 03:00 | 130 | 10:00 | Narshingdi | 134 | 01:00 | 127 | 10:00
Chandina | 142 | 04:00 | 134 | 10:00 | Natore | 139 | 05:00 | 129 | 13:00
Chandpur | 139 | 04:00 | 134 | 09:00 | Nawabganj | 138 | 05:00 | 127 | 11:00
Chandraghona | 141 | 04:00 | 135 | 16:00 | Netrakona | 130 | 23:00 | 117 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 141 | 05:00 | 132 | 08:00 | New | 139 | 03:00 | 125 | 10:00
Charsaidpur | 139 | 03:00 | 130 | 10:00 | Niamatpur | 141 | 06:00 | 133 | 09:00
Chauddagram | 138 | 02:00 | 132 | 10:00 | Noapara | 137 | 04:00 | 116 | 12:00
Chhatak | 136 | 04:00 | 130 | 13:00 | Pabna | 142 | 03:00 | 132 | 12:00
Chowmuhani | 136 | 05:00 | 129 | 16:00 | Palashbari | 135 | 04:00 | 124 | 08:00
Chuadanga | 142 | 05:00 | 123 | 12:00 | Panchagarh | 139 | 04:00 | 127 | 11:00
Coxsbazar | 132 | 03:00 | 122 | 12:00 | Patiya | 140 | 03:00 | 134 | 12:00
Cumilla(N) | 141 | 02:00 | 133 | 12:00 | Patuakhali | 137 | 04:00 | 134 | 12:00
Cumilla(S) | 141 | 02:00 | 124 | 12:00 | Payra | 140 | 01:00 | 135 | 12:00
Daganbhuiyan | 137 | 04:00 | 131 | 10:00 | PHP | 137 | 03:00 | 131 | 10:00
Daudkandi | 139 | 02:00 | 130 | 12:00 | Postogola | 138 | 05:00 | 128 | 10:00
DhakaUniversity | 134 | 02:00 | 125 | 12:00 | Purbachal | 135 | 03:00 | 124 | 12:00
Dhamrai | 140 | 02:00 | 130 | 14:00 | Purbasadipur | 135 | 04:00 | 120 | 13:00
Dhanmondi | 140.5 | 03:00 | 132 | 10:00 | Rahanpur | 142 | 03:00 | 134 | 11:00
Dohazari | 136 | 00:00 | 131 | 12:00 | Rahanpur-400 | 142 | 03:00 | 135 | 10:00
Faridpur | 139 | 05:00 | 131 | 12:00 | Rahim | 139 | 02:00 | 130 | 10:00
Fatullah | 141 | 04:00 | 127 | 10:00 | Rajbari | 140 | 03:00 | 131 | 11:00
Fenchuganj | 145 | 03:00 | 137 | 09:00 | Rajendrapur | 139 | 02:00 | 127 | 08:00
Feni | 135 | 05:00 | 129 | 10:00 | Rajshahi | 140 | 06:00 | 129 | 11:00
Feni-230 | 137 | 04:00 | 130 | 10:00 | Rajshahi-230 | 140 | 05:00 | 128 | 11:00
Ghatail | 133 | 04:00 | 123 | 18:00 | Ramganj | 136 | 01:00 | 130 | 16:00
Ghorashal | 134 | 01:00 | 121 | 10:00 | Rampur | 139 | 02:00 | 134 | 11:00
Goalpara | 139 | 02:00 | 127 | 13:00 | Rampura | 134 | 03:00 | 125 | 10:00
Gollamari | 139 | 04:00 | 129 | 12:00 | Rangamati | 140 | 03:00 | 134 | 12:00
Gopalganj | 142 | 04:00 | 132 | 12:00 | Rangpur | 135 | 03:00 | 125 | 11:00
Gopalganj-400 | 145 | 05:00 | 136 | 11:00 | Ruppur | 143 | 05:00 | 134 | 11:00
Gulshan | 133 | 01:00 | 124 | 12:00 | Saidpur | 138 | 05:00 | 123 | 11:00
Halishahar | 140 | 03:00 | 134 | 12:00 | Satkhira | 138 | 04:00 | 125 | 12:00
Haripur | 140 | 04:00 | 131 | 10:00 | Satmasjid | 140 | 04:00 | 130 | 09:00
HaripurSBU | 140 | 04:00 | 131 | 10:00 | Savar | 139 | 04:00 | 127 | 10:00
Hasnabad | 138 | 03:00 | 128 | 11:00 | SevenRings | 135 | 05:00 | 122 | 15:00
Hathazari | 140 | 05:00 | 128 | 18:30 | ShahCement | 139 | 03:00 | 130 | 10:00
Hatirjheel | 158 | 18:00 | 125 | 12:00 | Shahjadpur | 142 | 01:00 | 135 | 08:00
Ishurdi | 144 | 05:00 | 134 | 12:00 | Shahjibazar | 136 | 01:00 | 131 | 12:00
Jaldhaka | 134 | 05:00 | 121 | 08:00 | Shahmirpur | 139 | 00:00 | 133 | 07:00
Jamalpur | 137 | 11:00 | 124 | 06:00 | Shariatpur | 143 | 04:00 | 134 | 12:00
Jashore | 137 | 06:00 | 117 | 12:00 | Sherpur | 135 | 10:00 | 121 | 07:00
Jhenaidah | 140 | 05:00 | 121 | 10:00 | Shikalbaha | 127 | 07:00 | 124 | 00:00
Jhenaidah-230 | 142 | 04:00 | 124 | 12:00 | Shikalbaha-230 | 141 | 03:00 | 136 | 08:00
Joydebpur | 131 | 03:00 | 117 | 14:00 | Shitalakhya | 138 | 03:00 | 127 | 10:00
Joypurhat | 137 | 02:00 | 126 | 11:00 | Sholosohor | 140 | 03:00 | 135 | 12:00
Juldah | 139 | 01:00 | 134 | 18:00 | Shyampur | 139 | 06:00 | 130 | 10:00
Kabirpur | 141 | 05:00 | 123 | 20:00 | Shyampur-230 | 141 | 03:00 | 132 | 10:00
Kachua | 140 | 05:00 | 134 | 10:00 | Siddhirganj | 140 | 02:00 | 131 | 12:00
Kaliakoir | 144 | 04:00 | 130 | 19:30 | Sirajganj | 139 | 03:00 | 123 | 12:00
Kallyanpur | 138 | 06:00 | 129 | 10:00 | Sonargaon | 138 | 01:00 | 130 | 10:00
Kalurghat | 140 | 01:00 | 135 | 12:00 | Sreemongol | 138 | 06:00 | 132 | 12:00
Kamrangirchar | 138 | 04:00 | 127 | 10:00 | Sreepur | 140 | 04:00 | 129 | 10:00
Kaptai | 141 | 4:00 | 133 | 12:00 | Srinagar | 138 | 04:00 | 127 | 10:00
Kasba | 141 | 04:00 | 132 | 11:00 | SSM | 140 | 00:00 | 140 | 00:00
Kazla | 142 | 05:00 | 130 | 13:00 | Sunamganj | 134 | 00:00 | 131 | 11:00
Keranigonj | 138 | 03:00 | 128 | 10:00 | Sylhet | 137 | 02:00 | 133 | 13:00
Khagrachori | 140 | 03:00 | 134 | 12:00 | Sylhet-132 | 136 | 01:00 | 134 | 10:00
Khulna | 139 | 04:00 | 127 | 12:00 | Tangail | 134 | 04:00 | 124 | 16:00
Khulna(S) | 140 | 05:00 | 128 | 12:00 | Taraganj | 136 | 05:00 | 123 | 13:00
Khulshi | 138 | 04:00 | 133 | 12:00 | Tasnim | 139 | 04:00 | 130 | 11:00
Kishoreganj | 134 | 04:00 | 125 | 08:00 | Thakurgaon | 137 | 04:00 | 125 | 09:00
Kodda | 137 | 01:00 | 126 | 18:00 | TK | 139 | 00:00 | 135 | 12:00
KSRM | 140 | 01:00 | 134 | 18:00 | Tongi | 137 | 03:00 | 127 | 16:00
Kulaura | 140 | 03:00 | 136 | 09:00 | Ullahpara | 142 | 03:00 | 124 | 12:00
Kurigram | 132 | 06:00 | 118 | 13:00 | Ullon | 135 | 04:00 | 125 | 10:00
Kushtia | 138 | 05:00 | 127 | 12:00 | Uttara | 140 | 04:00 | 129 | 10:00
UttaraNew | 139 | 03:00 | 129 | 10:00 | Zigatola | 139 | 05:00 | 0.13 | 19:30
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division