## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 08-01-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-01-2026 | during | 08-01-2026 | during | 08-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 351 | 328 | 412 | 412 | 392 | 392 | FGMO, Gas Shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 450 | 450 | 240 | 240 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 15 | 47.6 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 12 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 30 | 25 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 15 | 15.1 | 15.1 | 15.1 | 15.1 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 15 | 45 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 120 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 21 | 152 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 28 | 0 | 22 | 0 | 22 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 450 | 530 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 90 | 10 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1286 | 1587.6 | 5154.45 | 5132.45 | 2455.13 | 2471.13
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 | 46 | 46 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 173 | 173 | 150 | 150 | 150 | 150 | Plant availability less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 15 | 54 | 105 | 105 | 105 | 105 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 40 | 64 | 40 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 51 | 51 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 8 | 28 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.25 | 0 | 3.38 | 0 | 3.38 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 50 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1150 | 1140 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 7 | 25 | 16 | 8 | 16 | 8 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 720 | 720 | 720 | 720 | 720 | 720 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2154.25 | 2236 | 3506.24 | 3506.86 | 3030.88 | 3031.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 201 | 175 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 280 | 300 | 353.35 | 353.35 | 353.35 | 353.35 | FGMO
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 340 | 215 | 393 | 393 | 363 | 363 | FGMO, Gas Shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 80 | 80 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | Machine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 8 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 109 | 109 | 163 | 163 | 115 | 115 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 12 | 89 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 122 | 120 | 84 | 82 | 126 | 126 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 7 | 15 | 24.5 | 24.5 | 24.5 | 24.5 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 64 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1186 | 1082 | 2385.75 | 2328.75 | 2114.75 | 2059.75
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-01-2026 | during | 08-01-2026 | during | 08-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 60 | 33 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.5 | 0 | 1.5 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 58 | 60 | 60 | 60 | 60 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 19 | 20 | 20 | 20 | 20 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 43.55 | 0 | 35.45 | 0 | 35.45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 14 | 22 | 22 | 18 | 18 | To be dispatched 18 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 182.55 | 124 | 350.95 | 314 | 346.95 | 310
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 41 | 41 | 41 | 41 | 41 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 60 | 60 | 60 | 60 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 141 | 151 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 78 | 81 | 81 | 81 | 81 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 160 | 158 | 160 | 160 | 158 | 158 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 305 | 341 | 341 | 0 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 529 | 844 | 901 | 901 | 542 | 849
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 409 | 408 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 226 | 140 | 410 | 410 | 369 | 369 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 78 | 0 | 70 | 0 | 70 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 913 | 1082 | 0 | 0 | 617.1 | 617.1 | U-2 Under Maintenance
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1626 | 1630 | 2342 | 2272 | 2163.2 | 2093.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 291 | 496 | 0 | 0 | 622 | 622 | Machine Problem
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 70 | 75 | 136 | 136 | 70 | 70 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 450 | 500 | 605 | 605 | 575 | 575 | FGMO, U1 under maintenance
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 224 | 307 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.51 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1255.51 | 1598 | 1529 | 1528 | 1902 | 1901
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 48.89 | 0 | 43.57 | 0 | 43.57 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 184 | 164 | 214 | 214 | 192.6 | 192.6 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 364 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.12 | 0 | 4 | 0 | 4 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1214 | 1445.94 | 1435.88 | 1435.88 | 1356 | 1356 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 55.25 | 0 | 55 | 0 | 55 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 93 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1964.26 | 2023.94 | 3095.44 | 2892.87 | 2512.78 | 2310.21
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 49 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.5 | 0 | 3.2 | 0 | 3.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 28 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 142 | 0 | 125.12 | 0 | 125.12 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 175.5 | 84 | 381.32 | 228 | 381.32 | 228
System Total |  |  |  |  | 28823.2 | 28382.248 | 10359.07 | 11209.54 | 19646.15 | 19103.93 | 15449.01 | 15253.79
Forecast Scenario (08-01-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8900 |  | 0 |  | 8900
|  |  |  | 1:00 | 8190 |  | 0 |  | 8190
|  |  |  | 2:00 | 7850 |  | 0 |  | 7850
|  |  |  | 3:00 | 7530 |  | 0 |  | 7530
|  |  |  | 4:00 | 7330 |  | 0 |  | 7330
|  |  |  | 5:00 | 7220 |  | 0 |  | 7220
|  |  |  | 6:00 | 7620 |  | 0 |  | 7620
|  |  |  | 7:00 | 8490 |  | 0 |  | 8490
|  |  |  | 8:00 | 9490 |  | 0 |  | 9490
|  |  |  | 9:00 | 10150 |  | 0 |  | 10150
|  |  |  | 10:00 | 10030 |  | 0 |  | 10030
|  |  |  | 11:00 | 9940 |  | 0 |  | 9940
|  |  |  | 12:00 | 10450 |  | 0 |  | 10450
|  |  |  | 13:00 | 10870 |  | 0 |  | 10870
|  |  |  | 14:00 | 10700 |  | 0 |  | 10700
|  |  |  | 15:00 | 10010 |  | 0 |  | 10010
|  |  |  | 16:00 | 9490 |  | 0 |  | 9490
|  |  |  | 17:00 | 9700 |  | 0 |  | 9700
|  |  |  | 18:00 | 10900 |  | 0 |  | 10900
|  |  |  | 18:30 | 11100 |  | 0 |  | 11100
|  |  |  | 19:00 | 11310 |  | 0 |  | 11310
|  |  |  | 19:30 | 11260 |  | 0 |  | 11260
|  |  |  | 20:00 | 11210 |  | 0 |  | 11210
|  |  |  | 21:00 | 10990 |  | 0 |  | 10990
|  |  |  | 22:00 | 10400 |  | 0 |  | 10400
|  |  |  | 23:00 | 9600 |  | 0 |  | 9600
Probable Maximum Temperature: |  |  | 20.00°C
Probable Maximum Demand at Day Peak: |  |  | 10450.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11310.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11310.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 228.37 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:27 hrs on 08-01-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 07-01-2026 | [28 empty] | Date: | 07-01-2026 | [28 empty] | Date: | 07-01-2026 | [28 empty] | Date: | 07-01-2026 | [28 empty] | Date: | 07-01-2026 | [17 empty] | Date: | 07-01-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [17 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 36 | 570 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 230 | 280 | 0 | 51 | 0 | 180 | 0 | 0 | 113 | 0 | 0 | 13 | 0 | 98 | 0 | 0 | 0 | 325 | 0 | 0 | 29 | 20 | 161 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 159 | 0 | 19 | 0 | 71 | 0 | 0 | 0 | 4644 | 408 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 797 | 0 | 0 | 0 | 845.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 140 | 220 | 0 | 258 | 400 | 0 | 4159.67 | 8803.67 | 97.25
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 5 | 570 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 716 | 0 | 0 | 0 | 230 | 280 | 0 | 5 | 0 | 180 | 0 | 0 | 113 | 0 | 0 | 11 | 0 | 84 | 0 | 0 | 0 | 310 | 0 | 0 | 29 | 20 | 144 | 0 | 5 | 0 | 42 | 20 | 0 | 0 | 160 | 0 | 19 | 0 | 71 | 0 | 0 | 0 | 4219 | 408 | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 771 | 0 | 0 | 0 | 829.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 70 | 220 | 0 | 257 | 350 | 0 | 3878.29 | 8097.29 | 97.25
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 5 | 600 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 611 | 0 | 0 | 0 | 230 | 280 | 0 | 5 | 0 | 150 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 80 | 0 | 0 | 0 | 315 | 0 | 0 | 29 | 20 | 141 | 0 | 5 | 0 | 5 | 20 | 0 | 0 | 160 | 0 | 8 | 0 | 91 | 0 | 0 | 0 | 4007 | 408 | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 788 | 0 | 0 | 0 | 836.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 70 | 180 | 0 | 257 | 250 | 0 | 3744.43 | 7751.43 | 97.25
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 5 | 600 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 609 | 0 | 0 | 0 | 230 | 280 | 0 | 5 | 0 | 150 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 88 | 0 | 0 | 0 | 315 | 0 | 0 | 29 | 20 | 140 | 0 | 5 | 0 | 5 | 20 | 0 | 0 | 159 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 3929 | 264 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 784 | 0 | 0 | 0 | 824.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 70 | 180 | 0 | 255 | 250 | 0 | 3509.74 | 7438.74 | 97.24
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 5 | 600 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 610 | 0 | 0 | 0 | 230 | 280 | 0 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 76 | 0 | 0 | 0 | 310 | 0 | 0 | 29 | 20 | 140 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 159 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 3850 | 176 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 785 | 0 | 0 | 0 | 838.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 70 | 180 | 0 | 260 | 250 | 0 | 3381.17 | 7231.17 | 97.24
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 5 | 600 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 608 | 0 | 0 | 0 | 230 | 280 | 0 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 0 | 13 | 0 | 72 | 0 | 0 | 0 | 315 | 0 | 0 | 29 | 20 | 137 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 158 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 3810 | 176 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 776 | 0 | 0 | 0 | 828.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 70 | 180 | 0 | 260 | 250 | 0 | 3310.57 | 7120.57 | 97.24
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 5 | 600 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 609 | 0 | 0 | 0 | 230 | 280 | 0 | 0 | 0 | 212 | 0 | 0 | 50 | 0 | 0 | 13 | 0 | 78 | 0 | 0 | 0 | 320 | 0 | 0 | 29 | 20 | 149 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 159 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 3957 | 176 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 798 | 0 | 0 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 70 | 220 | 0 | 256 | 250 | 0 | 3567 | 7524 | 97.23
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0.02 | 46 | 0 | 15 | 661 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 794 | 0 | 0 | 0 | 230 | 280 | 0 | 13 | 0 | 200 | 0 | 0 | 115 | 0 | 0 | 11 | 0 | 88 | 0 | 1 | 0 | 320 | 0 | 0 | 41 | 50 | 163 | 0 | 5 | 0 | 78 | 30 | 0 | 0 | 159 | 0 | 2 | 5 | 92 | 0 | 0 | 0 | 4606.02 | 175 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 808 | 0 | 0 | 0 | 831.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68 | 0 | 0 | 0 | 0.21 | 181 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 249 | 70 | 220 | 0 | 259 | 305 | 0 | 3787.43 | 8393.45 | 97.23
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 465 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 9 | 720 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1045 | 2 | 0 | 0 | 240 | 280 | 0 | 51 | 0 | 206 | 0 | 0 | 115 | 0 | 0 | 11 | 0 | 94 | 0 | 7 | 0 | 180 | 0 | 0 | 41 | 60 | 161 | 1 | 17 | 0 | 78 | 30 | 0 | 0 | 159 | 0 | 19 | 47 | 62 | 0 | 2.96 | 0 | 4945.96 | 408 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 879 | 0 | 0 | 0 | 1035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.73 | 16 | 0 | 0 | 5.66 | 169 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.31 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.8 | 13 | 0.06 | 0 | 256 | 70 | 220 | 0 | 280 | 395 | 0 | 4452.56 | 9398.52 | 97.23
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 470 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 26 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0.81 | 46 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1140 | 4 | 0 | 0 | 300 | 280 | 0 | 51 | 0 | 192 | 0 | 0 | 115 | 0 | 0 | 11 | 0 | 100 | 0 | 12 | 0 | 0 | 0 | 0 | 41 | 60 | 160 | 1 | 17 | 0 | 78 | 30 | 0 | 0 | 159 | 0 | 19 | 56 | 62 | 0 | 6.58 | 0 | 4948.39 | 408 | 257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 1068 | 0 | 0 | 0 | 1318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.59 | 44 | 0 | 0 | 16.15 | 161 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 1.27 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 1.5 | 35 | 0.18 | 0 | 246 | 70 | 180 | 0 | 356 | 493 | 0 | 5104.69 | 10053.08 | 97.22
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 425 | 0 | 0 | 0 | 0 | 0 | 21 | 52 | 25 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1.92 | 46 | 0 | 7 | 720 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1105 | 17 | 0 | 0 | 300 | 280 | 0 | 51 | 0 | 191 | 0 | 0 | 114 | 0 | 0 | 11 | 0 | 100 | 0 | 29 | 0 | 0 | 0 | 0 | 41 | 60 | 150 | 2 | 17 | 0 | 78 | 30 | 0 | 0 | 159 | 0 | 19 | 56 | 62 | 1 | 16.3 | 0 | 4940.22 | 408 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 1017 | 0 | 0 | 0 | 1278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.31 | 70 | 0 | 0 | 37.32 | 156 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 2.63 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 3 | 68 | 0.38 | 0 | 220 | 70 | 180 | 0 | 303 | 490 | 0 | 4995.64 | 9935.86 | 97.22
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 17 | 0 | 180 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 26 | 52 | 28.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2.8 | 46 | 0 | 6 | 720 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1090 | 19 | 0 | 0 | 300 | 280 | 0 | 51 | 0 | 193 | 0 | 0 | 114 | 8 | 0 | 5 | 0 | 114 | 0 | 61 | 0 | 0 | 0 | 0 | 41 | 60 | 142 | 2 | 17 | 0 | 42 | 30 | 0 | 0 | 160 | 0 | 19 | 58 | 62 | 2 | 33.93 | 0 | 4950.23 | 408 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 913 | 0 | 0 | 0 | 1226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.55 | 88 | 0 | 0 | 48.71 | 178 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 4.56 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 5.2 | 136 | 0.49 | 0 | 199 | 70 | 180 | 0 | 267 | 450 | 0 | 4895.51 | 9845.74 | 97.22
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 15 | 0 | 34 | 0 | 15 | 0 | 12 | 21 | 0 | 225 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 28 | 90 | 30 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 12 | 3.25 | 46 | 0 | 8 | 720 | 0 | 0 | 0 | 0 | 15 | 173 | 0 | 0 | 0 | 1150 | 20 | 0 | 0 | 340 | 280 | 0 | 51 | 0 | 201 | 0 | 0 | 109 | 12 | 0 | 7 | 0 | 122 | 0 | 64 | 0 | 0 | 0 | 0 | 41 | 60 | 141 | 2 | 17 | 0 | 78 | 30 | 0 | 0 | 160 | 0 | 19 | 58 | 60 | 2 | 43.55 | 0 | 5337.8 | 409 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 913 | 0 | 0 | 0 | 1214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.89 | 93 | 0 | 0 | 55.25 | 184 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 5.12 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 5.5 | 142 | 0.51 | 0 | 224 | 70 | 220 | 0 | 291 | 450 | 0 | 5021.27 | 10359.07 | 97.21
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 27.5 | 0 | 46 | 0 | 80 | 0 | 18 | 102 | 0 | 225 | 0 | 490 | 0 | 25 | 0 | 0 | 0 | 27 | 108 | 30 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 12 | 3.08 | 46 | 0 | 17 | 720 | 0 | 0 | 0 | 0 | 17 | 173 | 0 | 0 | 0 | 1135 | 19 | 0 | 0 | 260 | 280 | 0 | 51 | 0 | 195 | 0 | 0 | 108 | 26 | 0 | 7 | 0 | 120 | 0 | 62 | 0 | 0 | 0 | 0 | 41 | 60 | 159 | 2 | 17 | 0 | 78 | 30 | 0 | 0 | 160 | 0 | 19 | 58 | 29 | 2 | 42.4 | 0 | 5507.98 | 409 | 211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 977 | 0 | 0 | 0 | 1326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.39 | 89 | 0 | 0 | 50.89 | 184 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 4.65 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 5.2 | 140 | 0.51 | 0 | 274 | 70 | 180 | 0 | 307 | 500 | 0 | 5264.64 | 10772.62 | 97.21
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 33.7 | 0 | 70 | 0 | 80 | 0 | 35 | 103 | 0 | 225 | 0 | 440 | 0 | 35 | 0 | 0 | 0 | 22 | 108 | 31 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 2.65 | 46 | 0 | 10 | 720 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1145 | 16 | 0 | 0 | 240 | 280 | 0 | 51 | 0 | 194 | 0 | 0 | 106 | 17 | 0 | 11 | 0 | 126 | 0 | 52 | 0 | 0 | 0 | 0 | 41 | 60 | 158 | 4 | 17 | 0 | 78 | 30 | 0 | 0 | 161 | 0 | 19 | 58 | 30 | 2 | 34.43 | 0 | 5444.78 | 409 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 993 | 0 | 0 | 0 | 1271.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.54 | 77 | 0 | 0 | 40.3 | 185 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.73 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 5 | 114 | 0.41 | 0 | 258 | 68 | 220 | 0 | 307 | 480 | 0 | 5161.71 | 10606.49 | 97.21
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 31.8 | 0 | 70 | 0 | 80 | 0 | 50 | 150 | 0 | 225 | 0 | 375 | 0 | 35 | 0 | 0 | 0 | 15 | 108 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 1.75 | 46 | 0 | 7 | 720 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1150 | 12 | 0 | 0 | 215 | 315 | 0 | 51 | 0 | 190 | 0 | 0 | 105 | 17 | 0 | 11 | 0 | 112 | 0 | 37 | 0 | 10 | 0 | 0 | 41 | 60 | 156 | 5 | 17 | 0 | 78 | 30 | 0 | 0 | 161 | 0 | 19 | 58 | 30 | 1 | 25.72 | 0 | 5365.27 | 409 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 872 | 0 | 0 | 0 | 1181.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.76 | 59 | 0 | 0 | 23.67 | 182 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 2.17 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 3 | 85 | 0.3 | 0 | 180 | 50 | 180 | 0 | 280 | 400 | 0 | 4549.77 | 9915.04 | 97.2
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 32.8 | 0 | 70 | 0 | 80 | 0 | 54 | 157 | 0 | 225 | 0 | 370 | 0 | 35 | 0 | 0 | 0 | 6 | 108 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0.91 | 46 | 0 | 7 | 720 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1090 | 6 | 0 | 0 | 215 | 315 | 0 | 51 | 0 | 179 | 0 | 0 | 106 | 17 | 0 | 11 | 0 | 114 | 0 | 21 | 0 | 50 | 0 | 0 | 41 | 60 | 159 | 2 | 17 | 0 | 78 | 30 | 0 | 0 | 159 | 0 | 19 | 58 | 33 | 0 | 10.78 | 0 | 5301.49 | 408 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 785 | 0 | 0 | 0 | 1072.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.88 | 27 | 0 | 0 | 9.46 | 180 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0.78 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 1.5 | 39 | 0.13 | 0 | 182 | 65 | 180 | 0 | 255 | 300 | 0 | 4094.19 | 9395.68 | 97.2
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 32.8 | 0 | 75 | 0 | 80 | 0 | 55 | 155 | 0 | 180 | 0 | 445 | 0 | 35 | 0 | 0 | 0 | 1 | 108 | 25 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 12 | 0 | 12 | 12 | 0.09 | 46 | 0 | 7 | 720 | 0 | 0 | 0 | 0 | 10 | 173 | 0 | 0 | 0 | 1050 | 1 | 12 | 0 | 215 | 290 | 0 | 51 | 0 | 177 | 0 | 0 | 106 | 24 | 0 | 11 | 0 | 106 | 0 | 2 | 0 | 110 | 0 | 0 | 41 | 60 | 156 | 0 | 17 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 58 | 33 | 0 | 1.52 | 0 | 5364.41 | 408 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 775 | 0 | 0 | 0 | 1285.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.72 | 5 | 0 | 0 | 1.53 | 177 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0.14 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.3 | 6 | 0.02 | 0 | 179 | 65 | 180 | 0 | 290 | 315 | 0 | 4242.3 | 9606.71 | 97.2
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 40 | 0 | 98 | 0 | 130 | 0 | 55 | 156 | 0 | 225 | 0 | 475 | 0 | 35 | 0 | 0 | 0 | 0 | 108 | 25 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 32 | 0 | 12 | 38 | 0 | 46 | 0 | 17 | 720 | 0 | 0 | 0 | 0 | 20 | 173 | 0 | 0 | 0 | 1132 | 0 | 12 | 0 | 215 | 315 | 0 | 51 | 0 | 169 | 0 | 12 | 108 | 37 | 8 | 11 | 0 | 120 | 0 | 0 | 0 | 270 | 0 | 0 | 41 | 60 | 155 | 0 | 17 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 58 | 33 | 0 | 0 | 1 | 5901 | 408 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 928 | 0 | 0 | 0 | 1452.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 65 | 220 | 0 | 366 | 392 | 0 | 4903.4 | 10804.4 | 97.19
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 47.6 | 0 | 120 | 0 | 45 | 0 | 55 | 152 | 0 | 225 | 0 | 530 | 0 | 35 | 0 | 0 | 0 | 0 | 10 | 25 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 50 | 0 | 46 | 0 | 28 | 720 | 0 | 0 | 0 | 0 | 54 | 173 | 0 | 0 | 0 | 1140 | 0 | 8 | 0 | 215 | 300 | 0 | 51 | 0 | 175 | 0 | 0 | 109 | 89 | 0 | 15 | 0 | 120 | 0 | 0 | 0 | 305 | 0 | 0 | 41 | 60 | 151 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 58 | 33 | 0 | 0 | 14 | 5873.6 | 408 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1082 | 0 | 0 | 0 | 1445.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 75 | 220 | 0 | 496 | 500 | 0 | 5335.94 | 11209.54 | 97.19
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 50 | 0 | 120 | 0 | 0 | 0 | 0 | 158 | 0 | 225 | 0 | 530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 50 | 0 | 46 | 0 | 23 | 720 | 0 | 0 | 0 | 0 | 64 | 173 | 0 | 0 | 0 | 1148 | 0 | 0 | 0 | 215 | 305 | 0 | 51 | 0 | 177 | 0 | 0 | 109 | 100 | 0 | 19 | 0 | 118 | 0 | 0 | 0 | 305 | 0 | 0 | 41 | 60 | 153 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 58 | 33 | 0 | 0 | 18 | 5777 | 409 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 0 | 0 | 0 | 1447.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 75 | 220 | 0 | 503 | 580 | 0 | 5387.07 | 11164.07 | 97.19
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 47.3 | 0 | 120 | 0 | 0 | 0 | 0 | 154 | 0 | 225 | 0 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 50 | 0 | 46 | 0 | 24 | 720 | 0 | 0 | 0 | 0 | 63 | 173 | 0 | 0 | 0 | 1135 | 0 | 0 | 0 | 215 | 285 | 0 | 51 | 0 | 173 | 0 | 0 | 110 | 97 | 0 | 19 | 0 | 116 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 60 | 154 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 58 | 33 | 0 | 0 | 18 | 5724.3 | 409 | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 0 | 0 | 1445.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 77 | 220 | 0 | 502 | 590 | 0 | 5390.31 | 11114.61 | 97.19
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 24 | 0 | 55 | 0 | 0 | 0 | 0 | 153 | 0 | 225 | 0 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 25 | 0 | 46 | 0 | 32 | 720 | 0 | 0 | 0 | 0 | 17 | 173 | 0 | 0 | 0 | 1155 | 0 | 0 | 0 | 215 | 300 | 0 | 51 | 0 | 164 | 0 | 0 | 109 | 96 | 0 | 19 | 0 | 106 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 60 | 152 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 58 | 33 | 0 | 0 | 0 | 5557 | 408 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1092 | 0 | 0 | 0 | 1458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 75 | 220 | 0 | 502 | 605 | 0 | 5340 | 10897 | 97.18
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 35 | 720 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1155 | 0 | 0 | 0 | 215 | 305 | 0 | 51 | 0 | 130 | 0 | 0 | 111 | 0 | 0 | 19 | 0 | 110 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 60 | 153 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 45 | 33 | 0 | 0 | 0 | 5141 | 409 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 0 | 0 | 0 | 1458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 80 | 220 | 0 | 500 | 605 | 0 | 5174 | 10315 | 97.18
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 490 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 38 | 720 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1155 | 0 | 0 | 0 | 215 | 295 | 0 | 51 | 0 | 130 | 0 | 0 | 111 | 0 | 0 | 19 | 0 | 108 | 0 | 0 | 0 | 305 | 0 | 0 | 41 | 60 | 150 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 35 | 34 | 0 | 0 | 0 | 5106 | 409 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1038 | 0 | 0 | 0 | 1165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 80 | 220 | 0 | 408 | 520 | 0 | 4606 | 9712 | 97.18
Total KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8416800 | 0 | 0 | 338040 | 0 | 819360 | 0 | 625265 | 0 | 335966 | 1375200 | 0 | 4984500 | 0 | 10460012 | 0 | 234118 | 12545 | 0 | 0 | 166290 | 805200 | 478200 | 338760 | 0 | 0 | 0 | 0 | 0 | 0 | 436800 | 0 | 46600 | 0 | 25920 | 204480 | 17426 | 1100220 | 0 | 384960 | 16429090.91 | 0 | 0 | 0 | 0 | 231673 | 4140475 | 0 | 0 | 0 | 23498179 | 114615 | 41818 | 0 | 5879500 | 7231600 | 0 | 983692 | 0 | 4386000 | 0 | 29760 | 2337257 | 526560 | 18480 | 318130 | 0 | 2434560 | 0 | 345836 | 0 | 4758350 | 0 | 0 | 881000 | 1168080 | 3635673 | 21750 | 330072 | 0 | 1393920 | 628704 | 0 | 0 | 3443760 | 0 | 349200 | 904800 | 1204800 | 9900 | 216750 | 46800 | 119547446.91 | 8908363 | 5022720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 457920 | 22007270 | 0 | 0 | 0 | 26998909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 288136 | 586610 | 0 | 0 | 284256 | 3939273 | 0 | 0 | 0 | 0 | 0 | 9129746 | 0 | 25020 | 0 | 0 | 57863 | 141556 | 128486 | 0 | 0 | 0 | 30075.24 | 777601 | 2938 | 0 | 5345000 | 1749000 | 5226460 | 0 | 7840000 | 10568727.27 | 0 | 109515929.51 | 229063376.42

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 07-01-2026
Power Supply Scenario
| Day Peak Generation |  |  | 10359.07 | MW | 12:00 Hr. | Energy Generated |  |  | 229.0634 |  | MKWHr.
| Day Peak Demand |  |  | 10359.07 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11209.54 | MW | 19:00 Hr. | Energy Demand |  |  | 229.0634 |  | MKWHr.
| Evening Peak Demand |  |  | 11209.54 | MW | 19:00 Hr. | Maximum Temperature |  |  | 21.7 |  | °C
| Minimum Generation of the Day |  |  | 7120.57 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 687.39 |  | MMCFD
| Maximum Generation of the Day |  |  | 11209.54 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.7744 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 24.6908 | 0 | 4.5331 | 0 | 0 | 0.16629 | 0 | 0 | 29.3903 | Gas | 92.864 | Gas | 326390550.36
| Chattogram Zone |  |  | 4.5254 | 39.9273 | 0.50867 | 0 | 1.1002 | 0.13204 | 0 | 0.4368 | 46.6304 | Coal | 85.6883 | Coal | 568981621.0889
| Cumilla Zone |  |  | 21.1362 | 0 | 0.61662 | 0 | 0 | 0.34584 | 2.4346 | 0 | 24.5332 | HFO | 7.1456 | HFO | 120339364.3
| Mymensingh Zone |  |  | 1.2048 | 0 | 1.3008 | 0 | 0 | 0.22665 | 0 | 0 | 2.7323 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 16.2396 | 0 | 0 | 0 | 0 | 0.02175 | 0 | 0 | 16.2613 | Hydro | 1.1002 | Hydro | 110022
| Khulna Zone |  |  | 5.0227 | 22.0073 | 0 | 0 | 0 | 0.45792 | 8.9084 | 0 | 36.3963 | Solar | 3.4867 | Solar | 55162603.368
| Barishal Zone |  |  | 6.9755 | 23.7537 | 0 | 0 | 0 | 0.002938 | 0 | 0 | 30.7321 | Import | 38.3418 | Import | 245295665.6
| Rajshahi Zone |  |  | 13.069 | 0 | 0 | 0 | 0 | 1.184 | 26.9989 | 0 | 41.252 | Wind | 0.4368 | Wind | 6425328
| Rangpur Zone |  |  | 0 | 0 | 0.18635 | 0 | 0 | 0.94923 | 0 | 0 | 1.1356
| Total |  |  | 92.864 | 85.6883 | 7.1456 | 0 | 1.1002 | 3.4867 | 38.3418 | 0.4368 | 229.0634
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 326390550.36 |  | Hydro | 110022
|  |  |  | Coal | 568981621.0889 |  | Solar | 55162603.368
|  |  |  | HFO | 120339364.3 |  | Import | 245295665.6
|  |  |  | HSD | 0 |  | Wind | 6425328
[5 empty] | Total: | 132,27,05,154 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 8.9084 | Peak Hr Flow | 408.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 34765272.73 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.9989 | Peak Hr Flow | 1445.94 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1847 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.4346 | Peak Hr Flow | 120.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2012 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 38.3418 | Peak Hr Flow | 1973.94 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4030
|  |  |  | Chattogram |  | 0 |  | 1240
|  |  |  | Cumilla |  | 0 |  | 959
|  |  |  | Mymensingh |  | 0 |  | 861
|  |  |  | Sylhet |  | 0 |  | 399
|  |  |  | Khulna |  | 0 |  | 1311
|  |  |  | Barishal |  | 0 |  | 324
|  |  |  | Rajshahi |  | 0 |  | 1017
|  |  |  | Rangpur |  | 0 |  | 752
|  |  |  | Total |  | 0 |  | 10893
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Rangpur 20 MW GTPP |  |  | 20
|  | 2 | Baghabari 100 MW GTPP |  |  | 100
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 320 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 320
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:21 | 16:46 | Jamalpur United (20MW)- Sherpur 132kV Ckt-2 Scheduled S/D from Sherpur 132/33kV end Due
to Annual Maintenances
| 08:21 | 16:45 | Gopalganj 400/132kV S/S 400kV Amtoli Ckt-2 Scheduled S/D
| 08:22 | 16:57 | Jamalpur United (20MW)-Jamalpur 132kV Ckt-2 Scheduled S/D from Jamalpur 132/33kV end Due
to Annual Maintenance
| 08:22 | 16:55 | Haripur-Siddirganj 132kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to Annual
Maintenance. and from Siddhirganj 132/33kV end Due to Annual Maintenance.
| 08:24 | 16:22 | Chauddagram-Feni 132 kV Ckt-2 Scheduled S/D from Chauddagram 132/33kV end Due to Yearly
Maintenanc. and from Feni 230/132kV end Due to Annual maintenance chauddagram end
| 08:28 |  | Aminbazar-Kaliakoir 230kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to CT
Changing Works
| 08:29 | 17:15 | Aminbazar-Airport(Old) 230kV Ckt-1 Scheduled S/D from Agargaon 230/132kV end Due to
Annual Maintenance ( Deep Cleaning of Insulator Disc)
| 08:30 | 16:51 | Halishahar 132/33kV S/S 415T(TR-2) HT Project Work S/D Due to Painting work at radiator
of transformer
| 08:34 | 15:55 | Magura-Narail 132kV Ckt-1 Scheduled S/D from Narail 132/33kV end Due to Annual
Maintenance and from Magura 132/33kV end Due to Annual Maintenance.
| 08:40 | 16:32 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Scheduled S/D from Brahmanbaria 132/33kV end. and
from Shahjibazar 132/33kV end Due to Annual Maintenance
| 08:40 | 17:05 | Jhenaidah-Khulna 230kV Ckt-2 Scheduled S/D from Jhenaidah 230/132kV end Due to Annual
Maintenance and from Khulna(S) 230/132kV end Due to None
| 08:44 |  | Aminbazar-Kaliakoir 230kV Ckt-1 Scheduled S/D from Kaliakoir 400/230/132kV end Due to
NLDC. Works for Aminbazar end.
| 08:55 | 09:38 | Fenchuganj-Kulaura 132 kV Ckt-1 Tripped from Kulaura 132/33kV end showing Distance
protection Relay relays Due to None
| 08:56 | 15:42 | Chauddagram-Feni 132 kV Ckt-2 Scheduled S/D from Feni 132/33kV end Due to For annual
maintenance and from Feni 230/132kV end Due to feni end Annual maintenance
| 08:58 | 17:12 | Mirpur 132/33kV S/S T1 LT Scheduled S/D Due to Annual Maintenance work
| 08:58 | 17:12 | Mirpur 132/33kV S/S T1 HT Scheduled S/D Due to Annual maintenance work.
| 09:12 | 15:53 | Cox'sbazar-Dohazari 132 kV Ckt-1 Scheduled S/D from Coxsbazar 132/33kV end Due to Doh-Cox
Ckt-1 Annual Maintenance (Cox’s Bazar side) and from Dohazari 132/33kV end Due to Annual
maintenance
| 09:15 | 16:09 | Aminbazar 400/230/132kV S/S Gopalganj-2 Scheduled S/D Due to Annual Maintenance
| 09:15 | 11:56 | Sylhet 132/33kV S/S T2 HT Scheduled S/D Due to Ten Delta Test Purpose.
| 09:15 | 11:56 | Sylhet 132/33kV S/S T2 LT Scheduled S/D Due to Ten Delta Test Purpose.
| 09:17 | 17:20 | Ishurdi 230/132kV S/S 230/132 kV T-02 LT Scheduled S/D Due to Annual Maintenance
| 09:17 | 17:21 | Ishurdi 230/132kV S/S 230/132 kV T-02 HT Scheduled S/D Due to Annual Maintenance
| 09:23 | 16:23 | BIPTC S/S 400kV Bus-2 Scheduled S/D
| 09:25 | 17:11 | Mirpur 132/33kV S/S Reserve Bus Scheduled S/D Due to Annual Maintenance work
| 09:26 | 15:25 | Satkhira 132/33kV S/S Transformer-2 (T-2) LT Scheduled S/D Due to Annual maintenance work
| 09:26 | 15:25 | Satkhira 132/33kV S/S Transformer-2 (T-2) HT Scheduled S/D Due to Annual maintenance work
| 09:29 | 13:59 | Bogura-Bogura (New)) 132 kV Ckt-1 Scheduled S/D from Bogura 230/132kV end Due to Annual
Maintenance and from Bogura 132/33kV end Due to Annual maintenance.
| 09:31 | 16:09 | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-2 Scheduled S/D
| 09:43 | 15:56 | Bagerhat-Mongla 132 kV Ckt-2 Scheduled S/D from Bagerhat 132/33kV end Due to Annual
maintenance and from Mongla 132/33kV end Due to Annual maintenances
| 09:44 | 16:32 | Tongi 230/132/33kV S/S 230 kV Bus-2 Scheduled S/D Due to Annual Maintenance
| 09:49 | 11:33 | Sonargaon 132/33kV S/S Tr-2 LT Scheduled S/D Due to PBS underground cable maintenance | [7 empty] | 52.0MW load
interrup.
| 09:50 | 11:30 | Sonargaon 132/33kV S/S Tr-2 HT Scheduled S/D Due to PBS underground cable maintenance | [7 empty] | 52.0MW load
interrup.
| 09:52 | 20:00 | Payra_P/S-Payra 400kV Ckt-1 Scheduled S/D from Payra 400/132/33kV end Due to Annual
Maintenance
| 09:52 | 20:00 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-01 HT Scheduled S/D Due to Annual
Maintenance
| 09:53 | 15:02 | Jhenaidah 132/33kV S/S Transformer T-3 HT Scheduled S/D Due to Annual maintenance
| 09:53 | 15:03 | Jhenaidah 132/33kV S/S Transformer T-3 LT Scheduled S/D Due to Annual maintenance
| 10:03 | 16:50 | Mymensingh RPCL-Tangail 132kV Ckt-2 Scheduled S/D from Ghatail 132/33kV end Due to dead
line checking and from Muktagacha 132/33kVend.
| 10:03 | 17:08 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 Scheduled S/D Due to Annual
Maintenance
| 10:16 | 10:57 | Joypurhat 132/33kV S/S Naogaon Ckt.-2 Tripped showing Distance Relay relays Due to | [7 empty] | 29.0MW load
|  |  | Protection Fault | [7 empty] | interrup.
| 10:16 |  | Full interruption (29 MW) is occurring under Joypurhat Substation as Bogura (S) to
Joypurhat 132kV ckt tripped.
| 10:49 | 17:05 | Bhaluka 132/33kV S/S Sreepur Ckt- 02 Scheduled S/D Due to Annual maintenance | [7 empty] | 30.0MW load
interrup.
| 11:09 | 17:03 | Sreepur 230/132/33kV S/S Sreepur-Valuka Ckt-2 Scheduled S/D Due to Annual Maintenance
| 11:12 | 17:04 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Forced S/D Due to Maintenance Works EGCB ends
| 11:15 | 17:14 | Bhaluka-Mymensingh 132 kV Ckt-1 Forced S/D from Bhaluka 132/33kV end Due to CB open by
NLDC
| 11:29 | 17:31 | Kaliakoir 400/230/132kV S/S Bibiyana1 Scheduled S/D Due to Dead Line checking.
| 11:46 | 13:58 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) LT Scheduled S/D Due to Due to maintenance
work
| 11:47 | 13:56 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) HT Scheduled S/D Due to Due to maintenance
work
| 11:58 | 14:30 | Sylhet 132/33kV S/S T4 LT Scheduled S/D Due to Ten-delta test
| 11:58 | 14:30 | Sylhet 132/33kV S/S T4 HT Scheduled S/D Due to Ten-delta test
| 12:00 |  | Day Peak Generation: 10356 MW.
| 14:24 | 15:52 | Cox'sbazar-Dohazari 132 kV Ckt-1 Scheduled S/D from Dohazari 132/33kV end Due to Annual
maintenance
| 14:39 | 14:55 | Aftabnagar-Rampura 132kV Ckt-1 Scheduled S/D from Agargaon 230/132kV end Due to Relay
Testing
|  | 15:30 | Khulshi-Madunaghat 132kV Ckt-2 is restored.
|  | 15:34 | APR-Hasnabad 230kV Ckt-2 is restored.
|  | 15:35 | Shyampur 230/132kV S/S 230 kV APR (D04) is restored.
| 16:07 | 16:42 | Bogura(New)-Naogaon 132 kV Ckt-1 Tripped from Bogura 230/132kV end showing E/F,
Location-71km, Zone-1, Phase-A, 1439Amp, relays Due to Unknown
| 16:08 |  | Joypurhat 132/33kV S/S Transformer T-4 (437 T) HT Tripped showing no relays Due to 132 Kv
T-4 R-Phase LA Brust
| 16:30 |  | Joypurhat 132/33kV S/S Transformer T-4 (437 T) LT Scheduled S/D Due to 132 Kv T-4 R-Phase
LA Brust
| 16:30 |  | Joypurhat 132/33kV S/S Transformer T-4 (437 T) HT Scheduled S/D Due to 132 Kv T-4 R-Phase
LA Brust
|  | 17:45 | Bibiyana-Fenchuganj 230 kV Ckt-2 is restored.
|  | 18:57 | Muradnagar 132/33kV S/S 132KV Transformar-01 HT is restored.
|  | 18:58 | Muradnagar 132/33kV S/S 132KV Transformar-01 LT is restored.
| 19:00 |  | Evening peak generation: 11210 MW
| 22:22 |  | Siddhirganj 335 MW CCPP GT was synchronized
| 01:04 |  | Siddhirganj 335 MW CCPP ST was synchronized
| 01:15 | 03:16 | Chhatak 132/33kV S/S T-1 LT Forced S/D Due to 33kV Sunamganj PDB Feeder Maintenance work.
| 01:16 | 03:16 | Chhatak 132/33kV S/S T-1 HT Forced S/D Due to PDB 33kV feeder maintenance work.
| 04:37 |  | Meghnaghat 450 MW CCPP (MPL) Shutdown with remarks:- GT-2,ST
| 05:00 |  | Minimum generation 7383 MW
| 07:25 |  | Haripur-Meghnaghat 230kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to MK box
changing work.
| 07:38 |  | Bibiyana-Fenchuganj 230 kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Deadline Checking
| 07:52 |  | Khulshi-Madunaghat 132kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end Due to Annual
Maintenance
| 08:00 |  | Cumilla(N)-Kachua 132 kV Ckt-2 Scheduled S/D from Kachua 230/132/33kV end Due to For
annual maintenance work.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 07-01-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 328 | 8416800 | FGMO, Gas Shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4984500 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 12545 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 47.6 | 338040 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 335966 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 234118 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 25 | 478200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 338760 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 45 | 625265 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 120 | 819360 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 152 | 1375200 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 166290 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 530 | 10460012 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 10 | 805200 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1587.6 | 29390256
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 114615 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1100220 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 173 | 4140475 | Plant availability less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 54 | 231673 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 46600 | temp problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 25920 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 28 | 384960 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 17426 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 204480 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1140 | 23498179 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 25 | 436800 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 720 | 16429090.91 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 2236 | 46630438.91
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 175 | 4386000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 300 | 7231600 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 215 | 5879500 | FGMO, Gas Shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 983692 | Machine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 8 | 41818 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 109 | 2337257 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 89 | 526560 | -
| Import (Tripura) |  | Import | 0 | 160 | 120 | 2434560 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 15 | 318130 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 18480 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 29760 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 345836 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1082 | 24533193
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 33 | 1204800 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9900 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 904800 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 349200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 216750 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 14 | 46800 | To be dispatched 18 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 124 | 2732250
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 21750 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 881000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1168080 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 151 | 3635673 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 628704 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1393920 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 158 | 3443760 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 330072 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 4758350 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 844 | 16261309
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 408 | 8908363 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 140 | 5022720 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 457920 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1082 | 22007270 | U-2 Under Maintenance
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1630 | 36396273
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 496 | 7840000 | Machine Problem
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 75 | 1749000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 500 | 10568727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5226460 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5345000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2938 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1598 | 30732125.27
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 288136 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 164 | 3939273 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9129746 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 25020 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1445.94 | 26998909 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 284256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 586610 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2023.94 | 41251950
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 128486 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 30075.24 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 57863 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 141556 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 777601 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 84 | 1135581.24
Eastern Grid Total |  |  |  |  | 17398.245 | 5873.6 | 119547446.91
Western Grid Total |  |  |  |  | 10984.003 | 5335.94 | 109515929.51
National Grid Total |  |  |  |  | 28382.248 | 11209.54 | 229063376.42
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 07-01-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7488.32 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3404 | MW
i) Dhaka area |  |  | 4029.82 |  | MW | i) Khulna area |  |  |  | 1311 | MW
ii) Chattogram area |  |  | 1239.5 |  | MW | ii) Barishal area |  |  |  | 324 | MW
iii) Cumilla area |  |  | 959 |  | MW | iii) Rajshahi area |  |  |  | 1017 | MW
iv) Mymensingh area |  |  | 861 |  | MW | iv) Rangpur area |  |  |  | 752 | MW
v) Sylhet area |  |  | 399 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10892.32 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 69 | 19:30 | 133 | Netrakona | 107 | 18:30
2 | AKSML | 113 | 09:00 | 68 | Hathazari | 60 | 18:00 | 134 | New | 66 | 14:00
3 | Aftabnagar | 26 | 13:00 | 69 | Hatirjheel | 27 | 16:00 | 135 | Niamatpur | 55 | 13:00
4 | Agargaon | 77 | 15:00 | 70 | Ishurdi | 53 | 18:30 | 136 | Noapara | 39 | 18:30
5 | Agrabad | 32 | 18:00 | 71 | Jaldhaka | 50 | 18:00 | 137 | PHP | 6 | 23:00
6 | Amnura | 25 | 08:00 | 72 | Jamalpur | 91 | 08:00 | 138 | Pabna | 77 | 18:30
7 | Ashuganj | 56 | 15:00 | 73 | Jashore | 104 | 14:00 | 139 | Palashbari | 85 | 18:00
8 | BSRM | 210 | 02:00 | 74 | Jhenaidah | 103 | 18:00 | 140 | Panchagarh | 49 | 18:00
9 | Bagerhat | 64 | 18:00 | 75 | Joydebpur | 107 | 12:00 | 141 | Patiya | 6.5 | 18:00
10 | Bajitpur | 68 | 18:00 | 76 | Joypurhat | 44 | 18:00 | 142 | Patuakhali | 40 | 19:30
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 15 | 13:00 | 143 | Payra | 28 | 18:30
12 | Bakulia | 61 | 13:00 | 78 | KSRM | 48 | 19:00 | 144 | Postogola | 43 | 13:00
13 | Banani | 31 | 18:00 | 79 | Kabirpur | 182 | 18:30 | 145 | Purbachal | 20 | 13:00
14 | Bangabhaban | 9 | 12:00 | 80 | Kachua | 50 | 19:30 | 146 | Purbasadipur | 120 | 18:30
15 | Barapukuria | 47 | 18:30 | 81 | Kallyanpur | 87 | 12:00 | 147 | Rahanpur | 24 | 18:00
16 | Barguna | 16 | 21:00 | 82 | Kalurghat | 28 | 09:00 | 148 | Rahim | 37 | 16:00
17 | Barishal | 79 | 22:00 | 83 | Kamrangirchar | 68 | 13:00 | 149 | Rajbari | 63 | 18:30
18 | Barishal-230 | 80 | 18:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 118 | 18:00
19 | Baroaulia | 52 | 17:00 | 85 | Kasba | 23 | 19:30 | 151 | Rajshahi | 76 | 13:00
20 | Baroirhat | 41 | 13:00 | 86 | Kazla | 98 | 13:00 | 152 | Rajshahi-230 | 69 | 13:00
21 | Bashundhara | 130 | 13:00 | 87 | Keranigonj | 76 | 13:00 | 153 | Ramganj | 92 | 18:00
22 | BashundharaCement | 7 | 00:00 | 88 | Khagrachori | 24 | 18:00 | 154 | Rampur | 26 | 14:00
23 | Beanibazar | 48 | 18:30 | 89 | Khulna | 50 | 12:00 | 155 | Rangamati | 13 | 18:30
24 | Benapole | 60 | 08:00 | 90 | Khulshi | 158 | 18:30 | 156 | Rangpur | 116 | 18:00
25 | Bhaluka | 135 | 18:30 | 91 | Kishoreganj | 91 | 18:30 | 157 | Ruppur | 1.4 | 06:00
26 | Bhandaria | 37 | 21:00 | 92 | Kodda | 244 | 10:00 | 158 | SSM | 9 | 22:00
27 | Bhangura | 24 | 18:00 | 93 | Kulaura | 27 | 19:00 | 159 | Saidpur | 95 | 18:30
28 | Bheramara(GK) | 43 | 18:00 | 94 | Kurigram | 54 | 18:00 | 160 | Satkhira | 93 | 18:30
29 | Bhulta | 210 | 16:00 | 95 | Kushtia | 120 | 18:00 | 161 | Satmasjid | 78 | 13:00
30 | Bog-Sherpur | 54 | 19:00 | 96 | Laksam | 23 | 13:00 | 162 | Savar | 170 | 12:00
31 | Bogura | 112 | 18:30 | 97 | Lakshmipur | 16 | 18:00 | 163 | SevenRings | 15.45 | 21:00
32 | Borhanuddin | 65 | 21:00 | 98 | Lalbag | 56 | 13:00 | 164 | ShahCement | 35 | 01:00
33 | Brahmanbaria | 92 | 18:00 | 99 | Lalmonirhat | 50 | 18:00 | 165 | Shahjadpur | 60 | 18:30
34 | Cantonment | 90 | 13:00 | 100 | MI_Cement | 15.7 | 23:00 | 166 | Shahjibazar | 84 | 18:00
35 | Chandina | 15 | 13:00 | 101 | Madanganj | 41 | 09:00 | 167 | Shahmirpur | 38 | 18:00
36 | Chandpur | 52 | 21:00 | 102 | Madaripur | 74 | 19:00 | 168 | Shariatpur | 57 | 19:30
37 | Chandraghona | 26 | 18:00 | 103 | Madartek | 53 | 14:00 | 169 | Sherpur | 114 | 08:00
38 | Chapai | 55 | 13:00 | 104 | Madunaghat | 36 | 13:00 | 170 | Shikalbaha | 20 | 14:00
39 | Charsaidpur | 29 | 18:30 | 105 | Magura | 49 | 18:00 | 171 | Shitalakhya | 67.3 | 12:00
40 | Chauddagram | 47 | 13:00 | 106 | Mahasthangarh | 48 | 18:30 | 172 | Sholosohor | 34 | 12:00
41 | Chhatak | 23 | 16:00 | 107 | Maijdee | 26 | 18:30 | 173 | Shyampur | 158 | 13:00
42 | Chowmuhani | 116 | 18:00 | 108 | Manikganj | 107 | 18:30 | 174 | Siddhirganj | 93 | 12:00
43 | Chuadanga | 81 | 18:00 | 109 | Maniknagar | 50 | 13:00 | 175 | Sirajganj | 84 | 18:30
44 | Coxsbazar | 103 | 18:30 | 110 | Matarbari | 82 | 05:00 | 176 | Sonargaon | 114 | 18:30
45 | Cumilla(N) | 95 | 19:30 | 111 | Matuail | 44 | 11:00 | 177 | Sreemongol | 54 | 20:00
46 | Cumilla(S) | 124 | 14:00 | 112 | Metrorail_Motijheel | 80 | 03:00 | 178 | Sreepur | 87 | 18:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 7 | 09:00 | 179 | Srinagar | 31 | 20:00
48 | Daudkandi | 114 | 18:30 | 114 | Millgate | 71 | 12:00 | 180 | Sunamganj | 42 | 18:00
49 | DhakaUniversity | 50 | 13:00 | 115 | Mirpur | 112 | 14:00 | 181 | Sylhet | 40 | 14:00
50 | Dhamrai | 88 | 10:00 | 116 | Mirsorai | 10 | 18:00 | 182 | Sylhet-132 | 79 | 18:00
51 | Dhanmondi | 75 | 13:00 | 117 | Mirzapur | 40 | 13:00 | 183 | TK | 18 | 18:00
52 | Dohazari | 70 | 18:00 | 118 | Mithapukur | 44 | 18:30 | 184 | Tangail | 118 | 13:00
53 | Faridpur | 117 | 18:00 | 119 | Modern | N/A | N/A | 185 | Taraganj | 16 | 18:30
54 | Fatullah | 80 | 12:00 | 120 | Mogbazar | 50.4 | 14:00 | 186 | Tasnim | 26 | 15:00
55 | Fenchuganj | 25 | 18:00 | 121 | Mongla | 34 | 18:30 | 187 | Thakurgaon | 77 | 18:30
56 | Feni | 78 | 14:00 | 122 | Motijheel | 33 | 13:00 | 188 | Tongi | 108 | 09:00
57 | GPH | 68 | 18:30 | 123 | Muktagacha | 28 | 14:00 | 189 | Ullahpara | 31 | 12:00
58 | Ghatail | 60 | 08:00 | 124 | Munshiganj | 71 | 14:00 | 190 | Ullon | 38 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 0 | 00:00 | 191 | Uttara | 47 | 13:00
60 | Ghorashal-230 | 76 | 11:00 | 126 | Mymensingh | 142 | 19:30 | 192 | UttaraNew | 30 | 13:00
61 | Goalpara | 30 | 13:00 | 127 | Naogaon | 92 | 13:00 | 193 | Zigatola | 70 | 13:00
62 | Gollamari | 90 | 13:00 | 128 | Narail | 45 | 18:00
63 | Gopalganj | 82 | 18:30 | 129 | Narinda | 52 | 13:00
64 | Gulshan | 72 | 14:00 | 130 | Narshingdi | 141 | 19:00
65 | Halishahar | 54 | 20:00 | 131 | Natore | 102 | 20:00
66 | HaripurSBU | 87 | 18:00 | 132 | Nawabganj | 30.4 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 07-01-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 8803.67 | 0 |  | 8803.67
1:00 | 8097.29 | 0 |  | 8097.29
2:00 | 7751.43 | 0 |  | 7751.43
3:00 | 7438.74 | 0 |  | 7438.74
4:00 | 7231.17 | 0 |  | 7231.17
5:00 | 7120.57 | 0 |  | 7120.57
6:00 | 7524 | 0 |  | 7524
7:00 | 8393.45 | 0 |  | 8393.45
8:00 | 9398.52 | 0 |  | 9398.52
9:00 | 10053.08 | 0 |  | 10053.08
10:00 | 9935.86 | 0 |  | 9935.86
11:00 | 9845.74 | 0 |  | 9845.74
12:00 | 10359.07 | 0 |  | 10359.07
13:00 | 10772.62 | 0 |  | 10772.62
14:00 | 10606.49 | 0 |  | 10606.49
15:00 | 9915.04 | 0 |  | 9915.04
16:00 | 9395.68 | 0 |  | 9395.68
17:00 | 9606.71 | 0 |  | 9606.71
18:00 | 10804.4 | 0 |  | 10804.4
19:00 | 11209.54 | 0 |  | 11209.54
19:30 | 11164.07 | 0 |  | 11164.07
20:00 | 11114.61 | 0 |  | 11114.61
21:00 | 10897 | 0 |  | 10897
22:00 | 10315 | 0 |  | 10315
23:00 | 9712 | 0 |  | 9712
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 07-01-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4644 | 4159.67 | 8803.67 | DAILY GENERATION CURVE
00:30 | 4431.5 | 4018.98 | 8450.48
01:00 | 4219 | 3878.29 | 8097.29 | 07-01-2026
01:30 | 4113 | 3811.36 | 7924.36
02:00 | 4007 | 3744.43 | 7751.43
02:30 | 3968 | 3627.085 | 7595.085
03:00 | 3929 | 3509.74 | 7438.74
03:30 | 3889.5 | 3445.455 | 7334.955
04:00 | 3850 | 3381.17 | 7231.17
04:30 | 3830 | 3345.87 | 7175.87
05:00 | 3810 | 3310.57 | 7120.57
05:30 | 3883.5 | 3438.785 | 7322.285
06:00 | 3957 | 3567 | 7524
06:30 | 4281.51 | 3677.215 | 7958.725
07:00 | 4606.02 | 3787.43 | 8393.45
07:30 | 4775.99 | 4119.995 | 8895.985
08:00 | 4945.96 | 4452.56 | 9398.52
08:30 | 4947.175 | 4778.625 | 9725.8
09:00 | 4948.39 | 5104.69 | 10053.08
09:30 | 4944.305 | 5050.165 | 9994.47
10:00 | 4940.22 | 4995.64 | 9935.86
10:30 | 4945.225 | 4945.575 | 9890.8
11:00 | 4950.23 | 4895.51 | 9845.74
11:30 | 5144.015 | 4958.39 | 10102.405
12:00 | 5337.8 | 5021.27 | 10359.07
12:30 | 5422.89 | 5142.955 | 10565.845
13:00 | 5507.98 | 5264.64 | 10772.62
13:30 | 5476.38 | 5213.175 | 10689.555
14:00 | 5444.78 | 5161.71 | 10606.49
14:30 | 5405.025 | 4855.74 | 10260.765
15:00 | 5365.27 | 4549.77 | 9915.04
15:30 | 5333.38 | 4321.98 | 9655.36
16:00 | 5301.49 | 4094.19 | 9395.68
16:30 | 5332.95 | 4168.245 | 9501.195
17:00 | 5364.41 | 4242.3 | 9606.71
17:30 | 5632.705 | 4572.85 | 10205.555
18:00 | 5901 | 4903.4 | 10804.4
18:30 | 5887.3 | 5119.67 | 11006.97
19:00 | 5873.6 | 5335.94 | 11209.54
19:30 | 5777 | 5387.07 | 11164.07
20:00 | 5724.3 | 5390.31 | 11114.61
20:30 | 5640.65 | 5365.155 | 11005.805 |  | Executive Engineer
21:00 | 5557 | 5340 | 10897 |  | Network Operation Division
21:30 | 5349 | 5257 | 10606
22:00 | 5141 | 5174 | 10315
22:30 | 5123.5 | 4890 | 10013.5
23:00 | 5106 | 4606 | 9712

## En-Curve
QF-LDC-12
Date | 07-01-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2632 | 1617 | 408 | 0 | 98 | 845.67 | 46 | 3096 | 0 | 0 | 19 | 0 | 0 | 42 | 0 | DAILY ENERGY CURVE
00:30 | 2573 | 1485.5 | 408 | 0 | 91 | 837.48 | 46 | 2950 | 0 | 0 | 19 | 0 | 0 | 40.5 | 0 | 07-01-2026
01:00 | 2514 | 1354 | 408 | 0 | 84 | 829.29 | 46 | 2804 | 0 | 0 | 19 | 0 | 0 | 39 | 0
01:30 | 2473.5 | 1304 | 408 | 0 | 82 | 832.86 | 46 | 2725 | 0 | 0 | 13.5 | 0 | 0 | 39.5 | 0 | Energy Generated | 229.0634 |  | MKWHr
02:00 | 2433 | 1254 | 408 | 0 | 80 | 836.43 | 46 | 2646 | 0 | 0 | 8 | 0 | 0 | 40 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2383 | 1226 | 336 | 0 | 84 | 830.585 | 46 | 2642 | 0 | 0 | 4 | 0 | 0 | 43.5 | 0 | Total Energy Requirement | 229.0634 |  | MKWHr
03:00 | 2333 | 1198 | 264 | 0 | 88 | 824.74 | 46 | 2638 | 0 | 0 | 0 | 0 | 0 | 47 | 0
03:30 | 2305 | 1170.5 | 220 | 0 | 82 | 831.455 | 46 | 2641.5 | 0 | 0 | 0 | 0 | 0 | 38.5 | 0
04:00 | 2277 | 1143 | 176 | 0 | 76 | 838.17 | 46 | 2645 | 0 | 0 | 0 | 0 | 0 | 30 | 0
04:30 | 2240 | 1142.5 | 176 | 0 | 74 | 833.37 | 46 | 2639.5 | 0 | 0 | 0 | 0 | 0 | 24.5 | 0
05:00 | 2203 | 1142 | 176 | 0 | 72 | 828.57 | 46 | 2634 | 0 | 0 | 0 | 0 | 0 | 19 | 0
05:30 | 2335 | 1183 | 176 | 0 | 75 | 826.785 | 46 | 2664 | 0 | 0 | 0 | 0 | 0 | 16.5 | 0
06:00 | 2467 | 1224 | 176 | 0 | 78 | 825 | 46 | 2694 | 0 | 0 | 0 | 0 | 0 | 14 | 0
06:30 | 2569.5 | 1354.5 | 175.5 | 0 | 83 | 828.26 | 46 | 2885 | 1.965 | 0 | 3.5 | 0 | 0 | 11.5 | 0
07:00 | 2672 | 1485 | 175 | 0 | 88 | 831.52 | 46 | 3076 | 3.93 | 0 | 7 | 0 | 0 | 9 | 0
07:30 | 2659.5 | 1466 | 291.5 | 0 | 91 | 933.26 | 46 | 3325.5 | 41.225 | 0 | 36.5 | 0 | 0 | 5.5 | 0
08:00 | 2647 | 1447 | 408 | 0 | 94 | 1035 | 46 | 3575 | 78.52 | 0 | 66 | 0 | 0 | 2 | 0
08:30 | 2645.5 | 1340 | 408 | 0 | 97 | 1176.5 | 46 | 3799 | 141.3 | 0 | 70.5 | 0 | 0 | 2 | 0
09:00 | 2644 | 1233 | 408 | 0 | 100 | 1318 | 46 | 4023 | 204.08 | 0 | 75 | 0 | 0 | 2 | 0
09:30 | 2601.5 | 1208.5 | 408 | 0 | 100 | 1298 | 46 | 3939 | 290.47 | 26 | 75 | 0 | 0 | 2 | 0
10:00 | 2559 | 1184 | 408 | 0 | 100 | 1278 | 46 | 3855 | 376.86 | 52 | 75 | 0 | 0 | 2 | 0
10:30 | 2568.5 | 1132.75 | 408 | 0 | 107 | 1252 | 46 | 3747 | 473.05 | 52 | 102.5 | 0 | 0 | 2 | 0
11:00 | 2578 | 1081.5 | 408 | 0 | 114 | 1226 | 46 | 3639 | 569.24 | 52 | 130 | 0 | 0 | 2 | 0
11:30 | 2613.5 | 1161.75 | 408.5 | 0 | 118 | 1220 | 46 | 3693.5 | 594.155 | 71 | 171.5 | 0 | 0 | 4.5 | 0
12:00 | 2649 | 1242 | 409 | 0 | 122 | 1214 | 46 | 3748 | 619.07 | 90 | 213 | 0 | 0 | 7 | 0
12:30 | 2603 | 1255.5 | 409 | 0 | 121 | 1270 | 46 | 3830.5 | 603.095 | 99 | 321.75 | 0 | 0 | 7 | 0
13:00 | 2557 | 1269 | 409 | 0 | 120 | 1326 | 46 | 3913 | 587.12 | 108 | 430.5 | 0 | 0 | 7 | 0
13:30 | 2546 | 1262.5 | 409 | 0 | 123 | 1298.865 | 46 | 3908 | 540.59 | 108 | 440.6 | 0 | 0 | 7 | 0
14:00 | 2535 | 1256 | 409 | 0 | 126 | 1271.73 | 46 | 3903 | 494.06 | 108 | 450.7 | 0 | 0 | 7 | 0
14:30 | 2496 | 1190.5 | 409 | 0 | 119 | 1226.8 | 46 | 3752.5 | 425.215 | 108 | 480.75 | 0 | 0 | 7 | 0
15:00 | 2457 | 1125 | 409 | 0 | 112 | 1181.87 | 46 | 3602 | 356.37 | 108 | 510.8 | 0 | 0 | 7 | 0
15:30 | 2459.5 | 1144 | 408.5 | 0 | 113 | 1127.155 | 46 | 3467 | 259.905 | 108 | 516.8 | 0 | 0 | 5.5 | 0
16:00 | 2462 | 1163 | 408 | 0 | 114 | 1072.44 | 46 | 3332 | 163.44 | 108 | 522.8 | 0 | 0 | 4 | 0
16:30 | 2447.5 | 1215 | 408 | 0 | 110 | 1179.015 | 46 | 3330.5 | 94.38 | 114 | 551.3 | 0 | 0 | 5.5 | 0
17:00 | 2433 | 1267 | 408 | 0 | 106 | 1285.59 | 46 | 3329 | 25.32 | 120 | 579.8 | 0 | 0 | 7 | 0
17:30 | 2446.5 | 1409 | 408 | 0 | 113 | 1368.995 | 46 | 3572 | 12.66 | 130 | 689.9 | 0 | 0 | 9.5 | 0
18:00 | 2460 | 1551 | 408 | 0 | 120 | 1452.4 | 46 | 3815 | 0 | 140 | 800 | 0 | 0 | 12 | 0
18:30 | 2437.5 | 1607.5 | 408 | 0 | 120 | 1449.17 | 46 | 4030 | 0 | 75 | 815.3 | 0 | 0 | 18.5 | 0
19:00 | 2415 | 1664 | 408 | 0 | 120 | 1445.94 | 46 | 4245 | 0 | 10 | 830.6 | 0 | 0 | 25 | 0
19:30 | 2421 | 1666 | 409 | 0 | 118 | 1447.07 | 46 | 4346 | 0 | 0 | 686 | 0 | 0 | 25 | 0
20:00 | 2385 | 1663 | 409 | 0 | 116 | 1445.31 | 46 | 4349 | 0 | 0 | 675.3 | 0 | 0 | 26 | 0
20:30 | 2373 | 1665.5 | 408.5 | 0 | 111 | 1451.655 | 46 | 4365 | 0 | 0 | 561.15 | 0 | 0 | 24 | 0
21:00 | 2361 | 1668 | 408 | 0 | 106 | 1458 | 46 | 4381 | 0 | 0 | 447 | 0 | 0 | 22 | 0
21:30 | 2282.5 | 1660 | 408.5 | 0 | 108 | 1458 | 46 | 4363.5 | 0 | 0 | 255.5 | 0 | 0 | 24 | 0
22:00 | 2204 | 1652 | 409 | 0 | 110 | 1458 | 46 | 4346 | 0 | 0 | 64 | 0 | 0 | 26 | 0
22:30 | 2173.5 | 1638 | 409 | 0 | 109 | 1311.5 | 46 | 4232.5 | 0 | 0 | 59 | 0 | 0 | 35 | 0
23:00 | 2143 | 1624 | 409 | 0 | 108 | 1165 | 46 | 4119 | 0 | 0 | 54 | 0 | 0 | 44 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 07-01-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 425 | 05:00 | 383 | 12:00 | Meghnaghat | 428 | 04:00 | 391 | 12:00
Ashuganj | 413 | 5:00 | 388 | 10:00 | Payra | 423 | 04:00 | 412 | 12:00
Bhulta | 406 | 04:00 | 374 | 12:00 | Rahanpur | 422 | 04:00 | 401 | 13:00
Bibiana | 423 | 03:00 | 381 | 12:00 | Rampal | 418 | 03:00 | 395 | 12:00
BIPTC | 409 | 03:00 | 396 | 12:00
Bogura | 419 | 05:00 | 391 | 13:00
Gopalganj | 424 | 05:00 | 396 | 12:00
Kaliakoir | 425 | 05:00 | 373 | 12:00
Korerhat | 425 | 04:00 | 400 | 12:00
Madunaghat | 415 | 05:00 | 400 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 245 | 04:00 | 218 | 12:00 | Kachua | 240 | 18:30 | 228 | 12:00
AKSML | 240 | 03:00 | 228 | 12:00 | Kaliakoir | 241 | 04:00 | 218 | 12:00
Aminbazar | 243 | 05:00 | 220 | 12:00 | Keranigonj | 243 | 04:00 | 218 | 12:00
Ashuganj | 239 | 03:00 | 224 | 12:00 | Khulna(S) | 247 | 04:00 | 229 | 13:00
Ashuganj-400 | 239 | 03:00 | 224 | 12:00 | Korerhat | 242 | 04:00 | 227 | 12:00
Baghabari | 241 | 01:00 | 230 | 12:00 | Madunaghat | 240 | 02:00 | 230 | 11:00
Barapukuria | 234 | 04:00 | 213 | 18:00 | Madunaghat-400 | 240 | 04:00 | 231 | 10:00
Barapukuria-230 | 234 | 04:00 | 213 | 18:00 | Maniknagar | 241 | 02:00 | 220 | 12:00
Barishal | 240 | 02:00 | 229 | 12:00 | Meghnaghat | 243 | 07:00 | 226 | 12:00
Bheramara | 243 | 04:00 | 224 | 12:00 | Meghnaghat-400 | 243 | 05:00 | 211 | 12:00
Bhulta | 244 | 04:00 | 222 | 12:00 | Mirsorai | 241 | 00:00 | 229 | 10:00
Bibiana | 251 | 04:00 | 226 | 12:00 | Rajshahi | 243 | 05:00 | 223 | 13:00
BIPTC | 243 | 04:00 | 222 | 12:00 | Rampal | 244 | 04:00 | 226 | 12:00
Bogura | 246 | 05:00 | 229 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 244 | 04:00 | 228 | 13:00 | Rampura | 244 | 05:00 | 221 | 12:00
Borhanuddin | 242 | 01:00 | 234 | 12:00 | Shikalbaha | 238 | 04:00 | 228 | 08:00
BSRM | 242 | 04:00 | 227 | 12:00 | Shyampur | 243 | 05:00 | 219 | 12:00
Cumilla(N) | 241 | 05:00 | 225 | 13:00 | Siddhirganj | 244 | 03:00 | 222 | 13:00
Faridpur | 241 | 04:00 | 225 | 12:00 | Sirajgonj | 247 | 04:00 | 237 | 09:00
Fenchuganj | 249 | 06:00 | 232 | 12:00 | Sreepur | 239 | 04:00 | 225 | 12:00
Feni | 242 | 03:00 | 226 | 12:00 | Tongi | 237 | 18:00 | 220 | 12:00
Ghorashal | 240 | 02:00 | 230 | 12:00
Ghorashal-230 | 236 | 04:00 | 214 | 12:00
Gopalganj | 239 | 04:00 | 223 | 12:00
GPH | 240 | 03:00 | 228 | 12:00
Haripur | 243 | 04:00 | 221 | 12:00
Hasnabad | 241 | 01:00 | 219 | 12:00
Hathazari | 235 | 04:00 | 224 | 12:00
Ishurdi | 245 | 05:00 | 226 | 12:00
Jhenaidah | 244 | 04:00 | 221 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 03:00 | 120 | 11:00 | Laksam | 140 | 04:00 | 132 | 10:00
Agargaon | 140 | 04:00 | 123 | 12:00 | Lakshmipur | 136 | 03:00 | 127 | 12:00
Agrabad | 139 | 02:00 | 132 | 12:00 | Lalbag | 137 | 06:00 | 125 | 10:00
AKS | 136 | 02:00 | 130 | 12:00 | Lalmonirhat | 132 | 05:00 | 118 | 18:00
Aminbazar | 139 | 04:00 | 124 | 12:00 | Madanganj | 136 | 05:00 | 133 | 00:00
Amnura | 139 | 05:00 | 129 | 11:00 | Madaripur | 142 | 04:00 | 134 | 12:00
Ashuganj | 141 | 01:00 | 134 | 11:00 | Madartek | 133 | 05:00 | 121 | 12:00
Bagerhat | 137 | 04:00 | 123 | 13:00 | Madunaghat | 140 | 02:00 | 133 | 11:00
Bajitpur | 134 | 03:00 | 126 | 12:00 | Magura | 140 | 04:00 | 124 | 13:00
Bakerganj | 136 | 02:00 | 134 | 13:00 | Mahasthangarh | 138 | 03:00 | 128 | 13:00
Bakulia | 140 | 04:00 | 133 | 12:00 | Maijdee | 136 | 04:00 | 127 | 12:00
Banani | 134 | 03:00 | 122 | 12:00 | Manikganj | 133 | 04:00 | 120 | 12:00
Bangabhaban | 141 | 05:00 | 125 | 12:00 | Maniknagar | 141 | 04:00 | 125 | 12:00
Barapukuria | 140 | 04:00 | 127 | 18:00 | Matarbari | 138 | 05:00 | 126 | 12:00
Barguna | 139 | 04:00 | 134 | 12:00 | Matuail | 140 | 07:00 | 127 | 12:00
Barishal | 140 | 00:00 | 132 | 14:00 | Metrorail_Motijheel | 141 | 04:00 | 125 | 12:00
Barishal-230 | 141 | 02:00 | 133 | 12:00 | Metrorail_Uttara | 138 | 03:00 | 123 | 12:00
Baroaulia | 138 | 00:00 | 133 | 11:00 | Millgate | 137 | 03:00 | 121 | 12:00
Baroirhat | 138 | 05:00 | 128 | 12:00 | Mirpur | 139 | 04:00 | 123 | 12:00
Bashundhara | 134 | 02:00 | 122 | 10:00 | Mirzapur | 134 | 04:00 | 124 | 12:00
BashundharaCement | 137 | 00:00 | 134 | 01:00 | Mithapukur | 138 | 05:00 | 124 | 18:00
Beanibazar | 137 | 05:00 | 130 | 12:00 | MI_Cement | 138 | 04:00 | 120 | 12:00
Benapole | 138 | 03:00 | 116 | 13:00 | Modern | N/A | N/A | N/A | N/A
Bhaluka | 137 | 05:00 | 126 | 19:30 | Mogbazar | 136 | 02:00 | 124 | 11:00
Bhandaria | 139 | 04:00 | 132 | 13:00 | Mongla | 135 | 06:00 | 123 | 13:00
Bhangura | 141 | 04:00 | 133 | 09:00 | Motijheel | 141 | 05:00 | 125 | 12:00
Bheramara | 143 | 04:00 | 134 | 18:00 | Muktagacha | 136 | 11:00 | 126 | 05:00
Bheramara(GK) | 142 | 04:00 | 134 | 18:00 | Munshiganj | 138 | 03:00 | 125 | 12:00
Bhulta | 129 | 02:00 | 121 | 12:00 | Muradnagar | 138 | 01:00 | 128 | 12:00
Bog-Sherpur | 140 | 04:00 | 130 | 13:00 | Mymensingh | 136 | 11:00 | 122 | 12:00
Bogura | 140 | 03:00 | 131 | 09:00 | Naogaon | 136 | 01:00 | 125 | 09:00
Bogura-230 | 140 | 04:00 | 130 | 18:00 | Narail | 140 | 05:00 | 122 | 13:00
Brahmanbaria | 136 | 02:00 | 127 | 12:00 | Narinda | 141 | 04:00 | 125 | 12:00
Cantonment | 139 | 02:00 | 123 | 12:00 | Narshingdi | 136 | 02:00 | 123 | 12:00
Chandina | 141 | 03:00 | 130 | 12:00 | Natore | 138 | 05:00 | 130 | 13:00
Chandpur | 139 | 04:00 | 131 | 12:00 | Nawabganj | 137 | 05:00 | 121 | 12:00
Chandraghona | 140 | 02:00 | 133 | 12:00 | Netrakona | 130 | 00:00 | 120 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 140 | 02:00 | 132 | 13:00 | New | 139 | 05:00 | 121 | 09:00
Charsaidpur | 138 | 03:00 | 126 | 12:00 | Niamatpur | 141 | 04:00 | 132 | 13:00
Chauddagram | 139 | 04:00 | 129 | 12:00 | Noapara | 139 | 04:00 | 117 | 13:00
Chhatak | 136 | 00:00 | 130 | 07:00 | Pabna | 142 | 04:00 | 132 | 18:00
Chowmuhani | 134 | 00:00 | 128 | 08:00 | Palashbari | 133 | 03:00 | 123 | 18:00
Chuadanga | 139 | 04:00 | 122 | 13:00 | Panchagarh | 139 | 04:00 | 127 | 12:00
Coxsbazar | 131 | 01:00 | 123 | 09:00 | Patiya | 139 | 02:00 | 132 | 12:00
Cumilla(N) | 141 | 05:00 | 129 | 12:00 | Patuakhali | 137 | 01:00 | 133 | 12:00
Cumilla(S) | 139 | 05:00 | 125 | 10:00 | Payra | 140 | 04:00 | 135 | 12:00
Daganbhuiyan | 137 | 04:00 | 127 | 12:00 | PHP | 137 | 04:00 | 128 | 11:00
Daudkandi | 138 | 04:00 | 125 | 12:00 | Postogola | 139 | 05:00 | 122 | 12:00
DhakaUniversity | 134 | 04:00 | 122 | 12:00 | Purbachal | 135 | 04:00 | 122 | 11:00
Dhamrai | 137 | 18:00 | 121 | 09:00 | Purbasadipur | 132 | 01:00 | 119 | 18:00
Dhanmondi | 141 | 04:00 | 128 | 12:00 | Rahanpur | 141 | 01:00 | 134 | 13:00
Dohazari | 135 | 00:00 | 130 | 12:00 | Rahanpur-400 | 142 | 04:00 | 135 | 09:00
Faridpur | 140 | 04:00 | 130 | 12:00 | Rahim | 139 | 04:00 | 126 | 12:00
Fatullah | 140 | 04:00 | 120 | 12:00 | Rajbari | 140 | 04:00 | 129 | 12:00
Fenchuganj | 141 | 05:00 | 133 | 12:00 | Rajendrapur | 138 | 05:00 | 128 | 09:00
Feni | 135 | 02:00 | 126 | 12:00 | Rajshahi | 139 | 06:00 | 129 | 13:00
Feni-230 | 137 | 05:00 | 127 | 12:00 | Rajshahi-230 | 140 | 04:00 | 128 | 13:00
Ghatail | 132 | 17:00 | 123 | 08:00 | Ramganj | 136 | 01:00 | 128 | 11:00
Ghorashal | 133 | 01:00 | 119 | 11:00 | Rampur | 139 | 02:00 | 132 | 11:00
Goalpara | 140 | 05:00 | 127 | 12:00 | Rampura | 138 | 18:00 | 122 | 11:00
Gollamari | 139 | 05:00 | 127 | 12:00 | Rangamati | 139 | 03:00 | 133 | 12:00
Gopalganj | 142 | 04:00 | 131 | 12:00 | Rangpur | 136 | 06:00 | 126 | 12:00
Gopalganj-400 | 145 | 05:00 | 134 | 12:00 | Ruppur | 142 | 05:00 | 134 | 13:00
Gulshan | 133 | 05:00 | 121 | 12:00 | Saidpur | 136 | 02:00 | 124 | 13:00
Halishahar | 140 | 03:00 | 132 | 12:00 | Satkhira | 137 | 03:00 | 123 | 13:00
Haripur | 139 | 03:00 | 127 | 12:00 | Satmasjid | 139 | 04:00 | 123 | 12:00
HaripurSBU | 138 | 03:00 | 127 | 12:00 | Savar | 138 | 05:00 | 122 | 12:00
Hasnabad | 138 | 03:00 | 125 | 11:00 | SevenRings | 138 | 16:00 | 119 | 12:00
Hathazari | 139 | 03:00 | 133 | 11:00 | ShahCement | 138 | 03:00 | 126 | 12:00
Hatirjheel | 134 | 03:00 | 122 | 12:00 | Shahjadpur | 142 | 00:00 | 134 | 12:00
Ishurdi | 144 | 04:00 | 134 | 18:00 | Shahjibazar | 136 | 01:00 | 129 | 12:00
Jaldhaka | 133 | 04:00 | 121 | 18:00 | Shahmirpur | 138 | 00:00 | 133 | 11:00
Jamalpur | 135 | 11:00 | 125 | 00:00 | Shariatpur | 143 | 02:00 | 133 | 13:00
Jashore | 138 | 06:00 | 118 | 13:00 | Sherpur | 131 | 11:00 | 121 | 07:00
Jhenaidah | 141 | 04:00 | 117 | 18:00 | Shikalbaha | 129 | 06:00 | 123 | 13:00
Jhenaidah-230 | 142 | 04:00 | 126 | 13:00 | Shikalbaha-230 | 141 | 02:00 | 134 | 11:00
Joydebpur | 131 | 00:00 | 118 | 12:00 | Shitalakhya | 138 | 04:00 | 120 | 12:00
Joypurhat | 137 | 04:00 | 126 | 18:00 | Sholosohor | 140 | 03:00 | 133 | 12:00
Juldah | 139 | 04:00 | 132 | 12:00 | Shyampur | 138 | 05:00 | 125 | 12:00
Kabirpur | 137 | 18:00 | 120 | 12:00 | Shyampur-230 | 141 | 05:00 | 126 | 12:00
Kachua | 140 | 04:00 | 131 | 12:00 | Siddhirganj | 139 | 01:00 | 127 | 13:00
Kaliakoir | 139 | 18:00 | 124 | 09:00 | Sirajganj | 139 | 03:00 | 128 | 20:00
Kallyanpur | 139 | 01:00 | 124 | 12:00 | Sonargaon | 138 | 02:00 | 126 | 12:00
Kalurghat | 139 | 04:00 | 133 | 12:00 | Sreemongol | 138 | 06:00 | 129 | 12:00
Kamrangirchar | 139 | 04:00 | 121 | 12:00 | Sreepur | 139 | 04:00 | 130 | 09:00
Kaptai | 141 | 1:00 | 136 | 10:00 | Srinagar | 138 | 04:00 | 121 | 12:00
Kasba | 140 | 03:00 | 128 | 12:00 | SSM | 142 | 00:00 | 138 | 12:00
Kazla | 141 | 05:00 | 126 | 12:00 | Sunamganj | 135 | 02:00 | 128 | 12:00
Keranigonj | 138 | 05:00 | 121 | 12:00 | Sylhet | 137 | 03:00 | 130 | 13:00
Khagrachori | 139 | 00:00 | 132 | 12:00 | Sylhet-132 | 136 | 00:00 | 132 | 11:00
Khulna | 137 | 03:00 | 125 | 13:00 | Tangail | 131 | 17:00 | 120 | 09:00
Khulna(S) | 139 | 03:00 | 128 | 12:00 | Taraganj | 136 | 04:00 | 121 | 18:00
Khulshi | 138 | 01:00 | 131 | 12:00 | Tasnim | 139 | 04:00 | 126 | 12:00
Kishoreganj | 132 | 01:00 | 124 | 13:00 | Thakurgaon | 137 | 04:00 | 125 | 12:00
Kodda | 135 | 18:00 | 120 | 09:00 | TK | 139 | 01:00 | 134 | 11:00
KSRM | 139 | 02:00 | 133 | 15:00 | Tongi | 137 | 18:00 | 125 | 10:00
Kulaura | 140 | 02:00 | 132 | 12:00 | Ullahpara | 141 | 03:00 | 130 | 18:00
Kurigram | 132 | 04:00 | 119 | 18:00 | Ullon | 133 | 01:00 | 123 | 10:00
Kushtia | 137 | 03:00 | 125 | 18:00 | Uttara | 139 | 04:00 | 123 | 12:00
Zigatola | 137 | 02:00 | 122 | 12:00 | UttaraNew | 138 | 03:00 | 123 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division