## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 09-01-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-01-2026 | during | 09-01-2026 | during | 09-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 340 | 310 | 412 | 412 | 392 | 392 | FGMO, Gas Shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 240 | 240 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 280 | 335 | 335 | 0 | 0 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 15.4 | 50.4 | 53.97 | 53.97 | 53.97 | 53.97 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 14 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 24 | 24 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 15 | 15.1 | 15.1 | 15.1 | 15.1 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 15 | 145 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 40 | 144 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 50 | 152 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 28 | 0 | 24 | 0 | 24 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 375 | 400 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 108 | 70 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1323.4 | 1680.4 | 5331.25 | 5307.25 | 2457.13 | 2471.13
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 | 46 | 46 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 173 | 173 | 150 | 150 | 150 | 150 | Plant availability less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 101 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 38 | 40 | 64 | 40 | 64 | Machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 51 | 51 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 38 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 20 | 37 | 35 | 40 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.25 | 0 | 3.24 | 0 | 3.24 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 45 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 31 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 7 | 50 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1160 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 3 | 1 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 570 | 570 | 150 | 150 | 720 | 720 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2001.25 | 2290 | 2950.1 | 2956.86 | 3014.74 | 3035.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 163 | 150 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 280 | 280 | 353.35 | 353.35 | 353.35 | 353.35 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 215 | 215 | 393 | 393 | 363 | 363 | FGMO, Gas Shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 80 | 80 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | Machine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 120 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 108 | 108 | 163 | 163 | 115 | 115 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 147 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 116 | 108 | 84 | 76 | 126 | 126 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 13 | 24.5 | 24.5 | 24.5 | 24.5 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 9 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 30 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 67 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1028 | 1231 | 2390.75 | 2322.75 | 2119.75 | 2059.75
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-01-2026 | during | 09-01-2026 | during | 09-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 26 | 11 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.5 | 0 | 1.5 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 58 | 60 | 60 | 60 | 60 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 19 | 20 | 20 | 20 | 20 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 45.21 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 18 | 22 | 22 | 18 | 18 | To be dispatched 18 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 167.21 | 106 | 357.5 | 314 | 353.5 | 310
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 41 | 41 | 41 | 41 | 41 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 60 | 60 | 60 | 60 | Machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 139 | 154 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 77 | 81 | 81 | 81 | 81 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 157 | 157 | 160 | 160 | 158 | 158 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 341 | 320 | 341 | 341 | 0 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 874 | 860 | 901 | 901 | 542 | 849
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 409 | 408 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 56 | 0 | 410 | 410 | 369 | 369 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 74 | 0 | 79 | 0 | 79 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 964 | 1118 | 1148.28 | 1148.28 | 617.1 | 617.1 | U-2 Under Maintenance
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1503 | 1526 | 3499.28 | 3420.28 | 2172.2 | 2093.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 308 | 308 | 0 | 0 | 622 | 622 | Machine Problem
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 140 | 132 | 136 | 136 | 70 | 70 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 470 | 580 | 622 | 622 | 575 | 575 | FGMO, U1 under maintenance
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 243 | 277 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.52 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1381.52 | 1517 | 1546 | 1545 | 1902 | 1901
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 51.99 | 0 | 49.32 | 0 | 49.32 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 130 | 132 | 214 | 214 | 192.6 | 192.6 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 280 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0 | 0 | 4 | 0 | 4 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1277.06 | 1358 | 1435.88 | 1435.88 | 1356 | 1356 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 54.81 | 0 | 30 | 0 | 30 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 99 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1892.86 | 1939 | 3104.19 | 2920.87 | 2489.53 | 2306.21
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 92 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.9 | 0 | 0 | 0 | 0 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 146 | 0 | 127.66 | 0 | 127.66 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 181.9 | 162 | 394.66 | 242 | 380.66 | 228
System Total |  |  |  |  | 28823.2 | 28382.248 | 10353.14 | 11311.4 | 20474.73 | 19930.01 | 15431.51 | 15253.79
Forecast Scenario (09-01-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8850 |  | 0 |  | 8850
|  |  |  | 1:00 | 8110 |  | 0 |  | 8110
|  |  |  | 2:00 | 7680 |  | 0 |  | 7680
|  |  |  | 3:00 | 7430 |  | 0 |  | 7430
|  |  |  | 4:00 | 7260 |  | 0 |  | 7260
|  |  |  | 5:00 | 6970 |  | 0 |  | 6970
|  |  |  | 6:00 | 7240 |  | 0 |  | 7240
|  |  |  | 7:00 | 7310 |  | 0 |  | 7310
|  |  |  | 8:00 | 7990 |  | 0 |  | 7990
|  |  |  | 9:00 | 8600 |  | 0 |  | 8600
|  |  |  | 10:00 | 8790 |  | 0 |  | 8790
|  |  |  | 11:00 | 8940 |  | 0 |  | 8940
|  |  |  | 12:00 | 9660 |  | 0 |  | 9660
|  |  |  | 13:00 | 10690 |  | 0 |  | 10690
|  |  |  | 14:00 | 9190 |  | 0 |  | 9190
|  |  |  | 15:00 | 7870 |  | 0 |  | 7870
|  |  |  | 16:00 | 7640 |  | 0 |  | 7640
|  |  |  | 17:00 | 8000 |  | 0 |  | 8000
|  |  |  | 18:00 | 9470 |  | 0 |  | 9470
|  |  |  | 18:30 | 9500 |  | 0 |  | 9500
|  |  |  | 19:00 | 9560 |  | 0 |  | 9560
|  |  |  | 19:30 | 9530 |  | 0 |  | 9530
|  |  |  | 20:00 | 9600 |  | 0 |  | 9600
|  |  |  | 21:00 | 9560 |  | 0 |  | 9560
|  |  |  | 22:00 | 9320 |  | 0 |  | 9320
|  |  |  | 23:00 | 8720 |  | 0 |  | 8720
Probable Maximum Temperature: |  |  | 19.00°C
Probable Maximum Demand at Day Peak: |  |  | 9660.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 9600.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 9600.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 204.45 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:42 hrs on 09-01-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 08-01-2026 | [28 empty] | Date: | 08-01-2026 | [28 empty] | Date: | 08-01-2026 | [28 empty] | Date: | 08-01-2026 | [28 empty] | Date: | 08-01-2026 | [17 empty] | Date: | 08-01-2026
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [17 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 495 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 39 | 640 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 930 | 0 | 0 | 0 | 215 | 305 | 0 | 51 | 0 | 130 | 0 | 0 | 113 | 0 | 0 | 11 | 0 | 92 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 60 | 153 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 8 | 34 | 0 | 0 | 0 | 4774 | 409 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1036 | 0 | 0 | 0 | 1054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 100 | 220 | 0 | 380 | 440 | 0 | 4313 | 9087 | 97.17
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 495 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 625 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 850 | 0 | 0 | 0 | 215 | 315 | 0 | 0 | 0 | 163 | 0 | 0 | 111 | 0 | 0 | 8 | 0 | 92 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 20 | 153 | 0 | 5 | 0 | 78 | 20 | 0 | 0 | 158 | 0 | 8 | 8 | 34 | 0 | 0 | 0 | 4557 | 409 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 970 | 0 | 0 | 0 | 867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 220 | 0 | 370 | 350 | 0 | 3878 | 8435 | 97.17
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 490 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 625 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 800 | 0 | 0 | 0 | 215 | 305 | 0 | 0 | 0 | 196 | 0 | 0 | 111 | 0 | 0 | 11 | 0 | 80 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 20 | 158 | 0 | 0 | 0 | 5 | 20 | 0 | 0 | 158 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 4511 | 409 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 812 | 0 | 0 | 0 | 847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 220 | 0 | 379 | 260 | 0 | 3599 | 8110 | 97.17
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 400 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 625 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 215 | 285 | 0 | 0 | 0 | 182 | 0 | 0 | 111 | 0 | 0 | 11 | 0 | 80 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 20 | 159 | 0 | 0 | 0 | 5 | 20 | 0 | 0 | 158 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 4301 | 263 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 793 | 0 | 0 | 0 | 843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 220 | 0 | 342 | 250 | 0 | 3493 | 7794 | 97.16
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 440 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 625 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 610 | 0 | 0 | 0 | 215 | 295 | 0 | 0 | 0 | 142 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 80 | 0 | 0 | 0 | 305 | 0 | 0 | 41 | 20 | 154 | 0 | 0 | 0 | 5 | 20 | 0 | 0 | 158 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 4160 | 176 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 792 | 0 | 0 | 0 | 835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 280 | 250 | 0 | 3298 | 7458 | 97.16
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 625 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 615 | 0 | 0 | 0 | 215 | 305 | 0 | 0 | 0 | 142 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 82 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 20 | 151 | 0 | 0 | 0 | 5 | 20 | 0 | 0 | 158 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 4073 | 176 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 795 | 0 | 0 | 0 | 837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 100 | 180 | 0 | 257 | 250 | 0 | 3310 | 7383 | 97.16
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 720 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 710 | 0 | 0 | 0 | 215 | 285 | 0 | 4 | 0 | 140 | 0 | 0 | 114 | 0 | 0 | 11 | 0 | 86 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 60 | 145 | 0 | 5 | 0 | 60 | 30 | 0 | 0 | 158 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 4470 | 176 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 801 | 0 | 0 | 0 | 879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 100 | 180 | 0 | 256 | 280 | 0 | 3421 | 7891 | 97.15
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 335 | 0 | 0 | 1 | 0 | 13 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0.03 | 46 | 0 | 39 | 720 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 890 | 1 | 0 | 0 | 230 | 295 | 0 | 51 | 0 | 170 | 0 | 0 | 114 | 0 | 0 | 8 | 0 | 80 | 0 | 1 | 0 | 310 | 0 | 0 | 41 | 60 | 137 | 0 | 17 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 2 | 5 | 54 | 0 | 0.6 | 0 | 4822.63 | 176 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 858 | 0 | 0 | 0 | 960 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57 | 0 | 0 | 0 | 0.62 | 130 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 243 | 90 | 220 | 0 | 250 | 340 | 0 | 3711.26 | 8533.89 | 97.15
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 335 | 0 | 0 | 6 | 0 | 13 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0.46 | 46 | 0 | 22 | 720 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1010 | 7 | 0 | 0 | 230 | 305 | 0 | 51 | 0 | 177 | 0 | 0 | 114 | 0 | 0 | 10 | 0 | 96 | 0 | 6 | 0 | 310 | 0 | 0 | 41 | 60 | 154 | 1 | 17 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 56 | 30 | 0 | 8.62 | 0 | 5072.08 | 409 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 993 | 0 | 0 | 0 | 1149.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8 | 18 | 0 | 0 | 9.59 | 140 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.83 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.3 | 12 | 0.1 | 0 | 307 | 90 | 220 | 0 | 291 | 428 | 0 | 4596.19 | 9668.27 | 97.15
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 390 | 0 | 0 | 335 | 0 | 0 | 15 | 0 | 23 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 1.08 | 46 | 0 | 18 | 720 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1160 | 12 | 0 | 0 | 215 | 300 | 0 | 51 | 0 | 163 | 0 | 0 | 114 | 0 | 0 | 11 | 0 | 96 | 0 | 23 | 0 | 305 | 0 | 0 | 41 | 60 | 150 | 2 | 17 | 0 | 78 | 30 | 0 | 0 | 159 | 0 | 19 | 56 | 30 | 1 | 22.52 | 10 | 5238.6 | 408 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 1103 | 0 | 0 | 0 | 1385.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.56 | 45 | 0 | 0 | 27.57 | 140 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 22 | 0.24 | 0 | 279 | 90 | 180 | 0 | 303 | 520 | 0 | 4999.87 | 10238.47 | 97.14
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 370 | 0 | 0 | 335 | 0 | 0 | 23 | 52 | 23 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 2.63 | 46 | 0 | 18 | 680 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1100 | 17 | 0 | 0 | 215 | 280 | 0 | 51 | 0 | 170 | 0 | 0 | 111 | 0 | 0 | 11 | 0 | 96 | 0 | 53 | 0 | 310 | 0 | 0 | 41 | 60 | 134 | 3 | 17 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 56 | 29 | 0 | 34.34 | 18 | 5217.97 | 409 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 994 | 0 | 0 | 0 | 1279.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.1 | 73 | 0 | 0 | 41.02 | 140 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 1.8 | 22 | 0.39 | 0 | 277 | 88 | 180 | 0 | 306 | 480 | 0 | 4766.88 | 9984.85 | 97.14
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 370 | 0 | 0 | 335 | 0 | 0 | 26 | 90 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 3.08 | 46 | 0 | 17 | 580 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1100 | 18 | 0 | 0 | 215 | 280 | 0 | 51 | 0 | 167 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 100 | 0 | 63 | 0 | 315 | 0 | 0 | 41 | 60 | 136 | 4 | 17 | 0 | 78 | 30 | 0 | 0 | 157 | 0 | 19 | 56 | 29 | 1 | 40.89 | 18 | 5188.97 | 409 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 947 | 0 | 0 | 0 | 1229.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.76 | 92 | 0 | 0 | 48.46 | 136 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 5.5 | 76 | 0.47 | 0 | 235 | 115 | 180 | 0 | 304 | 472 | 0 | 4751.32 | 9940.29 | 97.14
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 15.4 | 0 | 40 | 0 | 15 | 0 | 14 | 50 | 0 | 0 | 0 | 375 | 0 | 0 | 300 | 0 | 0 | 28 | 108 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 7 | 3.25 | 46 | 0 | 20 | 570 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1160 | 19 | 0 | 0 | 215 | 280 | 0 | 51 | 0 | 163 | 0 | 0 | 108 | 17 | 0 | 11 | 0 | 116 | 0 | 67 | 0 | 341 | 0 | 0 | 41 | 60 | 139 | 11 | 17 | 0 | 78 | 30 | 0 | 0 | 157 | 0 | 19 | 58 | 26 | 1 | 45.21 | 18 | 5393.86 | 409 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 964 | 0 | 0 | 0 | 1277.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.99 | 99 | 0 | 0 | 54.81 | 130 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 5.9 | 146 | 0.52 | 0 | 243 | 140 | 220 | 0 | 308 | 470 | 0 | 4959.28 | 10353.14 | 97.13
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 23.7 | 0 | 58 | 0 | 95 | 0 | 18 | 112 | 0 | 0 | 0 | 390 | 0 | 30 | 300 | 0 | 0 | 28 | 108 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 3.04 | 46 | 0 | 26 | 570 | 0 | 0 | 0 | 0 | 13 | 173 | 0 | 0 | 0 | 1156 | 18 | 0 | 0 | 215 | 280 | 0 | 51 | 0 | 160 | 0 | 0 | 105 | 40 | 0 | 11 | 0 | 124 | 0 | 64 | 0 | 341 | 0 | 0 | 41 | 60 | 159 | 11 | 17 | 0 | 78 | 30 | 0 | 0 | 157 | 0 | 19 | 58 | 26 | 2 | 42.62 | 18 | 5701.36 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 1033 | 0 | 0 | 0 | 1364.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.68 | 95 | 0 | 0 | 53.99 | 130 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 5.6 | 143 | 0.51 | 0 | 279 | 140 | 220 | 0 | 303 | 502 | 0 | 5177.95 | 10879.31 | 97.13
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 30.8 | 0 | 65 | 0 | 60 | 0 | 35 | 115 | 0 | 0 | 0 | 370 | 0 | 35 | 300 | 0 | 0 | 24 | 100 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 2.64 | 46 | 0 | 26 | 570 | 0 | 0 | 0 | 0 | 30 | 173 | 0 | 0 | 0 | 1156 | 16 | 0 | 0 | 215 | 280 | 0 | 51 | 0 | 161 | 0 | 0 | 104 | 81 | 0 | 11 | 0 | 126 | 0 | 55 | 0 | 320 | 0 | 0 | 41 | 60 | 152 | 9 | 17 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 19 | 58 | 26 | 2 | 35.59 | 18 | 5655.03 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 998 | 0 | 0 | 0 | 1237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.94 | 83 | 0 | 0 | 42.93 | 130 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 4.4 | 125 | 0.39 | 0 | 276 | 135 | 220 | 0 | 308 | 450 | 0 | 4898.66 | 10553.69 | 97.13
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 32.2 | 0 | 50 | 0 | 45 | 0 | 17 | 66 | 0 | 0 | 0 | 378 | 0 | 17 | 280 | 0 | 0 | 18 | 90 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 12 | 1.82 | 46 | 0 | 23 | 570 | 0 | 0 | 0 | 0 | 16 | 173 | 0 | 0 | 0 | 1086 | 12 | 0 | 0 | 215 | 285 | 0 | 51 | 0 | 160 | 0 | 0 | 104 | 34 | 0 | 11 | 0 | 112 | 0 | 38 | 0 | 320 | 0 | 0 | 41 | 60 | 158 | 6 | 17 | 0 | 78 | 30 | 0 | 0 | 157 | 0 | 19 | 58 | 25 | 1 | 24.41 | 18 | 5331.43 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 910 | 0 | 0 | 0 | 1227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.09 | 61 | 0 | 0 | 26.94 | 130 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 3.4 | 88 | 0.29 | 0 | 223 | 132 | 220 | 0 | 304 | 450 | 0 | 4628.72 | 9960.15 | 97.12
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 34.4 | 0 | 50 | 0 | 45 | 0 | 17 | 34 | 0 | 0 | 0 | 380 | 0 | 17 | 280 | 0 | 0 | 9 | 90 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0.93 | 46 | 0 | 24 | 570 | 0 | 0 | 0 | 0 | 15 | 173 | 0 | 0 | 0 | 1121 | 7 | 0 | 0 | 215 | 285 | 0 | 51 | 0 | 160 | 0 | 0 | 103 | 34 | 0 | 11 | 0 | 110 | 0 | 19 | 0 | 315 | 0 | 0 | 41 | 60 | 160 | 3 | 17 | 0 | 78 | 30 | 0 | 0 | 157 | 0 | 19 | 58 | 25 | 0 | 8.99 | 17 | 5282.32 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 920 | 0 | 0 | 0 | 1142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.42 | 30 | 0 | 0 | 12.32 | 130 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 1.6 | 36 | 0.12 | 0 | 225 | 132 | 220 | 0 | 307 | 450 | 0 | 4408.46 | 9690.78 | 97.12
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 31.2 | 0 | 60 | 0 | 80 | 0 | 17 | 64 | 0 | 0 | 0 | 380 | 0 | 17 | 280 | 0 | 0 | 2 | 52 | 24 | 14 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 8 | 0 | 12 | 12 | 0.08 | 46 | 1 | 29 | 570 | 0 | 0 | 0 | 0 | 28 | 173 | 0 | 0 | 0 | 1089 | 1 | 26 | 0 | 215 | 285 | 0 | 51 | 0 | 160 | 0 | 6 | 103 | 47 | 5 | 11 | 0 | 110 | 0 | 2 | 0 | 320 | 0 | 0 | 41 | 60 | 157 | 0 | 17 | 0 | 78 | 30 | 0 | 0 | 157 | 0 | 19 | 58 | 25 | 0 | 1.31 | 15 | 5333.59 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 988 | 0 | 0 | 0 | 1237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.94 | 5 | 0 | 0 | 2.03 | 130 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.19 | 0 | 0 | 35 | 1 | 34 | 0 | 0 | 0 | 0.3 | 5 | 0.02 | 0 | 219 | 132 | 180 | 0 | 306 | 470 | 0 | 4572.48 | 9906.07 | 97.12
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 50 | 0 | 84 | 0 | 145 | 0 | 50 | 154 | 0 | 0 | 0 | 385 | 0 | 45 | 280 | 0 | 0 | 0 | 70 | 24 | 15 | 0 | 0 | 0 | 18 | 0 | 0 | 3 | 0 | 24 | 0 | 25 | 50 | 0 | 46 | 17 | 32 | 570 | 0 | 0 | 0 | 0 | 56 | 173 | 0 | 0 | 0 | 1160 | 0 | 73 | 0 | 215 | 285 | 0 | 51 | 0 | 160 | 0 | 16 | 107 | 93 | 9 | 13 | 0 | 114 | 0 | 0 | 0 | 325 | 0 | 0 | 41 | 60 | 157 | 0 | 17 | 0 | 78 | 30 | 0 | 0 | 157 | 0 | 19 | 58 | 11 | 0 | 0 | 18 | 5959 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 0 | 0 | 0 | 1408 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 73 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 132 | 220 | 0 | 301 | 520 | 0 | 5064 | 11023 | 97.11
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 50.4 | 0 | 144 | 0 | 145 | 0 | 35 | 152 | 0 | 0 | 0 | 400 | 0 | 55 | 280 | 0 | 0 | 0 | 70 | 24 | 15 | 0 | 0 | 0 | 45 | 0 | 0 | 1 | 0 | 38 | 0 | 38 | 50 | 0 | 46 | 31 | 37 | 570 | 0 | 0 | 0 | 0 | 101 | 173 | 0 | 0 | 0 | 1160 | 0 | 120 | 0 | 215 | 280 | 0 | 51 | 0 | 150 | 0 | 30 | 108 | 147 | 9 | 13 | 0 | 108 | 0 | 0 | 0 | 320 | 0 | 0 | 41 | 60 | 154 | 0 | 21 | 0 | 77 | 30 | 0 | 0 | 157 | 0 | 19 | 58 | 11 | 0 | 0 | 18 | 6167.4 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1118 | 0 | 0 | 0 | 1358 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 132 | 220 | 0 | 308 | 580 | 0 | 5144 | 11311.4 | 97.11
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 50.4 | 0 | 113 | 0 | 95 | 0 | 35 | 157 | 0 | 0 | 0 | 410 | 0 | 55 | 280 | 0 | 0 | 0 | 70 | 24 | 14 | 0 | 0 | 0 | 15 | 0 | 0 | 1 | 0 | 38 | 0 | 12 | 50 | 0 | 46 | 16 | 37 | 570 | 0 | 0 | 0 | 0 | 100 | 172 | 0 | 0 | 0 | 1175 | 0 | 40 | 0 | 215 | 280 | 0 | 51 | 0 | 150 | 0 | 17 | 108 | 150 | 9 | 13 | 0 | 106 | 0 | 0 | 0 | 325 | 0 | 0 | 41 | 60 | 152 | 0 | 21 | 0 | 77 | 30 | 0 | 0 | 157 | 0 | 19 | 58 | 11 | 0 | 0 | 18 | 5995.4 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 0 | 0 | 0 | 1376 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 132 | 220 | 0 | 305 | 595 | 0 | 5169 | 11164.4
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 48.3 | 0 | 120 | 0 | 95 | 0 | 35 | 157 | 0 | 0 | 0 | 395 | 0 | 55 | 280 | 0 | 0 | 0 | 52 | 19 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 38 | 0 | 0 | 50 | 0 | 46 | 15 | 40 | 570 | 0 | 0 | 0 | 0 | 98 | 173 | 0 | 0 | 0 | 1160 | 0 | 40 | 0 | 215 | 280 | 0 | 51 | 0 | 150 | 0 | 16 | 109 | 145 | 9 | 13 | 0 | 102 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 60 | 157 | 0 | 21 | 0 | 77 | 30 | 0 | 0 | 157 | 0 | 19 | 58 | 11 | 0 | 0 | 18 | 5888.3 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1126 | 0 | 0 | 0 | 1376 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 132 | 220 | 0 | 305 | 610 | 0 | 5196 | 11084.3 | 97.11
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 50.1 | 0 | 113 | 0 | 45 | 0 | 35 | 153 | 0 | 0 | 0 | 410 | 0 | 17 | 280 | 0 | 0 | 0 | 35 | 19 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 50 | 0 | 46 | 0 | 41 | 570 | 0 | 0 | 0 | 0 | 105 | 173 | 0 | 0 | 0 | 1160 | 0 | 12 | 0 | 215 | 280 | 0 | 51 | 0 | 140 | 0 | 0 | 109 | 146 | 0 | 13 | 0 | 108 | 0 | 0 | 0 | 320 | 0 | 0 | 41 | 60 | 163 | 0 | 21 | 0 | 77 | 30 | 0 | 0 | 157 | 0 | 19 | 58 | 11 | 0 | 0 | 18 | 5713.1 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1142 | 0 | 0 | 0 | 1369.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 132 | 220 | 0 | 304 | 610 | 0 | 5166.59 | 10879.69 | 97.1
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 40.7 | 0 | 88 | 0 | 30 | 0 | 35 | 108 | 0 | 0 | 0 | 440 | 0 | 17 | 280 | 0 | 0 | 0 | 17 | 18 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 50 | 0 | 46 | 0 | 42 | 570 | 0 | 0 | 0 | 0 | 68 | 173 | 0 | 0 | 0 | 1130 | 0 | 12 | 0 | 215 | 280 | 0 | 51 | 0 | 140 | 0 | 0 | 110 | 120 | 0 | 13 | 0 | 110 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 60 | 159 | 0 | 21 | 0 | 77 | 30 | 0 | 0 | 157 | 0 | 19 | 58 | 11 | 0 | 0 | 18 | 5514.7 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1128 | 0 | 0 | 0 | 1317.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 132 | 220 | 0 | 309 | 610 | 0 | 5077.6 | 10592.3 | 97.1
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 18 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 570 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1170 | 0 | 0 | 0 | 215 | 280 | 0 | 51 | 0 | 140 | 0 | 0 | 110 | 0 | 0 | 13 | 0 | 98 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 60 | 155 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 157 | 0 | 19 | 45 | 11 | 0 | 0 | 0 | 4801 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1122 | 0 | 0 | 0 | 1321.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 284 | 132 | 220 | 0 | 300 | 610 | 0 | 4846.52 | 9647.52 | 97.1
Total KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8251200 | 0 | 0 | 432720 | 0 | 1014048 | 0 | 853091 | 0 | 350457 | 1257120 | 0 | 886000 | 0 | 9483530 | 0 | 317089 | 6321657 | 0 | 0 | 179251 | 876000 | 462000 | 340560 | 0 | 0 | 0 | 80291 | 0 | 0 | 436320 | 0 | 90044 | 0 | 76800 | 361920 | 17277 | 1098000 | 82000 | 606720 | 14705454.55 | 0 | 0 | 0 | 0 | 632291 | 4107590 | 0 | 0 | 0 | 24229088 | 121635 | 332872 | 0 | 5247000 | 7315400 | 0 | 1010253 | 0 | 3933000 | 0 | 82560 | 2500129 | 1031040 | 34440 | 280820 | 0 | 2382720 | 0 | 394345 | 0 | 7736500 | 0 | 0 | 977000 | 1270320 | 3671427 | 51239 | 344328 | 0 | 1393920 | 673632 | 0 | 0 | 4417950 | 0 | 332400 | 943200 | 597120 | 8050 | 265840 | 257280 | 125154938.55 | 8856000 | 1111968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 469440 | 23338180 | 0 | 0 | 0 | 27915273 | 0 | 0 | 0 | 0 | 139680 | 0 | 0 | 0 | 0 | 315792 | 614769 | 0 | 0 | 321008 | 3226273 | 0 | 0 | 0 | 0 | 0 | 8385381 | 0 | 2160 | 0 | 0 | 437221 | 142953 | 469075 | 0 | 0 | 0 | 29111.52 | 690480 | 3069 | 0 | 5738000 | 2779000 | 5281510 | 0 | 7345455 | 11266909.09 | 0 | 108878707.61 | 234033646.16

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 08-01-2026
Power Supply Scenario
| Day Peak Generation |  |  | 10353.14 | MW | 12:00 Hr. | Energy Generated |  |  | 234.0336 |  | MKWHr.
| Day Peak Demand |  |  | 10353.14 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11311.4 | MW | 19:00 Hr. | Energy Demand |  |  | 234.0336 |  | MKWHr.
| Evening Peak Demand |  |  | 11311.4 | MW | 19:00 Hr. | Maximum Temperature |  |  | 24.5 |  | °C
| Minimum Generation of the Day |  |  | 7383 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 679.02 |  | MMCFD
| Maximum Generation of the Day |  |  | 11311.4 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.9418 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 25.7449 | 0 | 5.1005 | 0 | 0 | 0.17925 | 0 | 0 | 31.0247 | Gas | 92.6122 | Gas | 325927264.05
| Chattogram Zone |  |  | 4.7143 | 38.9345 | 1.3233 | 0 | 1.098 | 0.13891 | 0 | 0.43632 | 46.6454 | Coal | 86.6231 | Coal | 574781556.7937
| Cumilla Zone |  |  | 20.2866 | 0 | 1.4809 | 0 | 0 | 0.39435 | 2.3827 | 0 | 24.5446 | HFO | 10.4836 | HFO | 176020957.85
| Mymensingh Zone |  |  | 0.59712 | 0 | 1.5329 | 0 | 0 | 0.27389 | 0 | 0 | 2.4039 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 20.4851 | 0 | 0 | 0 | 0 | 0.051239 | 0 | 0 | 20.5363 | Hydro | 1.098 | Hydro | 109800
| Khulna Zone |  |  | 1.112 | 23.3382 | 0 | 0 | 0 | 0.46944 | 8.856 | 0 | 33.7756 | Solar | 3.6264 | Solar | 56459781.244
| Barishal Zone |  |  | 8.0605 | 24.3504 | 0 | 0 | 0 | 0.003069 | 0 | 0 | 32.4139 | Import | 39.154 | Import | 250860480.12
| Rajshahi Zone |  |  | 11.6117 | 0 | 0.13968 | 0 | 0 | 1.2537 | 27.9153 | 0 | 40.9203 | Wind | 0.43632 | Wind | 6418267.2
| Rangpur Zone |  |  | 0 | 0 | 0.9063 | 0 | 0 | 0.86254 | 0 | 0 | 1.7688
| Total |  |  | 92.6122 | 86.6231 | 10.4836 | 0 | 1.098 | 3.6264 | 39.154 | 0.43632 | 234.0336
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 325927264.05 |  | Hydro | 109800
|  |  |  | Coal | 574781556.7937 |  | Solar | 56459781.244
|  |  |  | HFO | 176020957.85 |  | Import | 250860480.12
|  |  |  | HSD | 0 |  | Wind | 6418267.2
[5 empty] | Total: | 139,05,78,107 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 8.856 | Peak Hr Flow | 408.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 34348163.64 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.9153 | Peak Hr Flow | 1358.00 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1619 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.3827 | Peak Hr Flow | 108.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2019 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 39.154 | Peak Hr Flow | 1874.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4165
|  |  |  | Chattogram |  | 0 |  | 1130
|  |  |  | Cumilla |  | 0 |  | 934
|  |  |  | Mymensingh |  | 0 |  | 893
|  |  |  | Sylhet |  | 0 |  | 398
|  |  |  | Khulna |  | 0 |  | 1309
|  |  |  | Barishal |  | 0 |  | 320
|  |  |  | Rajshahi |  | 0 |  | 1017
|  |  |  | Rangpur |  | 0 |  | 741
|  |  |  | Total |  | 0 |  | 10907
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Rangpur 20 MW GTPP |  |  | 20
|  | 2 | Baghabari 100 MW GTPP |  |  | 100
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 320 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 320
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:00 | 16:02 | Cumilla(N)-Kachua 132 kV Ckt-2 Scheduled S/D from Kachua 230/132/33kV end Due to For
annual maintenance work.
| 08:00 |  | Haripur-Meghnaghat 230kV Ckt-2 Scheduled S/D from Meghnaghat 230/132kV end Due to Clam
connector assembly work
| 08:08 | 16:15 | Magura-Narail 132kV Ckt-1 Scheduled S/D from Magura 132/33kV end Due to Annual
Maintenance. and from Narail 132/33kV end Due to For Annual maintenance work.
| 08:08 | 16:33 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 HT Scheduled S/D Due to Annual
Maintenance
| 08:08 | 16:33 | Payra_P/S-Payra 400kV Ckt-2 Scheduled S/D from Payra 400/132/33kV end Due to Annual
Maintenance
| 08:17 |  | Chhatak 132/33kV S/S T-1 LT Scheduled S/D Due to For Tan Delta Test
| 08:18 |  | Chhatak 132/33kV S/S T-1 HT Scheduled S/D Due to For Tan Delta Test
| 08:30 | 17:03 | Kaliakoir 400/230/132kV S/S Bibiyana1 Scheduled S/D Due to Annual maintenance.
| 08:30 | 15:52 | Rajshahi 230/132/33kV S/S 230 Kv BIPTC Ckt-02 Scheduled S/D Due to Annual Maintenance
work.
| 08:31 | 17:46 | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-2 Scheduled S/D Due to Annual Maintenance
| 08:31 | 17:34 | Aminbazar 400/230/132kV S/S Gopalganj-2 Scheduled S/D Due to Annual Maintenance
| 08:39 | 15:49 | Jhenaidah 132/33kV S/S Transformer T-1 HT Scheduled S/D Due to Annual maintenance
| 08:39 | 15:50 | Jhenaidah 132/33kV S/S Transformer T-1 LT Scheduled S/D Due to Annual maintenance
| 08:41 | 16:21 | Jamalpur United (20MW)- Sherpur 132kV Ckt-2 Scheduled S/D from Sherpur 132/33kV end Due
to Annual maintenance.
| 08:42 | 12:43 | Jhenaidah-Khulna 230kV Ckt-2 Scheduled S/D from Khulna(S) 230/132kV end Due to Annual
Maintenance Work. and from Jhenaidah 230/132kV end Due to annual Maintenance
| 08:52 | 16:32 | HVDC Bheramera- Rajshahi 230kV Ckt-2 Scheduled S/D from BIPTC end.
| 08:54 | 16:21 | Chauddagram-Feni 132 kV Ckt-2 Scheduled S/D from Feni 132/33kV end Due to Deadline Check
and from Chauddagram 132/33kV end Due to Yearly maintenance and from Feni 230/132kV end
Due to Annual maintenance and from Feni 230/132kV end Due to Annual maintenance
| 08:59 | 17:02 | Jamalpur United (20MW)-Jamalpur 132kV Ckt-2 Scheduled S/D from Jamalpur 132/33kV end Due
to Annual Maintenance
| 09:00 |  | Sirajgonj 225MW CCPP Unit-1, FGMO is OFF with remarks:-
| 09:04 | 16:35 | Mirpur 132/33kV S/S T2 LT Scheduled S/D Due to Annual maintenance work on 132 kV Bay
equipment of T2 Xfr.
| 09:08 | 16:35 | Mirpur 132/33kV S/S T2 HT Scheduled S/D Due to Annual maintenance work on 132 kV Bay
equipment of T2 Xfr.
| 09:16 | 16:15 | Tongi 230/132/33kV S/S T-01 LT Scheduled S/D Due to Annual maintenance work
| 09:17 | 16:15 | Tongi 230/132/33kV S/S T-01 HT Scheduled S/D Due to Annual maintenance work
| 09:20 | 14:19 | Rangpur 132/33kV S/S 132KV Bus B Project Work S/D Due to Re-conducting work
| 09:21 | 17:33 | Gopalganj 400/132kV S/S 400kV Amtoli Ckt-2 Scheduled S/D Due to Annual Maintenance
| 09:25 | 18:10 | Rangpur 132/33kV S/S Rangpur-GTPS Project Work S/D Due to Re-conducting work
| 09:26 | 16:42 | Mirpur 132/33kV S/S Reserve Bus Scheduled S/D Due to Annual maintenance work on 132 kV
Reserve Bus Bay equipment of T2 Xfr.
| 09:27 |  | Bagerhat-Mongla 132 kV Ckt-2 Scheduled S/D from Mongla 132/33kV end Due to Annual
maintenances and from Bagerhat 132/33kV end Due to Yearly maintenance
| 09:31 | 16:53 | Kabirpur -Kodda 132kV Ckt-1 Scheduled S/D from Kabirpur 132/33kV end Due to Annual
maintenance
| 09:34 | 18:17 | BIPTC S/S 230kV Bus-2 Scheduled S/D
| 09:34 | 15:02 | Cox'sbazar-Dohazari 132 kV Ckt-1 Scheduled S/D from Coxsbazar 132/33kV end Due to Annual
maintenance and from Dohazari 132/33kV end Due to Annual maintenance
| 09:38 | 15:01 | Bogura-Bogura (New)) 132 kV Ckt-2 Scheduled S/D from Bogura 230/132kV end Due to annual
Maintenance work and from Bogura 132/33kV end Due to Annual /maintenance
| 10:05 | 13:26 | Kurigram-Lalmonirhat 132kV Ckt-1 Scheduled S/D from Kurigram 132/33kV end Due to Annual
Maintenance
| 10:09 | 15:52 | Thakurgaon 132/33kV S/S T-1(422T) LT Scheduled S/D Due to Oil leakage at Bukholz.
| 10:10 | 15:52 | Thakurgaon 132/33kV S/S T-1(422T) HT Scheduled S/D Due to Oil leakage at Bukholz
| 10:20 |  | Muradnagar 132/33kV S/S 132KV Transformar-02 LT Scheduled S/D Due to For PBS project
works
| 10:21 |  | Muradnagar 132/33kV S/S 132KV Transformar-02 HT Scheduled S/D Due to For PBS Project
works.
| 10:30 | 16:06 | Bhaluka 132/33kV S/S Sreepur Ckt- 02 Scheduled S/D Due to Dead line check at sripur end. | [7 empty] | 30.0MW load
interrup.
| 10:32 | 16:10 | Bhaluka-Mymensingh 132 kV Ckt-1 Forced S/D from Bhaluka 132/33kV end Due to Load
Management
| 10:58 | 16:04 | Sreepur 230/132/33kV S/S Sreepur-Valuka Ckt-2 Scheduled S/D Due to annual Maintenance
| 11:05 | 17:30 | New Tongi S/S T1(403T) HT Scheduled S/D Due to Annual Maintanance
| 11:40 |  | Purbasadipur-Saidpur 132kV Ckt-2 Scheduled S/D from Saidpur 132/33kV end Due to By the
instructions of ALDC, Bogura and from Purbasadipur 132/33kV end Due to EEGBPS project
shutdown for equipment dismentale for GIS connection. No loadshed because Load served by
GIS to AIS connection.
| 12:10 |  | Chandpur 132/33kV S/S 402T (T-01) LT Forced S/D Due to N/A
|  | 12:10 | Chandpur 132/33kV S/S 422T(T-5) LT is restored.
|  | 12:30 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) HT is restored.
|  | 12:31 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) LT is restored.
| 12:45 | 16:28 | Chhatak 132/33kV S/S T-2 LT Scheduled S/D Due to Tan Delta test
| 12:46 | 16:28 | Chhatak 132/33kV S/S T-2 HT Scheduled S/D Due to Tan Delta Test
| 12:53 | 15:37 | Cumilla(N)-Cumilla(S) 132 kV Ckt-1 Scheduled S/D from Cumilla(S) 132/33kV end Due to
Annual Maintenance
| 12:57 |  | Bheramara 410 MW CCPP Shutdown with remarks:- ST
| 12:59 |  | Bheramara 410 MW CCPP was shutdown due to gas shortage.
| 12:59 |  | Bheramara 410 MW CCPP Shutdown with remarks:- GT
| 13:12 | 16:01 | Jamalpur-Mymensingh 132kV Ckt-2 Scheduled S/D from Jamalpur 132/33kV end Due to Annual
maintenance.
| 13:38 | 15:01 | Cox'sbazar-Dohazari 132 kV Ckt-1 Scheduled S/D from Dohazari 132/33kV end Due to Annual
Maintenance
|  | 16:32 | HVDC Bheramera- Rajshahi 230kV Ckt-2 is restored.
| 16:32 |  | Rajshahi 230/132/33kV S/S- 230 Kv BIPTC Ckt-02 CB closed BIPTC side.
|  | 18:04 | Bibiyana-Fenchuganj 230 kV Ckt-2 is restored.
|  | 18:21 | Aminbazar-Kaliakoir 230kV Ckt-1 is restored.
|  | 18:21 | Aminbazar-Kaliakoir 230kV Ckt-1 is restored.
| 18:32 | 19:28 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 HT Forced S/D Due to LA Maintenance
| 18:32 | 19:29 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 LT Forced S/D Due to LA Maintenance
| 19:00 |  | Evening peak generation: 11311 MW
| 01:44 |  | Matarbari 2*600 MW (CPGCBL) Unit-2 was shutdown.
| 05:00 |  | Minimum Generation: 7436 MW.
| 06:30 |  | Ashuganj 420 MW CCPP (East) ST was shutdown due to filter change and offline water wash.
| 06:40 |  | Ashuganj 420 MW CCPP (East) GT was shutdown due to filter change and offline water wash.
| 06:49 |  | Rampura 230/132kV S/S Auto Transformer - 03 LT Scheduled S/D Due to Annual Maintenance
| 06:50 |  | Rampura 230/132kV S/S Auto Transformer - 03 HT Scheduled S/D Due to Annual Maintenance
| 07:00 |  | Meghnaghat 230/132kV S/S Bus1 Scheduled S/D Due to Maintenance work.
| 07:03 |  | Meghnaghat 400/230kV S/S 230kV BUS Section 01 Scheduled S/D Due to Instructed by NLDC
| 07:48 |  | Meghnaghat-Shyampur 230kV Ckt-2 Scheduled S/D from Shyampur 230/132kV end Due to
Deadline checking and from Meghnaghat 400/230kV end Due to Instructed by NLDC
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 08-01-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 310 | 8251200 | FGMO, Gas Shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 886000 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 6321657 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 50.4 | 432720 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 350457 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 317089 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 24 | 462000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 340560 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 853091 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 144 | 1014048 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 152 | 1257120 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 179251 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 400 | 9483530 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 70 | 876000 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1680.4 | 31024723
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 121635 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1098000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 173 | 4107590 | Plant availability less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 101 | 632291 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 38 | 90044 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 38 | 76800 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 37 | 606720 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 17277 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 45 | 80291 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 31 | 82000 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 361920 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1160 | 24229088 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 1 | 436320 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 570 | 14705454.55 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 2290 | 46645430.55
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 150 | 3933000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 280 | 7315400 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 215 | 5247000 | FGMO, Gas Shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1010253 | Machine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 120 | 332872 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 108 | 2500129 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 147 | 1031040 | -
| Import (Tripura) |  | Import | 0 | 160 | 108 | 2382720 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 280820 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 34440 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 30 | 82560 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 394345 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1231 | 24544579
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 11 | 597120 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 943200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 332400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 265840 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 257280 | To be dispatched 18 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 106 | 2403890
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 51239 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 977000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1270320 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 154 | 3671427 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 673632 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 77 | 1393920 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 157 | 4417950 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 344328 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7736500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 860 | 20536316
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 408 | 8856000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 1111968 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 469440 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1118 | 23338180 | U-2 Under Maintenance
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1526 | 33775588
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 308 | 7345455 | Machine Problem
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 132 | 2779000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 580 | 11266909.09 | FGMO, U1 under maintenance
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5281510 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 277 | 5738000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3069 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1517 | 32413943.09
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 315792 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 132 | 3226273 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8385381 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 139680 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 2160 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1358 | 27915273 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 321008 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 614769 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1939 | 40920336
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 92 | 469075 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 29111.52 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 437221 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 142953 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 690480 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 162 | 1768840.52
Eastern Grid Total |  |  |  |  | 17398.245 | 6167.4 | 125154938.55
Western Grid Total |  |  |  |  | 10984.003 | 5144 | 108878707.61
National Grid Total |  |  |  |  | 28382.248 | 11311.4 | 234033646.16
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 08-01-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7520.14 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3387.9 | MW
i) Dhaka area |  |  | 4165.14 |  | MW | i) Khulna area |  |  |  | 1309 | MW
ii) Chattogram area |  |  | 1130 |  | MW | ii) Barishal area |  |  |  | 320.5 | MW
iii) Cumilla area |  |  | 934 |  | MW | iii) Rajshahi area |  |  |  | 1017.4 | MW
iv) Mymensingh area |  |  | 893 |  | MW | iv) Rangpur area |  |  |  | 741 | MW
v) Sylhet area |  |  | 398 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10908.04 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 75 | 12:00 | 133 | Netrakona | 112 | 18:00
2 | AKSML | 131 | 01:00 | 68 | Hathazari | 63 | 13:00 | 134 | New | 75.7 | 12:00
3 | Aftabnagar | 26 | 13:00 | 69 | Hatirjheel | 27 | 15:00 | 135 | Niamatpur | 53 | 13:00
4 | Agargaon | 85 | 13:00 | 70 | Ishurdi | 51 | 18:30 | 136 | Noapara | 38 | 18:30
5 | Agrabad | 32 | 12:00 | 71 | Jaldhaka | 52 | 18:30 | 137 | PHP | 9 | 05:00
6 | Amnura | 23 | 09:00 | 72 | Jamalpur | 88 | 19:00 | 138 | Pabna | 78 | 18:30
7 | Ashuganj | 60 | 12:00 | 73 | Jashore | 101 | 13:00 | 139 | Palashbari | 88 | 18:30
8 | BSRM | 197 | 19:30 | 74 | Jhenaidah | 105 | 18:30 | 140 | Panchagarh | 46 | 18:30
9 | Bagerhat | 64 | 18:00 | 75 | Joydebpur | 109 | 14:00 | 141 | Patiya | 6 | 16:00
10 | Bajitpur | 71 | 18:00 | 76 | Joypurhat | 44 | 18:30 | 142 | Patuakhali | 41 | 21:00
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 14.4 | 16:00 | 143 | Payra | 28 | 18:00
12 | Bakulia | 63 | 13:00 | 78 | KSRM | 33 | 22:00 | 144 | Postogola | 44 | 14:00
13 | Banani | 35.6 | 13:00 | 79 | Kabirpur | 178 | 18:00 | 145 | Purbachal | 15 | 00:00
14 | Bangabhaban | 9 | 10:00 | 80 | Kachua | 58 | 19:30 | 146 | Purbasadipur | 123 | 18:30
15 | Barapukuria | 51 | 18:00 | 81 | Kallyanpur | 69 | 18:00 | 147 | Rahanpur | 23 | 19:30
16 | Barguna | 14 | 18:00 | 82 | Kalurghat | 28 | 15:00 | 148 | Rahim | 42 | 10:00
17 | Barishal | 88 | 13:00 | 83 | Kamrangirchar | 60 | 13:00 | 149 | Rajbari | 63 | 18:00
18 | Barishal-230 | 68 | 20:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 109 | 07:00
19 | Baroaulia | 57 | 13:00 | 85 | Kasba | 23 | 13:00 | 151 | Rajshahi | 74 | 20:00
20 | Baroirhat | 41 | 18:00 | 86 | Kazla | 100 | 13:00 | 152 | Rajshahi-230 | 75 | 13:00
21 | Bashundhara | 148 | 13:00 | 87 | Keranigonj | 65 | 18:00 | 153 | Ramganj | 76 | 21:00
22 | BashundharaCement | 9 | 13:00 | 88 | Khagrachori | 28 | 18:00 | 154 | Rampur | 28 | 14:00
23 | Beanibazar | 48 | 18:00 | 89 | Khulna | 50 | 13:00 | 155 | Rangamati | 13 | 18:00
24 | Benapole | 64 | 08:00 | 90 | Khulshi | 164 | 12:00 | 156 | Rangpur | 114 | 18:00
25 | Bhaluka | 116 | 19:00 | 91 | Kishoreganj | 92 | 19:00 | 157 | Ruppur | 2.4 | 09:00
26 | Bhandaria | 38 | 21:00 | 92 | Kodda | 244 | 18:00 | 158 | SSM | 8 | 00:00
27 | Bhangura | 25 | 18:00 | 93 | Kulaura | 29 | 18:00 | 159 | Saidpur | 97 | 18:30
28 | Bheramara(GK) | 43 | 18:00 | 94 | Kurigram | 52 | 18:00 | 160 | Satkhira | 98 | 08:00
29 | Bhulta | 192 | 13:00 | 95 | Kushtia | 116 | 13:00 | 161 | Satmasjid | 77 | 14:00
30 | Bog-Sherpur | 56 | 18:00 | 96 | Laksam | 23 | 13:00 | 162 | Savar | 192 | 11:00
31 | Bogura | 116 | 18:00 | 97 | Lakshmipur | 16 | 18:00 | 163 | SevenRings | 16.89 | 10:00
32 | Borhanuddin | 65 | 21:00 | 98 | Lalbag | 58 | 13:00 | 164 | ShahCement | 35 | 23:00
33 | Brahmanbaria | 92 | 19:30 | 99 | Lalmonirhat | 45 | 19:00 | 165 | Shahjadpur | 56 | 20:00
34 | Cantonment | 90 | 14:00 | 100 | MI_Cement | 16 | 07:00 | 166 | Shahjibazar | 84 | 21:00
35 | Chandina | 11 | 18:00 | 101 | Madanganj | 38 | 08:00 | 167 | Shahmirpur | 37 | 18:00
36 | Chandpur | 52 | 20:00 | 102 | Madaripur | 72 | 18:30 | 168 | Shariatpur | 58 | 20:00
37 | Chandraghona | 27 | 18:00 | 103 | Madartek | 56 | 13:00 | 169 | Sherpur | 114 | 08:00
38 | Chapai | 50 | 13:00 | 104 | Madunaghat | 37 | 18:00 | 170 | Shikalbaha | 20 | 00:00
39 | Charsaidpur | 40 | 20:00 | 105 | Magura | 51 | 18:30 | 171 | Shitalakhya | 61 | 12:00
40 | Chauddagram | 49 | 13:00 | 106 | Mahasthangarh | 50 | 18:00 | 172 | Sholosohor | 32 | 12:00
41 | Chhatak | 26 | 22:00 | 107 | Maijdee | 27 | 19:30 | 173 | Shyampur | 146 | 12:00
42 | Chowmuhani | 111 | 20:00 | 108 | Manikganj | 107 | 18:00 | 174 | Siddhirganj | 87 | 11:00
43 | Chuadanga | 79 | 18:00 | 109 | Maniknagar | 50 | 13:00 | 175 | Sirajganj | 78 | 19:00
44 | Coxsbazar | 110 | 19:00 | 110 | Matarbari | 40 | 18:00 | 176 | Sonargaon | 120 | 18:30
45 | Cumilla(N) | 102 | 13:00 | 111 | Matuail | 46 | 12:00 | 177 | Sreemongol | 55 | 18:00
46 | Cumilla(S) | 125 | 14:00 | 112 | Metrorail_Motijheel | 8 | 09:00 | 178 | Sreepur | 92 | 12:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 8 | 18:00 | 179 | Srinagar | 30.8 | 20:00
48 | Daudkandi | 108 | 19:30 | 114 | Millgate | 74 | 12:00 | 180 | Sunamganj | 39 | 18:00
49 | DhakaUniversity | 50 | 13:00 | 115 | Mirpur | 115.5 | 14:00 | 181 | Sylhet | 40 | 18:00
50 | Dhamrai | 88 | 18:00 | 116 | Mirsorai | 39 | 09:00 | 182 | Sylhet-132 | 75 | 13:00
51 | Dhanmondi | 78 | 14:00 | 117 | Mirzapur | 40 | 13:00 | 183 | TK | 15 | 00:00
52 | Dohazari | 68 | 18:00 | 118 | Mithapukur | 46 | 18:00 | 184 | Tangail | 132 | 18:00
53 | Faridpur | 118 | 18:30 | 119 | Modern | N/A | N/A | 185 | Taraganj | 16 | 18:30
54 | Fatullah | 95 | 15:00 | 120 | Mogbazar | 47.7 | 14:00 | 186 | Tasnim | 36 | 19:00
55 | Fenchuganj | 25 | 18:00 | 121 | Mongla | 35 | 18:00 | 187 | Thakurgaon | 79 | 18:30
56 | Feni | 76 | 14:00 | 122 | Motijheel | 32 | 13:00 | 188 | Tongi | 130 | 15:00
57 | GPH | 68 | 00:00 | 123 | Muktagacha | 28 | 08:00 | 189 | Ullahpara | 25 | 19:00
58 | Ghatail | 60 | 21:00 | 124 | Munshiganj | 74 | 19:00 | 190 | Ullon | 38 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 0 | 00:00 | 191 | Uttara | 50 | 18:00
60 | Ghorashal-230 | 85 | 19:00 | 126 | Mymensingh | 148 | 18:00 | 192 | UttaraNew | 30 | 13:00
61 | Goalpara | 30 | 13:00 | 127 | Naogaon | 92 | 13:00 | 193 | Zigatola | 72 | 13:00
62 | Gollamari | 84 | 13:00 | 128 | Narail | 43 | 18:00
63 | Gopalganj | 82 | 18:30 | 129 | Narinda | 51 | 12:00
64 | Gulshan | 72 | 13:00 | 130 | Narshingdi | 141 | 19:00
65 | Halishahar | 57 | 18:00 | 131 | Natore | 109 | 18:30
66 | HaripurSBU | 106 | 04:00 | 132 | Nawabganj | 31.2 | 14:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 08-01-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 9087 | 0 |  | 9087
1:00 | 8435 | 0 |  | 8435
2:00 | 8110 | 0 |  | 8110
3:00 | 7794 | 0 |  | 7794
4:00 | 7458 | 0 |  | 7458
5:00 | 7383 | 0 |  | 7383
6:00 | 7891 | 0 |  | 7891
7:00 | 8533.89 | 0 |  | 8533.89
8:00 | 9668.27 | 0 |  | 9668.27
9:00 | 10238.47 | 0 |  | 10238.47
10:00 | 9984.85 | 0 |  | 9984.85
11:00 | 9940.29 | 0 |  | 9940.29
12:00 | 10353.14 | 0 |  | 10353.14
13:00 | 10879.31 | 0 |  | 10879.31
14:00 | 10553.69 | 0 |  | 10553.69
15:00 | 9960.15 | 0 |  | 9960.15
16:00 | 9690.78 | 0 |  | 9690.78
17:00 | 9906.07 | 0 |  | 9906.07
18:00 | 11023 | 0 |  | 11023
19:00 | 11311.4 | 0 |  | 11311.4
19:30 | 11164.4 | 0 |  | 11164.4
20:00 | 11084.3 | 0 |  | 11084.3
21:00 | 10879.69 | 0 |  | 10879.69
22:00 | 10592.3 | 0 |  | 10592.3
23:00 | 9647.52 | 0 |  | 9647.52
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 08-01-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4774 | 4313 | 9087 | DAILY GENERATION CURVE
00:30 | 4665.5 | 4095.5 | 8761
01:00 | 4557 | 3878 | 8435 | 08-01-2026
01:30 | 4534 | 3738.5 | 8272.5
02:00 | 4511 | 3599 | 8110
02:30 | 4406 | 3546 | 7952
03:00 | 4301 | 3493 | 7794
03:30 | 4230.5 | 3395.5 | 7626
04:00 | 4160 | 3298 | 7458
04:30 | 4116.5 | 3304 | 7420.5
05:00 | 4073 | 3310 | 7383
05:30 | 4271.5 | 3365.5 | 7637
06:00 | 4470 | 3421 | 7891
06:30 | 4646.315 | 3566.13 | 8212.445
07:00 | 4822.63 | 3711.26 | 8533.89
07:30 | 4947.355 | 4153.725 | 9101.08
08:00 | 5072.08 | 4596.19 | 9668.27
08:30 | 5155.34 | 4798.03 | 9953.37
09:00 | 5238.6 | 4999.87 | 10238.47
09:30 | 5228.285 | 4883.375 | 10111.66
10:00 | 5217.97 | 4766.88 | 9984.85
10:30 | 5203.47 | 4759.1 | 9962.57
11:00 | 5188.97 | 4751.32 | 9940.29
11:30 | 5291.415 | 4855.3 | 10146.715
12:00 | 5393.86 | 4959.28 | 10353.14
12:30 | 5547.61 | 5068.615 | 10616.225
13:00 | 5701.36 | 5177.95 | 10879.31
13:30 | 5678.195 | 5038.305 | 10716.5
14:00 | 5655.03 | 4898.66 | 10553.69
14:30 | 5493.23 | 4763.69 | 10256.92
15:00 | 5331.43 | 4628.72 | 9960.15
15:30 | 5306.875 | 4518.59 | 9825.465
16:00 | 5282.32 | 4408.46 | 9690.78
16:30 | 5307.955 | 4490.47 | 9798.425
17:00 | 5333.59 | 4572.48 | 9906.07
17:30 | 5646.295 | 4818.24 | 10464.535
18:00 | 5959 | 5064 | 11023
18:30 | 6063.2 | 5104 | 11167.2
19:00 | 6167.4 | 5144 | 11311.4
19:30 | 5995.4 | 5169 | 11164.4
20:00 | 5888.3 | 5196 | 11084.3
20:30 | 5800.7 | 5181.295 | 10981.995 |  | Executive Engineer
21:00 | 5713.1 | 5166.59 | 10879.69 |  | Network Operation Division
21:30 | 5613.9 | 5122.095 | 10735.995
22:00 | 5514.7 | 5077.6 | 10592.3
22:30 | 5157.85 | 4962.06 | 10119.91
23:00 | 4801 | 4846.52 | 9647.52

## En-Curve
QF-LDC-12
Date | 08-01-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2174 | 1630 | 409 | 0 | 92 | 1054 | 46 | 3617 | 0 | 0 | 27 | 0 | 0 | 38 | 0 | DAILY ENERGY CURVE
00:30 | 2155 | 1575.5 | 409 | 0 | 92 | 960.5 | 46 | 3461 | 0 | 0 | 21.5 | 0 | 0 | 40.5 | 0 | 08-01-2026
01:00 | 2136 | 1521 | 409 | 0 | 92 | 867 | 46 | 3305 | 0 | 0 | 16 | 0 | 0 | 43 | 0
01:30 | 2196 | 1463.5 | 409 | 0 | 86 | 857 | 46 | 3160.5 | 0 | 0 | 8 | 0 | 0 | 46.5 | 0 | Energy Generated | 234.0336 |  | MKWHr
02:00 | 2256 | 1406 | 409 | 0 | 80 | 847 | 46 | 3016 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2321 | 1361.5 | 336 | 0 | 80 | 845 | 46 | 2913 | 0 | 0 | 0 | 0 | 0 | 49.5 | 0 | Total Energy Requirement | 234.0336 |  | MKWHr
03:00 | 2386 | 1317 | 263 | 0 | 80 | 843 | 46 | 2810 | 0 | 0 | 0 | 0 | 0 | 49 | 0
03:30 | 2335 | 1299.5 | 219.5 | 0 | 80 | 839 | 46 | 2753.5 | 0 | 0 | 0 | 0 | 0 | 53.5 | 0
04:00 | 2284 | 1282 | 176 | 0 | 80 | 835 | 46 | 2697 | 0 | 0 | 0 | 0 | 0 | 58 | 0
04:30 | 2358 | 1163 | 176 | 0 | 81 | 836 | 46 | 2706 | 0 | 0 | 0 | 0 | 0 | 54.5 | 0
05:00 | 2432 | 1044 | 176 | 0 | 82 | 837 | 46 | 2715 | 0 | 0 | 0 | 0 | 0 | 51 | 0
05:30 | 2471 | 1109 | 176 | 0 | 84 | 858 | 46 | 2843.5 | 0 | 0 | 0 | 0 | 0 | 49.5 | 0
06:00 | 2510 | 1174 | 176 | 0 | 86 | 879 | 46 | 2972 | 0 | 0 | 0 | 0 | 0 | 48 | 0
06:30 | 2584.5 | 1213.5 | 176 | 0 | 83 | 919.5 | 46 | 3136.5 | 3.445 | 0 | 3.5 | 0 | 0 | 46.5 | 0
07:00 | 2659 | 1253 | 176 | 0 | 80 | 960 | 46 | 3301 | 6.89 | 0 | 7 | 0 | 0 | 45 | 0
07:30 | 2691 | 1274 | 292.5 | 0 | 88 | 1054.785 | 46 | 3525 | 52.295 | 0 | 41 | 0 | 0 | 36.5 | 0
08:00 | 2723 | 1295 | 409 | 0 | 96 | 1149.57 | 46 | 3749 | 97.7 | 0 | 75 | 0 | 0 | 28 | 0
08:30 | 2672.5 | 1266.5 | 408.5 | 0 | 96 | 1267.535 | 46 | 3917 | 170.335 | 0 | 87.5 | 0 | 0 | 21.5 | 0
09:00 | 2622 | 1238 | 408 | 0 | 96 | 1385.5 | 46 | 4085 | 242.97 | 0 | 100 | 0 | 0 | 15 | 0
09:30 | 2581.5 | 1222 | 408.5 | 0 | 96 | 1332.535 | 46 | 3961 | 311.125 | 26 | 115.5 | 0 | 0 | 11.5 | 0
10:00 | 2541 | 1206 | 409 | 0 | 96 | 1279.57 | 46 | 3837 | 379.28 | 52 | 131 | 0 | 0 | 8 | 0
10:30 | 2546 | 1209.5 | 409 | 0 | 98 | 1254.35 | 46 | 3737.5 | 448.22 | 71 | 137 | 0 | 0 | 6 | 0
11:00 | 2551 | 1213 | 409 | 0 | 100 | 1229.13 | 46 | 3638 | 517.16 | 90 | 143 | 0 | 0 | 4 | 0
11:30 | 2525 | 1251.5 | 409 | 0 | 108 | 1253.095 | 46 | 3676.5 | 576.92 | 99 | 198.2 | 0 | 0 | 3.5 | 0
12:00 | 2499 | 1290 | 409 | 0 | 116 | 1277.06 | 46 | 3715 | 636.68 | 108 | 253.4 | 0 | 0 | 3 | 0
12:30 | 2508 | 1310.5 | 409 | 0 | 120 | 1320.615 | 46 | 3779 | 626.56 | 108 | 387.05 | 0 | 0 | 1.5 | 0
13:00 | 2517 | 1331 | 409 | 0 | 124 | 1364.17 | 46 | 3843 | 616.44 | 108 | 520.7 | 0 | 0 | 0 | 0
13:30 | 2505 | 1307 | 409 | 0 | 125 | 1300.585 | 46 | 3800.5 | 573.165 | 104 | 546.25 | 0 | 0 | 0 | 0
14:00 | 2493 | 1283 | 409 | 0 | 126 | 1237 | 46 | 3758 | 529.89 | 100 | 571.8 | 0 | 0 | 0 | 0
14:30 | 2485.5 | 1288.5 | 409 | 0 | 119 | 1232 | 46 | 3650.5 | 452.42 | 95 | 478 | 0 | 0 | 1 | 0
15:00 | 2478 | 1294 | 409 | 0 | 112 | 1227 | 46 | 3543 | 374.95 | 90 | 384.2 | 0 | 0 | 2 | 0
15:30 | 2480.5 | 1294 | 409 | 0 | 111 | 1184.5 | 46 | 3568 | 273.165 | 90 | 368.3 | 0 | 0 | 1 | 0
16:00 | 2483 | 1294 | 409 | 0 | 110 | 1142 | 46 | 3593 | 171.38 | 90 | 352.4 | 0 | 0 | 0 | 0
16:30 | 2514.5 | 1277.5 | 408.5 | 0 | 110 | 1189.5 | 46 | 3617.5 | 98.625 | 75 | 461.3 | 0 | 0 | 0 | 0
17:00 | 2546 | 1261 | 408 | 0 | 110 | 1237 | 46 | 3642 | 25.87 | 60 | 570.2 | 0 | 0 | 0 | 0
17:30 | 2560 | 1289 | 408 | 0 | 112 | 1322.5 | 46 | 3776.5 | 12.935 | 77 | 859.1 | 0 | 0 | 1.5 | 0
18:00 | 2574 | 1317 | 408 | 0 | 114 | 1408 | 46 | 3911 | 0 | 94 | 1148 | 0 | 0 | 3 | 0
18:30 | 2533.5 | 1324.5 | 408 | 0 | 111 | 1383 | 46 | 3962 | 0 | 101 | 1296.2 | 0 | 0 | 2 | 0
19:00 | 2493 | 1332 | 408 | 0 | 108 | 1358 | 46 | 4013 | 0 | 108 | 1444.4 | 0 | 0 | 1 | 0
19:30 | 2532 | 1344 | 409 | 0 | 106 | 1376 | 46 | 4036 | 0 | 108 | 1206.4 | 0 | 0 | 1 | 0
20:00 | 2515 | 1322 | 408 | 0 | 102 | 1376 | 46 | 4049 | 0 | 90 | 1175.3 | 0 | 0 | 1 | 0
20:30 | 2515.5 | 1335.5 | 408 | 0 | 105 | 1372.795 | 46 | 4056.5 | 0 | 62.5 | 1079.2 | 0 | 0 | 1 | 0
21:00 | 2516 | 1349 | 408 | 0 | 108 | 1369.59 | 46 | 4064 | 0 | 35 | 983.1 | 0 | 0 | 1 | 0
21:30 | 2507 | 1359.5 | 408.5 | 0 | 109 | 1343.595 | 46 | 4042 | 0 | 26 | 893.4 | 0 | 0 | 1 | 0
22:00 | 2498 | 1370 | 409 | 0 | 110 | 1317.6 | 46 | 4020 | 0 | 17 | 803.7 | 0 | 0 | 1 | 0
22:30 | 2465.5 | 1308.5 | 395 | 0 | 104 | 1319.56 | 46 | 4038 | 0 | 8.5 | 433.85 | 0 | 0 | 1 | 0
23:00 | 2433 | 1247 | 381 | 0 | 98 | 1321.52 | 46 | 4056 | 0 | 0 | 64 | 0 | 0 | 1 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 08-01-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 421 | 03:00 | 389 | 12:00 | Meghnaghat | 426 | 03:00 | 395 | 12:00
Ashuganj | 414 | 6:00 | 391 | 13:00 | Payra | 422 | 03:00 | 412 | 12:00
Bhulta | 405 | 05:00 | 381 | 12:00 | Rahanpur | 420 | 03:00 | 401 | 09:00
Bibiana | 417 | 02:00 | 398 | 12:00 | Rampal | 416 | 02:00 | 396 | 12:00
BIPTC | 410 | 03:00 | 391 | 13:00
Bogura | 416 | 03:00 | 392 | 09:00
Gopalganj | 421 | 03:00 | 397 | 12:00
Kaliakoir | 415 | 03:00 | 381 | 12:00
Korerhat | 425 | 03:00 | 403 | 12:00
Madunaghat | 415 | 03:00 | 400 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 245 | 03:00 | 223 | 12:00 | Kachua | 241 | 03:00 | 231 | 09:00
AKSML | 239 | 03:00 | 229 | 12:00 | Kaliakoir | 243 | 03:00 | 223 | 10:00
Aminbazar | 243 | 02:00 | 223 | 12:00 | Keranigonj | 242 | 03:00 | 222 | 12:00
Ashuganj | 239 | 13:00 | 228 | 12:00 | Khulna(S) | 245 | 03:00 | 228 | 13:00
Ashuganj-400 | 239 | 6:00 | 229 | 13:00 | Korerhat | 243 | 03:00 | 229 | 12:00
Baghabari | 242 | 03:00 | 230 | 09:00 | Madunaghat | 238 | 19:00 | 230 | 12:00
Barapukuria | 232 | 05:00 | 217 | 13:00 | Madunaghat-400 | 239 | 02:00 | 231 | 13:00
Barapukuria-230 | 232 | 5:00 | 218 | 12:00 | Maniknagar | 240 | 03:00 | 226 | 12:00
Barishal | 239 | 03:00 | 228 | 13:00 | Meghnaghat | 248 | 03:00 | 229 | 12:00
Bheramara | 241 | 04:00 | 223 | 08:00 | Meghnaghat-400 | 242 | 03:00 | 224 | 12:00
Bhulta | 243 | 03:00 | 227 | 12:00 | Mirsorai | 241 | 02:00 | 227 | 00:00
Bibiana | 246 | 06:00 | 234 | 12:00 | Rajshahi | 241 | 04:00 | 223 | 08:00
BIPTC | 241 | 04:00 | 234 | 16:00 | Rampal | 241 | 02:00 | 227 | 13:00
Bogura | 244 | 03:00 | 230 | 08:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 243 | 04:00 | 229 | 09:00 | Rampura | 242 | 05:00 | 226 | 12:00
Borhanuddin | 241 | 03:00 | 234 | 11:00 | Shikalbaha | 237 | 01:00 | 229 | 12:00
BSRM | 241 | 03:00 | 229 | 09:00 | Shyampur | 242 | 03:00 | 222 | 12:00
Cumilla(N) | 239 | 06:00 | 227 | 12:00 | Siddhirganj | 243 | 04:00 | 227 | 12:00
Faridpur | 238 | 04:00 | 226 | 12:00 | Sirajgonj | 247 | 05:00 | 237 | 08:00
Fenchuganj | 247 | 03:00 | 238 | 12:00 | Sreepur | 236 | 04:00 | 225 | 09:00
Feni | 243 | 03:00 | 229 | 12:00 | Tongi | 240 | 04:00 | 218 | 12:00
Ghorashal | 240 | 19:30 | 230 | 12:00
Ghorashal-230 | 236 | 04:00 | 214 | 18:30
Gopalganj | 237 | 03:00 | 224 | 12:00
GPH | 240 | 02:00 | 230 | 12:00
Haripur | 242 | 03:00 | 226 | 12:00
Hasnabad | 240 | 01:00 | 222 | 12:00
Hathazari | 237 | 18:30 | 226 | 12:00
Ishurdi | 242 | 04:00 | 225 | 08:00
Jhenaidah | 243 | 04:00 | 223 | 09:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 03:00 | 125 | 12:00 | Laksam | 139 | 02:00 | 132 | 12:00 | UttaraNew | 137 | 01:00 | 126 | 12:00
Agargaon | 139 | 03:00 | 126 | 12:00 | Lakshmipur | 136 | 03:00 | 129 | 09:00 | Zigatola | 137 | 04:00 | 123 | 13:00
Agrabad | 139 | 18:30 | 133 | 12:00 | Lalbag | 134 | 02:00 | 125 | 12:00
AKS | 135 | 03:00 | 131 | 12:00 | Lalmonirhat | 132 | 03:00 | 120 | 08:00
Aminbazar | 138 | 01:00 | 128 | 11:00 | Madanganj | 136 | 03:00 | 131 | 13:00
Amnura | 139 | 01:00 | 129 | 08:00 | Madaripur | 142 | 03:00 | 134 | 12:00
Ashuganj | 141 | 04:00 | 133 | 17:00 | Madartek | 135 | 04:00 | 124 | 12:00
Bagerhat | 134 | 04:00 | 124 | 10:00 | Madunaghat | 139 | 02:00 | 134 | 12:00
Bajitpur | 134 | 05:00 | 128 | 09:00 | Magura | 140 | 06:00 | 125 | 13:00
Bakerganj | 138 | 04:00 | 134 | 12:00 | Mahasthangarh | 137 | 02:00 | 127 | 08:00
Bakulia | 138 | 00:00 | 133 | 12:00 | Maijdee | 136 | 03:00 | 128 | 12:00
Banani | 135 | 02:00 | 124 | 12:00 | Manikganj | 133 | 01:00 | 120 | 12:00
Bangabhaban | 140 | 02:00 | 129 | 12:00 | Maniknagar | 140 | 02:00 | 129 | 13:00
Barapukuria | 139 | 05:00 | 130 | 13:00 | Matarbari | 132 | 02:00 | 124 | 18:00
Barguna | 138 | 05:00 | 134 | 13:00 | Matuail | 138 | 01:00 | 130 | 12:00
Barishal | 140 | 03:00 | 132 | 13:00 | Metrorail_Motijheel | 140 | 02:00 | 129 | 13:00
Barishal-230 | 141 | 03:00 | 133 | 12:00 | Metrorail_Uttara | 137 | 01:00 | 126 | 11:00
Baroaulia | 139 | 02:00 | 133 | 12:00 | Millgate | 137 | 02:00 | 121 | 12:00
Baroirhat | 137 | 01:00 | 130 | 12:00 | Mirpur | 137 | 18:30 | 126 | 11:00
Bashundhara | 135 | 02:00 | 125 | 12:00 | Mirzapur | 136 | 03:00 | 125 | 09:00
BashundharaCement | 136 | 04:00 | 131 | 13:00 | Mithapukur | 136 | 03:00 | 125 | 08:00
Beanibazar | 136 | 06:00 | 131 | 12:00 | MI_Cement | 137 | 03:00 | 122 | 12:00
Benapole | 138 | 03:00 | 119 | 09:00 | Modern | N/A | N/A | N/A | N/A
Bhaluka | 136 | 05:00 | 127 | 09:00 | Mogbazar | 137 | 05:00 | 124 | 11:00
Bhandaria | 140 | 07:00 | 138 | 01:00 | Mongla | 133 | 00:00 | 123 | 12:00
Bhangura | 140 | 03:00 | 132 | 13:00 | Motijheel | 140 | 02:00 | 129 | 12:00
Bheramara | 141 | 04:00 | 130 | 13:00 | Muktagacha | 133 | 11:00 | 125 | 08:00
Bheramara(GK) | 141 | 05:00 | 129 | 18:30 | Munshiganj | 137 | 03:00 | 128 | 12:00
Bhulta | 129 | 01:00 | 122 | 12:00 | Muradnagar | 138 | 01:00 | 132 | 09:00
Bog-Sherpur | 139 | 03:00 | 130 | 08:00 | Mymensingh | 134 | 11:00 | 123 | 08:00
Bogura | 139 | 03:00 | 130 | 08:00 | Naogaon | 135 | 04:00 | 127 | 13:00
Bogura-230 | 139 | 03:00 | 130 | 08:00 | Narail | 141 | 04:00 | 123 | 13:00
Brahmanbaria | 135 | 01:00 | 129 | 12:00 | Narinda | 140 | 2:00 | 129 | 13:00
Cantonment | 138 | 02:00 | 126 | 12:00 | Narshingdi | 136 | 05:00 | 126 | 12:00
Chandina | 141 | 02:00 | 133 | 12:00 | Natore | 136 | 00:00 | 130 | 08:00
Chandpur | 140 | 18:30 | 132 | 12:00 | Nawabganj | 137 | 06:00 | 124 | 12:00
Chandraghona | 140 | 02:00 | 134 | 12:00 | Netrakona | 129 | 06:00 | 120 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 139 | 04:00 | 133 | 08:00 | New | 137 | 03:00 | 123 | 12:00
Charsaidpur | 138 | 05:00 | 130 | 11:00 | Niamatpur | 139 | 04:00 | 132 | 09:00
Chauddagram | 138 | 01:00 | 131 | 12:00 | Noapara | 137 | 04:00 | 121 | 13:00
Chhatak | 136 | 02:00 | 130 | 13:00 | Pabna | 140 | 03:00 | 130 | 13:00
Chowmuhani | 134 | 22:00 | 128 | 09:00 | Palashbari | 135 | 03:00 | 123 | 08:00
Chuadanga | 141 | 04:00 | 124 | 13:00 | Panchagarh | 139 | 22:00 | 124 | 08:00
Coxsbazar | 132 | 15:00 | 125 | 13:00 | Patiya | 137 | 00:00 | 132 | 12:00
Cumilla(N) | 140 | 02:00 | 132 | 12:00 | Patuakhali | 138 | 03:00 | 133 | 13:00
Cumilla(S) | 141 | 03:00 | 125 | 12:00 | Payra | 139 | 02:00 | 135 | 13:00
Daganbhuiyan | 137 | 04:00 | 129 | 12:00 | PHP | 136 | 02:00 | 129 | 12:00
Daudkandi | 137 | 03:00 | 129 | 12:00 | Postogola | 138 | 04:00 | 124 | 12:00
DhakaUniversity | 135 | 02:00 | 125 | 12:00 | Purbachal | 135 | 01:00 | 124 | 12:00
Dhamrai | 139 | 04:00 | 126 | 09:00 | Purbasadipur | 134 | 22:00 | 117 | 08:00
Dhanmondi | 140 | 04:00 | 131 | 12:00 | Rahanpur | 140 | 06:00 | 134 | 09:00
Dohazari | 136 | 03:00 | 131 | 12:00 | Rahanpur-400 | 141 | 02:00 | 135 | 08:00
Faridpur | 138 | 05:00 | 130 | 12:00 | Rahim | 138 | 04:00 | 130 | 12:00
Fatullah | 139 | 02:00 | 122 | 12:00 | Rajbari | 138 | 02:00 | 129 | 13:00
Fenchuganj | 140 | 03:00 | 136 | 08:00 | Rajendrapur | 137 | 03:00 | 128 | 09:00
Feni | 136 | 05:00 | 129 | 12:00 | Rajshahi | 139 | 06:00 | 129 | 13:00
Feni-230 | 138 | 10:00 | 128 | 12:00 | Rajshahi-230 | 139 | 04:00 | 128 | 13:00
Ghatail | 130 | 05:00 | 123 | 08:00 | Ramganj | 137 | 18:30 | 130 | 12:00
Ghorashal | 133 | 03:00 | 127 | 12:00 | Rampur | 139 | 03:00 | 128 | 12:00
Goalpara | 138 | 03:00 | 128 | 12:00 | Rampura | 135 | 04:00 | 124 | 12:00
Gollamari | 137 | 03:00 | 128 | 12:00 | Rangamati | 138 | 00:00 | 133 | 12:00
Gopalganj | 140 | 02:00 | 131 | 12:00 | Rangpur | 134 | 01:00 | 123 | 08:00
Gopalganj-400 | 143 | 02:00 | 135 | 12:00 | Ruppur | 142 | 05:00 | 131 | 13:00
Gulshan | 134 | 04:00 | 124 | 12:00 | Saidpur | 136 | 05:00 | 127 | 08:00
Halishahar | 139 | 02:00 | 133 | 12:00 | Satkhira | 136 | 03:00 | 125 | 08:00
Haripur | 139 | 03:00 | 130 | 12:00 | Satmasjid | 138 | 03:00 | 126 | 12:00
HaripurSBU | 139 | 03:00 | 130 | 12:00 | Savar | 139 | 21:00 | 125 | 12:00
Hasnabad | 137 | 05:00 | 124 | 12:00 | SevenRings | 133 | 02:00 | 126 | 09:00
Hathazari | 139 | 19:00 | 133 | 12:00 | ShahCement | 138 | 05:00 | 130 | 11:00
Hatirjheel | 135 | 02:00 | 124 | 12:00 | Shahjadpur | 140 | 00:00 | 136 | 07:00
Ishurdi | 142 | 03:00 | 131 | 18:30 | Shahjibazar | 137 | 02:00 | 130 | 12:00
Jaldhaka | 133 | 05:00 | 118 | 08:00 | Shahmirpur | 139 | 01:00 | 135 | 09:00
Jamalpur | 134 | 10:00 | 124 | 00:00 | Shariatpur | 142 | 03:00 | 133 | 13:00
Jashore | 139 | 03:00 | 121 | 09:00 | Sherpur | 129 | 11:00 | 120 | 08:00
Jhenaidah | 142 | 04:00 | 109 | 18:30 | Shikalbaha | 128 | 05:00 | 122 | 16:00
Jhenaidah-230 | 142 | 04:00 | 128 | 09:00 | Shikalbaha-230 | 140 | 01:00 | 134 | 14:00
Joydebpur | 130 | 01:00 | 123 | 09:00 | Shitalakhya | 137 | 03:00 | 122 | 12:00
Joypurhat | 136 | 03:00 | 127 | 08:00 | Sholosohor | 139 | 02:00 | 133 | 12:00
Juldah | 139 | 19:00 | 133 | 12:00 | Shyampur | 139 | 05:00 | 128 | 12:00
Kabirpur | 138 | 04:00 | 120 | 12:00 | Shyampur-230 | 140 | 03:00 | 128 | 12:00
Kachua | 139 | 03:00 | 133 | 09:00 | Siddhirganj | 139 | 04:00 | 130 | 12:00
Kaliakoir | 140 | 05:00 | 128 | 09:00 | Sirajganj | 140 | 04:00 | 130 | 08:00
Kallyanpur | 138 | 01:00 | 126 | 12:00 | Sonargaon | 137 | 06:00 | 129 | 12:00
Kalurghat | 140 | 01:00 | 134 | 12:00 | Sreemongol | 137 | 04:00 | 131 | 12:00
Kamrangirchar | 137 | 03:00 | 123 | 12:00 | Sreepur | 138 | 04:00 | 130 | 09:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 137 | 02:00 | 124 | 12:00
Kasba | 140 | 03:00 | 131 | 12:00 | SSM | 141 | 00:00 | 138 | 14:00
Kazla | 140 | 02:00 | 129 | 13:00 | Sunamganj | 133 | 03:00 | 130 | 12:00
Keranigonj | 137 | 03:00 | 124 | 12:00 | Sylhet | 136 | 01:00 | 132 | 12:00
Khagrachori | 139 | 03:00 | 132 | 12:00 | Sylhet-132 | 136 | 01:00 | 132 | 12:00
Khulna | 137 | 04:00 | 126 | 13:00 | Tangail | 130 | 04:00 | 123 | 08:00
Khulna(S) | 138 | 03:00 | 127 | 13:00 | Taraganj | 135 | 18:00 | 120 | 08:00
Khulshi | 138 | 04:00 | 131 | 12:00 | Tasnim | 141 | 02:00 | 129 | 12:00
Kishoreganj | 132 | 01:00 | 126 | 09:00 | Thakurgaon | 138 | 22:00 | 121 | 08:00
Kodda | 136 | 18:30 | 120 | 09:00 | TK | 140 | 06:00 | 135 | 11:00
KSRM | 140 | 02:00 | 132 | 12:00 | Tongi | 140 | 04:00 | 126 | 12:00
Kulaura | 139 | 01:00 | 134 | 13:00 | Ullahpara | 140 | 01:00 | 131 | 18:30
Kurigram | 131 | 19:30 | 119 | 08:00 | Ullon | 135 | 02:00 | 124 | 12:00
Kushtia | 136 | 04:00 | 119 | 18:30 | Uttara | 139 | 05:00 | 127 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division