## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 10-01-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-01-2026 | during | 10-01-2026 | during | 10-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 336 | 337 | 412 | 412 | 392 | 392 | FGMO, Gas Shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 240 | 240 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 280 | 335 | 335 | 0 | 0 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 16.8 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 20 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 15 | 13 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 15 | 15.1 | 15.1 | 15.1 | 15.1 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 95 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 45 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 52 | 0 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 26 | 0 | 26 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 360 | 405 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 0 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1317.8 | 1050 | 5333.25 | 5307.25 | 2459.13 | 2471.13
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 | 46 | 46 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 167 | 166 | 150 | 150 | 150 | 150 | Plant availability less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 16 | 0 | 40 | 64 | 40 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 51 | 51 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 35 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 37 | 42 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0 | 0 | 4.07 | 0 | 4.07 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 0 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 892 | 1150 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 145 | 145 | 355 | 355 | 355 | 355 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1380 | 1549 | 3125.93 | 3141.86 | 2650.57 | 2666.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 201 | 198 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 340 | 335 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 33 | 33 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 30 | 55 | 55 | 55 | 55
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 35 | 145 | 195 | 195 | 195 | 195
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 28 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 24 | 24 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 108 | 108 | 163 | 163 | 115 | 115 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 22 | 0 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 120 | 92 | 84 | 80 | 126 | 126 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 13 | 24.5 | 24.5 | 24.5 | 24.5 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 64 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1013 | 1005 | 2016.75 | 1957.75 | 1866.75 | 1811.75
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-01-2026 | during | 10-01-2026 | during | 10-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 26 | 50 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 35 | 60 | 60 | 60 | 60 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 19 | 20 | 20 | 20 | 20 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 42.17 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 18 | 18 | To be dispatched 18 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 147.17 | 104 | 358.1 | 314 | 354.1 | 310
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 42 | 41 | 41 | 41 | 41 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 60 | 60 | 60 | 60 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 152 | 154 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 75 | 81 | 81 | 81 | 81 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 157 | 154 | 158 | 158 | 158 | 158 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 860 | 847 | 899 | 899 | 849 | 849
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 0 | 846 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 369 | 369 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 77 | 0 | 74 | 0 | 74 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1131 | 1090 | 0 | 0 | 1000 | 1148 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1208 | 1936 | 2016 | 1942 | 2550.1 | 2624.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 306 | 300 | 0 | 0 | 622 | 622 | Machine Problem
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 137 | 134 | 136 | 136 | 70 | 70 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 560 | 560 | 622 | 622 | 575 | 575 | FGMO, U1 under maintenance
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 278 | 278 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.52 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1501.52 | 1492 | 1546 | 1545 | 1902 | 1901
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 55.08 | 0 | 51.32 | 0 | 51.32 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 138 | 143 | 214 | 214 | 192.6 | 192.6 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.13 | 0 | 5.15 | 0 | 5.15 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1331 | 1323.93 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 56.76 | 0 | 55 | 0 | 55 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 90 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 2089.97 | 1880.93 | 3130.34 | 2918.87 | 2597.56 | 2386.09
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.8 | 0 | 3.2 | 0 | 3.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 145 | 0 | 132.26 | 0 | 132.26 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 181.8 | 34 | 427.46 | 262 | 393.46 | 228
System Total |  |  |  |  | 28823.2 | 28382.248 | 9699.26 | 9897.93 | 18852.83 | 18287.73 | 15622.67 | 15247.57
Forecast Scenario (10-01-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8360 |  | 0 |  | 8360
|  |  |  | 1:00 | 7800 |  | 0 |  | 7800
|  |  |  | 2:00 | 7430 |  | 0 |  | 7430
|  |  |  | 3:00 | 7090 |  | 0 |  | 7090
|  |  |  | 4:00 | 6870 |  | 0 |  | 6870
|  |  |  | 5:00 | 6830 |  | 0 |  | 6830
|  |  |  | 6:00 | 7340 |  | 0 |  | 7340
|  |  |  | 7:00 | 7670 |  | 0 |  | 7670
|  |  |  | 8:00 | 8450 |  | 0 |  | 8450
|  |  |  | 9:00 | 9160 |  | 0 |  | 9160
|  |  |  | 10:00 | 9080 |  | 0 |  | 9080
|  |  |  | 11:00 | 9010 |  | 0 |  | 9010
|  |  |  | 12:00 | 9670 |  | 0 |  | 9670
|  |  |  | 13:00 | 10160 |  | 0 |  | 10160
|  |  |  | 14:00 | 9800 |  | 0 |  | 9800
|  |  |  | 15:00 | 9130 |  | 0 |  | 9130
|  |  |  | 16:00 | 9010 |  | 0 |  | 9010
|  |  |  | 17:00 | 9460 |  | 0 |  | 9460
|  |  |  | 18:00 | 10770 |  | 0 |  | 10770
|  |  |  | 18:30 | 10820 |  | 0 |  | 10820
|  |  |  | 19:00 | 10880 |  | 0 |  | 10880
|  |  |  | 19:30 | 10950 |  | 0 |  | 10950
|  |  |  | 20:00 | 10820 |  | 0 |  | 10820
|  |  |  | 21:00 | 10650 |  | 0 |  | 10650
|  |  |  | 22:00 | 10070 |  | 0 |  | 10070
|  |  |  | 23:00 | 9430 |  | 0 |  | 9430
Probable Maximum Temperature: |  |  | 21.20°C
Probable Maximum Demand at Day Peak: |  |  | 9670.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 10950.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10950.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 214.94 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:04 hrs on 10-01-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 09-01-2026 | [28 empty] | Date: | 09-01-2026 | [28 empty] | Date: | 09-01-2026 | [28 empty] | Date: | 09-01-2026 | [28 empty] | Date: | 09-01-2026 | [17 empty] | Date: | 09-01-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [17 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 13.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 560 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1135 | 0 | 0 | 0 | 215 | 280 | 0 | 51 | 0 | 140 | 0 | 0 | 110 | 0 | 0 | 13 | 0 | 90 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 60 | 154 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 157 | 0 | 19 | 24 | 12 | 0 | 0 | 0 | 4712.5 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 0 | 0 | 0 | 1174.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254 | 132 | 220 | 0 | 303 | 550 | 0 | 4569.49 | 9281.99 | 97.09
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 13.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 520 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1070 | 0 | 0 | 0 | 215 | 280 | 0 | 51 | 0 | 140 | 0 | 0 | 111 | 0 | 0 | 13 | 0 | 86 | 0 | 0 | 0 | 305 | 0 | 0 | 41 | 60 | 150 | 0 | 17 | 0 | 78 | 20 | 0 | 0 | 157 | 0 | 19 | 0 | 22 | 0 | 0 | 0 | 4557.5 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 912 | 0 | 0 | 0 | 1025.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 132 | 220 | 0 | 287 | 450 | 0 | 4071.35 | 8628.85 | 97.09
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 360 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 990 | 0 | 0 | 0 | 215 | 300 | 0 | 51 | 0 | 140 | 0 | 0 | 50 | 0 | 0 | 13 | 0 | 84 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 60 | 146 | 0 | 17 | 0 | 5 | 20 | 0 | 0 | 156 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 4256 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 815 | 0 | 0 | 0 | 1000.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 132 | 220 | 0 | 250 | 400 | 0 | 3886.46 | 8142.46 | 97.09
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 360 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 905 | 0 | 0 | 0 | 215 | 320 | 0 | 51 | 0 | 140 | 0 | 0 | 50 | 0 | 0 | 8 | 0 | 84 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 60 | 141 | 0 | 17 | 0 | 5 | 20 | 0 | 0 | 156 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 4165 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 0 | 0 | 0 | 936.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 138 | 220 | 0 | 250 | 350 | 0 | 3597.63 | 7762.63 | 97.08
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 360 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 865 | 0 | 0 | 0 | 215 | 320 | 0 | 51 | 0 | 140 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 82 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 60 | 146 | 0 | 17 | 0 | 5 | 20 | 0 | 0 | 156 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 4144 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802 | 0 | 0 | 0 | 829.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 138 | 220 | 0 | 256 | 280 | 0 | 3411.26 | 7555.26 | 97.08
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 13.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 360 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 765 | 0 | 0 | 0 | 215 | 320 | 0 | 51 | 0 | 140 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 74 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 60 | 145 | 0 | 17 | 0 | 5 | 20 | 0 | 0 | 156 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 4024.5 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 792 | 0 | 0 | 0 | 837.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 138 | 220 | 0 | 258 | 280 | 0 | 3412.43 | 7436.93 | 97.08
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 36 | 360 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 785 | 0 | 0 | 0 | 215 | 320 | 0 | 51 | 0 | 217 | 0 | 0 | 112 | 0 | 0 | 11 | 0 | 78 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 60 | 151 | 0 | 17 | 0 | 60 | 30 | 0 | 0 | 156 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 4304 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 815 | 0 | 0 | 0 | 859.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 138 | 220 | 0 | 260 | 295 | 0 | 3504.94 | 7808.94 | 97.07
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 335 | 0 | 0 | 1 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0.11 | 46 | 0 | 37 | 340 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 892 | 1 | 0 | 0 | 0 | 360 | 0 | 51 | 0 | 210 | 0 | 0 | 114 | 0 | 0 | 11 | 0 | 84 | 0 | 2 | 0 | 310 | 0 | 0 | 41 | 60 | 159 | 0 | 17 | 0 | 72 | 30 | 0 | 0 | 156 | 0 | 0 | 0 | 34 | 0 | 0.03 | 0 | 4233.14 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.98 | 871 | 0 | 0 | 0 | 879.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53 | 0 | 0 | 0 | 0.49 | 130 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 100 | 180 | 0 | 307 | 362 | 0 | 3644.26 | 7877.4 | 97.07
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 335 | 0 | 0 | 5 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 10 | 5 | 0 | 46 | 0 | 37 | 340 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 892 | 0 | 0 | 0 | 0 | 330 | 0 | 51 | 0 | 198 | 14 | 0 | 114 | 1 | 0 | 11 | 0 | 74 | 0 | 7 | 0 | 315 | 0 | 0 | 41 | 60 | 163 | 3 | 17 | 0 | 41 | 30 | 0 | 0 | 156 | 0 | 7 | 56 | 28 | 0 | 4 | 0 | 4318 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.71 | 957 | 0 | 0 | 0 | 1127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.05 | 16 | 0 | 0 | 9.28 | 130 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.86 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.6 | 28 | 0.11 | 0 | 307 | 140 | 220 | 0 | 308 | 470 | 0 | 4258.61 | 8576.61 | 97.07
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 12.5 | 0 | 15 | 0 | 15 | 0 | 13 | 31 | 0 | 0 | 0 | 350 | 0 | 17 | 300 | 0 | 0 | 15 | 35 | 13 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 25 | 0 | 46 | 0 | 37 | 340 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 894 | 10 | 12 | 8 | 0 | 305 | 0 | 51 | 0 | 197 | 22 | 0 | 113 | 41 | 0 | 11 | 0 | 92 | 0 | 14 | 0 | 310 | 0 | 0 | 41 | 60 | 152 | 7 | 17 | 0 | 72 | 30 | 0 | 0 | 157 | 0 | 19 | 56 | 28 | 1 | 0 | 0 | 4516.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 1105 | 0 | 0 | 0 | 1179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.66 | 51 | 0 | 0 | 26.55 | 130 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 2.44 | 0 | 0 | 35 | 0 | 25 | 0 | 0 | 0 | 1.4 | 32 | 0.21 | 0 | 307 | 140 | 220 | 0 | 307 | 575 | 0 | 4573.26 | 9089.76 | 97.06
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 16.5 | 0 | 17 | 0 | 15 | 0 | 17 | 17 | 0 | 0 | 0 | 355 | 0 | 17 | 300 | 0 | 0 | 23 | 70 | 13 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 25 | 0 | 46 | 0 | 37 | 200 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 892 | 15 | 12 | 8 | 0 | 300 | 0 | 51 | 0 | 194 | 33 | 0 | 111 | 17 | 0 | 11 | 0 | 94 | 0 | 51 | 0 | 320 | 0 | 0 | 41 | 60 | 142 | 9 | 17 | 0 | 74 | 30 | 0 | 0 | 157 | 0 | 19 | 56 | 28 | 2 | 0 | 0 | 4455.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 1127 | 0 | 0 | 0 | 1173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.93 | 77 | 0 | 0 | 43.05 | 130 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 3.81 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 3.4 | 43 | 0.36 | 0 | 278 | 140 | 220 | 0 | 307 | 560 | 0 | 4583.55 | 9039.05 | 97.06
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 15.4 | 0 | 17 | 0 | 15 | 0 | 17 | 16 | 0 | 0 | 0 | 345 | 0 | 17 | 300 | 0 | 0 | 28 | 35 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 24 | 25 | 0 | 46 | 0 | 37 | 200 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 890 | 17 | 12 | 8 | 0 | 315 | 0 | 51 | 0 | 202 | 34 | 0 | 110 | 17 | 0 | 11 | 0 | 92 | 0 | 61 | 0 | 310 | 0 | 0 | 41 | 60 | 137 | 11 | 17 | 0 | 74 | 30 | 0 | 0 | 157 | 0 | 19 | 58 | 28 | 2 | 39.92 | 0 | 4477.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 1112 | 0 | 0 | 0 | 1171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.96 | 92 | 0 | 0 | 52.74 | 130 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 4.63 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 5.5 | 143 | 0.49 | 0 | 278 | 138 | 180 | 0 | 306 | 555 | 0 | 4691.32 | 9168.64 | 97.06
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 16.8 | 0 | 45 | 0 | 95 | 0 | 20 | 52 | 0 | 0 | 0 | 360 | 0 | 17 | 300 | 0 | 0 | 30 | 17 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 35 | 25 | 0 | 46 | 0 | 37 | 145 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 892 | 17 | 28 | 35 | 0 | 340 | 0 | 51 | 0 | 201 | 33 | 0 | 108 | 22 | 0 | 11 | 0 | 120 | 0 | 64 | 0 | 315 | 0 | 0 | 41 | 60 | 152 | 11 | 17 | 0 | 77 | 30 | 0 | 0 | 157 | 0 | 19 | 58 | 26 | 2 | 42.17 | 0 | 4717.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 1131 | 0 | 0 | 0 | 1331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.08 | 90 | 0 | 0 | 56.76 | 138 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.13 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 5.8 | 145 | 0.52 | 0 | 278 | 137 | 220 | 0 | 306 | 560 | 0 | 4981.29 | 9699.26 | 97.05
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 51 | 0 | 107 | 0 | 195 | 0 | 55 | 136 | 0 | 0 | 0 | 440 | 0 | 50 | 335 | 0 | 0 | 29 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1 | 0 | 46 | 0 | 61 | 25 | 2.83 | 46 | 0 | 40 | 145 | 0 | 0 | 10 | 0 | 0 | 167 | 0 | 0 | 0 | 889 | 17 | 105 | 117 | 0 | 345 | 0 | 51 | 0 | 202 | 30 | 0 | 105 | 86 | 0 | 11 | 0 | 120 | 0 | 63 | 0 | 320 | 0 | 0 | 41 | 60 | 161 | 11 | 17 | 0 | 77 | 30 | 0 | 0 | 158 | 0 | 19 | 58 | 28 | 2 | 39.57 | 0 | 5483.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 1143 | 0 | 0 | 0 | 1462 | 0 | 0 | 0 | 15 | 27 | 0 | 0 | 0 | 0 | 51.96 | 94 | 0 | 0 | 52.76 | 139 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.79 | 0 | 0 | 90 | 29 | 80 | 0 | 0 | 0 | 5.6 | 140 | 0.5 | 0 | 307 | 134 | 220 | 0 | 309 | 585 | 0 | 5381.61 | 10865.01 | 97.05
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 31 | 0 | 58 | 0 | 293 | 0 | 0 | 17 | 0 | 0 | 0 | 355 | 0 | 0 | 250 | 0 | 0 | 24 | 0 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 64 | 0 | 77 | 25 | 2.91 | 46 | 0 | 39 | 145 | 0 | 0 | 10 | 0 | 0 | 167 | 0 | 0 | 0 | 888 | 15 | 50 | 140 | 0 | 295 | 0 | 51 | 0 | 196 | 33 | 0 | 50 | 17 | 0 | 11 | 0 | 100 | 0 | 54 | 0 | 310 | 0 | 0 | 42 | 60 | 140 | 9 | 0 | 0 | 42 | 20 | 0 | 0 | 158 | 0 | 19 | 58 | 28 | 2 | 34.75 | 0 | 4775.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 1025 | 0 | 0 | 0 | 1244.64 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 45.42 | 76 | 0 | 0 | 38.04 | 139 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 3.6 | 0 | 0 | 0 | 22 | 34 | 0 | 0 | 0 | 4.6 | 133 | 0.42 | 0 | 246 | 100 | 180 | 0 | 303 | 500 | 0 | 4494.72 | 9270.38 | 97.05
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 17 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 250 | 0 | 0 | 16 | 0 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 12 | 25 | 1.69 | 46 | 0 | 37 | 145 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 883 | 11 | 0 | 145 | 0 | 300 | 0 | 51 | 0 | 198 | 33 | 0 | 50 | 0 | 0 | 13 | 0 | 86 | 0 | 34 | 0 | 320 | 0 | 0 | 42 | 60 | 141 | 5 | 17 | 0 | 42 | 20 | 0 | 0 | 155 | 0 | 19 | 25 | 32 | 1 | 26.06 | 0 | 4178.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 927 | 0 | 0 | 0 | 1118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.28 | 53 | 0 | 0 | 29.94 | 139 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 2.65 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 3 | 90 | 0.24 | 0 | 201 | 100 | 180 | 0 | 300 | 450 | 0 | 3985.11 | 8163.86 | 97.04
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 17 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 250 | 0 | 0 | 9 | 0 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 12 | 25 | 0.6 | 46 | 0 | 28 | 145 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 935 | 4 | 0 | 108 | 0 | 315 | 0 | 20 | 0 | 202 | 29 | 0 | 50 | 0 | 0 | 13 | 0 | 82 | 0 | 19 | 0 | 320 | 0 | 0 | 42 | 60 | 144 | 2 | 17 | 0 | 42 | 20 | 0 | 0 | 154 | 0 | 19 | 16 | 33 | 0 | 12.12 | 0 | 4036.72 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 861 | 0 | 0 | 0 | 1026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.72 | 27 | 0 | 0 | 11.69 | 139 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0.86 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 1.1 | 46 | 0.13 | 0 | 202 | 100 | 180 | 0 | 300 | 450 | 0 | 3833.5 | 7870.22 | 97.04
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 250 | 0 | 0 | 2 | 0 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 0.07 | 46 | 0 | 33 | 145 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 1003 | 1 | 0 | 108 | 0 | 290 | 0 | 20 | 4 | 199 | 29 | 0 | 50 | 0 | 0 | 11 | 0 | 86 | 0 | 3 | 0 | 315 | 0 | 0 | 42 | 60 | 140 | 0 | 17 | 0 | 42 | 20 | 0 | 0 | 155 | 0 | 19 | 20 | 33 | 0 | 1.91 | 0 | 4000.98 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 846 | 0 | 0 | 0 | 1132.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.13 | 5 | 0 | 0 | 1.81 | 139 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0.17 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 6 | 0.02 | 0 | 199 | 100 | 180 | 0 | 300 | 455 | 0 | 4052.75 | 8053.73 | 97.04
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 325 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 38 | 145 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 1160 | 0 | 0 | 162 | 0 | 345 | 0 | 37 | 11 | 202 | 33 | 0 | 106 | 0 | 0 | 11 | 0 | 96 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 60 | 142 | 0 | 17 | 0 | 72 | 30 | 0 | 0 | 154 | 0 | 19 | 56 | 55 | 0 | 0 | 7 | 4539 | 774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 964 | 0 | 0 | 0 | 1277.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 134 | 220 | 0 | 300 | 480 | 0 | 5049.76 | 9588.76 | 97.03
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 145 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 1150 | 0 | 0 | 145 | 0 | 330 | 0 | 51 | 30 | 196 | 33 | 0 | 108 | 0 | 0 | 13 | 0 | 90 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 60 | 158 | 0 | 17 | 0 | 75 | 30 | 0 | 0 | 154 | 0 | 19 | 45 | 45 | 0 | 0 | 0 | 4555 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1083 | 0 | 0 | 0 | 1318.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 134 | 220 | 0 | 300 | 550 | 0 | 5320.87 | 9875.87 | 97.03
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 13 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 145 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 1150 | 0 | 0 | 145 | 0 | 335 | 0 | 51 | 30 | 198 | 33 | 0 | 108 | 0 | 0 | 13 | 0 | 92 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 60 | 154 | 0 | 17 | 0 | 75 | 30 | 0 | 0 | 154 | 0 | 19 | 35 | 50 | 0 | 0 | 0 | 4555 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1090 | 0 | 0 | 0 | 1323.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 134 | 220 | 0 | 300 | 560 | 0 | 5342.93 | 9897.93
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 13 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 145 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 1140 | 0 | 0 | 145 | 0 | 335 | 0 | 51 | 30 | 198 | 33 | 0 | 109 | 0 | 0 | 13 | 0 | 98 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 60 | 156 | 0 | 17 | 0 | 75 | 30 | 0 | 0 | 154 | 0 | 19 | 25 | 47 | 0 | 0 | 0 | 4535 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1092 | 0 | 0 | 0 | 1329.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 134 | 220 | 0 | 300 | 575 | 0 | 5359.8 | 9894.8 | 97.03
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 13 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 145 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 1141 | 0 | 0 | 108 | 0 | 330 | 0 | 51 | 12 | 196 | 33 | 0 | 109 | 0 | 0 | 13 | 0 | 100 | 0 | 0 | 0 | 310 | 0 | 0 | 42 | 60 | 158 | 0 | 17 | 0 | 75 | 30 | 0 | 0 | 154 | 0 | 19 | 25 | 51 | 0 | 0 | 0 | 4480 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 0 | 0 | 0 | 1332.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 134 | 220 | 0 | 332 | 610 | 0 | 5399.26 | 9879.26 | 97.02
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 12.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 145 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1101 | 0 | 0 | 108 | 0 | 320 | 0 | 51 | 10 | 191 | 33 | 0 | 108 | 0 | 0 | 13 | 0 | 92 | 0 | 0 | 0 | 310 | 0 | 0 | 42 | 60 | 152 | 0 | 17 | 0 | 75 | 30 | 0 | 0 | 155 | 0 | 19 | 16 | 51 | 0 | 0 | 0 | 4380.5 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 965 | 0 | 0 | 0 | 1228.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 134 | 220 | 0 | 400 | 605 | 0 | 5237.39 | 9617.89 | 97.02
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 12.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 145 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1000 | 0 | 0 | 110 | 0 | 325 | 0 | 51 | 10 | 194 | 34 | 0 | 109 | 0 | 0 | 13 | 0 | 94 | 0 | 0 | 0 | 310 | 0 | 0 | 34 | 20 | 149 | 0 | 17 | 0 | 75 | 30 | 0 | 0 | 155 | 0 | 19 | 16 | 52 | 0 | 0 | 0 | 4227.5 | 847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 892 | 0 | 0 | 0 | 1065.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 138 | 220 | 0 | 320 | 550 | 0 | 4888.23 | 9115.73 | 97.02
Total KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8082000 | 0 | 0 | 146880 | 0 | 327456 | 0 | 677956 | 0 | 152021 | 306720 | 0 | 0 | 0 | 8673911 | 0 | 120165 | 7073339 | 0 | 0 | 178996 | 175200 | 312000 | 300240 | 0 | 0 | 0 | 0 | 5280 | 0 | 35520 | 0 | 125808 | 0 | 285120 | 229440 | 7965 | 1100460 | 0 | 951840 | 5752727.27 | 0 | 0 | 38880 | 0 | 0 | 3900383 | 0 | 0 | 0 | 23072725 | 109620 | 252581 | 1538909 | 1390000 | 7984400 | 0 | 1173649 | 112320 | 4625000 | 499752 | 0 | 2111494 | 267360 | 0 | 292840 | 0 | 2160960 | 0 | 371345 | 0 | 7640500 | 0 | 0 | 954000 | 1420320 | 3588627 | 68750 | 376368 | 0 | 1374720 | 633504 | 0 | 0 | 4389050 | 0 | 338400 | 667200 | 792960 | 11550 | 183250 | 20640 | 107383101.27 | 8145454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 485280 | 23076400 | 0 | 0 | 0 | 26852727 | 0 | 0 | 0 | 6432 | 141504 | 0 | 0 | 0 | 0 | 318876 | 597060 | 0 | 0 | 324000 | 3374727 | 0 | 0 | 0 | 0 | 0 | 9297018 | 0 | 28800 | 0 | 0 | 206576 | 160480 | 258681 | 0 | 0 | 0 | 31120.8 | 785520 | 3027 | 0 | 5913000 | 3082000 | 5300890 | 0 | 7171593 | 12045090.91 | 0 | 107606256.71 | 214989357.98

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 09-01-2026
Power Supply Scenario
| Day Peak Generation |  |  | 9699.26 | MW | 12:00 Hr. | Energy Generated |  |  | 214.9894 |  | MKWHr.
| Day Peak Demand |  |  | 9699.26 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 9897.93 | MW | 19:30 Hr. | Energy Demand |  |  | 214.9894 |  | MKWHr.
| Evening Peak Demand |  |  | 9897.93 | MW | 19:30 Hr. | Maximum Temperature |  |  | 26 |  | °C
| Minimum Generation of the Day |  |  | 7436.93 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 647.98 |  | MMCFD
| Maximum Generation of the Day |  |  | 10865.01 | MW | 13:00 Hr. | Production Cost per KWHr |  |  | 5.6454 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 24.4415 | 0 | 1.9064 | 0 | 0 | 0.179 | 0 | 0 | 26.5269 | Gas | 91.2468 | Gas | 324335078.63
| Chattogram Zone |  |  | 4.8522 | 28.8255 | 0.68453 | 0 | 1.1005 | 0.11758 | 0 | 0.03552 | 35.6158 | Coal | 77.0315 | Coal | 512369146.2609
| Cumilla Zone |  |  | 19.7284 | 0 | 0.51994 | 0 | 0 | 0.37134 | 2.161 | 0 | 22.7806 | HFO | 4.7503 | HFO | 80999505.88
| Mymensingh Zone |  |  | 0.79296 | 0 | 1.0262 | 0 | 0 | 0.1948 | 0 | 0 | 2.014 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 20.3771 | 0 | 0 | 0 | 0 | 0.06875 | 0 | 0 | 20.4458 | Hydro | 1.1005 | Hydro | 110046
| Khulna Zone |  |  | 0 | 23.0764 | 0 | 0 | 0 | 0.48528 | 8.1455 | 0 | 31.7071 | Solar | 3.6656 | Solar | 56860637.74
| Barishal Zone |  |  | 8.3829 | 25.1297 | 0 | 0 | 0 | 0.003027 | 0 | 0 | 33.5156 | Import | 37.1591 | Import | 238502466.2
| Rajshahi Zone |  |  | 12.6717 | 0 | 0.14794 | 0 | 0 | 1.2687 | 26.8527 | 0 | 40.9411 | Wind | 0.03552 | Wind | 522499.2
| Rangpur Zone |  |  | 0 | 0 | 0.46526 | 0 | 0 | 0.97712 | 0 | 0 | 1.4424
| Total |  |  | 91.2468 | 77.0315 | 4.7503 | 0 | 1.1005 | 3.6656 | 37.1591 | 0.03552 | 214.9894
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 324335078.63 |  | Hydro | 110046
|  |  |  | Coal | 512369146.2609 |  | Solar | 56860637.74
|  |  |  | HFO | 80999505.88 |  | Import | 238502466.2
|  |  |  | HSD | 0 |  | Wind | 522499.2
[5 empty] | Total: | 121,36,99,379 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 8.1455 | Peak Hr Flow | 846.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 36632963.64 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.8527 | Peak Hr Flow | 1323.93 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2099 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.161 | Peak Hr Flow | 92.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2221 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 37.1591 | Peak Hr Flow | 2261.93 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3195
|  |  |  | Chattogram |  | 0 |  | 1105
|  |  |  | Cumilla |  | 0 |  | 898
|  |  |  | Mymensingh |  | 0 |  | 844
|  |  |  | Sylhet |  | 0 |  | 378
|  |  |  | Khulna |  | 0 |  | 1188
|  |  |  | Barishal |  | 0 |  | 303
|  |  |  | Rajshahi |  | 0 |  | 943
|  |  |  | Rangpur |  | 0 |  | 672
|  |  |  | Total |  | 0 |  | 9526
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Baghabari 100 MW GTPP |  |  | 100
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 700 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:07 | 15:24 | BIPTC S/S 11T01 HT Scheduled S/D Due to Pole-01 is in shutdown for Annual maintenance
| 08:07 |  | Bheramara (HVDC ) Shutdown with remarks:- POLE1
| 08:08 | 13:04 | Sonargaon 132/33kV S/S Tr-2 LT Scheduled S/D Due to PBS 33KV underground cable | [7 empty] | 45.0MW load
|  |  | installation | [7 empty] | interrup.
| 08:08 | 13:02 | Sonargaon 132/33kV S/S Tr-2 HT Scheduled S/D Due to PBS 33KV underground cable | [7 empty] | 45.0MW load
|  |  | installation. | [7 empty] | interrup.
| 08:21 | 15:38 | Siddhirganj 132/33kV S/S T-2 LT Scheduled S/D Due to Annual Maintenance.
| 08:22 | 15:37 | Siddhirganj 132/33kV S/S T-2 HT Scheduled S/D Due to Annual maintenance
| 08:26 | 10:50 | Mymensingh 132/33kV S/S 50 MW Solar Plant Project Work S/D
| 08:43 |  | Aminbazar-Kaliakoir 230kV Ckt-2 Forced S/D from Kaliakoir 400/230/132kV end Due to By
NLDC and from Aminbazar 400/230/132kV end Due to C.T. Replace work
| 08:44 | 17:03 | Shikalbaha 230/132kV S/S ATR 02 LT Scheduled S/D
| 08:45 | 17:03 | Shikalbaha 230/132kV S/S ATR 02 HT Scheduled S/D Due to None
| 08:45 | 08:45 | Chandraghona 132/33kV S/S TR-01(406T) LT Scheduled S/D Due to Bus 2 shutdown
| 08:45 | 11:50 | Chandraghona 132/33kV S/S TR-02(416T) LT Scheduled S/D Due to Bus 2 shutdown
| 08:46 |  | Naogaon-Niyamatpur 132kV Ckt-1 Project Work S/D from Niamatpur 132/33kV end. and from
Naogaon 132/33kV end Due to Project work.
| 08:46 | 11:48 | Chandraghona 132/33kV S/S TR-02(416T) HT Scheduled S/D Due to Bus 2 shutdown
| 08:51 | 12:08 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Cumilla(N) Ckt-01 Scheduled S/D Due to
Maintenance period
| 08:54 | 10:26 | Mymensingh 132/33kV S/S Bus A Project Work S/D
| 09:11 |  | Patuakhali-Payra 132kV Ckt-2 Project Work S/D from Patuakhali 132/33kV end Due to
Project Work and from Payra 400/132/33kVend.
| 09:17 | 19:52 | Tongi 230/132/33kV S/S T-03 LT Scheduled S/D Due to Annual maintenance
| 09:18 | 19:52 | Tongi 230/132/33kV S/S T-03 HT Scheduled S/D Due to Annual maintenance
| 10:10 |  | Bheramara 410 MW CCPP GT Ready with remarks:- Plant is in standby condition as per
instruction of NLDC.
| 10:10 |  | Bheramara 410 MW CCPP ST Ready with remarks:- Plant is is standby condition as per
instruction of NLDC
| 10:22 | 16:46 | Haripur 230/132kV S/S Auto TR-1 HT Scheduled S/D Due to Annunciator Replacing Work By
Reverie Ltd.
| 10:22 | 16:46 | Haripur 230/132kV S/S Auto TR-1 LT Scheduled S/D
|  | 11:37 | Bheramara 230/132kV S/S Transformer-2 LT is restored.
| 12:00 |  | Day peak Generation is 9696 MW
| 12:09 | 14:53 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Cumilla(N) Ckt-02 Scheduled S/D
| 15:24 |  | Bheramara (HVDC ) Synchronized with remarks:- Pole 1
|  | 15:28 | Chhatak 132/33kV S/S T-1 LT is restored.
|  | 15:28 | Chhatak 132/33kV S/S T-1 HT is restored.
| 16:36 |  | Bheramara (HVDC ) Synchronized with remarks:- Pole 2
| 16:49 | 20:34 | Haripur 230/132kV S/S Auto TR-2 LT Scheduled S/D Due to Annunciator change
| 16:49 | 20:34 | Haripur 230/132kV S/S Auto TR-2 HT Scheduled S/D Due to Annunciator change
|  | 16:57 | Rampura 230/132kV S/S Auto Transformer - 03 HT is restored.
|  | 16:57 | Rampura 230/132kV S/S Auto Transformer - 03 LT is restored.
|  | 17:52 | Meghnaghat-Shyampur 230kV Ckt-2 is restored.
|  | 17:52 | Meghnaghat-Shyampur 230kV Ckt-2 is restored.
| 19:30 |  | Evening peak generation: 9897 MW
|  | 19:31 | Meghnaghat 400/230kV S/S 230kV BUS Section 01 is restored.
| 05:00 |  | Minimum Generation: 6846 MW
| 06:49 |  | Bogura(New)-Naogaon 132 kV Ckt-2 Project Work S/D from Naogaon 132/33kV end Due to
Project work and from Bogura 230/132kVend.
| 06:49 |  | Naogaon 132/33kV S/S Main Bus Project Work S/D Due to Project work | [7 empty] | 65.0MW load
interrup.
| 06:49 |  | Naogaon 132/33kV S/S Nao-SPPP Ckt-1 Project Work S/D Due to Project work.
| 07:07 |  | Coxsbazar 132/33kV S/S 405T-T1 HT Project Work S/D Due to T01- 33kV Bushing to incomer 2 | [7 empty] | 30.0MW load
|  |  | Loop cable remove | [7 empty] | interrup.
| 07:14 |  | Baroaulia-Khulshi 132 kV Ckt-1 Scheduled S/D from Baroaulia 132/33kV end Due to Annual
maintence of Bay Equipment at KHULSHI end.
| 07:16 |  | Shikalbaha 230/132kV S/S ATR 01 LT Scheduled S/D
| 07:16 |  | Shikalbaha 230/132kV S/S ATR 01 HT Scheduled S/D
| 07:21 |  | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt Project Work S/D from Barguna | [7 empty] | 12.0MW load
|  |  | 132/33kV end Due to Patuakhali- Barishal North 230kv Line project Work. | [7 empty] | interrup. Barguna
132/33kV end
| 07:24 |  | Bakerganj 132/33kV S/S T1 HT Scheduled S/D Due to Annual Maintenance
| 07:24 |  | Bakerganj 132/33kV S/S T1 LT Scheduled S/D Due to Due to Annual Maintenance
| 07:25 |  | Bakerganj 132/33kV S/S 132 kV Bakerganj Barguna Ckt Scheduled S/D Due to Annual
Maintenance
| 07:25 |  | Bakerganj 132/33kV S/S 132 kV Bakerganj Patuakhali Ckt Scheduled S/D Due to Annual
Maintenance
| 07:35 |  | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt Project Work S/D from Patuakhali
132/33kV end Due to Project work
| 07:41 |  | Barishal-Bhola 230 kV Ckt-1 Scheduled S/D from Barishal 230/132kV end Due to annual
mainntenance
| 07:42 |  | Mymensingh 132/33kV S/S Bus B Project Work S/D
| 07:43 |  | Meghnaghat-Shyampur 230kV Ckt-1 Scheduled S/D from Meghnaghat 400/230kV end Due to
Maintenance work and from Shyampur 230/132kV end Due to Deadline checking.
| 07:45 |  | Jamalpur-Mymensingh 132kV Ckt-2 Project Work S/D from Mymensingh 132/33kV end. and from
Jamalpur 132/33kV end Due to G2G project work mym Grid side
| 07:48 |  | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT Project Work S/D Due to Development Work
| 07:48 |  | Rajshahi 132/33kV S/S Transformer T-2(415T) HT Project Work S/D Due to Development Work
| 07:48 |  | Rajshahi 132/33kV S/S Transformer T-1(405T) HT Project Work S/D Due to Development Work
| 07:50 |  | Kishoreganj 132/33kV S/S Tr-2 (414T) HT Scheduled S/D Due to 33KV T-2 BUS SHUTDOWN BY | [7 empty] | 31.0MW load
|  |  | BPDB | [7 empty] | interrup.
| 07:50 |  | Kishoreganj 132/33kV S/S Tr-2 (414T) LT Scheduled S/D Due to 33KV T-2 BUS SHUTDOWN BY | [7 empty] | 31.0MW load
|  |  | BPDB | [7 empty] | interrup.
| 07:51 |  | Natore-Rajshahi 132kV Ckt-1 Project Work S/D from Rajshahi 132/33kV end Due to
Development Work
| 07:52 |  | Natore-Rajshahi 132kV Ckt-2 Project Work S/D from Rajshahi 132/33kV end Due to
Development Work
| 07:54 |  | Rajshahi 132/33kV S/S 132 kV PPP 50 Mw Project Work S/D Due to Development Work
| 07:56 |  | Rajshahi 132/33kV S/S Transfer Bus Project Work S/D Due to Development Work
| 07:56 |  | Rajshahi-Rajshahi(New) 132kV Ckt-2 Project Work S/D from Rajshahi 132/33kV end Due to
Development Work
| 07:56 |  | Rajshahi-Rajshahi(New) 132kV Ckt-1 Project Work S/D from Rajshahi 132/33kV end Due to
Development Work
| 07:56 |  | Bakulia-Khulshi 132 kV Ckt-1 Scheduled S/D from Bakulia 132/33kV end.
| 07:56 |  | Bakulia-MSML 132 kV Ckt-2 Scheduled S/D from Bakulia 132/33kV end.
| 07:59 |  | Patuakhali-Payra 132kV Ckt-1 Scheduled S/D from Payra 400/132/33kV end.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 09-01-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 337 | 8082000 | FGMO, Gas Shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 7073339 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 146880 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 152021 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 120165 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 13 | 312000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 300240 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 677956 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 327456 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 306720 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 178996 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 405 | 8673911 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 0 | 175200 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1050 | 26526884
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 109620 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 38880 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1100460 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 166 | 3900383 | Plant availability less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 125808 | temp problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 285120 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 42 | 951840 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 5280 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 7965 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 229440 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1150 | 23072725 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 35520 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 145 | 5752727.27 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4898.863 | 1549 | 35615768.27
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 198 | 4625000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 335 | 7984400 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 1390000 | FGMO, Gas Shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 33 | 499752 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 30 | 112320 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 145 | 1538909 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1173649 | Machine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 252581 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 108 | 2111494 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 267360 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 92 | 2160960 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 292840 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 371345 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1005 | 22780610
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 50 | 792960 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11550 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 35 | 667200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 338400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 183250 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 20640 | To be dispatched 18 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 104 | 2014000
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 68750 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 954000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1420320 | machine problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 154 | 3588627 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 633504 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 1374720 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 154 | 4389050 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 376368 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7640500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2325 | 847 | 20445839
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 846 | 8145454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 485280 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1090 | 23076400 | U-2 Under Maintenance
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1936 | 31707134
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 300 | 7171593 | Machine Problem
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 134 | 3082000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 560 | 12045090.91 | FGMO, U1 under maintenance
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5300890 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 278 | 5913000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3027 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1492 | 33515600.91
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 318876 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 143 | 3374727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9297018 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 141504 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 6432 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 28800 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1323.93 | 26852727 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 324000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 597060 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1880.93 | 40941144
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 258681 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 31120.8 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 206576 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 160480 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 785520 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 34 | 1442377.8
Eastern Grid Total |  |  |  |  | 17398.245 | 4555 | 107383101.27
Western Grid Total |  |  |  |  | 10984.003 | 5342.93 | 107606256.71
National Grid Total |  |  |  |  | 28382.248 | 9897.93 | 214989357.98
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 09-01-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6419.87 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3105.5 | MW
i) Dhaka area |  |  | 3194.77 |  | MW | i) Khulna area |  |  |  | 1187.5 | MW
ii) Chattogram area |  |  | 1105.1 |  | MW | ii) Barishal area |  |  |  | 303 | MW
iii) Cumilla area |  |  | 898 |  | MW | iii) Rajshahi area |  |  |  | 943 | MW
iv) Mymensingh area |  |  | 844 |  | MW | iv) Rangpur area |  |  |  | 672 | MW
v) Sylhet area |  |  | 378 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 9525.37 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 60 | 10:00 | 133 | Netrakona | 115 | 18:00
2 | AKSML | 123 | 13:00 | 68 | Hathazari | 53 | 12:00 | 134 | New | 40 | 12:00
3 | Aftabnagar | 28 | 12:00 | 69 | Hatirjheel | 23 | 18:00 | 135 | Niamatpur | 58 | 08:00
4 | Agargaon | 82 | 13:00 | 70 | Ishurdi | 48 | 18:30 | 136 | Noapara | 30 | 18:30
5 | Agrabad | 26 | 12:00 | 71 | Jaldhaka | 52 | 18:30 | 137 | PHP | 9 | 10:00
6 | Amnura | 22 | 09:00 | 72 | Jamalpur | 83 | 18:00 | 138 | Pabna | 69 | 13:00
7 | Ashuganj | 54 | 23:00 | 73 | Jashore | 111 | 13:00 | 139 | Palashbari | 76 | 13:00
8 | BSRM | 201 | 22:00 | 74 | Jhenaidah | 98 | 13:00 | 140 | Panchagarh | 43 | 18:30
9 | Bagerhat | 59 | 18:00 | 75 | Joydebpur | 94 | 13:00 | 141 | Patiya | 6.3 | 19:30
10 | Bajitpur | 67 | 18:30 | 76 | Joypurhat | 41 | 18:30 | 142 | Patuakhali | 39.5 | 21:00
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 13 | 00:00 | 143 | Payra | 28 | 13:00
12 | Bakulia | 61 | 13:00 | 78 | KSRM | 25 | 10:00 | 144 | Postogola | 41 | 13:00
13 | Banani | 27.8 | 13:00 | 79 | Kabirpur | 121 | 00:00 | 145 | Purbachal | 21 | 13:00
14 | Bangabhaban | 4 | 14:00 | 80 | Kachua | 67 | 13:00 | 146 | Purbasadipur | 126 | 13:00
15 | Barapukuria | 46 | 13:00 | 81 | Kallyanpur | 93 | 13:00 | 147 | Rahanpur | 25 | 20:00
16 | Barguna | 14 | 18:00 | 82 | Kalurghat | 18 | 18:00 | 148 | Rahim | 33 | 00:00
17 | Barishal | 87 | 13:00 | 83 | Kamrangirchar | 46 | 00:00 | 149 | Rajbari | 54 | 18:00
18 | Barishal-230 | 70 | 13:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 99 | 13:00
19 | Baroaulia | 51 | 09:00 | 85 | Kasba | 25 | 13:00 | 151 | Rajshahi | 74 | 13:00
20 | Baroirhat | 44 | 13:00 | 86 | Kazla | 94 | 13:00 | 152 | Rajshahi-230 | 88 | 13:00
21 | Bashundhara | 149 | 12:00 | 87 | Keranigonj | 63 | 13:00 | 153 | Ramganj | 88 | 13:00
22 | BashundharaCement | 7 | 00:00 | 88 | Khagrachori | 26 | 13:00 | 154 | Rampur | 26 | 12:00
23 | Beanibazar | 46 | 13:00 | 89 | Khulna | 44 | 13:00 | 155 | Rangamati | 13 | 18:00
24 | Benapole | 64 | 09:00 | 90 | Khulshi | 145 | 20:00 | 156 | Rangpur | 124 | 13:00
25 | Bhaluka | 102 | 09:00 | 91 | Kishoreganj | 92 | 18:30 | 157 | Ruppur | 2 | 09:00
26 | Bhandaria | 36 | 13:00 | 92 | Kodda | 187 | 01:00 | 158 | SSM | 10 | 00:00
27 | Bhangura | 23 | 13:00 | 93 | Kulaura | 30 | 13:00 | 159 | Saidpur | 86 | 13:00
28 | Bheramara(GK) | 38 | 18:00 | 94 | Kurigram | 46 | 13:00 | 160 | Satkhira | 95 | 08:00
29 | Bhulta | 175 | 00:00 | 95 | Kushtia | 104 | 13:00 | 161 | Satmasjid | 81 | 13:00
30 | Bog-Sherpur | 52 | 18:00 | 96 | Laksam | 24 | 22:00 | 162 | Savar | 139 | 12:00
31 | Bogura | 101 | 18:30 | 97 | Lakshmipur | 23 | 13:00 | 163 | SevenRings | 14.5 | 07:00
32 | Borhanuddin | 63 | 13:00 | 98 | Lalbag | 50 | 00:00 | 164 | ShahCement | 37 | 10:00
33 | Brahmanbaria | 98 | 13:00 | 99 | Lalmonirhat | 42 | 18:30 | 165 | Shahjadpur | 48 | 08:00
34 | Cantonment | 78 | 13:00 | 100 | MI_Cement | 16.2 | 00:00 | 166 | Shahjibazar | 80 | 21:00
35 | Chandina | 12 | 13:00 | 101 | Madanganj | 41 | 13:00 | 167 | Shahmirpur | 28 | 13:00
36 | Chandpur | 66 | 13:00 | 102 | Madaripur | 92 | 13:00 | 168 | Shariatpur | 56 | 20:00
37 | Chandraghona | 27 | 12:00 | 103 | Madartek | 68 | 13:00 | 169 | Sherpur | 116 | 18:30
38 | Chapai | 49 | 08:00 | 104 | Madunaghat | 32 | 19:30 | 170 | Shikalbaha | 21 | 16:00
39 | Charsaidpur | 38 | 08:00 | 105 | Magura | 48 | 13:00 | 171 | Shitalakhya | 44 | 12:00
40 | Chauddagram | 54 | 13:00 | 106 | Mahasthangarh | 44 | 18:00 | 172 | Sholosohor | 29 | 12:00
41 | Chhatak | 25 | 12:00 | 107 | Maijdee | 26 | 21:00 | 173 | Shyampur | 140 | 10:00
42 | Chowmuhani | 125 | 13:00 | 108 | Manikganj | 85 | 21:00 | 174 | Siddhirganj | 64 | 18:00
43 | Chuadanga | 82 | 13:00 | 109 | Maniknagar | 48 | 13:00 | 175 | Sirajganj | 66 | 18:30
44 | Coxsbazar | 116 | 13:00 | 110 | Matarbari | 38 | 18:00 | 176 | Sonargaon | 108 | 00:00
45 | Cumilla(N) | 99 | 13:00 | 111 | Matuail | 42 | 00:00 | 177 | Sreemongol | 53 | 12:00
46 | Cumilla(S) | 120 | 12:00 | 112 | Metrorail_Motijheel | 15 | 21:00 | 178 | Sreepur | 70 | 00:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 1 | 00:00 | 179 | Srinagar | 38.94 | 13:00
48 | Daudkandi | 106 | 20:00 | 114 | Millgate | 52 | 12:00 | 180 | Sunamganj | 38 | 19:30
49 | DhakaUniversity | 28 | 12:00 | 115 | Mirpur | 115 | 13:00 | 181 | Sylhet | 44 | 13:00
50 | Dhamrai | 72 | 00:00 | 116 | Mirsorai | 28 | 14:00 | 182 | Sylhet-132 | 67 | 13:00
51 | Dhanmondi | 70 | 13:00 | 117 | Mirzapur | 37 | 18:30 | 183 | TK | 18 | 13:00
52 | Dohazari | 69 | 13:00 | 118 | Mithapukur | 44 | 18:00 | 184 | Tangail | 126 | 13:00
53 | Faridpur | 103 | 19:00 | 119 | Modern | N/A | N/A | 185 | Taraganj | 15 | 08:00
54 | Fatullah | 66 | 00:00 | 120 | Mogbazar | 45.2 | 13:00 | 186 | Tasnim | 20 | 01:00
55 | Fenchuganj | 24 | 13:00 | 121 | Mongla | 28 | 00:00 | 187 | Thakurgaon | 73 | 18:30
56 | Feni | 89 | 13:00 | 122 | Motijheel | 31 | 13:00 | 188 | Tongi | 101 | 12:00
57 | GPH | 71 | 00:00 | 123 | Muktagacha | 31 | 13:00 | 189 | Ullahpara | 24 | 18:30
58 | Ghatail | 68 | 18:00 | 124 | Munshiganj | 81 | 13:00 | 190 | Ullon | 49 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 0 | 00:00 | 191 | Uttara | 48 | 13:00
60 | Ghorashal-230 | 71 | 00:00 | 126 | Mymensingh | 160 | 13:00 | 192 | UttaraNew | 33 | 13:00
61 | Goalpara | 33 | 13:00 | 127 | Naogaon | 90 | 19:30 | 193 | Zigatola | 80 | 13:00
62 | Gollamari | 86 | 13:00 | 128 | Narail | 43 | 18:30
63 | Gopalganj | 79 | 18:30 | 129 | Narinda | 42 | 13:00
64 | Gulshan | 62 | 13:00 | 130 | Narshingdi | 131 | 21:00
65 | Halishahar | 46 | 20:00 | 131 | Natore | 97 | 20:00
66 | HaripurSBU | 93 | 23:00 | 132 | Nawabganj | 48.2 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 09-01-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 9281.99 | 0 |  | 9281.99
1:00 | 8628.85 | 0 |  | 8628.85
2:00 | 8142.46 | 0 |  | 8142.46
3:00 | 7762.63 | 0 |  | 7762.63
4:00 | 7555.26 | 0 |  | 7555.26
5:00 | 7436.93 | 0 |  | 7436.93
6:00 | 7808.94 | 0 |  | 7808.94
7:00 | 7877.4 | 0 |  | 7877.4
8:00 | 8576.61 | 0 |  | 8576.61
9:00 | 9089.76 | 0 |  | 9089.76
10:00 | 9039.05 | 0 |  | 9039.05
11:00 | 9168.64 | 0 |  | 9168.64
12:00 | 9699.26 | 0 |  | 9699.26
13:00 | 10865.01 | 0 |  | 10865.01
14:00 | 9270.38 | 0 |  | 9270.38
15:00 | 8163.86 | 0 |  | 8163.86
16:00 | 7870.22 | 0 |  | 7870.22
17:00 | 8053.73 | 0 |  | 8053.73
18:00 | 9588.76 | 0 |  | 9588.76
19:00 | 9875.87 | 0 |  | 9875.87
19:30 | 9897.93 | 0 |  | 9897.93
20:00 | 9894.8 | 0 |  | 9894.8
21:00 | 9879.26 | 0 |  | 9879.26
22:00 | 9617.89 | 0 |  | 9617.89
23:00 | 9115.73 | 0 |  | 9115.73
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 09-01-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4712.5 | 4569.49 | 9281.99 | DAILY GENERATION CURVE
00:30 | 4635 | 4320.42 | 8955.42
01:00 | 4557.5 | 4071.35 | 8628.85 | 09-01-2026
01:30 | 4406.75 | 3978.905 | 8385.655
02:00 | 4256 | 3886.46 | 8142.46
02:30 | 4210.5 | 3742.045 | 7952.545
03:00 | 4165 | 3597.63 | 7762.63
03:30 | 4154.5 | 3504.445 | 7658.945
04:00 | 4144 | 3411.26 | 7555.26
04:30 | 4084.25 | 3411.845 | 7496.095
05:00 | 4024.5 | 3412.43 | 7436.93
05:30 | 4164.25 | 3458.685 | 7622.935
06:00 | 4304 | 3504.94 | 7808.94
06:30 | 4268.57 | 3574.6 | 7843.17
07:00 | 4233.14 | 3644.26 | 7877.4
07:30 | 4275.57 | 3951.435 | 8227.005
08:00 | 4318 | 4258.61 | 8576.61
08:30 | 4417.25 | 4415.935 | 8833.185
09:00 | 4516.5 | 4573.26 | 9089.76
09:30 | 4486 | 4578.405 | 9064.405
10:00 | 4455.5 | 4583.55 | 9039.05
10:30 | 4466.41 | 4637.435 | 9103.845
11:00 | 4477.32 | 4691.32 | 9168.64
11:30 | 4597.645 | 4836.305 | 9433.95
12:00 | 4717.97 | 4981.29 | 9699.26
12:30 | 5100.685 | 5181.45 | 10282.135
13:00 | 5483.4 | 5381.61 | 10865.01
13:30 | 5129.53 | 4938.165 | 10067.695
14:00 | 4775.66 | 4494.72 | 9270.38
14:30 | 4477.205 | 4239.915 | 8717.12
15:00 | 4178.75 | 3985.11 | 8163.86
15:30 | 4107.735 | 3909.305 | 8017.04
16:00 | 4036.72 | 3833.5 | 7870.22
16:30 | 4018.85 | 3943.125 | 7961.975
17:00 | 4000.98 | 4052.75 | 8053.73
17:30 | 4269.99 | 4551.255 | 8821.245
18:00 | 4539 | 5049.76 | 9588.76
18:30 | 4547 | 5185.315 | 9732.315
19:00 | 4555 | 5320.87 | 9875.87
19:30 | 4555 | 5342.93 | 9897.93
20:00 | 4535 | 5359.8 | 9894.8
20:30 | 4507.5 | 5379.53 | 9887.03 |  | Executive Engineer
21:00 | 4480 | 5399.26 | 9879.26 |  | Network Operation Division
21:30 | 4430.25 | 5318.325 | 9748.575
22:00 | 4380.5 | 5237.39 | 9617.89
22:30 | 4304 | 5062.81 | 9366.81
23:00 | 4227.5 | 4888.23 | 9115.73

## En-Curve
QF-LDC-12
Date | 09-01-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2429 | 1236.5 | 381 | 0 | 90 | 1174.49 | 46 | 3882 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2427 | 1227.5 | 381.5 | 0 | 88 | 1099.92 | 46 | 3654.5 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 09-01-2026
01:00 | 2425 | 1218.5 | 382 | 0 | 86 | 1025.35 | 46 | 3427 | 0 | 0 | 19 | 0 | 0 | 0 | 0
01:30 | 2445 | 1192.75 | 382 | 0 | 85 | 1012.905 | 46 | 3210.5 | 0 | 0 | 9.5 | 0 | 0 | 2 | 0 | Energy Generated | 214.9894 |  | MKWHr
02:00 | 2465 | 1167 | 382 | 0 | 84 | 1000.46 | 46 | 2994 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2472 | 1157 | 308 | 0 | 84 | 968.545 | 46 | 2909.5 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | Total Energy Requirement | 214.9894 |  | MKWHr
03:00 | 2479 | 1147 | 234 | 0 | 84 | 936.63 | 46 | 2825 | 0 | 0 | 0 | 0 | 0 | 11 | 0
03:30 | 2484 | 1156 | 215 | 0 | 83 | 882.945 | 46 | 2784 | 0 | 0 | 0 | 0 | 0 | 8 | 0
04:00 | 2489 | 1165 | 196 | 0 | 82 | 829.26 | 46 | 2743 | 0 | 0 | 0 | 0 | 0 | 5 | 0
04:30 | 2484 | 1164.25 | 196 | 0 | 78 | 833.345 | 46 | 2689.5 | 0 | 0 | 0 | 0 | 0 | 5 | 0
05:00 | 2479 | 1163.5 | 196 | 0 | 74 | 837.43 | 46 | 2636 | 0 | 0 | 0 | 0 | 0 | 5 | 0
05:30 | 2592 | 1195.75 | 196 | 0 | 76 | 848.685 | 46 | 2664 | 0 | 0 | 0 | 0 | 0 | 4.5 | 0
06:00 | 2705 | 1228 | 196 | 0 | 78 | 859.94 | 46 | 2692 | 0 | 0 | 0 | 0 | 0 | 4 | 0
06:30 | 2589.5 | 1221.5 | 196 | 0 | 81 | 869.575 | 46 | 2833 | 3.595 | 0 | 0 | 0 | 0 | 3 | 0
07:00 | 2474 | 1215 | 196 | 0 | 84 | 879.21 | 46 | 2974 | 7.19 | 0 | 0 | 0 | 0 | 2 | 0
07:30 | 2483 | 1247 | 146.5 | 0 | 79 | 1003.105 | 46 | 3124 | 52.4 | 0 | 44.5 | 0 | 0 | 1.5 | 0
08:00 | 2492 | 1279 | 97 | 0 | 74 | 1127 | 46 | 3274 | 97.61 | 0 | 89 | 0 | 0 | 1 | 0
08:30 | 2439 | 1267.5 | 48.5 | 0 | 83 | 1153 | 46 | 3401 | 162.435 | 17.5 | 214.75 | 0 | 0 | 0.5 | 0
09:00 | 2386 | 1256 | 0 | 0 | 92 | 1179 | 46 | 3528 | 227.26 | 35 | 340.5 | 0 | 0 | 0 | 0
09:30 | 2392 | 1259.5 | 0 | 0 | 93 | 1176 | 46 | 3446 | 302.905 | 52.5 | 296.5 | 0 | 0 | 0 | 0
10:00 | 2398 | 1263 | 0 | 0 | 94 | 1173 | 46 | 3364 | 378.55 | 70 | 252.5 | 0 | 0 | 0 | 0
10:30 | 2401.5 | 1231.5 | 0 | 0 | 93 | 1172 | 46 | 3352.5 | 494.395 | 60.5 | 252.45 | 0 | 0 | 0 | 0
11:00 | 2405 | 1200 | 0 | 0 | 92 | 1171 | 46 | 3341 | 610.24 | 51 | 252.4 | 0 | 0 | 0 | 0
11:30 | 2446.5 | 1252 | 0 | 0 | 106 | 1251 | 46 | 3326.5 | 621.35 | 42 | 342.6 | 0 | 0 | 0 | 0
12:00 | 2488 | 1304 | 0 | 0 | 120 | 1331 | 46 | 3312 | 632.46 | 33 | 432.8 | 0 | 0 | 0 | 0
12:30 | 2510 | 1386.5 | 0 | 0 | 120 | 1396.5 | 46 | 3345 | 626.735 | 48 | 802.9 | 0 | 0 | 0.5 | 0
13:00 | 2532 | 1469 | 0 | 0 | 120 | 1462 | 46 | 3378 | 621.01 | 63 | 1173 | 0 | 0 | 1 | 0
13:30 | 2345 | 1382 | 0 | 0 | 110 | 1353.32 | 46 | 3242.5 | 575.375 | 63.5 | 948.5 | 0 | 0 | 1.5 | 0
14:00 | 2158 | 1295 | 0 | 0 | 100 | 1244.64 | 46 | 3107 | 529.74 | 64 | 724 | 0 | 0 | 2 | 0
14:30 | 2165 | 1309 | 0 | 0 | 93 | 1181.32 | 46 | 3006.5 | 447.3 | 32 | 433.5 | 0 | 0 | 3.5 | 0
15:00 | 2172 | 1323 | 0 | 0 | 86 | 1118 | 46 | 2906 | 364.86 | 0 | 143 | 0 | 0 | 5 | 0
15:30 | 2184 | 1261 | 72.5 | 0 | 84 | 1072 | 46 | 2899.5 | 271.04 | 0 | 123.5 | 0 | 0 | 3.5 | 0
16:00 | 2196 | 1199 | 145 | 0 | 82 | 1026 | 46 | 2893 | 177.22 | 0 | 104 | 0 | 0 | 2 | 0
16:30 | 2179 | 1188 | 263 | 0 | 84 | 1079.26 | 46 | 2920.5 | 102.715 | 0 | 98.5 | 0 | 0 | 1 | 0
17:00 | 2162 | 1177 | 381 | 0 | 86 | 1132.52 | 46 | 2948 | 28.21 | 0 | 93 | 0 | 0 | 0 | 0
17:30 | 2334 | 1277 | 577.5 | 0 | 91 | 1205.14 | 46 | 3137.5 | 14.105 | 8.5 | 130.5 | 0 | 0 | 0 | 0
18:00 | 2506 | 1377 | 774 | 0 | 96 | 1277.76 | 46 | 3327 | 0 | 17 | 168 | 0 | 0 | 0 | 0
18:30 | 2489.5 | 1437.5 | 810 | 0 | 93 | 1298.315 | 46 | 3416.5 | 0 | 8.5 | 133 | 0 | 0 | 0 | 0
19:00 | 2473 | 1498 | 846 | 0 | 90 | 1318.87 | 46 | 3506 | 0 | 0 | 98 | 0 | 0 | 0 | 0
19:30 | 2484 | 1495 | 846 | 0 | 92 | 1323.93 | 46 | 3523 | 0 | 0 | 88 | 0 | 0 | 0 | 0
20:00 | 2481 | 1492 | 846 | 0 | 98 | 1329.8 | 46 | 3530 | 0 | 0 | 72 | 0 | 0 | 0 | 0
20:30 | 2482.5 | 1463 | 846 | 0 | 99 | 1331.03 | 46 | 3561.5 | 0 | 0 | 58 | 0 | 0 | 0 | 0
21:00 | 2484 | 1434 | 846 | 0 | 100 | 1332.26 | 46 | 3593 | 0 | 0 | 44 | 0 | 0 | 0 | 0
21:30 | 2471.5 | 1427.25 | 846 | 0 | 96 | 1280.325 | 46 | 3542 | 0 | 0 | 39.5 | 0 | 0 | 0 | 0
22:00 | 2459 | 1420.5 | 846 | 0 | 92 | 1228.39 | 46 | 3491 | 0 | 0 | 35 | 0 | 0 | 0 | 0
22:30 | 2443.5 | 1417.5 | 846.5 | 0 | 93 | 1146.81 | 46 | 3338.5 | 0 | 0 | 35 | 0 | 0 | 0 | 0
23:00 | 2428 | 1414.5 | 847 | 0 | 94 | 1065.23 | 46 | 3186 | 0 | 0 | 35 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 09-01-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 423 | 06:00 | 411 | 00:00 | Meghnaghat | 428 | 06:00 | 417 | 00:00
Ashuganj | 415 | 4:00 | 400 | 11:00 | Payra | 423 | 04:00 | 417 | 13:00
Bhulta | 407 | 04:00 | 394 | 11:00 | Rahanpur | 420 | 04:00 | 404 | 12:00
Bibiana | 421 | 05:00 | 413 | 00:00 | Rampal | 416 | 04:00 | 403 | 13:00
BIPTC | 408 | 03:00 | 395 | 19:00
Bogura | 417 | 05:00 | 396 | 18:30
Gopalganj | 422 | 04:00 | 411 | 12:00
Kaliakoir | 419 | 05:00 | 408 | 00:00
Korerhat | 428 | 06:00 | 416 | 00:00
Madunaghat | 416 | 05:00 | 407 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 246 | 06:00 | 238 | 00:00 | Kachua | 241 | 15:00 | 238 | 00:00
AKSML | 240.7 | 08:00 | 234.6 | 12:00 | Kaliakoir | 246 | 14:00 | 238 | 00:00
Aminbazar | 246 | 06:00 | 238 | 00:00 | Keranigonj | 244 | 05:00 | 236 | 00:00
Ashuganj | 241 | 06:00 | 235 | 11:00 | Khulna(S) | 245 | 04:00 | 230 | 13:00
Ashuganj-400 | 241 | 06:00 | 235 | 11:00 | Korerhat | 243 | 06:00 | 237 | 11:00
Baghabari | 241 | 06:00 | 231 | 18:30 | Madunaghat | 239 | 03:00 | 227 | 10:00
Barapukuria | 233 | 06:00 | 216 | 18:00 | Madunaghat-400 | 240 | 04:00 | 235 | 12:00
Barapukuria-230 | 233 | 06:00 | 216 | 18:00 | Maniknagar | 243 | 04:00 | 236 | 00:00
Barishal | 239 | 04:00 | 232 | 13:00 | Meghnaghat | 247 | 06:00 | 238 | 15:00
Bheramara | 239 | 04:00 | 222 | 18:00 | Meghnaghat-400 | 243 | 06:00 | 236 | 13:00
Bhulta | 244 | 04:00 | 237 | 11:00 | Mirsorai | 243 | 05:00 | 236 | 00:00
Bibiana | 244 | 05:00 | 236 | 11:00 | Rajshahi | 239 | 05:00 | 220 | 18:00
BIPTC | 239 | 05:00 | 221 | 13:00 | Rampal | 242 | 04:00 | 229 | 13:00
Bogura | 244 | 04:00 | 233 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 244 | 05:00 | 231 | 18:30 | Rampura | 244 | 06:00 | 236 | 11:00
Borhanuddin | 240 | 00:00 | 237 | 10:00 | Shikalbaha | 239 | 06:00 | 232 | 18:00
BSRM | 244 | 06:00 | 236 | 13:00 | Shyampur | 243 | 06:00 | 235 | 00:00
Cumilla(N) | 240 | 06:00 | 235 | 00:00 | Siddhirganj | 242 | 16:00 | 233 | 10:00
Faridpur | 239 | 05:00 | 231 | 13:00 | Sirajgonj | 244 | 04:00 | 238 | 13:00
Fenchuganj | 244 | 10:00 | 241 | 01:00 | Sreepur | 239 | 06:00 | 230 | 13:00
Feni | 244 | 06:00 | 237 | 00:00 | Tongi | 244 | 13:00 | 233 | 00:00
Ghorashal | 245 | 04:00 | 238 | 15:00
Ghorashal-230 | 234 | 06:00 | 218 | 13:00
Gopalganj | 237 | 04:00 | 230 | 12:00
GPH | 242 | 05:00 | 236 | 00:00
Haripur | 244 | 06:00 | 237 | 00:00
Hasnabad | 244 | 06:00 | 237 | 10:00
Hathazari | 238 | 04:00 | 234 | 18:00
Ishurdi | 241 | 06:00 | 224 | 13:00
Jhenaidah | 242 | 04:00 | 222 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 04:00 | 129 | 12:00 | Laksam | 140 | 04:00 | 136 | 00:00
Agargaon | 140 | 04:00 | 135 | 00:00 | Lakshmipur | 137 | 05:00 | 132 | 21:00
Agrabad | 140 | 04:00 | 134 | 12:00 | Lalbag | 137 | 06:00 | 132 | 00:00
AKS | 136 | 07:00 | 132 | 03:00 | Lalmonirhat | 132 | 02:00 | 122 | 08:00
Aminbazar | 140 | 05:00 | 135 | 00:00 | Madanganj | 137 | 09:00 | 134 | 01:00
Amnura | 139 | 03:00 | 128 | 18:00 | Madaripur | 142 | 03:00 | 138 | 12:00
Ashuganj | 141 | 06:00 | 138 | 12:00 | Madartek | 135 | 03:00 | 130 | 11:00
Bagerhat | 135 | 04:00 | 127 | 13:00 | Madunaghat | 140 | 04:00 | 137 | 11:00
Bajitpur | 134 | 04:00 | 130 | 12:00 | Magura | 139 | 03:00 | 123 | 13:00
Bakerganj | 138 | 03:00 | 135.5 | 12:00 | Mahasthangarh | 138 | 05:00 | 129 | 12:00
Bakulia | 139 | 07:00 | 135 | 11:00 | Maijdee | 136 | 04:00 | 132 | 00:00
Banani | 136 | 03:00 | 129 | 12:00 | Manikganj | 136 | 14:00 | 125 | 13:00
Bangabhaban | 141 | 06:00 | 136 | 12:00 | Maniknagar | 141 | 05:00 | 136 | 11:00
Barapukuria | 139 | 05:00 | 129 | 12:00 | Matarbari | 130 | 02:00 | 123 | 18:00
Barguna | 139 | 04:00 | 136 | 11:00 | Matuail | 139 | 05:00 | 136 | 00:00
Barishal | 140 | 02:00 | 135 | 13:00 | Metrorail_Motijheel | 141 | 05:00 | 136 | 11:00
Barishal-230 | 141 | 04:00 | 135 | 13:00 | Metrorail_Uttara | 138 | 01:00 | 134 | 00:00
Baroaulia | 138 | 03:00 | 135 | 12:00 | Millgate | 139 | 04:00 | 131 | 18:00
Baroirhat | 137 | 03:00 | 133 | 13:00 | Mirpur | 139 | 01:00 | 134 | 00:00
Bashundhara | 136 | 04:00 | 130 | 12:00 | Mirzapur | 136 | 04:00 | 131 | 00:00
BashundharaCement | 137 | 09:00 | 134 | 01:00 | Mithapukur | 137 | 04:00 | 128 | 12:00
Beanibazar | 136 | 05:00 | 132 | 12:00 | MI_Cement | 137.8 | 04:00 | 133 | 00:00
Benapole | 138 | 03:00 | 117 | 13:00 | Modern | N/A | N/A | N/A | N/A
Bhaluka | 136 | 04:00 | 131 | 12:00 | Mogbazar | 136 | 02:00 | 131 | 08:00
Bhandaria | 140 | 03:00 | 134 | 13:00 | Mongla | 137 | 06:00 | 128 | 13:00
Bhangura | 141 | 04:00 | 133 | 18:00 | Motijheel | 141 | 06:00 | 136 | 12:00
Bheramara | 140 | 05:00 | 129 | 18:00 | Muktagacha | 135 | 14:00 | 126 | 00:00
Bheramara(GK) | 139 | 04:00 | 129 | 18:00 | Munshiganj | 138 | 03:00 | 134 | 00:00
Bhulta | 132 | 05:00 | 129 | 00:00 | Muradnagar | 140 | 04:00 | 134 | 13:00
Bog-Sherpur | 139 | 04:00 | 131 | 18:00 | Mymensingh | 134 | 14:00 | 122 | 13:00
Bogura | 139 | 05:00 | 132 | 18:00 | Naogaon | 135 | 01:00 | 126 | 12:00
Bogura-230 | 139 | 04:00 | 132 | 12:00 | Narail | 140 | 04:00 | 127 | 13:00
Brahmanbaria | 135 | 04:00 | 131 | 12:00 | Narinda | 141 | 05:00 | 136 | 11:00
Cantonment | 140 | 04:00 | 134 | 12:00 | Narshingdi | 137 | 15:00 | 131 | 13:00
Chandina | 142 | 06:00 | 137 | 13:00 | Natore | 136 | 06:00 | 129 | 13:00
Chandpur | 139 | 04:00 | 136 | 00:00 | Nawabganj | 138 | 05:00 | 132 | 12:00
Chandraghona | 141 | 06:00 | 136 | 12:00 | Netrakona | 131 | 00:00 | 118 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 140 | 02:00 | 133 | 12:00 | New | 141 | 14:00 | 132 | 19:00
Charsaidpur | 138 | 06:00 | 135 | 00:00 | Niamatpur | 140 | 01:00 | 133 | 12:00
Chauddagram | 138 | 02:00 | 134 | 12:00 | Noapara | 138 | 04:00 | 120 | 13:00
Chhatak | 135 | 03:00 | 130 | 13:00 | Pabna | 139 | 04:00 | 131 | 13:00
Chowmuhani | 136 | 02:00 | 131 | 20:00 | Palashbari | 134 | 14:00 | 126 | 12:00
Chuadanga | 139 | 03:00 | 123 | 13:00 | Panchagarh | 138 | 04:00 | 126 | 19:00
Coxsbazar | 130 | 00:00 | 124 | 13:00 | Patiya | 138 | 07:00 | 133 | 13:00
Cumilla(N) | 140 | 05:00 | 137 | 13:00 | Patuakhali | 137 | 03:00 | 134 | 18:30
Cumilla(S) | 141 | 05:00 | 125 | 12:00 | Payra | 139 | 05:00 | 137 | 00:00
Daganbhuiyan | 138 | 04:00 | 132 | 13:00 | PHP | 137 | 05:00 | 132 | 13:00
Daudkandi | 138 | 05:00 | 133 | 12:00 | Postogola | 138 | 05:00 | 134 | 12:00
DhakaUniversity | 136 | 03:00 | 130 | 12:00 | Purbachal | 136 | 06:00 | 129 | 13:00
Dhamrai | 139 | 04:00 | 136 | 18:00 | Purbasadipur | 132 | 05:00 | 124 | 12:00
Dhanmondi | 140.7 | 06:00 | 137 | 00:00 | Rahanpur | 141 | 05:00 | 135 | 12:00
Dohazari | 136 | 08:00 | 131 | 12:00 | Rahanpur-400 | 141 | 03:00 | 135 | 12:00
Faridpur | 139 | 04:00 | 134 | 18:00 | Rahim | 139 | 05:00 | 135 | 12:00
Fatullah | 140 | 04:00 | 133 | 00:00 | Rajbari | 139 | 04:00 | 133 | 13:00
Fenchuganj | 139 | 06:00 | 137 | 00:00 | Rajendrapur | 137 | 04:00 | 131 | 13:00
Feni | 136 | 05:00 | 132 | 18:00 | Rajshahi | 138 | 03:00 | 128 | 13:00
Feni-230 | 137 | 04:00 | 133 | 11:00 | Rajshahi-230 | 138 | 04:00 | 127 | 13:00
Ghatail | 132 | 11:00 | 124 | 18:00 | Ramganj | 136 | 05:00 | 133 | 11:00
Ghorashal | 134 | 04:00 | 130 | 12:00 | Rampur | 139 | 03:00 | 134 | 12:00
Goalpara | 139 | 04:00 | 130 | 13:00 | Rampura | 136 | 05:00 | 130 | 12:00
Gollamari | 138 | 06:00 | 130 | 13:00 | Rangamati | 140 | 03:00 | 135 | 09:00
Gopalganj | 140 | 03:00 | 133 | 13:00 | Rangpur | 136 | 02:00 | 129 | 09:00
Gopalganj-400 | 143 | 04:00 | 139 | 12:00 | Ruppur | 141 | 04:00 | 131 | 18:00
Gulshan | 135 | 05:00 | 129 | 13:00 | Saidpur | 137 | 06:00 | 126 | 12:00
Halishahar | 141 | 05:00 | 135 | 12:00 | Satkhira | 136 | 05:00 | 126 | 13:00
Haripur | 139 | 04:00 | 136 | 00:00 | Satmasjid | 140 | 05:00 | 128 | 13:00
HaripurSBU | 140 | 05:00 | 136 | 00:00 | Savar | 138 | 04:00 | 132 | 00:00
Hasnabad | 138 | 04:00 | 134 | 00:00 | SevenRings | 134 | 04:00 | 129 | 13:00
Hathazari | 140 | 06:00 | 135 | 19:00 | ShahCement | 139 | 06:00 | 135 | 00:00
Hatirjheel | 136 | 04:00 | 130 | 13:00 | Shahjadpur | 141 | 01:00 | 135 | 13:00
Ishurdi | 141 | 04:00 | 131 | 13:00 | Shahjibazar | 136 | 06:00 | 132 | 13:00
Jaldhaka | 135 | 05:00 | 125 | 10:00 | Shahmirpur | 140 | 08:00 | 135 | 12:00
Jamalpur | 135 | 14:00 | 122 | 07:00 | Shariatpur | 142 | 03:00 | 136 | 13:00
Jashore | 138 | 01:00 | 119 | 13:00 | Sherpur | 132 | 14:00 | 117 | 07:00
Jhenaidah | 141 | 05:00 | 111 | 13:00 | Shikalbaha | 129 | 05:00 | 124 | 13:00
Jhenaidah-230 | 141 | 04:00 | 126 | 13:00 | Shikalbaha-230 | 141 | 06:00 | 130 | 14:00
Joydebpur | 133 | 05:00 | 127 | 13:00 | Shitalakhya | 137.8 | 05:00 | 133 | 00:00
Joypurhat | 136 | 04:00 | 128 | 12:00 | Sholosohor | 140 | 05:00 | 136 | 12:00
Juldah | 140 | 05:00 | 135 | 12:00 | Shyampur | 138 | 04:00 | 133 | 10:00
Kabirpur | 140 | 13:00 | 130 | 18:00 | Shyampur-230 | 141 | 06:00 | 136 | 00:00
Kachua | 140 | 03:00 | 137 | 00:00 | Siddhirganj | 140 | 02:00 | 137 | 00:00
Kaliakoir | 141 | 04:00 | 136 | 00:00 | Sirajganj | 139 | 03:00 | 131 | 18:30
Kallyanpur | 139 | 01:00 | 125 | 13:00 | Sonargaon | 139 | 06:00 | 135 | 14:00
Kalurghat | 141 | 04:00 | 137 | 10:00 | Sreemongol | 137 | 04:00 | 133 | 10:00
Kamrangirchar | 138 | 04:00 | 132 | 12:00 | Sreepur | 140 | 04:00 | 134 | 13:00
Kaptai | 140 | 03:00 | 134 | 09:00 | Srinagar | 138 | 06:00 | 133 | 00:00
Kasba | 140 | 04:00 | 134 | 13:00 | SSM | 141 | 00:00 | 140 | 01:00
Kazla | 140 | 03:00 | 135 | 13:00 | Sunamganj | 134 | 03:00 | 130 | 12:00
Keranigonj | 138 | 05:00 | 133 | 00:00 | Sylhet | 136 | 03:00 | 132 | 13:00
Khagrachori | 140 | 05:00 | 135 | 11:00 | Sylhet-132 | 135 | 00:00 | 134 | 09:00
Khulna | 135 | 01:00 | 129 | 13:00 | Tangail | 133 | 14:00 | 126 | 00:00
Khulna(S) | 138 | 05:00 | 130 | 13:00 | Taraganj | 136 | 06:00 | 126 | 18:00
Khulshi | 138 | 05:00 | 133 | 12:00 | Tasnim | 139 | 04:00 | 135 | 12:00
Kishoreganj | 133 | 03:00 | 129 | 12:00 | Thakurgaon | 136 | 04:00 | 125 | 19:00
Kodda | 138 | 13:00 | 130 | 00:00 | TK | 140 | 05:00 | 136 | 11:00
KSRM | 140 | 05:00 | 135 | 11:00 | Tongi | 142 | 13:00 | 133 | 21:00
Kulaura | 138 | 02:00 | 136 | 11:00 | Ullahpara | 140 | 05:00 | 132 | 13:00
Kurigram | 132 | 03:00 | 120 | 12:00 | Ullon | 135 | 03:00 | 130 | 11:00
Kushtia | 135 | 04:00 | 120 | 13:00 | Uttara | 139 | 04:00 | 134 | 11:00
UttaraNew | 138 | 01:00 | 134 | 00:00 | Zigatola | 138 | 03:00 | 133 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division