## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 11-01-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-01-2026 | during | 11-01-2026 | during | 11-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 331 | 349 | 412 | 412 | 392 | 392 | FGMO, Gas Shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 240 | 240 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 35 | 335 | 335 | 0 | 0 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 49 | 53.97 | 53.97 | 53.97 | 53.97 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 28 | 25 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 15.1 | 15.1 | 15.1 | 15.1 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 45 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 140 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 156 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 28 | 0 | 10 | 0 | 14 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 54 | 55 | 55 | 17 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 310 | 550 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 108 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1116 | 1647 | 5317.25 | 5307.25 | 2411.13 | 2471.13
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 10 | 0 | 12 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 | 46 | 46 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 167 | 167 | 150 | 150 | 150 | 150 | Plant availability less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 99 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 40 | 64 | 40 | 64 | Temp problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 51 | 51 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 20 | 0 | 100 | 100 | 12 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 7 | 21 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.24 | 0 | 1.79 | 0 | 1.25 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 38 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 976 | 1152 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 345 | 345 | 345 | 345 | 200 | 355 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1614.24 | 1868 | 3104.65 | 3123.86 | 2485.75 | 2747.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 209 | 202 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 335 | 305 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 318.81 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 36 | 34 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 5 | 49 | 55 | 55 | 55 | 55 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 117 | 86 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 8 | 51 | 51 | 51 | 51 | 51 | Machine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 50 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 24 | 24 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 106 | 108 | 163 | 163 | 115 | 115 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 114 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 118 | 112 | 76 | 82 | 76 | 82 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 13 | 24.5 | 24.5 | 24.5 | 24.5 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 62 | 0 | 20 | 0 | 30 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1009 | 1124 | 2366.75 | 2352.75 | 2110.56 | 1767.75
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-01-2026 | during | 11-01-2026 | during | 11-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 65 | 64 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 0.5 | 0 | 1.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 35 | 59 | 60 | 60 | 60 | 60 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 19 | 0 | 0 | 20 | 20 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 0 | 0 | 15.8 | 0 | 15.8 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 18 | 22 | 22 | 18 | 18 | To be dispatched 18 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 120 | 160 | 310.3 | 294 | 327 | 310
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 41 | 41 | 41 | 41 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 60 | 60 | 60 | 60 | Machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 102 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 75 | 75 | 80 | 80 | 81 | 81 | Machine problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 158 | 157 | 158 | 158 | 158 | 158 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 4 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 854 | 785 | 898 | 898 | 849 | 849
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 847 | 663 | 950 | 1000 | 950 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 369 | 369 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 76.08 | 0 | 42 | 0 | 41 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 780 | 1090 | 0 | 0 | 1108 | 1148 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1703.08 | 1753 | 2264 | 2272 | 2575.1 | 2624.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 256 | 500 | 0 | 0 | 622 | 622 | Machine Problem
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 132 | 130 | 136 | 136 | 136 | 70 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 350 | 540 | 622 | 622 | 575 | 575 | FGMO, U1 under maintenance
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 175 | 278 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.49 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1133.49 | 1668 | 1546 | 1545 | 1968 | 1901
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 49.4 | 0 | 24.25 | 0 | 25.83 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 198 | 176 | 214 | 214 | 192.6 | 192.6 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 364 | 0 | 0 | 0 | 0 | -
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.83 | 0 | 1.8 | 0 | 1.8 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 932.06 | 1470 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 54.15 | 0 | 20 | 0 | 27 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 100 | 0 | 50 | 0 | 50 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1752.44 | 2010 | 2603.13 | 2507.08 | 2118.31 | 2013.68
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5 | 0 | 1.8 | 0 | 1.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 23 | 0 | 8 | 0 | 8 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 141 | 0 | 42.15 | 0 | 42.15 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 169 | 105 | 313.95 | 262 | 279.95 | 228
System Total |  |  |  |  | 28823.2 | 28382.248 | 9471.25 | 11120 | 18724.03 | 18561.94 | 15124.8 | 14912.16
Forecast Scenario (11-01-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8880 |  | 0 |  | 8880
|  |  |  | 1:00 | 8110 |  | 0 |  | 8110
|  |  |  | 2:00 | 7770 |  | 0 |  | 7770
|  |  |  | 3:00 | 7510 |  | 0 |  | 7510
|  |  |  | 4:00 | 7360 |  | 0 |  | 7360
|  |  |  | 5:00 | 7080 |  | 0 |  | 7080
|  |  |  | 6:00 | 7710 |  | 0 |  | 7710
|  |  |  | 7:00 | 8370 |  | 0 |  | 8370
|  |  |  | 8:00 | 9410 |  | 0 |  | 9410
|  |  |  | 9:00 | 10160 |  | 0 |  | 10160
|  |  |  | 10:00 | 9910 |  | 0 |  | 9910
|  |  |  | 11:00 | 9750 |  | 0 |  | 9750
|  |  |  | 12:00 | 10090 |  | 0 |  | 10090
|  |  |  | 13:00 | 10570 |  | 0 |  | 10570
|  |  |  | 14:00 | 10450 |  | 0 |  | 10450
|  |  |  | 15:00 | 9670 |  | 0 |  | 9670
|  |  |  | 16:00 | 9460 |  | 0 |  | 9460
|  |  |  | 17:00 | 9720 |  | 0 |  | 9720
|  |  |  | 18:00 | 10990 |  | 0 |  | 10990
|  |  |  | 18:30 | 11000 |  | 0 |  | 11000
|  |  |  | 19:00 | 11100 |  | 0 |  | 11100
|  |  |  | 19:30 | 10970 |  | 0 |  | 10970
|  |  |  | 20:00 | 10950 |  | 0 |  | 10950
|  |  |  | 21:00 | 10690 |  | 0 |  | 10690
|  |  |  | 22:00 | 10140 |  | 0 |  | 10140
|  |  |  | 23:00 | 9240 |  | 0 |  | 9240
Probable Maximum Temperature: |  |  | 21.40°C
Probable Maximum Demand at Day Peak: |  |  | 10160.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11100.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11100.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 225.09 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:05 hrs on 11-01-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 10-01-2026 | [28 empty] | Date: | 10-01-2026 | [28 empty] | Date: | 10-01-2026 | [28 empty] | Date: | 10-01-2026 | [28 empty] | Date: | 10-01-2026 | [17 empty] | Date: | 10-01-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 11.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 990 | 0 | 0 | 110 | 0 | 320 | 0 | 0 | 0 | 193 | 34 | 0 | 109 | 0 | 0 | 13 | 0 | 92 | 0 | 0 | 0 | 310 | 0 | 0 | 34 | 20 | 151 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 156 | 0 | 19 | 0 | 52 | 0 | 0 | 0 | 4011.5 | 755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 895 | 0 | 0 | 0 | 921.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 138 | 220 | 0 | 256 | 550 | 0 | 4593.3 | 8604.8 | 97.01
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 10.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 950 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 193 | 34 | 0 | 110 | 0 | 0 | 13 | 0 | 82 | 0 | 0 | 0 | 305 | 0 | 0 | 34 | 10 | 146 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 156 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 3732.5 | 612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764 | 0 | 0 | 0 | 865.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 138 | 220 | 0 | 256 | 549 | 0 | 4200.15 | 7932.65 | 97.01
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 10.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 195 | 36 | 0 | 50 | 0 | 0 | 13 | 0 | 82 | 0 | 0 | 0 | 305 | 0 | 0 | 34 | 10 | 135 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 156 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 3542.5 | 568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 833.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 100 | 180 | 0 | 256 | 520 | 0 | 3927.94 | 7470.44 | 97.01
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 8.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 201 | 36 | 0 | 51 | 0 | 0 | 13 | 0 | 76 | 0 | 0 | 0 | 310 | 0 | 0 | 34 | 10 | 138 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 156 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 3575.5 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 768 | 0 | 0 | 0 | 829.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 100 | 180 | 0 | 256 | 480 | 0 | 3660.27 | 7235.77 | 97
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 9 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 193 | 0 | 0 | 51 | 0 | 0 | 13 | 0 | 74 | 0 | 0 | 0 | 310 | 0 | 0 | 34 | 10 | 139 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 157 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 3508 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 772 | 0 | 0 | 0 | 834.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 100 | 180 | 0 | 256 | 450 | 0 | 3480.98 | 6988.98 | 97
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 9 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 200 | 0 | 0 | 50 | 0 | 0 | 13 | 0 | 74 | 0 | 0 | 0 | 315 | 0 | 0 | 34 | 10 | 140 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 157 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 3543 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 777 | 0 | 0 | 0 | 833.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 100 | 180 | 0 | 256 | 350 | 0 | 3303.08 | 6846.08 | 97
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 9 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 35 | 145 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 925 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 200 | 0 | 0 | 112 | 0 | 0 | 12 | 0 | 84 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 60 | 155 | 0 | 0 | 0 | 57 | 30 | 0 | 0 | 157 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 3944 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 0 | 0 | 827.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 130 | 220 | 0 | 296 | 350 | 0 | 3579.57 | 7523.57 | 96.99
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 290 | 0 | 0 | 1 | 0 | 9 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 46 | 0 | 35 | 145 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1000 | 1 | 0 | 16 | 0 | 310 | 0 | 36 | 0 | 198 | 27 | 0 | 112 | 0 | 0 | 12 | 0 | 78 | 0 | 2 | 0 | 305 | 0 | 0 | 41 | 60 | 151 | 0 | 9 | 0 | 75 | 30 | 0 | 0 | 156 | 0 | 4 | 5 | 109 | 0 | 0.51 | 0 | 4067.64 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 762 | 0 | 0 | 0 | 822.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 | 0.13 | 173 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 133 | 220 | 0 | 400 | 345 | 0 | 3868.43 | 7936.07 | 96.99
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 290 | 0 | 0 | 5 | 35 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0.73 | 46 | 0 | 13 | 145 | 0 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 0 | 1120 | 7 | 0 | 100 | 0 | 315 | 0 | 51 | 0 | 204 | 25 | 0 | 112 | 0 | 0 | 12 | 0 | 92 | 0 | 15 | 0 | 315 | 0 | 0 | 41 | 60 | 148 | 0 | 17 | 0 | 75 | 30 | 0 | 0 | 157 | 0 | 19 | 35 | 108 | 0 | 5.45 | 0 | 4477.18 | 661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 855 | 0 | 0 | 0 | 988.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.13 | 10 | 0 | 0 | 3.47 | 150 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0.3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.4 | 9 | 0.09 | 0 | 281 | 133 | 220 | 0 | 430 | 382 | 0 | 4495.6 | 8972.78 | 96.99
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 300 | 0 | 0 | 8 | 52 | 28 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 1.58 | 46 | 0 | 7 | 200 | 0 | 0 | 18 | 0 | 0 | 160 | 0 | 0 | 0 | 1028 | 11 | 0 | 117 | 0 | 305 | 0 | 5 | 0 | 199 | 32 | 0 | 50 | 0 | 0 | 11 | 0 | 102 | 0 | 33 | 0 | 310 | 0 | 0 | 41 | 60 | 139 | 0 | 17 | 0 | 75 | 30 | 0 | 0 | 157 | 0 | 19 | 35 | 95 | 0 | 7.35 | 0 | 4401.93 | 789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 850 | 0 | 0 | 0 | 1091.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.08 | 45 | 0 | 0 | 9.16 | 148 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 21 | 0.21 | 0 | 196 | 120 | 180 | 0 | 436 | 470 | 0 | 4774.98 | 9176.91 | 96.98
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 300 | 0 | 0 | 21 | 70 | 28 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 12 | 25 | 2.36 | 46 | 0 | 5 | 230 | 0 | 0 | 6 | 0 | 0 | 160 | 0 | 0 | 0 | 990 | 15 | 0 | 118 | 0 | 290 | 0 | 5 | 0 | 191 | 33 | 0 | 50 | 0 | 0 | 11 | 0 | 100 | 0 | 48 | 0 | 315 | 0 | 0 | 42 | 60 | 142 | 0 | 17 | 0 | 75 | 30 | 0 | 0 | 157 | 0 | 19 | 35 | 90 | 0 | 0 | 0 | 4378.36 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.55 | 780 | 0 | 0 | 0 | 1026.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.62 | 76 | 0 | 0 | 36.12 | 149 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 2.94 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 1.4 | 49 | 0.34 | 0 | 169 | 100 | 180 | 0 | 282 | 450 | 0 | 4591.71 | 8970.07 | 96.98
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 335 | 0 | 0 | 26 | 70 | 28 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 2.82 | 46 | 0 | 7 | 345 | 0 | 0 | 6 | 0 | 0 | 161 | 0 | 0 | 0 | 953 | 14 | 0 | 117 | 0 | 305 | 0 | 5 | 0 | 198 | 33 | 0 | 50 | 0 | 0 | 11 | 0 | 112 | 0 | 55 | 0 | 310 | 0 | 0 | 42 | 60 | 137 | 0 | 17 | 0 | 75 | 30 | 0 | 0 | 159 | 0 | 19 | 35 | 68 | 0 | 0 | 0 | 4499.82 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.69 | 763 | 0 | 0 | 0 | 930.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.58 | 92 | 0 | 0 | 49.8 | 164 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 4.45 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 4.7 | 88 | 0.44 | 0 | 171 | 100 | 180 | 0 | 256 | 350 | 0 | 4495.11 | 8994.93 | 96.98
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 335 | 0 | 0 | 28 | 70 | 28 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 25 | 3.24 | 46 | 0 | 7 | 345 | 0 | 0 | 6 | 0 | 0 | 167 | 0 | 0 | 0 | 976 | 19 | 0 | 117 | 0 | 335 | 0 | 8 | 5 | 209 | 36 | 0 | 106 | 0 | 0 | 13 | 0 | 118 | 0 | 62 | 0 | 315 | 0 | 0 | 42 | 60 | 157 | 0 | 17 | 0 | 75 | 30 | 0 | 0 | 158 | 0 | 19 | 35 | 65 | 1 | 0 | 0 | 4713.24 | 847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.08 | 780 | 0 | 0 | 0 | 932.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.4 | 100 | 0 | 0 | 54.15 | 198 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.83 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 5 | 141 | 0.49 | 0 | 175 | 132 | 220 | 0 | 256 | 350 | 0 | 4758.01 | 9471.25 | 96.97
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 17 | 32 | 0 | 0 | 0 | 355 | 0 | 45 | 210 | 0 | 0 | 28 | 120 | 28 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 25 | 0.69 | 46 | 0 | 18 | 345 | 0 | 0 | 15 | 0 | 0 | 167 | 0 | 0 | 0 | 1108 | 18 | 0 | 143 | 0 | 315 | 0 | 44 | 28 | 192 | 36 | 0 | 105 | 0 | 0 | 13 | 0 | 130 | 0 | 58 | 0 | 325 | 0 | 0 | 42 | 60 | 141 | 10 | 17 | 0 | 75 | 30 | 0 | 0 | 157 | 0 | 19 | 56 | 65 | 2 | 0 | 0 | 5072.69 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.56 | 840 | 0 | 0 | 0 | 1032.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.57 | 98 | 0 | 0 | 50.26 | 214 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 4.43 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 3.8 | 124 | 0.48 | 0 | 216 | 132 | 220 | 0 | 288 | 350 | 0 | 4958.27 | 10030.96 | 96.97
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 28 | 0 | 45 | 0 | 31 | 33 | 0 | 0 | 0 | 285 | 0 | 35 | 145 | 0 | 0 | 23 | 142 | 28 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 50 | 25 | 2.54 | 46 | 0 | 18 | 345 | 0 | 0 | 19 | 0 | 0 | 167 | 0 | 0 | 0 | 1100 | 15 | 0 | 147 | 0 | 290 | 0 | 44 | 48 | 192 | 33 | 0 | 104 | 0 | 0 | 13 | 0 | 116 | 0 | 44 | 0 | 310 | 0 | 0 | 42 | 60 | 144 | 8 | 17 | 0 | 75 | 30 | 0 | 0 | 157 | 0 | 19 | 56 | 65 | 2 | 0 | 0 | 4965.54 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.98 | 892 | 0 | 0 | 0 | 1021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.56 | 85 | 0 | 0 | 42.74 | 187 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 3.68 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 4.6 | 127 | 0.37 | 0 | 216 | 100 | 180 | 0 | 256 | 400 | 0 | 4818.93 | 9784.47 | 96.97
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 39 | 0 | 58 | 0 | 45 | 0 | 35 | 32 | 0 | 0 | 0 | 280 | 0 | 35 | 29 | 0 | 0 | 17 | 142 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 50 | 25 | 0.44 | 46 | 0 | 7 | 345 | 0 | 0 | 19 | 0 | 0 | 167 | 0 | 0 | 0 | 1055 | 11 | 0 | 153 | 0 | 295 | 0 | 44 | 49 | 191 | 33 | 0 | 103 | 0 | 0 | 13 | 0 | 104 | 0 | 30 | 0 | 310 | 0 | 0 | 42 | 60 | 96 | 6 | 17 | 0 | 75 | 30 | 0 | 0 | 156 | 0 | 19 | 59 | 62 | 1 | 0 | 12 | 4849.44 | 847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 845 | 0 | 0 | 0 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.69 | 66 | 0 | 0 | 28.32 | 171 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 2.9 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 3.3 | 58 | 0.24 | 0 | 179 | 100 | 180 | 0 | 250 | 380 | 0 | 4451.45 | 9300.89 | 96.96
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 51.6 | 0 | 69 | 0 | 30 | 4 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 40 | 0 | 0 | 9 | 108 | 25.8 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 12 | 12 | 0.88 | 46 | 0 | 8 | 345 | 0 | 0 | 6 | 0 | 0 | 167 | 0 | 0 | 0 | 1050 | 6 | 0 | 143 | 0 | 330 | 0 | 44 | 49 | 211 | 30 | 0 | 103 | 0 | 0 | 13 | 0 | 104 | 0 | 12 | 0 | 320 | 0 | 0 | 42 | 60 | 104 | 2 | 17 | 0 | 78 | 30 | 0 | 0 | 156 | 0 | 19 | 59 | 63 | 0 | 0 | 18 | 4703.28 | 847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.12 | 833 | 0 | 0 | 0 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.16 | 30 | 0 | 0 | 12.69 | 177 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 0.89 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 1.7 | 39 | 0.11 | 0 | 189 | 100 | 180 | 0 | 250 | 320 | 0 | 4330.67 | 9033.95 | 96.96
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 52.3 | 0 | 69 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 435 | 0 | 0 | 40 | 0 | 0 | 1 | 134 | 25.8 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 12 | 12 | 0.09 | 46 | 0 | 11 | 345 | 0 | 0 | 6 | 0 | 0 | 167 | 0 | 0 | 0 | 1051 | 1 | 5 | 143 | 0 | 305 | 0 | 44 | 47 | 200 | 30 | 0 | 104 | 0 | 0 | 13 | 0 | 110 | 0 | 2 | 0 | 320 | 0 | 0 | 42 | 60 | 109 | 0 | 17 | 0 | 75 | 30 | 0 | 0 | 157 | 0 | 19 | 59 | 64 | 0 | 0 | 18 | 4839.19 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.68 | 895 | 0 | 0 | 0 | 1089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 5 | 0 | 0 | 1.8 | 185 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.17 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.3 | 6 | 0.02 | 0 | 196 | 100 | 180 | 0 | 271 | 310 | 0 | 4506.77 | 9345.96 | 96.96
18:00 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 49.7 | 3 | 75 | 0 | 140 | 43 | 30 | 139 | 0 | 0 | 0 | 450 | 0 | 30 | 42 | 0 | 0 | 0 | 142 | 26 | 14 | 0 | 0 | 0 | 15 | 0 | 0 | 3 | 0 | 10 | 0 | 12 | 38 | 0 | 46 | 5 | 17 | 345 | 0 | 0 | 6 | 0 | 29 | 167 | 0 | 0 | 0 | 1142 | 0 | 110 | 145 | 0 | 290 | 0 | 44 | 47 | 196 | 33 | 0 | 106 | 14 | 0 | 13 | 0 | 114 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 60 | 103 | 0 | 0 | 0 | 75 | 30 | 0 | 0 | 157 | 0 | 19 | 58 | 64 | 0 | 0 | 18 | 5425.7 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995 | 0 | 0 | 0 | 1424 | 0 | 0 | 0 | 15 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 120 | 220 | 0 | 340 | 350 | 0 | 5270 | 10695.7 | 96.96
19:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 45.8 | 30 | 130 | 0 | 145 | 15 | 55 | 153 | 0 | 0 | 0 | 470 | 0 | 35 | 35 | 0 | 0 | 0 | 126 | 25 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 38 | 0 | 46 | 14 | 20 | 345 | 0 | 0 | 6 | 0 | 90 | 167 | 0 | 0 | 0 | 1147 | 0 | 100 | 117 | 0 | 295 | 0 | 51 | 49 | 183 | 34 | 11 | 106 | 100 | 0 | 13 | 0 | 112 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 60 | 99 | 0 | 4 | 0 | 75 | 30 | 0 | 0 | 157 | 0 | 19 | 59 | 65 | 0 | 0 | 18 | 5633.8 | 663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085 | 0 | 0 | 0 | 1447 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 130 | 220 | 0 | 495 | 455 | 0 | 5415 | 11048.8 | 96.95
19:30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 49 | 54 | 140 | 0 | 45 | 15 | 55 | 156 | 0 | 0 | 0 | 550 | 0 | 35 | 35 | 0 | 0 | 0 | 108 | 25 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 46 | 0 | 21 | 345 | 0 | 0 | 0 | 0 | 99 | 167 | 0 | 0 | 0 | 1152 | 0 | 50 | 86 | 0 | 305 | 0 | 51 | 49 | 202 | 34 | 0 | 108 | 114 | 0 | 13 | 0 | 112 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 60 | 102 | 0 | 4 | 0 | 75 | 30 | 0 | 0 | 157 | 0 | 19 | 59 | 64 | 0 | 0 | 18 | 5584 | 663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1090 | 0 | 0 | 0 | 1470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 130 | 220 | 0 | 500 | 540 | 0 | 5536 | 11120 | 96.95
20:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 47.5 | 54 | 140 | 0 | 45 | 15 | 55 | 157 | 0 | 0 | 0 | 540 | 0 | 35 | 104 | 0 | 0 | 0 | 98 | 21.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 46 | 0 | 24 | 345 | 0 | 0 | 0 | 0 | 100 | 167 | 0 | 0 | 0 | 1145 | 0 | 50 | 76 | 0 | 290 | 0 | 51 | 49 | 215 | 34 | 0 | 108 | 114 | 0 | 13 | 0 | 106 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 60 | 103 | 0 | 4 | 0 | 80 | 30 | 0 | 0 | 157 | 0 | 19 | 59 | 65 | 0 | 0 | 18 | 5613 | 663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 0 | 0 | 1440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 130 | 220 | 0 | 500 | 535 | 0 | 5482 | 11095 | 96.95
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 45.1 | 0 | 95 | 0 | 15 | 0 | 17 | 148 | 0 | 0 | 0 | 470 | 0 | 17 | 335 | 0 | 0 | 0 | 52 | 21.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 46 | 0 | 24 | 345 | 0 | 0 | 0 | 0 | 93 | 167 | 0 | 0 | 0 | 1145 | 0 | 10 | 76 | 0 | 295 | 0 | 51 | 49 | 192 | 34 | 0 | 106 | 108 | 0 | 13 | 0 | 108 | 0 | 0 | 0 | 305 | 0 | 0 | 41 | 60 | 99 | 0 | 4 | 0 | 80 | 30 | 0 | 0 | 157 | 0 | 19 | 59 | 64 | 0 | 0 | 0 | 5379.6 | 662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085 | 0 | 0 | 0 | 1443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 136 | 220 | 0 | 500 | 530 | 0 | 5472 | 10851.6 | 96.94
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 28.5 | 0 | 35 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 0 | 385 | 0 | 0 | 335 | 0 | 0 | 0 | 10 | 21.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 46 | 0 | 27 | 345 | 0 | 0 | 0 | 0 | 17 | 167 | 0 | 0 | 0 | 1140 | 0 | 0 | 76 | 0 | 290 | 0 | 51 | 48 | 191 | 34 | 0 | 108 | 51 | 0 | 13 | 0 | 110 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 60 | 89 | 0 | 4 | 0 | 78 | 30 | 0 | 0 | 157 | 0 | 19 | 35 | 64 | 0 | 0 | 0 | 4855 | 862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085 | 0 | 0 | 0 | 1333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 136 | 220 | 0 | 500 | 540 | 0 | 5537 | 10392 | 96.94
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 21.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 34 | 345 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 1150 | 0 | 0 | 8 | 0 | 290 | 0 | 51 | 18 | 192 | 34 | 0 | 110 | 0 | 0 | 13 | 0 | 100 | 0 | 0 | 0 | 305 | 0 | 0 | 41 | 60 | 32 | 0 | 4 | 0 | 78 | 30 | 0 | 0 | 157 | 0 | 19 | 16 | 62 | 0 | 0 | 0 | 4426.3 | 871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 0 | 0 | 0 | 1328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 136 | 180 | 0 | 506 | 535 | 0 | 5229 | 9655.3 | 94.94
Total KWH | 0 | 41866 | 0 | 0 | 0 | 0 | 0 | 0 | 8143200 | 0 | 0 | 353160 | 119520 | 759024 | 0 | 510851 | 120688 | 290122 | 744480 | 0 | 0 | 0 | 8750000 | 0 | 233198 | 5501184 | 0 | 0 | 167192 | 1363200 | 478200 | 327600 | 0 | 0 | 0 | 23084 | 0 | 0 | 48960 | 0 | 21580 | 0 | 256320 | 402240 | 16422 | 1106460 | 20910 | 335040 | 6363636.36 | 0 | 0 | 144000 | 0 | 405636 | 3836837 | 0 | 0 | 0 | 24529088 | 113265 | 344581 | 1839999 | 0 | 7684100 | 0 | 741275 | 495840 | 4943000 | 699120 | 21120 | 2159810 | 470880 | 0 | 295780 | 0 | 2354880 | 0 | 364655 | 0 | 7596500 | 0 | 0 | 949000 | 1196520 | 2892355 | 28760 | 208536 | 0 | 1344000 | 674592 | 0 | 0 | 3400130 | 0 | 331200 | 804000 | 1549440 | 5100 | 18560 | 123600 | 109064296.36 | 16235636 | 36576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 465120 | 21243700 | 0 | 0 | 0 | 25270909 | 0 | 0 | 0 | 37152 | 52608 | 0 | 0 | 0 | 0 | 286684 | 616040 | 0 | 0 | 282736 | 4192273 | 0 | 0 | 0 | 0 | 0 | 8455636 | 0 | 24900 | 0 | 0 | 171549 | 116734 | 317894 | 0 | 0 | 0 | 26229.6 | 688320 | 2793 | 0 | 5498000 | 2689000 | 5105440 | 0 | 8181133 | 10887272.73 | 0 | 110884335.33 | 219948631.69

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 10-01-2026
Power Supply Scenario
| Day Peak Generation |  |  | 9471.25 | MW | 12:00 Hr. | Energy Generated |  |  | 219.9486 |  | MKWHr.
| Day Peak Demand |  |  | 9471.25 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11120 | MW | 19:30 Hr. | Energy Demand |  |  | 219.9486 |  | MKWHr.
| Evening Peak Demand |  |  | 11120 | MW | 19:30 Hr. | Maximum Temperature |  |  | 24.5 |  | °C
| Minimum Generation of the Day |  |  | 6846.08 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 675.21 |  | MMCFD
| Maximum Generation of the Day |  |  | 11120 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 5.8083 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 23.2002 | 0 | 4.5361 | 0 | 0 | 0.16719 | 0 | 0 | 27.9035 | Gas | 86.521 | Gas | 306936371.2
| Chattogram Zone |  |  | 4.1719 | 30.8927 | 1.2738 | 0 | 1.1065 | 0.12969 | 0 | 0.04896 | 37.6235 | Coal | 76.7028 | Coal | 509949255.6642
| Cumilla Zone |  |  | 18.8589 | 0 | 0.83658 | 0 | 0 | 0.36466 | 2.3549 | 0 | 22.415 | HFO | 8.4845 | HFO | 146288931.5
| Mymensingh Zone |  |  | 1.5494 | 0 | 1.2588 | 0 | 0 | 0.02366 | 0 | 0 | 2.8319 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 18.2616 | 0 | 0 | 0 | 0 | 0.02876 | 0 | 0 | 18.2904 | Hydro | 1.1065 | Hydro | 110646
| Khulna Zone |  |  | 0.036576 | 21.2437 | 0 | 0 | 0 | 0.46512 | 16.2356 | 0 | 37.981 | Solar | 3.2235 | Solar | 49411557.87
| Barishal Zone |  |  | 7.7944 | 24.5664 | 0 | 0 | 0 | 0.002793 | 0 | 0 | 32.3636 | Import | 43.8614 | Import | 264100630.84
| Rajshahi Zone |  |  | 12.6479 | 0 | 0.08976 | 0 | 0 | 1.2104 | 25.2709 | 0 | 39.2189 | Wind | 0.04896 | Wind | 720201.6
| Rangpur Zone |  |  | 0 | 0 | 0.48944 | 0 | 0 | 0.83128 | 0 | 0 | 1.3207
| Total |  |  | 86.521 | 76.7028 | 8.4845 | 0 | 1.1065 | 3.2235 | 43.8614 | 0.04896 | 219.9486
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 306936371.2 |  | Hydro | 110646
|  |  |  | Coal | 509949255.6642 |  | Solar | 49411557.87
|  |  |  | HFO | 146288931.5 |  | Import | 264100630.84
|  |  |  | HSD | 0 |  | Wind | 720201.6
[5 empty] | Total: | 127,75,17,594 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 16.2356 | Peak Hr Flow | 663.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 38465781.83 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 25.2709 | Peak Hr Flow | 1470.00 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1951 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.3549 | Peak Hr Flow | 112.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2315 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 43.8614 | Peak Hr Flow | 2245.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3928
|  |  |  | Chattogram |  | 0 |  | 1126
|  |  |  | Cumilla |  | 0 |  | 966
|  |  |  | Mymensingh |  | 0 |  | 914
|  |  |  | Sylhet |  | 0 |  | 411
|  |  |  | Khulna |  | 0 |  | 1303
|  |  |  | Barishal |  | 0 |  | 342
|  |  |  | Rajshahi |  | 0 |  | 1023
|  |  |  | Rangpur |  | 0 |  | 728
|  |  |  | Total |  | 0 |  | 10741
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:09 | 10:15 | Chandraghona 132/33kV S/S TR-01(406T) LT Scheduled S/D Due to BPDB 33KV Bus Maintenances | [7 empty] | 17.0MW load
|  |  | Work. | [7 empty] | interrup.
| 08:10 | 10:15 | Chandraghona 132/33kV S/S TR-01(406T) HT Scheduled S/D Due to BPDB 33KV Bus Maintenance | [7 empty] | 17.0MW load
|  |  | Work. | [7 empty] | interrup.
| 08:11 | 12:15 | Sunamganj 132/33kV S/S Tr-1 HT Scheduled S/D Due to Tan Delta Test | [7 empty] | 3.0MW load
interrup.
| 08:12 | 18:20 | Agargaon 230/132kV S/S 230kV Transformer-1 ( 705T1) HT Scheduled S/D Due to Annual
Maintenance
| 08:12 | 18:22 | Agargaon 230/132kV S/S 230kV Transformer-1 ( 705T1) LT Scheduled S/D Due to Annual
Maintenance
| 08:19 | 17:15 | Fenchuganj 230/132/33kV S/S 230 KV Bus-1 Scheduled S/D Due to Annual Maintenance
| 08:21 |  | Patuakhali-Payra 132kV Ckt-1 Project Work S/D from Patuakhali 132/33kV end Due to | [7 empty] | 27.0MW load
|  |  | Project work | [7 empty] | interrup.
Patuakhali 132/33kV
end
| 08:29 | 18:10 | Bhaluka 132/33kV S/S 02. Transformer- 02 HT Scheduled S/D Due to Annual maintenance | [7 empty] | 10.0MW load
interrup.
| 08:29 | 18:11 | Bhaluka 132/33kV S/S 02. Transformer- 02 LT Scheduled S/D Due to Annual maintenance | [7 empty] | 10.0MW load
interrup.
| 08:30 | 16:10 | Magura-Narail 132kV Ckt-2 Scheduled S/D from Narail 132/33kV end Due to Annual
Maintenance and from Magura 132/33kV end Due to Annual Maintenance.
| 08:30 | 17:25 | Pabna 132/33kV S/S T-1 LT Scheduled S/D Due to Annual Maintenance Work.
| 08:30 | 16:52 | Dhamrai-Kaliakoir 132 kV Ckt-2 Scheduled S/D from Dhamrai 132/33kV end Due to Due to
annual maintenance.
| 08:31 | 17:25 | Pabna 132/33kV S/S T-1 HT Scheduled S/D Due to Annual Maintenance Work.
| 08:32 | 17:21 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) HT Scheduled S/D Due to TR-03 Shutdown for
Annual Maintenance Work
| 08:32 | 17:22 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) LT Scheduled S/D Due to TR-03 Shutdown for
Annual Maintenance Work
| 08:35 | 16:30 | Jamalpur United (20MW)- Sherpur 132kV Ckt-2 Scheduled S/D from Sherpur 132/33kV end Due
to Annual maintenance
| 08:52 | 15:30 | Cumilla(N)-Kachua 132 kV Ckt-2 Scheduled S/D from Kachua 230/132/33kV end Due to Annual
maintenance
| 08:52 | 15:34 | Haripur-Siddirganj 230kV Ckt-2 Scheduled S/D from Siddhirganj 132/33kV end Due to Annual
Maintenance
| 08:53 | 15:30 | Cumilla(S)-Kachua 132 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
Annual maintenance
| 09:01 | 17:24 | Rajshahi 230/132/33kV S/S 230 Kv BIPTC Ckt-02 Scheduled S/D Due to Annual maintenance
| 09:02 |  | Kaliakoir-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Annual
maintenance
| 09:05 | 12:17 | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D Due to 33kv bus maintenance (wzpdl) | [7 empty] | 30.0MW load
interrup.
| 09:05 | 16:02 | Bhangura 132/33kV S/S Tr-1(403T) LT Scheduled S/D Due to Annual Maintenance 33kv side | [7 empty] | 8.0MW load
interrup.
| 09:06 | 12:16 | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D Due to 33 kv bus maintenance | [7 empty] | 30.0MW load
interrup.
| 09:07 | 19:04 | Aminbazar-Kallyanpur 132kV Ckt-1 Scheduled S/D from Kallyanpur 132/33kV end Due to Dead
line checking work.
| 09:09 | 16:03 | Bhangura 132/33kV S/S Tr-2(413T) LT Scheduled S/D Due to Annual Maintenance 33kv side | [7 empty] | 8.0MW load
interrup.
| 09:09 |  | Bogura(New)-Naogaon 132 kV Ckt-1 Project Work S/D from Bogura 230/132kV end.
| 09:09 | 16:01 | Bhangura 132/33kV S/S Tr-1(403T) HT Scheduled S/D Due to Annual Maintenance 33kv side | [7 empty] | 8.0MW load
interrup.
| 09:10 | 16:03 | Bhangura 132/33kV S/S Tr-2(413T) HT Scheduled S/D Due to Annual Maintenance 33kv side | [7 empty] | 8.0MW load
interrup.
|  | 09:12 | Naogaon 132/33kV S/S Main Bus is restored.
| 09:13 | 17:24 | HVDC Bheramera- Rajshahi 230kV Ckt-2 Scheduled S/D from BIPTC end Due to Shutdown has
been taken from Rajshahi end.
| 09:20 | 11:27 | Jamalpur 132/33kV S/S T-2 HT Scheduled S/D Due to 132KV CT Conductor Temperature Remove | [7 empty] | 20.0MW load
|  |  | Work. | [7 empty] | interrup.
| 09:20 | 11:27 | Jamalpur 132/33kV S/S T-2 LT Scheduled S/D Due to 132KV CT Conductor Temperature Remove | [7 empty] | 20.0MW load
|  |  | Work. | [7 empty] | interrup.
| 09:20 | 15:13 | BSRM 230/33kV S/S GPH Ispat Ckt. -01 Scheduled S/D Due to 0
| 09:27 | 15:12 | GPH 230/33kV S/S BSRM CKT-1 Scheduled S/D Due to shedule shutdown
| 09:29 | 18:38 | Chattak-Sylhet 132 kV Ckt-2 Scheduled S/D from Chhatak 132/33kV end Due to For Dead Line
Checking.
| 09:30 | 17:42 | Gopalganj 400/132kV S/S 400kV Amtoli Ckt-2 Scheduled S/D Due to Annual Maintenance
| 09:34 | 14:24 | Khulna (S)-Rampal Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end Due to Annual
Maintenance Work.
| 09:38 | 16:35 | Dhamrai 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Due to annual maintenance.
| 09:38 | 16:34 | Dhamrai 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Due to annual maintenance.
| 09:39 |  | Aminbazar 400/230/132kV S/S ATR-01 HT Scheduled S/D Due to Scheduled shutdown
| 09:40 |  | Aminbazar 400/230/132kV S/S ATR-01 LT Scheduled S/D Due to Scheduled shutdown
| 09:40 | 18:26 | Netrakona 132/33kV S/S Main Bus Scheduled S/D Due to A/M
| 09:43 | 17:18 | Kurigram-Lalmonirhat 132kV Ckt-1 Scheduled S/D from Kurigram 132/33kV end Due to annual
maintance
|  | 09:43 | Mymensingh 132/33kV S/S Bus B is restored.
| 09:46 |  | Joypurhat 132/33kV S/S Naogaon Ckt.-2 Forced S/D Due to Load shift to line ckt-1.
| 09:49 | 18:37 | Chattak-Sylhet 132 kV Ckt-2 Scheduled S/D from Sylhet 132/33kV end Due to dead line
checking
| 09:55 | 18:08 | Bhaluka 132/33kV S/S Sreepur Ckt- 01 Scheduled S/D Due to S/D taken by Shripur grid for
annual maintenance purpose.
| 09:55 | 19:25 | Sylhet 132/33kV S/S Sylhet-90MW P/S Scheduled S/D Due to OPGW change
| 10:05 | 18:07 | Sreepur 230/132/33kV S/S Sreepur-Valuka Ckt-1 Scheduled S/D Due to Annual Maintenance
| 10:07 | 14:29 | Barapukuria 230/132/33kV S/S 132 KV Bus A Project Work S/D Due to Rangpur Bay bus loop
upgradetion
|  | 10:13 | Coxsbazar 132/33kV S/S 405T-T1 HT is restored.
| 10:19 | 20:16 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 Scheduled S/D Due to Annual
Maintenance work
| 10:20 | 20:16 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 Scheduled S/D Due to Annual
Maintenance work
| 10:25 | 11:44 | Faridpur 132/33kV S/S Transformer-3 HT Scheduled S/D Due to Maintenance | [7 empty] | 5.0MW load
interrup.
| 10:25 | 11:46 | Faridpur 132/33kV S/S Transformer-3 LT Scheduled S/D Due to Maintenance | [7 empty] | 5.0MW load
interrup.
| 10:33 | 13:45 | Keraniganj-Sreenagar 132kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to As
instruction of NLDC.
| 10:48 | 13:45 | Keraniganj-Sreenagar 132kV Ckt-1 Scheduled S/D from Srinagar 132/33kV end Due to Purpose
OPGW wire cutting.
| 10:50 | 11:22 | Naogaon 132/33kV S/S T-1 LT Forced S/D Due to 132 kV Transformer-1 CB maintenance (Pole
discrepancy problem)
| 10:50 | 11:19 | Naogaon 132/33kV S/S T-1 HT Forced S/D Due to 132 kV Transformer-1 CB maintenance (Pole
discrepancy problem)
| 12:00 |  | Day peak generation 9469 MW
| 12:09 | 17:03 | Kodda-Rajendrapur 132kV Ckt-2 Forced S/D from Rajendrapur 132/33kV end Due to Sreepur
end redhot problem, they taken shutdown.
|  | 12:09 | Kodda-Rajendrapur 132kV Ckt-1 is restored.
| 13:10 | 16:35 | Sreepur 230/132/33kV S/S 132 kV BUS-1 Forced S/D Due to rajendrapur-1 Redhot Maintenance.
| 13:10 | 16:50 | Faridpur 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Maintanance | [7 empty] | 40.0MW load
interrup.
| 13:11 | 16:50 | Faridpur 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Maintanance | [7 empty] | 40.0MW load
interrup.
|  | 13:15 | Natore-Rajshahi 132kV Ckt-1 is restored.
|  | 13:17 | Rajshahi 132/33kV S/S Transformer T-1(405T) HT is restored.
| 13:21 | 15:09 | Feni 230/132kV S/S ATR-1 LT Scheduled S/D Due to Due to oil leakage at 33 kv neutral
bushing
| 13:21 | 15:08 | Feni 230/132kV S/S ATR-1 HT Scheduled S/D Due to Due to oil leakage at 33kv neutral
bushing.
|  | 13:23 | Narail 132/33kV S/S Capacitor Bank Bay is restored.
|  | 13:30 | Rajshahi-Rajshahi(New) 132kV Ckt-1 is restored.
|  | 13:34 | Rajshahi 132/33kV S/S Transformer T-2(415T) HT is restored.
| 13:35 |  | Sonargaon 132/33kV S/S Bus-Coupler Forced S/D Due to A bus and B bus individual
|  | 13:35 | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT is restored.
|  | 13:42 | Rajshahi-Rajshahi(New) 132kV Ckt-2 is restored.
| 13:43 | 20:31 | Fenchuganj-Fenchuganj 132 kV Ckt-4 Project Work S/D from Fenchuganj 230/132/33kV end Due
to OFCN Work
|  | 13:52 | Natore-Rajshahi 132kV Ckt-2 is restored.
|  | 14:03 | Rajshahi 132/33kV S/S 132 kV PPP 50 Mw is restored.
|  | 14:18 | Baroaulia-Khulshi 132 kV Ckt-1 is restored.
|  | 14:19 | Khulshi 132/33kV S/S Main Bus is restored.
|  | 14:38 | Bogura(New)-Naogaon 132 kV Ckt-2 is restored.
|  | 14:52 | AKSML-Khulshi 132kV Ckt-1 is restored.
|  | 14:59 | Meghnaghat-Shyampur 230kV Ckt-1 is restored.
|  | 15:02 | Bakulia-Khulshi 132 kV Ckt-1 is restored.
|  | 15:08 | Bakulia-MSML 132 kV Ckt-2 is restored.
|  | 15:19 | Rampur 230/132/33 S/S Khulshi-1 is restored.
|  | 15:19 | Rampur 230/132/33 S/S Khulshi-2 is restored.
| 15:20 |  | Rampur 230/132/33 S/S Anandabazar-1 Tripped showing REL670 relays.
|  | 15:24 | Kishoreganj 132/33kV S/S Tr-2 (414T) HT is restored.
|  | 15:25 | Kishoreganj 132/33kV S/S Tr-2 (414T) LT is restored.
| 15:48 | 17:01 | Feni 230/132kV S/S ATR-3 HT Scheduled S/D Due to due to oil leakage at 33kv neutral
bushing
| 15:49 | 17:02 | Feni 230/132kV S/S ATR-3 LT Scheduled S/D Due to Due to oil leakage at 33kv neutral
bushing
|  | 16:17 | Shikalbaha 230/132kV S/S ATR 01 HT is restored.
|  | 16:17 | Shikalbaha 230/132kV S/S ATR 01 LT is restored.
|  | 16:48 | Halishahar 132/33kV S/S Halishahar-Khulshi-Ckt.-3 is restored.
| 17:02 |  | Kodda-Rajendrapur 132kV Ckt-1 Forced S/D from Rajendrapur 132/33kV end Due to Sreepur
end Red Hot issue solved & Load shift from Kodda ckt to Sreepur ckt.
|  | 17:23 | Barishal-Bhola 230 kV Ckt-1 is restored.
| 17:30 |  | BIPTC S/S 20DF21 Tripped showing Differential Relay relays Due to C1 unbalance 60/61
instant L1
|  | 17:53 | Aminbazar-Kaliakoir 230kV Ckt-2 is restored.
|  | 17:54 | Bakerganj 132/33kV S/S T1 HT is restored.
|  | 17:54 | Bakerganj 132/33kV S/S T1 LT is restored.
|  | 17:54 | Bakerganj 132/33kV S/S 132 kV Bakerganj Patuakhali Ckt is restored.
|  | 18:08 | Bakerganj 132/33kV S/S 132 kV Bakerganj Barguna Ckt is restored.
| 18:20 |  | Rampur 230/132/33 S/S Anandabazar-1 Forced S/D Due to anandabazar 1 trip after trail
|  | 18:25 | Muradnagar 132/33kV S/S 132KV Transformar-02 HT is restored.
|  | 18:26 | Muradnagar 132/33kV S/S 132KV Transformar-02 LT is restored.
| 19:00 | 22:08 | Rampur 230/132/33 S/S Anandabazar-2 Forced S/D Due to due to meger in anandabazar ckt 1
| 19:30 |  | Evening peak Generation is 11118 MW
|  | 21:01 | Jamalpur-Mymensingh 132kV Ckt-2 is restored.
| 22:45 | 00:15 | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to 33kv CT redhot maintenance
| 22:46 | 00:13 | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to 33kv CT redhot maintenance.
| 23:10 |  | Sirajgonj 400 MW CCPP Unit-4 Shutdown with remarks:- ST
| 23:18 |  | Bheramara 410 MW CCPP Synchronized with remarks:- GT
| 23:18 |  | Bheramara 410 MW CCPP GT was sync.
| 23:22 |  | Sirajganj unit-4 was shut down due to auxiliary overhauling purposes.
| 23:22 |  | Sirajgonj 400 MW CCPP Unit-4 Shutdown with remarks:- GT
|  | 00:07 | Haripur-Meghnaghat 230kV Ckt-2 is restored.
|  | 00:07 | Haripur-Meghnaghat 230kV Ckt-2 is restored.
| 00:11 |  | Ashuganj 420 MW CCPP (East) GT was sync.
| 02:37 |  | Kushiara 163MW CCPP ST was sync.
| 03:27 |  | Ashuganj 420 MW CCPP (East) ST was sync.
| 04:59 | 05:47 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-2 Tripped from Thakurgaon 132/33kV end showing | [7 empty] | 40.0MW load
|  |  | Thakurgaon-Panchagarh Ckt-1: Areva Micom P442 Thakurgaon-Panchagarh Ckt-2: SIEMENS | [7 empty] | interrup.
|  |  | SIPROTEC 7SA87 EPVTL-Thakurgaon Ckt-2: Earth Fault Relay Pickup relays Due to অদ্য | [7 empty] | Thakurgaon 132/33kV
|  |  | ১১-০১-২০২৫ ইং তারিখে ০৪:৫৯ মিনিটে গ্রিড পাওয়ার চলে যায়। এ সময় EPVTL-Thakurgaon Ckt-2 | [7 empty] | end
ট্রিপ করে অর্থাৎ 905B ও 902B ব্রেকার ট্রিপ করে। উল্লেখ্য যে, EPVTL-Thakurgaon
Ckt-1 রি-কন্ডাক্টিং কাজের জন্য শুধু লাইন আইসোলেটর দিয়ে আগে থেকে শাট ডাউনে ছিল।
| 05:25 |  | Bheramara 410 MW CCPP Synchronized with remarks:- ST
| 06:56 |  | Baroirhat-Hathazari 132 kV Ckt-1 Project Work S/D from Baroirhat 132/33kV end. and from
Hathazari 230/132/33kV end Due to Project work
| 06:57 |  | Baroirhat-Hathazari 132 kV Ckt-2 Project Work S/D from Baroirhat 132/33kV end. and from
Hathazari 230/132/33kV end Due to Project work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 10-01-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 349 | 8143200 | FGMO, Gas Shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 120688 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 35 | 5501184 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 49 | 353160 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 290122 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 233198 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 25 | 478200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 327600 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 45 | 510851 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 140 | 759024 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 41866 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 156 | 744480 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 167192 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 119520 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 550 | 8750000 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 108 | 1363200 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1647 | 27903485
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 113265 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 144000 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1106460 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 167 | 3836837 | Plant availability less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 99 | 405636 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 21580 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 256320 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 21 | 335040 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 16422 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 23084 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 20910 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 38 | 402240 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1152 | 24529088 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 48960 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 345 | 6363636.36 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4898.863 | 1868 | 37623478.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 202 | 4943000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 305 | 7684100 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 34 | 699120 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 49 | 495840 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 86 | 1839999 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 741275 | Machine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 50 | 344581 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 108 | 2159810 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 114 | 470880 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 112 | 2354880 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 295780 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 21120 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 364655 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1124 | 22415040
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 64 | 1549440 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 5100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 59 | 804000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 331200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 18560 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 123600 | To be dispatched 18 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 160 | 2831900
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 28760 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 949000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1196520 | machine problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 102 | 2892355 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 674592 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 1344000 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 157 | 3400130 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 4 | 208536 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7596500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 785 | 18290393
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 663 | 16235636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 36576 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 465120 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1090 | 21243700 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1753 | 37981032
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 500 | 8181133 | Machine Problem
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 2689000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 540 | 10887272.73 | FGMO, U1 under maintenance
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5105440 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 278 | 5498000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2793 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1668 | 32363638.73
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 286684 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 176 | 4192273 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 364 | 8455636 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 52608 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 37152 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 24900 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1470 | 25270909 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 282736 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 616040 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2010 | 39218938
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 317894 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 26229.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 171549 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 116734 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 688320 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 105 | 1320726.6
Eastern Grid Total |  |  |  |  | 17398.245 | 5584 | 109064296.36
Western Grid Total |  |  |  |  | 10984.003 | 5536 | 110884335.33
National Grid Total |  |  |  |  | 28382.248 | 11120 | 219948631.69
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 10-01-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7345.62 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3396.5 | MW
i) Dhaka area |  |  | 3928.12 |  | MW | i) Khulna area |  |  |  | 1303 | MW
ii) Chattogram area |  |  | 1126.5 |  | MW | ii) Barishal area |  |  |  | 342.5 | MW
iii) Cumilla area |  |  | 966 |  | MW | iii) Rajshahi area |  |  |  | 1023 | MW
iv) Mymensingh area |  |  | 914 |  | MW | iv) Rangpur area |  |  |  | 728 | MW
v) Sylhet area |  |  | 411 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10742.12 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 91 | 14:00 | 133 | Netrakona | 130 | 19:00
2 | AKSML | 38 | 23:00 | 68 | Hathazari | 58 | 13:00 | 134 | New | 55.4 | 12:00
3 | Aftabnagar | 26 | 13:00 | 69 | Hatirjheel | 25 | 13:00 | 135 | Niamatpur | 60 | 13:00
4 | Agargaon | 75 | 19:00 | 70 | Ishurdi | 57 | 18:30 | 136 | Noapara | 38 | 18:30
5 | Agrabad | 48 | 14:00 | 71 | Jaldhaka | 55 | 18:00 | 137 | PHP | 9 | 11:00
6 | Amnura | 30 | 08:00 | 72 | Jamalpur | 88 | 18:00 | 138 | Pabna | 72 | 14:00
7 | Ashuganj | 55 | 12:00 | 73 | Jashore | 103 | 13:00 | 139 | Palashbari | 90 | 18:30
8 | BSRM | 200 | 23:00 | 74 | Jhenaidah | 102 | 18:30 | 140 | Panchagarh | 45 | 18:30
9 | Bagerhat | 64 | 18:00 | 75 | Joydebpur | 104 | 18:00 | 141 | Patiya | 6 | 17:00
10 | Bajitpur | 71 | 18:00 | 76 | Joypurhat | 44 | 19:00 | 142 | Patuakhali | 56.7 | 18:30
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 14 | 16:00 | 143 | Payra | 28 | 18:00
12 | Bakulia | 89 | 13:00 | 78 | KSRM | 24 | 08:00 | 144 | Postogola | 41 | 13:00
13 | Banani | 30 | 13:00 | 79 | Kabirpur | 171 | 18:00 | 145 | Purbachal | 19 | 18:30
14 | Bangabhaban | 5 | 12:00 | 80 | Kachua | 57 | 19:30 | 146 | Purbasadipur | 123 | 18:00
15 | Barapukuria | 52 | 18:00 | 81 | Kallyanpur | 87 | 13:00 | 147 | Rahanpur | 25 | 20:00
16 | Barguna | 20 | 19:30 | 82 | Kalurghat | 30 | 18:00 | 148 | Rahim | 33 | 15:00
17 | Barishal | 79 | 18:30 | 83 | Kamrangirchar | 56 | 12:00 | 149 | Rajbari | 63 | 18:00
18 | Barishal-230 | 68 | 18:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 111 | 18:00
19 | Baroaulia | 59 | 18:00 | 85 | Kasba | 27 | 13:00 | 151 | Rajshahi | 69 | 18:00
20 | Baroirhat | 43 | 13:00 | 86 | Kazla | 96 | 12:00 | 152 | Rajshahi-230 | 106 | 13:00
21 | Bashundhara | 148 | 13:00 | 87 | Keranigonj | 64 | 18:30 | 153 | Ramganj | 68 | 14:00
22 | BashundharaCement | 3 | 14:00 | 88 | Khagrachori | 26 | 18:00 | 154 | Rampur | 35 | 16:00
23 | Beanibazar | 48 | 18:00 | 89 | Khulna | 49 | 13:00 | 155 | Rangamati | 13 | 18:00
24 | Benapole | 62 | 08:00 | 90 | Khulshi | 122 | 00:00 | 156 | Rangpur | 116 | 18:30
25 | Bhaluka | 146 | 19:00 | 91 | Kishoreganj | 100 | 18:00 | 157 | Ruppur | 1.4 | 09:00
26 | Bhandaria | 36 | 21:00 | 92 | Kodda | 243 | 18:00 | 158 | SSM | 2 | 00:00
27 | Bhangura | 26 | 18:00 | 93 | Kulaura | 30 | 18:00 | 159 | Saidpur | 92 | 18:00
28 | Bheramara(GK) | 45 | 18:30 | 94 | Kurigram | 50 | 18:00 | 160 | Satkhira | 98 | 18:30
29 | Bhulta | 176 | 09:00 | 95 | Kushtia | 120 | 13:00 | 161 | Satmasjid | 84 | 13:00
30 | Bog-Sherpur | 56 | 18:00 | 96 | Laksam | 22 | 14:00 | 162 | Savar | 164 | 18:30
31 | Bogura | 117 | 21:00 | 97 | Lakshmipur | 25 | 14:00 | 163 | SevenRings | 14.35 | 23:00
32 | Borhanuddin | 67 | 18:00 | 98 | Lalbag | 58 | 13:00 | 164 | ShahCement | 32 | 12:00
33 | Brahmanbaria | 92 | 18:00 | 99 | Lalmonirhat | 44 | 18:30 | 165 | Shahjadpur | 53 | 18:30
34 | Cantonment | 72 | 13:00 | 100 | MI_Cement | 16.1 | 23:00 | 166 | Shahjibazar | 88 | 20:00
35 | Chandina | 13 | 06:00 | 101 | Madanganj | 51 | 01:00 | 167 | Shahmirpur | 37 | 18:00
36 | Chandpur | 50 | 18:30 | 102 | Madaripur | 75 | 21:00 | 168 | Shariatpur | 57 | 20:00
37 | Chandraghona | 28 | 18:00 | 103 | Madartek | 58 | 13:00 | 169 | Sherpur | 124 | 18:00
38 | Chapai | 52 | 18:30 | 104 | Madunaghat | 37 | 18:00 | 170 | Shikalbaha | 21 | 18:30
39 | Charsaidpur | 42 | 23:00 | 105 | Magura | 50 | 18:00 | 171 | Shitalakhya | 65.9 | 13:00
40 | Chauddagram | 52 | 13:00 | 106 | Mahasthangarh | 48 | 18:30 | 172 | Sholosohor | 38 | 15:00
41 | Chhatak | 27 | 19:00 | 107 | Maijdee | 31 | 21:00 | 173 | Shyampur | 148 | 10:00
42 | Chowmuhani | 116 | 18:00 | 108 | Manikganj | 100 | 18:00 | 174 | Siddhirganj | 97 | 12:00
43 | Chuadanga | 81 | 18:30 | 109 | Maniknagar | 48 | 13:00 | 175 | Sirajganj | 78 | 18:30
44 | Coxsbazar | 117 | 18:00 | 110 | Matarbari | 37 | 14:00 | 176 | Sonargaon | 119 | 18:00
45 | Cumilla(N) | 102 | 18:30 | 111 | Matuail | 45 | 12:00 | 177 | Sreemongol | 60 | 19:00
46 | Cumilla(S) | 130 | 13:00 | 112 | Metrorail_Motijheel | 18 | 16:00 | 178 | Sreepur | 97 | 12:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 0 | 00:00 | 179 | Srinagar | 34 | 18:00
48 | Daudkandi | 116 | 18:30 | 114 | Millgate | 73 | 12:00 | 180 | Sunamganj | 44 | 19:30
49 | DhakaUniversity | 46 | 13:00 | 115 | Mirpur | 113 | 13:00 | 181 | Sylhet | 41 | 19:00
50 | Dhamrai | 80 | 18:00 | 116 | Mirsorai | 33 | 12:00 | 182 | Sylhet-132 | 91 | 18:00
51 | Dhanmondi | 75 | 14:00 | 117 | Mirzapur | 39 | 13:00 | 183 | TK | 17.5 | 18:00
52 | Dohazari | 68 | 19:00 | 118 | Mithapukur | 46 | 18:00 | 184 | Tangail | 122 | 18:00
53 | Faridpur | 145 | 18:30 | 119 | Modern | N/A | N/A | 185 | Taraganj | 17 | 18:30
54 | Fatullah | 89 | 16:00 | 120 | Mogbazar | 49.7 | 14:00 | 186 | Tasnim | 22 | 19:00
55 | Fenchuganj | 22 | 17:00 | 121 | Mongla | 32 | 21:00 | 187 | Thakurgaon | 79 | 19:00
56 | Feni | 74 | 19:30 | 122 | Motijheel | 31 | 13:00 | 188 | Tongi | 127 | 12:00
57 | GPH | 79 | 06:00 | 123 | Muktagacha | 28 | 18:30 | 189 | Ullahpara | 26 | 18:30
58 | Ghatail | 76 | 18:00 | 124 | Munshiganj | 72 | 18:00 | 190 | Ullon | 41 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 0 | 00:00 | 191 | Uttara | 51 | 19:00
60 | Ghorashal-230 | 77 | 19:00 | 126 | Mymensingh | 135 | 19:00 | 192 | UttaraNew | 30 | 13:00
61 | Goalpara | 30 | 13:00 | 127 | Naogaon | 93 | 18:30 | 193 | Zigatola | 75 | 13:00
62 | Gollamari | 86 | 13:00 | 128 | Narail | 43.5 | 18:00
63 | Gopalganj | 79.6 | 18:30 | 129 | Narinda | 52 | 13:00
64 | Gulshan | 64 | 13:00 | 130 | Narshingdi | 140 | 18:30
65 | Halishahar | 57 | 14:00 | 131 | Natore | 108 | 18:30
66 | HaripurSBU | 110 | 22:00 | 132 | Nawabganj | 38.6 | 18:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 10-01-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 8604.8 | 0 |  | 8604.8
1:00 | 7932.65 | 0 |  | 7932.65
2:00 | 7470.44 | 0 |  | 7470.44
3:00 | 7235.77 | 0 |  | 7235.77
4:00 | 6988.98 | 0 |  | 6988.98
5:00 | 6846.08 | 0 |  | 6846.08
6:00 | 7523.57 | 0 |  | 7523.57
7:00 | 7936.07 | 0 |  | 7936.07
8:00 | 8972.78 | 0 |  | 8972.78
9:00 | 9176.91 | 0 |  | 9176.91
10:00 | 8970.07 | 0 |  | 8970.07
11:00 | 8994.93 | 0 |  | 8994.93
12:00 | 9471.25 | 0 |  | 9471.25
13:00 | 10030.96 | 0 |  | 10030.96
14:00 | 9784.47 | 0 |  | 9784.47
15:00 | 9300.89 | 0 |  | 9300.89
16:00 | 9033.95 | 0 |  | 9033.95
17:00 | 9345.96 | 0 |  | 9345.96
18:00 | 10695.7 | 0 |  | 10695.7
19:00 | 11048.8 | 0 |  | 11048.8
19:30 | 11120 | 0 |  | 11120
20:00 | 11095 | 0 |  | 11095
21:00 | 10851.6 | 0 |  | 10851.6
22:00 | 10392 | 0 |  | 10392
23:00 | 9655.3 | 0 |  | 9655.3
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 10-01-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4011.5 | 4593.3 | 8604.8 | DAILY GENERATION CURVE
00:30 | 3872 | 4396.725 | 8268.725
01:00 | 3732.5 | 4200.15 | 7932.65 | 10-01-2026
01:30 | 3637.5 | 4064.045 | 7701.545
02:00 | 3542.5 | 3927.94 | 7470.44
02:30 | 3559 | 3794.105 | 7353.105
03:00 | 3575.5 | 3660.27 | 7235.77
03:30 | 3541.75 | 3570.625 | 7112.375
04:00 | 3508 | 3480.98 | 6988.98
04:30 | 3525.5 | 3392.03 | 6917.53
05:00 | 3543 | 3303.08 | 6846.08
05:30 | 3743.5 | 3441.325 | 7184.825
06:00 | 3944 | 3579.57 | 7523.57
06:30 | 4005.82 | 3724 | 7729.82
07:00 | 4067.64 | 3868.43 | 7936.07
07:30 | 4272.41 | 4182.015 | 8454.425
08:00 | 4477.18 | 4495.6 | 8972.78
08:30 | 4439.555 | 4635.29 | 9074.845
09:00 | 4401.93 | 4774.98 | 9176.91
09:30 | 4390.145 | 4683.345 | 9073.49
10:00 | 4378.36 | 4591.71 | 8970.07
10:30 | 4439.09 | 4543.41 | 8982.5
11:00 | 4499.82 | 4495.11 | 8994.93
11:30 | 4606.53 | 4626.56 | 9233.09
12:00 | 4713.24 | 4758.01 | 9471.25
12:30 | 4892.965 | 4858.14 | 9751.105
13:00 | 5072.69 | 4958.27 | 10030.96
13:30 | 5019.115 | 4888.6 | 9907.715
14:00 | 4965.54 | 4818.93 | 9784.47
14:30 | 4907.49 | 4635.19 | 9542.68
15:00 | 4849.44 | 4451.45 | 9300.89
15:30 | 4776.36 | 4391.06 | 9167.42
16:00 | 4703.28 | 4330.67 | 9033.95
16:30 | 4771.235 | 4418.72 | 9189.955
17:00 | 4839.19 | 4506.77 | 9345.96
17:30 | 5132.445 | 4888.385 | 10020.83
18:00 | 5425.7 | 5270 | 10695.7
18:30 | 5529.75 | 5342.5 | 10872.25
19:00 | 5633.8 | 5415 | 11048.8
19:30 | 5584 | 5536 | 11120
20:00 | 5613 | 5482 | 11095
20:30 | 5496.3 | 5477 | 10973.3 |  | Executive Engineer
21:00 | 5379.6 | 5472 | 10851.6 |  | Network Operation Division
21:30 | 5117.3 | 5504.5 | 10621.8
22:00 | 4855 | 5537 | 10392
22:30 | 4640.65 | 5383 | 10023.65
23:00 | 4426.3 | 5229 | 9655.3

## En-Curve
QF-LDC-12
Date | 10-01-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2434 | 1225.5 | 755 | 0 | 92 | 921.3 | 46 | 3112 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2382.5 | 1140 | 683.5 | 0 | 87 | 893.225 | 46 | 3027 | 0 | 0 | 9.5 | 0 | 0 | 0 | 0 | 10-01-2026
01:00 | 2331 | 1054.5 | 612 | 0 | 82 | 865.15 | 46 | 2942 | 0 | 0 | 0 | 0 | 0 | 0 | 0
01:30 | 2280 | 1026.5 | 590 | 0 | 82 | 849.545 | 46 | 2827.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Generated | 219.9486 |  | MKWHr
02:00 | 2229 | 998.5 | 568 | 0 | 82 | 833.94 | 46 | 2713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2242 | 1006.5 | 461.5 | 0 | 79 | 831.605 | 46 | 2686.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total Energy Requirement | 219.9486 |  | MKWHr
03:00 | 2255 | 1014.5 | 355 | 0 | 76 | 829.27 | 46 | 2660 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2222.5 | 1015.25 | 275.5 | 0 | 75 | 832.125 | 46 | 2646 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:00 | 2190 | 1016 | 196 | 0 | 74 | 834.98 | 46 | 2632 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2162.5 | 1019 | 196 | 0 | 74 | 834.03 | 46 | 2585.5 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0
05:00 | 2135 | 1022 | 196 | 0 | 74 | 833.08 | 46 | 2539 | 0 | 0 | 0 | 0 | 0 | 1 | 0
05:30 | 2304 | 1102.5 | 196 | 0 | 79 | 830.325 | 46 | 2626.5 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0
06:00 | 2473 | 1183 | 196 | 0 | 84 | 827.57 | 46 | 2714 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:30 | 2463 | 1195.5 | 288.5 | 0 | 81 | 825.13 | 46 | 2822.5 | 3.69 | 0 | 4.5 | 0 | 0 | 0 | 0
07:00 | 2453 | 1208 | 381 | 0 | 78 | 822.69 | 46 | 2931 | 7.38 | 0 | 9 | 0 | 0 | 0 | 0
07:30 | 2457 | 1267 | 521 | 0 | 85 | 905.45 | 46 | 3072 | 42.975 | 17.5 | 40.5 | 0 | 0 | 0 | 0
08:00 | 2461 | 1326 | 661 | 0 | 92 | 988.21 | 46 | 3213 | 78.57 | 35 | 72 | 0 | 0 | 0 | 0
08:30 | 2414.5 | 1285 | 725 | 0 | 97 | 1039.95 | 46 | 3196.5 | 136.895 | 43.5 | 90.5 | 0 | 0 | 0 | 0
09:00 | 2368 | 1244 | 789 | 0 | 102 | 1091.69 | 46 | 3180 | 195.22 | 52 | 109 | 0 | 0 | 0 | 0
09:30 | 2336.5 | 1230 | 817.5 | 0 | 101 | 1059.215 | 46 | 3040.5 | 275.275 | 61 | 103 | 0 | 0 | 3.5 | 0
10:00 | 2305 | 1216 | 846 | 0 | 100 | 1026.74 | 46 | 2901 | 355.33 | 70 | 97 | 0 | 0 | 7 | 0
10:30 | 2342.5 | 1208.5 | 846 | 0 | 106 | 978.595 | 46 | 2869.5 | 414.905 | 70 | 97 | 0 | 0 | 3.5 | 0
11:00 | 2380 | 1201 | 846 | 0 | 112 | 930.45 | 46 | 2838 | 474.48 | 70 | 97 | 0 | 0 | 0 | 0
11:30 | 2499 | 1243.5 | 846.5 | 0 | 115 | 931.255 | 46 | 2860 | 520.835 | 70 | 101 | 0 | 0 | 0 | 0
12:00 | 2618 | 1286 | 847 | 0 | 118 | 932.06 | 46 | 2882 | 567.19 | 70 | 105 | 0 | 0 | 0 | 0
12:30 | 2539 | 1353.5 | 846.5 | 0 | 124 | 982.115 | 46 | 3014.5 | 554.49 | 95 | 196 | 0 | 0 | 0 | 0
13:00 | 2460 | 1421 | 846 | 0 | 130 | 1032.17 | 46 | 3147 | 541.79 | 120 | 287 | 0 | 0 | 0 | 0
13:30 | 2355.5 | 1372 | 846 | 0 | 123 | 1026.585 | 46 | 3178 | 509.63 | 131 | 314 | 0 | 0 | 6 | 0
14:00 | 2251 | 1323 | 846 | 0 | 116 | 1021 | 46 | 3209 | 477.47 | 142 | 341 | 0 | 0 | 12 | 0
14:30 | 2223 | 1287 | 846.5 | 0 | 110 | 965 | 46 | 3131.5 | 395.68 | 142 | 384.5 | 0 | 0 | 11.5 | 0
15:00 | 2195 | 1251 | 847 | 0 | 104 | 909 | 46 | 3054 | 313.89 | 142 | 428 | 0 | 0 | 11 | 0
15:30 | 2243.5 | 1267.4 | 847 | 0 | 104 | 913 | 46 | 3020.5 | 235.22 | 125 | 354.3 | 0 | 0 | 11.5 | 0
16:00 | 2292 | 1283.8 | 847 | 0 | 104 | 917 | 46 | 2987 | 156.55 | 108 | 280.6 | 0 | 0 | 12 | 0
16:30 | 2283.5 | 1358.8 | 846.5 | 0 | 107 | 1003 | 46 | 3027.5 | 90.705 | 121 | 296.45 | 0 | 0 | 9.5 | 0
17:00 | 2275 | 1433.8 | 846 | 0 | 110 | 1089 | 46 | 3068 | 24.86 | 134 | 312.3 | 0 | 0 | 7 | 0
17:30 | 2250 | 1451.4 | 846 | 0 | 112 | 1256.5 | 46 | 3259.5 | 12.43 | 147.5 | 634.5 | 0 | 0 | 5 | 0
18:00 | 2225 | 1469 | 846 | 0 | 114 | 1424 | 46 | 3451 | 0 | 161 | 956.7 | 0 | 0 | 3 | 0
18:30 | 2185.5 | 1470.5 | 754.5 | 0 | 113 | 1435.5 | 46 | 3626 | 0 | 162 | 1077.75 | 0 | 0 | 1.5 | 0
19:00 | 2146 | 1472 | 663 | 0 | 112 | 1447 | 46 | 3801 | 0 | 163 | 1198.8 | 0 | 0 | 0 | 0
19:30 | 2223 | 1525 | 663 | 0 | 112 | 1470 | 46 | 3905 | 0 | 125 | 1051 | 0 | 0 | 0 | 0
20:00 | 2267 | 1510.5 | 663 | 0 | 106 | 1440 | 46 | 3896 | 0 | 115 | 1051.5 | 0 | 0 | 0 | 0
20:30 | 2366 | 1468.5 | 662.5 | 0 | 107 | 1441.5 | 46 | 3888 | 0 | 83.5 | 910.3 | 0 | 0 | 0 | 0
21:00 | 2465 | 1426.5 | 662 | 0 | 108 | 1443 | 46 | 3880 | 0 | 52 | 769.1 | 0 | 0 | 0 | 0
21:30 | 2465 | 1381.5 | 762 | 0 | 109 | 1388 | 46 | 3882.5 | 0 | 31 | 556.8 | 0 | 0 | 0 | 0
22:00 | 2465 | 1336.5 | 862 | 0 | 110 | 1333 | 46 | 3885 | 0 | 10 | 344.5 | 0 | 0 | 0 | 0
22:30 | 2365 | 1220 | 866.5 | 0 | 105 | 1330.5 | 46 | 3888 | 0 | 5 | 197.65 | 0 | 0 | 0 | 0
23:00 | 2265 | 1103.5 | 871 | 0 | 100 | 1328 | 46 | 3891 | 0 | 0 | 50.8 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 10-01-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 424 | 04:00 | 398 | 13:00 | Meghnaghat | 427 | 04:00 | 404 | 13:00
Ashuganj | 411 | 3:00 | 389 | 13:00 | Payra | 422 | 02:00 | 415 | 12:00
Bhulta | 405 | 04:00 | 383 | 12:00 | Rahanpur | 421 | 04:00 | 401 | 18:00
Bibiana | 424 | 05:00 | 407 | 12:00 | Rampal | 417 | 03:00 | 400 | 13:00
BIPTC | 408 | 05:00 | 388 | 12:00
Bogura | 418 | 04:00 | 394 | 18:00
Gopalganj | 423 | 04:00 | 402 | 13:00
Kaliakoir | 419 | 05:00 | 392 | 12:00
Korerhat | 427 | 03:00 | 409 | 13:00
Madunaghat | 418 | 04:00 | 406 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 247 | 04:00 | 226 | 12:00 | Kachua | 241 | 00:00 | 233 | 12:00
AKSML | 242 | 04:00 | 231 | 16:00 | Kaliakoir | 247 | 04:00 | 227 | 12:00
Aminbazar | 248 | 04:00 | 223 | 12:00 | Keranigonj | 245 | 05:00 | 224 | 12:00
Ashuganj | 240 | 00:00 | 232 | 12:00 | Khulna(S) | 246 | 04:00 | 226 | 13:00
Ashuganj-400 | 240 | 3:00 | 230 | 13:00 | Korerhat | 243 | 03:00 | 232 | 13:00
Baghabari | 241 | 03:00 | 230 | 13:00 | Madunaghat | 239 | 05:00 | 232 | 16:00
Barapukuria | 232 | 04:00 | 218 | 08:00 | Madunaghat-400 | 239 | 03:00 | 233 | 13:00
Barapukuria-230 | 232 | 4:00 | 219 | 12:00 | Maniknagar | 243 | 04:00 | 228 | 13:00
Barishal | 241 | 03:00 | 229 | 12:00 | Meghnaghat | 245 | 22:00 | 231 | 13:00
Bheramara | 242 | 04:00 | 221 | 13:00 | Meghnaghat-400 | 243 | 04:00 | 228 | 13:00
Bhulta | 244 | 04:00 | 230 | 12:00 | Mirsorai | 242 | 04:00 | 231 | 13:00
Bibiana | 243 | 04:00 | 232 | 13:00 | Rajshahi | 243 | 05:00 | 218 | 13:00
BIPTC | 243 | 04:00 | 222 | 12:00 | Rampal | 242 | 04:00 | 227 | 13:00
Bogura | 245 | 04:00 | 232 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 245 | 04:00 | 231 | 18:00 | Rampura | 243 | 05:00 | 229 | 13:00
Borhanuddin | 240 | 01:00 | 235 | 13:00 | Shikalbaha | 237 | 05:00 | 230 | 15:00
BSRM | 242 | 04:00 | 232 | 12:00 | Shyampur | 244 | 04:00 | 225 | 12:00
Cumilla(N) | 239 | 02:00 | 228 | 12:00 | Siddhirganj | 243 | 03:00 | 229 | 12:00
Faridpur | 240 | 04:00 | 228 | 13:00 | Sirajgonj | 248 | 04:00 | 238 | 12:00
Fenchuganj | 244 | 04:00 | 235 | 13:00 | Sreepur | 238 | 05:00 | 227 | 12:00
Feni | 243 | 05:00 | 232 | 12:00 | Tongi | 241 | 04:00 | 218 | 12:00
Ghorashal | 242 | 00:00 | 236 | 15:00
Ghorashal-230 | 236 | 05:00 | 212 | 13:00
Gopalganj | 238 | 04:00 | 225 | 13:00
GPH | 241 | 04:00 | 232 | 16:00
Haripur | 244 | 04:00 | 228 | 13:00
Hasnabad | 244 | 04:00 | 225 | 12:00
Hathazari | 238 | 01:00 | 228 | 16:00
Ishurdi | 244 | 04:00 | 225 | 12:00
Jhenaidah | 243 | 04:00 | 220 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 04:00 | 127 | 12:00 | Laksam | 139 | 03:00 | 133 | 16:00 | UttaraNew | 141 | 03:00 | 127 | 12:00
Agargaon | 141 | 04:00 | 126 | 13:00 | Lakshmipur | 136 | 04:00 | 130 | 12:00 | Zigatola | 138 | 02:00 | 124 | 13:00
Agrabad | 138 | 01:00 | 132 | 12:00 | Lalbag | 138 | 04:00 | 125 | 12:00
AKS | 136 | 02:00 | 132 | 15:00 | Lalmonirhat | 132 | 04:00 | 122 | 08:00
Aminbazar | 140 | 03:00 | 127 | 12:00 | Madanganj | 137 | 01:00 | 136 | 00:00
Amnura | 139 | 01:00 | 126 | 12:00 | Madaripur | 140 | 00:00 | 136 | 07:00
Ashuganj | 140 | 00:00 | 136 | 12:00 | Madartek | 134 | 00:00 | 126 | 13:00
Bagerhat | 135 | 04:00 | 125 | 13:00 | Madunaghat | 140 | 05:00 | 135 | 13:00
Bajitpur | 135 | 06:00 | 129 | 21:00 | Magura | 139 | 04:00 | 122 | 13:00
Bakerganj | 138 | 01:00 | 134 | 18:00 | Mahasthangarh | 138 | 03:00 | 130 | 13:00
Bakulia | 139 | 04:00 | 133 | 12:00 | Maijdee | 136 | 04:00 | 130 | 12:00
Banani | 136 | 02:00 | 126 | 13:00 | Manikganj | 135 | 02:00 | 118 | 12:00
Bangabhaban | 142 | 04:00 | 131 | 13:00 | Maniknagar | 142 | 04:00 | 131 | 13:00
Barapukuria | 139 | 04:00 | 128 | 13:00 | Matarbari | 138 | 13:00 | 123 | 18:00
Barguna | 139 | 04:00 | 133 | 19:00 | Matuail | 141 | 05:00 | 132 | 13:00
Barishal | 140 | 03:00 | 134 | 12:00 | Metrorail_Motijheel | 142 | 04:00 | 131 | 13:00
Barishal-230 | 142 | 03:00 | 134 | 12:00 | Metrorail_Uttara | 141 | 03:00 | 127 | 12:00
Baroaulia | 138 | 04:00 | 135 | 16:00 | Millgate | 137 | 03:00 | 118 | 12:00
Baroirhat | 136 | 00:00 | 130 | 13:00 | Mirpur | 138 | 00:00 | 127 | 12:00
Bashundhara | 135 | 01:00 | 125 | 02:00 | Mirzapur | 137 | 04:00 | 128 | 12:00
BashundharaCement | 137 | 01:00 | 136 | 00:00 | Mithapukur | 138 | 04:00 | 128 | 13:00
Beanibazar | 135 | 03:00 | 131 | 18:00 | MI_Cement | 139 | 04:00 | 123 | 13:00
Benapole | 137 | 03:00 | 114 | 13:00 | Modern | N/A | N/A | N/A | N/A
Bhaluka | 137 | 10:00 | 125 | 22:00 | Mogbazar | 138 | 05:00 | 129 | 13:00
Bhandaria | 139 | 05:00 | 131 | 13:00 | Mongla | 138 | 04:00 | 125 | 13:00
Bhangura | 141 | 04:00 | 133 | 12:00 | Motijheel | 142 | 04:00 | 131 | 13:00
Bheramara | 141 | 04:00 | 129 | 13:00 | Muktagacha | 134 | 16:00 | 128 | 00:00
Bheramara(GK) | 140 | 05:00 | 128 | 13:00 | Munshiganj | 138 | 02:00 | 130 | 13:00
Bhulta | 133 | 18:00 | 122 | 15:00 | Muradnagar | 141 | 04:00 | 130 | 15:00
Bog-Sherpur | 140 | 04:00 | 132 | 13:00 | Mymensingh | 135 | 17:00 | 122 | 21:00
Bogura | 139 | 05:00 | 132 | 13:00 | Naogaon | 136 | 04:00 | 126 | 13:00
Bogura-230 | 140 | 04:00 | 132 | 13:00 | Narail | 140 | 05:00 | 122 | 13:00
Brahmanbaria | 135 | 04:00 | 126 | 12:00 | Narinda | 142 | 4:00 | 131 | 13:00
Cantonment | 140 | 03:00 | 126 | 12:00 | Narshingdi | 137 | 04:00 | 120 | 18:30
Chandina | 142 | 04:00 | 133 | 13:00 | Natore | 138 | 06:00 | 129 | 13:00
Chandpur | 139 | 03:00 | 133 | 12:00 | Nawabganj | 138 | 02:00 | 124 | 13:00
Chandraghona | 139 | 00:00 | 135 | 12:00 | Netrakona | 130 | 09:00 | 118 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 140 | 04:00 | 134 | 12:00 | New | 138 | 03:00 | 120 | 12:00
Charsaidpur | 139 | 04:00 | 130 | 13:00 | Niamatpur | 140 | 02:00 | 133 | 18:00
Chauddagram | 138 | 03:00 | 131 | 13:00 | Noapara | 138 | 04:00 | 116 | 13:00
Chhatak | 136 | 05:00 | 128 | 18:00 | Pabna | 139 | 02:00 | 130 | 09:00
Chowmuhani | 132 | 00:00 | 129 | 13:00 | Palashbari | 135 | 05:00 | 127 | 08:00
Chuadanga | 137 | 00:00 | 126 | 08:00 | Panchagarh | 140 | 04:00 | 128 | 08:00
Coxsbazar | 131 | 09:00 | 124 | 18:00 | Patiya | 139 | 04:00 | 132 | 12:00
Cumilla(N) | 141 | 02:00 | 133 | 13:00 | Patuakhali | 135 | 05:00 | 132 | 19:00
Cumilla(S) | 140 | 05:00 | 125 | 13:00 | Payra | 138 | 00:00 | 136 | 12:00
Daganbhuiyan | 137 | 04:00 | 130 | 13:00 | PHP | 136 | 02:00 | 130 | 13:00
Daudkandi | 139 | 02:00 | 125 | 18:30 | Postogola | 138 | 01:00 | 126 | 12:00
DhakaUniversity | 136 | 03:00 | 127 | 12:00 | Purbachal | 136 | 02:00 | 125 | 13:00
Dhamrai | 139 | 05:00 | 130 | 13:00 | Purbasadipur | 138 | 23:00 | 125 | 08:00
Dhanmondi | 141 | 04:00 | 132 | 12:00 | Rahanpur | 141 | 01:00 | 134 | 16:00
Dohazari | 136 | 02:00 | 130 | 12:00 | Rahanpur-400 | 141 | 02:00 | 134 | 19:30
Faridpur | 140 | 04:00 | 132 | 12:00 | Rahim | 139 | 05:00 | 130 | 13:00
Fatullah | 141 | 04:00 | 124 | 12:00 | Rajbari | 139 | 04:00 | 131 | 13:00
Fenchuganj | 139 | 06:00 | 135 | 13:00 | Rajendrapur | 138 | 04:00 | 122 | 13:00
Feni | 135 | 05:00 | 130 | 13:00 | Rajshahi | 139 | 04:00 | 131 | 18:00
Feni-230 | 137 | 04:00 | 130 | 12:00 | Rajshahi-230 | 140 | 05:00 | 125 | 12:00
Ghatail | 132 | 07:00 | 128 | 01:00 | Ramganj | 136 | 00:00 | 130 | 13:00
Ghorashal | 133 | 00:00 | 130 | 11:00 | Rampur | 139 | 04:00 | 132 | 12:00
Goalpara | 140 | 04:00 | 127 | 13:00 | Rampura | 135 | 04:00 | 126 | 13:00
Gollamari | 138 | 04:00 | 127 | 13:00 | Rangamati | 139 | 03:00 | 134 | 12:00
Gopalganj | 141 | 04:00 | 132 | 13:00 | Rangpur | 136 | 01:00 | 128 | 12:00
Gopalganj-400 | 144 | 04:00 | 136 | 12:00 | Ruppur | 141 | 04:00 | 130 | 13:00
Gulshan | 135 | 04:00 | 125 | 13:00 | Saidpur | 137 | 05:00 | 126 | 13:00
Halishahar | 140 | 05:00 | 133 | 12:00 | Satkhira | 136 | 02:00 | 124 | 13:00
Haripur | 140 | 04:00 | 131 | 13:00 | Satmasjid | 140 | 04:00 | 126 | 12:00
HaripurSBU | 139 | 04:00 | 131 | 13:00 | Savar | 139 | 03:00 | 126 | 12:00
Hasnabad | 138 | 01:00 | 125 | 13:00 | SevenRings | 134 | 03:00 | 129 | 12:00
Hathazari | 140 | 02:00 | 134 | 16:00 | ShahCement | 139 | 04:00 | 130 | 13:00
Hatirjheel | 136 | 04:00 | 126 | 13:00 | Shahjadpur | 140 | 04:00 | 135 | 12:00
Ishurdi | 143 | 04:00 | 132 | 12:00 | Shahjibazar | 136 | 06:00 | 128 | 19:00
Jaldhaka | 135 | 03:00 | 125 | 13:00 | Shahmirpur | 137 | 00:00 | 134 | 11:00
Jamalpur | 133 | 16:00 | 124 | 01:00 | Shariatpur | 143 | 04:00 | 134 | 13:00
Jashore | 136 | 00:00 | 116 | 13:00 | Sherpur | 129 | 07:00 | 120 | 12:00
Jhenaidah | 140 | 01:00 | 112 | 13:00 | Shikalbaha | 128 | 03:00 | 124 | 11:00
Jhenaidah-230 | 141 | 04:00 | 125 | 13:00 | Shikalbaha-230 | 140 | 03:00 | 134 | 12:00
Joydebpur | 131 | 03:00 | 126 | 12:00 | Shitalakhya | 139 | 04:00 | 123 | 13:00
Joypurhat | 136 | 05:00 | 126 | 12:00 | Sholosohor | 139 | 02:00 | 134 | 16:00
Juldah | 138 | 00:00 | 133 | 16:00 | Shyampur | 137 | 06:00 | 126 | 13:00
Kabirpur | 140 | 20:00 | 118 | 12:00 | Shyampur-230 | 141 | 04:00 | 130 | 12:00
Kachua | 139 | 00:00 | 134 | 12:00 | Siddhirganj | 140 | 02:00 | 132 | 12:00
Kaliakoir | 142 | 03:00 | 132 | 12:00 | Sirajganj | 138 | 02:00 | 129 | 13:00
Kallyanpur | 140 | 05:00 | 129 | 12:00 | Sonargaon | 136 | 21:00 | 124 | 14:00
Kalurghat | 139 | 01:00 | 135 | 12:00 | Sreemongol | 135 | 03:00 | 129 | 19:30
Kamrangirchar | 138 | 04:00 | 124 | 12:00 | Sreepur | 139 | 04:00 | 127 | 22:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 138 | 05:00 | 125 | 12:00
Kasba | 140 | 04:00 | 130 | 16:00 | SSM | 142 | 02:00 | 133 | 08:00
Kazla | 142 | 04:00 | 130 | 13:00 | Sunamganj | 133 | 03:00 | 126 | 18:00
Keranigonj | 139 | 05:00 | 125 | 12:00 | Sylhet | 135 | 01:00 | 132 | 13:00
Khagrachori | 139 | 04:00 | 133 | 12:00 | Sylhet-132 | 135 | 01:00 | 133 | 12:00
Khulna | 136 | 06:00 | 126 | 13:00 | Tangail | 132 | 03:00 | 126 | 12:00
Khulna(S) | 138 | 03:00 | 127 | 13:00 | Taraganj | 136 | 04:00 | 126 | 08:00
Khulshi | 139 | 06:00 | 131 | 16:00 | Tasnim | 140 | 08:00 | 123 | 16:00
Kishoreganj | 134 | 04:00 | 126 | 21:00 | Thakurgaon | 138 | 04:00 | 126 | 08:00
Kodda | 138 | 19:00 | 123 | 12:00 | TK | 139 | 04:00 | 134 | 12:00
KSRM | 139 | 03:00 | 133 | 16:00 | Tongi | 139 | 04:00 | 123 | 12:00
Kulaura | 138 | 03:00 | 134 | 12:00 | Ullahpara | 140 | 05:00 | 130 | 12:00
Kurigram | 131 | 15:00 | 121 | 08:00 | Ullon | 135 | 05:00 | 125 | 13:00
Kushtia | 137 | 06:00 | 120 | 13:00 | Uttara | 140 | 03:00 | 120 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division