## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 12-01-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-01-2026 | during | 12-01-2026 | during | 12-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 318 | 316 | 412 | 412 | 392 | 392 | FGMO, Gas Shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 240 | 240 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 20 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 335 | 335 | 335 | 0 | 0 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 48.6 | 48 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 26.8 | 24 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 15.1 | 15.1 | 15.1 | 15.1 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 110 | 195 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 50 | 151 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 26 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 335 | 395 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 35 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1334.4 | 1713 | 5335.25 | 5307.25 | 2445.13 | 2455.13
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 | 46 | 46 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 160 | 161 | 150 | 150 | 150 | 150 | Plant availability less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 15 | 51 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 40 | 64 | 40 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 51 | 51 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 5 | 10 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.63 | 0 | 3.22 | 0 | 3.22 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 38 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1187 | 1212 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 1 | 1 | 1 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 312 | 315 | 315 | 315 | 355 | 355 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1768.63 | 1850 | 3085.08 | 3091.86 | 2639.72 | 2734.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 209 | 191 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 226 | 40 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 0 | 0 | Under maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 230 | 393 | 393 | 393 | 393 | 393 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 51 | 51 | 51 | 51 | 51 | Gas shortage
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 24 | 24 | 50 | 50 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 106 | 104 | 163 | 163 | 115 | 115 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 49 | 111 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 116 | 116 | 84 | 84 | 122 | 122 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 13 | 24.5 | 24.5 | 24.5 | 24.5 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 38 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1031 | 1019 | 2409.75 | 2354.75 | 2239.05 | 2184.05
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-01-2026 | during | 12-01-2026 | during | 12-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 32 | 32 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 57 | 60 | 60 | 60 | 60 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 19 | 20 | 20 | 20 | 20 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 38.27 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 18 | 22 | 22 | 18 | 18 | To be dispatched 18 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 149.27 | 126 | 358.1 | 314 | 354.1 | 310
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 41 | 41 | 41 | 41 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 60 | 60 | 60 | 60 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 152 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 81 | 80 | 80 | 81 | 81 | machine problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 160 | 152 | 158 | 158 | 158 | 158 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 851 | 848 | 898 | 898 | 849 | 849
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 876 | 876 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 265 | 280 | 410 | 410 | 369 | 369 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 79 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 921 | 1113 | 1148.28 | 1148.28 | 1000 | 1148 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2141 | 2269 | 3495.28 | 3420.28 | 2551.1 | 2624.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 429 | 508 | 0 | 0 | 622 | 622 | Machine Problem
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 132 | 130 | 136 | 136 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 505 | 585 | 622 | 622 | 575 | 575 | FGMO, U1 under maintenance
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 289 | 307 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.47 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1575.47 | 1750 | 1546 | 1546 | 1968 | 1968
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 48.82 | 0 | 47.32 | 0 | 47.32 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 196 | 186 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0 | -
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 28 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.17 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1075.88 | 1442.07 | 1435.88 | 1435.88 | 1356 | 1356 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 47.24 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 102 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1474.11 | 1691.07 | 2709.9 | 2507.08 | 2136.62 | 1933.8
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 63 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.4 | 0 | 4.8 | 0 | 4.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 127 | 0 | 136.85 | 0 | 136.85 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 162.4 | 113 | 433.65 | 262 | 399.65 | 228
System Total |  |  |  |  | 28823.2 | 28382.248 | 10487.28 | 11379.07 | 20271.01 | 19701.22 | 15582.37 | 15286.58
Forecast Scenario (12-01-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9220 |  | 0 |  | 9220
|  |  |  | 1:00 | 8580 |  | 0 |  | 8580
|  |  |  | 2:00 | 8160 |  | 0 |  | 8160
|  |  |  | 3:00 | 7810 |  | 0 |  | 7810
|  |  |  | 4:00 | 7510 |  | 0 |  | 7510
|  |  |  | 5:00 | 7500 |  | 0 |  | 7500
|  |  |  | 6:00 | 8070 |  | 0 |  | 8070
|  |  |  | 7:00 | 8590 |  | 0 |  | 8590
|  |  |  | 8:00 | 9700 |  | 0 |  | 9700
|  |  |  | 9:00 | 10310 |  | 0 |  | 10310
|  |  |  | 10:00 | 10000 |  | 0 |  | 10000
|  |  |  | 11:00 | 10160 |  | 0 |  | 10160
|  |  |  | 12:00 | 10590 |  | 0 |  | 10590
|  |  |  | 13:00 | 11030 |  | 0 |  | 11030
|  |  |  | 14:00 | 10590 |  | 0 |  | 10590
|  |  |  | 15:00 | 10110 |  | 0 |  | 10110
|  |  |  | 16:00 | 9800 |  | 0 |  | 9800
|  |  |  | 17:00 | 10280 |  | 0 |  | 10280
|  |  |  | 18:00 | 11350 |  | 0 |  | 11350
|  |  |  | 18:30 | 11320 |  | 0 |  | 11320
|  |  |  | 19:00 | 11270 |  | 0 |  | 11270
|  |  |  | 19:30 | 11290 |  | 0 |  | 11290
|  |  |  | 20:00 | 11230 |  | 0 |  | 11230
|  |  |  | 21:00 | 10980 |  | 0 |  | 10980
|  |  |  | 22:00 | 10340 |  | 0 |  | 10340
|  |  |  | 23:00 | 9710 |  | 0 |  | 9710
Probable Maximum Temperature: |  |  | 22.70°C
Probable Maximum Demand at Day Peak: |  |  | 10590.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11350.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11350.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 232.89 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:11 hrs on 12-01-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 11-01-2026
Power Supply Scenario
| Day Peak Generation |  |  | 10487.28 | MW | 12:00 Hr. | Energy Generated |  |  | 235.2467 |  | MKWHr.
| Day Peak Demand |  |  | 10487.28 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11379.07 | MW | 19:00 Hr. | Energy Demand |  |  | 235.2467 |  | MKWHr.
| Evening Peak Demand |  |  | 11379.07 | MW | 19:00 Hr. | Maximum Temperature |  |  | 25.7 |  | °C
| Minimum Generation of the Day |  |  | 7521 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 670.65 |  | MMCFD
| Maximum Generation of the Day |  |  | 11379.07 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.9332 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 24.4875 | 0 | 6.4163 | 0 | 0 | 0.15413 | 0 | 0 | 31.0579 | Gas | 87.0109 | Gas | 309084467.46
| Chattogram Zone |  |  | 4.2163 | 34.4709 | 1.2387 | 0 | 1.0949 | 0.081962 | 0 | 0.00768 | 41.1105 | Coal | 85.6644 | Coal | 569632558.9343
| Cumilla Zone |  |  | 20.1693 | 0 | 1.2748 | 0 | 0 | 0.25509 | 2.497 | 0 | 24.1961 | HFO | 10.6893 | HFO | 179198313.32
| Mymensingh Zone |  |  | 1.1078 | 0 | 1.3046 | 0 | 0 | 0.23389 | 0 | 0 | 2.6464 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 19.2721 | 0 | 0 | 0 | 0 | 0.04762 | 0 | 0 | 19.3198 | Hydro | 1.0949 | Hydro | 109488
| Khulna Zone |  |  | 4.9484 | 23.1491 | 0 | 0 | 0 | 0.41472 | 17.9156 | 0 | 46.4279 | Solar | 3.3535 | Solar | 53114946.042
| Barishal Zone |  |  | 8.2929 | 28.0444 | 0 | 0 | 0 | 0.002649 | 0 | 0 | 36.3399 | Import | 47.4261 | Import | 284523131.44
| Rajshahi Zone |  |  | 4.5164 | 0 | 0.084096 | 0 | 0 | 1.2028 | 27.0135 | 0 | 32.8167 | Wind | 0.00768 | Wind | 112972.8
| Rangpur Zone |  |  | 0 | 0 | 0.37078 | 0 | 0 | 0.96066 | 0 | 0 | 1.3314
| Total |  |  | 87.0109 | 85.6644 | 10.6893 | 0 | 1.0949 | 3.3535 | 47.4261 | 0.00768 | 235.2467
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 309084467.46 |  | Hydro | 109488
|  |  |  | Coal | 569632558.9343 |  | Solar | 53114946.042
|  |  |  | HFO | 179198313.32 |  | Import | 284523131.44
|  |  |  | HSD | 0 |  | Wind | 112972.8
[5 empty] | Total: | 139,57,75,877 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 17.9156 | Peak Hr Flow | 876.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 6011509.1 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.0135 | Peak Hr Flow | 1442.07 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2247 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.497 | Peak Hr Flow | 116.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2341 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 47.4261 | Peak Hr Flow | 2434.07 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4086
|  |  |  | Chattogram |  | 0 |  | 1142
|  |  |  | Cumilla |  | 0 |  | 950
|  |  |  | Mymensingh |  | 0 |  | 931
|  |  |  | Sylhet |  | 0 |  | 411
|  |  |  | Khulna |  | 0 |  | 1315
|  |  |  | Barishal |  | 0 |  | 312
|  |  |  | Rajshahi |  | 0 |  | 1042
|  |  |  | Rangpur |  | 0 |  | 790
|  |  |  | Total |  | 0 |  | 10979
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:03 | 17:25 | Barishal-Bhola 230 kV Ckt-1 Scheduled S/D from Barishal 230/132kV end Due to Annual
maintenance
| 08:05 | 15:06 | Fenchuganj 230/132/33kV S/S 230 KV Bus-1 Scheduled S/D Due to Annual maintenance
| 08:13 | 07:14 | Hasnabad-Keraniganj 230kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to
Annual Maintenance work at Hasnabad end. and from Hasnabad 230/132kV end Due to Deadline
checking
| 08:19 | 16:15 | Magura-Narail 132kV Ckt-2 Scheduled S/D from Narail 132/33kV end Due to Annual
Maintenance work purpose. and from Magura 132/33kV end Due to For Annual Maintenance.
| 08:28 | 17:35 | Rajshahi 230/132/33kV S/S 230 Kv BIPTC Ckt-02 Scheduled S/D Due to A/M
| 08:28 | 17:53 | Chandpur 132/33kV S/S Bus A Scheduled S/D Due to Annual maintenance
| 08:30 | 15:05 | Cumilla(N)-Kachua 132 kV Ckt-2 Scheduled S/D from Kachua 230/132/33kV end Due to for
annual maintenance work.
| 08:40 | 17:36 | Mirpur 132/33kV S/S T2 LT Scheduled S/D
| 08:41 | 17:35 | Mirpur 132/33kV S/S T2 HT Scheduled S/D
| 08:45 | 17:35 | HVDC Bheramera- Rajshahi 230kV Ckt-2 Scheduled S/D from BIPTC end Due to Annual
Maintenance
| 08:50 | 14:13 | Gopalganj 132/33kV S/S T2 LT Scheduled S/D Due to 33 kv CT oil leakage maintenance
| 08:50 | 17:36 | Dhamrai-Kaliakoir 132 kV Ckt-2 Scheduled S/D from Dhamrai 132/33kV end Due to Annual
Maintenance and from Kaliakoir 400/230/132kV end Due to NLDC.
| 08:51 | 14:12 | Gopalganj 132/33kV S/S T2 HT Scheduled S/D Due to 33 kv CT oil leakage maintenance.
| 08:52 |  | Rajshahi-Rajshahi(New) 132kV Ckt-2 Project Work S/D from Rajshahi 132/33kV end Due to
Project work
| 09:01 | 16:50 | Aminbazar-Kallyanpur 132kV Ckt-1 Scheduled S/D from Kallyanpur 132/33kV end.
| 09:08 |  | Purbasadipur-Saidpur 132kV Ckt-1 Scheduled S/D from Saidpur 132/33kV end Due to Annual
maintenance and from Purbasadipur 132/33kV end Due to Annual Maintenance
| 09:15 | 16:59 | Madanganj 132/33kV S/S Madanganj -Shitalakhya 132 kv Ckt Scheduled S/D Due to Annual
Maintenance
| 09:17 | 17:34 | Mirpur 132/33kV S/S Main Bus Scheduled S/D
| 09:18 |  | Gopalganj 400/132kV S/S 400kV Bus-02 Scheduled S/D Due to Annual Maintenance
| 09:20 | 15:25 | Chandraghona-Rangamati 132 kV Ckt-1 Scheduled S/D from Rangamati 132/33kV end Due to
Right Of Way
| 09:21 | 17:01 | Rampura-Ullon-2 132kV Ckt-1 Scheduled S/D from Rampura 230/132kV end Due to Annual
Maintenance
| 09:21 | 16:20 | Khulna (S)-Rampal Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end. and from Rampal
400/230kV end Due to Khulna ALDC Demand Annual Maintenance
| 09:23 | 16:04 | Brahmanbaria-Narsinghdi 132 kV Ckt-1 Scheduled S/D from Brahmanbaria 132/33kV end Due to
None
| 09:26 | 18:49 | Fenchuganj-Fenchuganj 132 kV Ckt-4 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
OPGW work
| 09:27 | 15:45 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) LT Scheduled S/D Due to Annual Maintenance.
| 09:28 | 19:58 | Sylhet 132/33kV S/S Sylhet-90MW P/S Project Work S/D Due to CB Open Request by NLDC AE
Desk
| 09:28 | 15:44 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) HT Scheduled S/D Due to Annual Maintenance.
| 09:29 | 17:09 | Dhamrai 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Annual Maintenance
| 09:29 | 17:08 | Dhamrai 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Annual Maintenance
| 09:30 | 17:52 | Bhulta-Ghorasal 230 kV Ckt-1 Scheduled S/D from Bhulta 400/230kV end Due to Annual
Maintenance Work
| 09:30 | 16:46 | Kurigram-Lalmonirhat 132kV Ckt-1 Scheduled S/D from Kurigram 132/33kV end Due to annual
maintenance
| 09:34 | 16:48 | Bogura 230/132kV S/S T-03 HT Scheduled S/D Due to Oil Refill
| 09:34 | 16:50 | Bogura 230/132kV S/S T-03 LT Scheduled S/D
| 09:44 | 17:21 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 Scheduled S/D Due to Annual
maintenance
| 09:44 | 17:21 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 Scheduled S/D Due to Annual
maintenance
| 09:45 | 10:09 | BIPTC S/S 20DF21 Forced S/D
| 09:57 | 16:30 | Jamalpur United (20MW)- Sherpur 132kV Ckt-2 Scheduled S/D from Sherpur 132/33kV end Due
to Annual Maintenance Work.
| 10:04 | 16:25 | BSRM 230/33kV S/S GPH Ispat Ckt. -01 Scheduled S/D Due to Annual Maintenance
| 10:05 | 16:24 | GPH 230/33kV S/S BSRM CKT-1 Scheduled S/D Due to Annual Maintenance
| 10:16 |  | Aminbazar-Kaliakoir 230kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Annual Maintenance
| 10:28 | 15:34 | BIPTC S/S 20DF31 Forced S/D
| 10:28 | 17:33 | Cox'sbazar-Dohazari 132 kV Ckt-1 Scheduled S/D from Dohazari 132/33kV end Due to Annual
Maintenance and from Coxsbazar 132/33kV end Due to Annual maitenance.
| 10:40 |  | Bheramara 410 MW CCPP GT Synchronized with remarks:- None
| 10:40 |  | Bheramara 410 MW CCPP ST Synchronized with remarks:- None
| 10:40 | 12:13 | Bogura-Bogura (New)) 132 kV Ckt-1 Forced S/D from Bogura 230/132kV end. and from Bogura
132/33kV end Due to Replacing SF6 pressure gauge to CB
| 10:44 | 17:21 | Kaliakoir-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Annual
Maintenance Work and from Kaliakoir 400/230/132kV end Due to NLDC
| 11:15 | 15:18 | Haripur-Madanganj 132kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to
Annunciator Replacement Work.
| 11:20 | 13:03 | Narshingdi 132/33kV S/S T-2 HT Forced S/D Due to oil Leakage
| 11:20 | 13:03 | Narshingdi 132/33kV S/S T-2 LT Forced S/D Due to Oil Leakage 33 Kv Bushing
| 12:00 |  | Day Peak Generation: 10482 MW.
| 12:06 | 15:51 | AKSML-Baroaulia 132kV Ckt-1 Scheduled S/D from Baroaulia 132/33kV end Due to Braulia
AKSPL line CVT Y-phase loop change at AKSPL S/S
| 12:13 | 07:13 | Hasnabad-Keraniganj 230kV Ckt-2 Scheduled S/D from Keranigonj 230/132/33kV end Due to
Shutdown taken by NLDC
| 12:24 |  | Aminbazar-Keraniganj 230kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to
Annual Maintenance work at Aminbazar End.
| 12:29 | 16:31 | Hasnabad-Keraniganj 230kV Ckt-2 Scheduled S/D from Hasnabad 230/132kV end Due to dead
line checking.
| 12:37 | 13:19 | BIPTC S/S 20DF13 Forced S/D Due to None
| 12:54 |  | Aminbazar-Keraniganj 230kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Annual Maintenance
| 13:12 | 19:17 | Kodda-Rajendrapur 132kV Ckt-2 Forced S/D from Rajendrapur 132/33kV end Due to Sreepur
Sub- Station BUS Maintenance. NB:. Kodda 2 means, Rajendrapur Sreepur CKT 1.
|  | 13:13 | Kodda-Rajendrapur 132kV Ckt-1 is restored.
| 13:35 | 17:07 | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-2 Scheduled S/D Due to Annual Maintenance
| 14:38 | 16:44 | Sreepur 230/132/33kV S/S 132 kV BUS-2 Forced S/D Due to Rajendrapur-1 Redhot Maintenance
| 14:53 |  | Bogura(New)-Naogaon 132 kV Ckt-1 Scheduled S/D from Naogaon 132/33kV end Due to Project
work.
| 15:30 | 18:43 | Joypurhat-Naogaon 132kV Ckt-1 Scheduled S/D from Naogaon 132/33kV end Due to Project
work for parameter test by SPMD.
|  | 15:40 | Sonargaon 132/33kV S/S Bus-Coupler is restored.
|  | 16:01 | Rajendrapur 132/33kV S/S MTR-2 HT is restored.
|  | 16:03 | Rajendrapur 132/33kV S/S MTR-2 LT is restored.
|  | 16:03 | Khulshi-Madunaghat 132kV Ckt-1 is restored.
| 16:18 | 17:34 | Cox'sbazar-Dohazari 132 kV Ckt-1 Scheduled S/D from Dohazari 132/33kV end Due to Annual
Maintenance
|  | 17:36 | Aminbazar 400/230/132kV S/S ATR-01 HT is restored.
|  | 18:58 | Niamatpur 132/33kV S/S 132 kV Naogaon ckt-2 is restored.
|  | 18:58 | Niamatpur 132/33kV S/S 132 kV Naogaon ckt-2 is restored.
| 19:00 |  | Evening peak generation 11379 MW
| 19:10 |  | Korerhat 400/230/132 kV grid substation's 132 kV Bus-1 was charged for the first time
through Baroihat-Korerhat 132 kV ckt-1
| 19:16 |  | Kodda-Rajendrapur 132kV Ckt-1 Forced S/D from Rajendrapur 132/33kV end.
| 19:21 |  | Korerhat 400/230/132 kV grid substation's 132 kV Bus-2 was charged for the first time
through Baroihat-Korerhat 132 kV ckt-1
|  | 19:45 | Baroirhat-Hathazari 132 kV Ckt-1 is restored.
| 19:50 |  | Korerhat-Hathazari 132 kV ckt-1 was switched ON for the first time
| 20:07 |  | Korerhat-Baroihat 132 kV ckt-2 was switched ON for the first time
|  | 20:20 | Baroirhat-Hathazari 132 kV Ckt-2 is restored.
| 20:20 |  | Korerhat-Hathazari 132 kV ckt-2 was switched ON for the first time
| 20:35 |  | Ashuganj North 360 MW CCPP ST was synchronized
| 05:00 |  | Minimum Generation: 7643 MW
| 06:43 |  | Chattak-Sylhet 132 kV Ckt-2 Scheduled S/D from Chhatak 132/33kV end Due to Dead Line
Checking and from Sylhet 132/33kV end Due to Sylhet-Chatak CKT-2 SD due to CB pole
Replace at Chatak Grid SS Direction by NLDC (01713201801).
| 07:14 |  | Aminbazar 400/230/132kV S/S 230 kv Bus 01 Scheduled S/D Due to Annual maintenance
| 07:34 |  | Aminbazar-Keraniganj 230kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Annual maintenance and from Keranigonj 230/132/33kV end Due to Maintenance work at
Aminbazar end.
| 07:43 |  | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) LT Scheduled S/D Due to oil leakage
repair
| 07:44 |  | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) HT Scheduled S/D Due to oil leakage
repair
| 07:51 |  | Chandpur 132/33kV S/S Bus-B Scheduled S/D Due to Annual maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 11-01-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 316 | 7812000 | FGMO, Gas Shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 170863 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7178094 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 48 | 462240 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 185313 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 301707 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 24 | 521400 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 336960 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 1928989 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1224432 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 66240 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 151 | 1383840 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 154132 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 41040 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 395 | 8639091 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 35 | 651600 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1713 | 31057941
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 68040 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 28800 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1094880 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 161 | 3814106 | Plant availability less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 557854 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 12518 | temp problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 47143 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 84480 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 10 | 402240 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 13922 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 37636 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 28131 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 34290 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 38 | 374400 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 30109 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 3345 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1212 | 26558179 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 7680 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 315 | 7912727.27 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4898.863 | 1850 | 41110480.27
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 191 | 4942000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 40 | 5139400 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 5847500 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 253080 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 70560 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1024057 | Machine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 192363 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 104 | 2591228 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 111 | 1055520 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 116 | 2496960 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 301510 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 26880 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 255091 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1019 | 24196149
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 32 | 1107840 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 57 | 883200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 337200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 224840 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 84240 | To be dispatched 18 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 126 | 2646370
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 47620 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 986000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1446960 | machine problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3249900 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 651168 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1687680 | machine problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 152 | 3398920 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 233520 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7618000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 848 | 19319768
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 876 | 17915636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 280 | 4948416 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 414720 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1113 | 23149100 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2269 | 46427872
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 508 | 9120000 | Machine Problem
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 3017000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 585 | 12356363.64 | FGMO, U1 under maintenance
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5275920 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6568000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2649 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1750 | 36339932.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 281536 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 186 | 4516364 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 0 | 0 | -
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 28 | 48576 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 35520 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 24300 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1442.07 | 27013494 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 271504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 625440 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1691.07 | 32816734
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 63 | 191260 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 32183.76 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 179524 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 175356 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 753120 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 113 | 1331443.76
Eastern Grid Total |  |  |  |  | 17398.245 | 5556 | 118330708.27
Western Grid Total |  |  |  |  | 10984.003 | 5823.07 | 116915982.4
National Grid Total |  |  |  |  | 28382.248 | 11379.07 | 235246690.67
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 11-01-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7520.42 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3459.2 | MW
i) Dhaka area |  |  | 4086.12 |  | MW | i) Khulna area |  |  |  | 1314.8 | MW
ii) Chattogram area |  |  | 1142.3 |  | MW | ii) Barishal area |  |  |  | 312 | MW
iii) Cumilla area |  |  | 950 |  | MW | iii) Rajshahi area |  |  |  | 1042.4 | MW
iv) Mymensingh area |  |  | 931 |  | MW | iv) Rangpur area |  |  |  | 790 | MW
v) Sylhet area |  |  | 411 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10979.62 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 77 | 14:00 | 133 | Netrakona | 122 | 18:00
2 | AKSML | 107 | 17:00 | 68 | Hathazari | 61 | 13:00 | 134 | New | 52 | 18:30
3 | Aftabnagar | 26 | 13:00 | 69 | Hatirjheel | 27 | 15:00 | 135 | Niamatpur | 59 | 13:00
4 | Agargaon | 88 | 13:00 | 70 | Ishurdi | 49 | 18:30 | 136 | Noapara | 39 | 19:00
5 | Agrabad | 44 | 18:00 | 71 | Jaldhaka | 54 | 18:00 | 137 | PHP | 8 | 09:00
6 | Amnura | 26 | 08:00 | 72 | Jamalpur | 88 | 18:30 | 138 | Pabna | 79 | 18:30
7 | Ashuganj | 59 | 13:00 | 73 | Jashore | 101 | 13:00 | 139 | Palashbari | 84 | 18:30
8 | BSRM | 201 | 14:00 | 74 | Jhenaidah | 99 | 18:00 | 140 | Panchagarh | 48 | 18:30
9 | Bagerhat | 67 | 18:30 | 75 | Joydebpur | 110 | 18:00 | 141 | Patiya | 6.3 | 18:30
10 | Bajitpur | 63 | 18:00 | 76 | Joypurhat | 44 | 18:00 | 142 | Patuakhali | 40 | 21:00
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 16 | 10:00 | 143 | Payra | 28 | 18:00
12 | Bakulia | 63 | 13:00 | 78 | KSRM | 18 | 10:00 | 144 | Postogola | 42 | 13:00
13 | Banani | 32 | 14:00 | 79 | Kabirpur | 178 | 12:00 | 145 | Purbachal | 20 | 12:00
14 | Bangabhaban | 9 | 12:00 | 80 | Kachua | 57 | 19:30 | 146 | Purbasadipur | 124 | 18:30
15 | Barapukuria | 52 | 18:30 | 81 | Kallyanpur | 75 | 13:00 | 147 | Rahanpur | 24 | 20:00
16 | Barguna | 14 | 00:00 | 82 | Kalurghat | 32 | 12:00 | 148 | Rahim | 47 | 13:00
17 | Barishal | 90 | 13:00 | 83 | Kamrangirchar | 66 | 12:00 | 149 | Rajbari | 61 | 18:00
18 | Barishal-230 | 64 | 18:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 109 | 18:00
19 | Baroaulia | 50 | 18:00 | 85 | Kasba | 23 | 18:00 | 151 | Rajshahi | 70 | 21:00
20 | Baroirhat | 43 | 20:00 | 86 | Kazla | 81 | 18:30 | 152 | Rajshahi-230 | 74 | 13:00
21 | Bashundhara | 149 | 13:00 | 87 | Keranigonj | 65 | 13:00 | 153 | Ramganj | 66 | 19:30
22 | BashundharaCement | 7 | 08:00 | 88 | Khagrachori | 26 | 18:00 | 154 | Rampur | 26 | 12:00
23 | Beanibazar | 48 | 19:00 | 89 | Khulna | 50 | 13:00 | 155 | Rangamati | 13 | 18:00
24 | Benapole | 68 | 08:00 | 90 | Khulshi | 151 | 13:00 | 156 | Rangpur | 110 | 18:30
25 | Bhaluka | 132 | 20:00 | 91 | Kishoreganj | 95 | 18:00 | 157 | Ruppur | 2.2 | 09:00
26 | Bhandaria | 36 | 21:00 | 92 | Kodda | 247 | 18:00 | 158 | SSM | 3 | 06:00
27 | Bhangura | 25 | 18:00 | 93 | Kulaura | 29 | 18:00 | 159 | Saidpur | 96 | 18:00
28 | Bheramara(GK) | 43 | 18:00 | 94 | Kurigram | 51 | 08:00 | 160 | Satkhira | 97 | 18:30
29 | Bhulta | 195 | 08:00 | 95 | Kushtia | 121 | 18:00 | 161 | Satmasjid | 77 | 13:00
30 | Bog-Sherpur | 58 | 18:30 | 96 | Laksam | 23 | 18:00 | 162 | Savar | 186 | 12:00
31 | Bogura | 114 | 18:30 | 97 | Lakshmipur | 24 | 18:30 | 163 | SevenRings | 15.72 | 16:00
32 | Borhanuddin | 65 | 20:00 | 98 | Lalbag | 56 | 13:00 | 164 | ShahCement | 32 | 00:00
33 | Brahmanbaria | 94 | 18:00 | 99 | Lalmonirhat | 45 | 18:30 | 165 | Shahjadpur | 60 | 19:30
34 | Cantonment | 72 | 13:00 | 100 | MI_Cement | 15.8 | 00:00 | 166 | Shahjibazar | 94 | 21:00
35 | Chandina | 11 | 19:30 | 101 | Madanganj | 37 | 14:00 | 167 | Shahmirpur | 39 | 18:00
36 | Chandpur | 52 | 19:30 | 102 | Madaripur | 77 | 13:00 | 168 | Shariatpur | 56 | 20:00
37 | Chandraghona | 27 | 18:00 | 103 | Madartek | 52 | 13:00 | 169 | Sherpur | 122 | 08:00
38 | Chapai | 52 | 13:00 | 104 | Madunaghat | 36 | 18:00 | 170 | Shikalbaha | 20 | 10:00
39 | Charsaidpur | 44 | 11:00 | 105 | Magura | 51 | 18:00 | 171 | Shitalakhya | 60.4 | 12:00
40 | Chauddagram | 48 | 18:00 | 106 | Mahasthangarh | 48 | 18:30 | 172 | Sholosohor | 34 | 12:00
41 | Chhatak | 21 | 19:00 | 107 | Maijdee | 30 | 20:00 | 173 | Shyampur | 156 | 13:00
42 | Chowmuhani | 107 | 19:30 | 108 | Manikganj | 102 | 18:00 | 174 | Siddhirganj | 104 | 12:00
43 | Chuadanga | 81 | 18:00 | 109 | Maniknagar | 48 | 13:00 | 175 | Sirajganj | 84 | 19:00
44 | Coxsbazar | 109 | 18:00 | 110 | Matarbari | 53 | 18:00 | 176 | Sonargaon | 125 | 18:30
45 | Cumilla(N) | 101 | 18:00 | 111 | Matuail | 45 | 09:00 | 177 | Sreemongol | 54 | 18:00
46 | Cumilla(S) | 124 | 13:00 | 112 | Metrorail_Motijheel | 28 | 20:00 | 178 | Sreepur | 93 | 12:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 0 | 00:00 | 179 | Srinagar | 30.8 | 21:00
48 | Daudkandi | 108 | 12:00 | 114 | Millgate | 70 | 10:00 | 180 | Sunamganj | 40 | 18:00
49 | DhakaUniversity | 46 | 14:00 | 115 | Mirpur | 114 | 14:00 | 181 | Sylhet | 44 | 18:00
50 | Dhamrai | 82 | 18:00 | 116 | Mirsorai | 32 | 11:00 | 182 | Sylhet-132 | 78 | 13:00
51 | Dhanmondi | 74 | 14:00 | 117 | Mirzapur | 39 | 21:00 | 183 | TK | 14.5 | 09:00
52 | Dohazari | 71 | 20:00 | 118 | Mithapukur | 78 | 19:00 | 184 | Tangail | 126 | 18:00
53 | Faridpur | 115 | 18:00 | 119 | Modern | N/A | N/A | 185 | Taraganj | 17 | 18:00
54 | Fatullah | 94 | 12:00 | 120 | Mogbazar | 46.4 | 13:00 | 186 | Tasnim | 19 | 11:00
55 | Fenchuganj | 26 | 18:00 | 121 | Mongla | 43 | 14:00 | 187 | Thakurgaon | 71 | 18:30
56 | Feni | 81 | 13:00 | 122 | Motijheel | 31 | 13:00 | 188 | Tongi | 121 | 11:00
57 | GPH | 83 | 19:00 | 123 | Muktagacha | 29 | 08:00 | 189 | Ullahpara | 25 | 18:00
58 | Ghatail | 66 | 08:00 | 124 | Munshiganj | 71 | 15:00 | 190 | Ullon | 40 | 14:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 0 | 00:00 | 191 | Uttara | 54 | 18:00
60 | Ghorashal-230 | 82 | 18:00 | 126 | Mymensingh | 145 | 18:00 | 192 | UttaraNew | 31 | 13:00
61 | Goalpara | 33 | 13:00 | 127 | Naogaon | 94 | 13:00 | 193 | Zigatola | 72 | 13:00
62 | Gollamari | 78 | 13:00 | 128 | Narail | 44 | 18:30
63 | Gopalganj | 80 | 18:30 | 129 | Narinda | 54 | 13:00
64 | Gulshan | 70 | 13:00 | 130 | Narshingdi | 138 | 18:30
65 | Halishahar | 58 | 15:00 | 131 | Natore | 106 | 18:00
66 | HaripurSBU | 123 | 11:00 | 132 | Nawabganj | 31 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 11-01-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 9190 | 0 |  | 9190
1:00 | 8560 | 0 |  | 8560
2:00 | 8020 | 0 |  | 8020
3:00 | 7751 | 0 |  | 7751
4:00 | 7582 | 0 |  | 7582
5:00 | 7521 | 0 |  | 7521
6:00 | 7920 | 0 |  | 7920
7:00 | 8726.66 | 0 |  | 8726.66
8:00 | 9845.55 | 0 |  | 9845.55
9:00 | 10396.79 | 0 |  | 10396.79
10:00 | 9981.98 | 0 |  | 9981.98
11:00 | 9970.05 | 0 |  | 9970.05
12:00 | 10487.28 | 0 |  | 10487.28
13:00 | 11073.39 | 0 |  | 11073.39
14:00 | 10573.2 | 0 |  | 10573.2
15:00 | 10080 | 0 |  | 10080
16:00 | 9716.58 | 0 |  | 9716.58
17:00 | 9814.67 | 0 |  | 9814.67
18:00 | 11126.21 | 0 |  | 11126.21
19:00 | 11379.07 | 0 |  | 11379.07
19:30 | 11073.05 | 0 |  | 11073.05
20:00 | 11031.64 | 0 |  | 11031.64
21:00 | 10953.1 | 0 |  | 10953.1
22:00 | 10354.17 | 0 |  | 10354.17
23:00 | 10047.69 | 0 |  | 10047.69
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 11-01-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4288 | 4902 | 9190 | DAILY GENERATION CURVE
00:30 | 4284.5 | 4590.5 | 8875
01:00 | 4281 | 4279 | 8560 | 11-01-2026
01:30 | 4248 | 4042 | 8290
02:00 | 4215 | 3805 | 8020
02:30 | 4221.5 | 3664 | 7885.5
03:00 | 4228 | 3523 | 7751
03:30 | 4258.5 | 3408 | 7666.5
04:00 | 4289 | 3293 | 7582
04:30 | 4301.5 | 3250 | 7551.5
05:00 | 4314 | 3207 | 7521
05:30 | 4429.5 | 3291 | 7720.5
06:00 | 4545 | 3375 | 7920
06:30 | 4679.42 | 3643.91 | 8323.33
07:00 | 4813.84 | 3912.82 | 8726.66
07:30 | 4830.73 | 4455.375 | 9286.105
08:00 | 4847.62 | 4997.93 | 9845.55
08:30 | 4884.535 | 5236.635 | 10121.17
09:00 | 4921.45 | 5475.34 | 10396.79
09:30 | 4855.665 | 5333.72 | 10189.385
10:00 | 4789.88 | 5192.1 | 9981.98
10:30 | 4859.41 | 5116.605 | 9976.015
11:00 | 4928.94 | 5041.11 | 9970.05
11:30 | 5031.62 | 5197.045 | 10228.665
12:00 | 5134.3 | 5352.98 | 10487.28
12:30 | 5270.725 | 5509.61 | 10780.335
13:00 | 5407.15 | 5666.24 | 11073.39
13:30 | 5411.575 | 5411.72 | 10823.295
14:00 | 5416 | 5157.2 | 10573.2
14:30 | 5343.165 | 4983.435 | 10326.6
15:00 | 5270.33 | 4809.67 | 10080
15:30 | 5179.285 | 4719.005 | 9898.29
16:00 | 5088.24 | 4628.34 | 9716.58
16:30 | 5157.085 | 4608.54 | 9765.625
17:00 | 5225.93 | 4588.74 | 9814.67
17:30 | 5518.965 | 4951.475 | 10470.44
18:00 | 5812 | 5314.21 | 11126.21
18:30 | 5684 | 5568.64 | 11252.64
19:00 | 5556 | 5823.07 | 11379.07
19:30 | 5348 | 5725.05 | 11073.05
20:00 | 5300 | 5731.64 | 11031.64
20:30 | 5274.25 | 5718.12 | 10992.37 |  | Executive Engineer
21:00 | 5248.5 | 5704.6 | 10953.1 |  | Network Operation Division
21:30 | 5011.25 | 5642.385 | 10653.635
22:00 | 4774 | 5580.17 | 10354.17
22:30 | 4674 | 5526.93 | 10200.93
23:00 | 4574 | 5473.69 | 10047.69

## En-Curve
QF-LDC-12
Date | 11-01-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2140 | 1104 | 871 | 0 | 94 | 1223 | 46 | 3693 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2147.5 | 1096 | 826 | 0 | 89 | 1124.5 | 46 | 3536.5 | 0 | 0 | 9.5 | 0 | 0 | 0 | 0 | 11-01-2026
01:00 | 2155 | 1088 | 781 | 0 | 84 | 1026 | 46 | 3380 | 0 | 0 | 0 | 0 | 0 | 0 | 0
01:30 | 2179.5 | 1056.5 | 734.5 | 0 | 84 | 940.5 | 46 | 3249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Generated | 235.2467 |  | MKWHr
02:00 | 2204 | 1025 | 688 | 0 | 84 | 855 | 46 | 3118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2228.5 | 1036 | 558 | 0 | 81 | 847.5 | 46 | 3088.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total Energy Requirement | 235.2467 |  | MKWHr
03:00 | 2253 | 1047 | 428 | 0 | 78 | 840 | 46 | 3059 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2271.5 | 1065.5 | 325 | 0 | 77 | 837.5 | 46 | 3044 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:00 | 2290 | 1084 | 222 | 0 | 76 | 835 | 46 | 3029 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2274.5 | 1114.5 | 222 | 0 | 80 | 835 | 46 | 2979.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:00 | 2259 | 1145 | 222 | 0 | 84 | 835 | 46 | 2930 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 2353.5 | 1178 | 222 | 0 | 82 | 837.5 | 46 | 3001.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:00 | 2448 | 1211 | 222 | 0 | 80 | 840 | 46 | 3073 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:30 | 2542 | 1231.5 | 341 | 0 | 84 | 890.5 | 46 | 3166.5 | 4.33 | 0 | 17.5 | 0 | 0 | 0 | 0
07:00 | 2636 | 1252 | 460 | 0 | 88 | 941 | 46 | 3260 | 8.66 | 0 | 35 | 0 | 0 | 0 | 0
07:30 | 2591.5 | 1253.5 | 574.5 | 0 | 94 | 1101.575 | 46 | 3520 | 50.03 | 0 | 55 | 0 | 0 | 0 | 0
08:00 | 2547 | 1255 | 689 | 0 | 100 | 1262.15 | 46 | 3780 | 91.4 | 0 | 75 | 0 | 0 | 0 | 0
08:30 | 2474 | 1213.75 | 782.5 | 0 | 103 | 1290.685 | 46 | 3844 | 161.735 | 26 | 179.5 | 0 | 0 | 0 | 0
09:00 | 2401 | 1172.5 | 876 | 0 | 106 | 1319.22 | 46 | 3908 | 232.07 | 52 | 284 | 0 | 0 | 0 | 0
09:30 | 2433.5 | 1133.5 | 876.5 | 0 | 105 | 1216.315 | 46 | 3712.5 | 285.32 | 52 | 328.75 | 0 | 0 | 0 | 0
10:00 | 2466 | 1094.5 | 877 | 0 | 104 | 1113.41 | 46 | 3517 | 338.57 | 52 | 373.5 | 0 | 0 | 0 | 0
10:30 | 2445 | 1130.5 | 877 | 0 | 108 | 1060.48 | 46 | 3464.5 | 411.285 | 52 | 381.25 | 0 | 0 | 0 | 0
11:00 | 2424 | 1166.5 | 877 | 0 | 112 | 1007.55 | 46 | 3412 | 484 | 52 | 389 | 0 | 0 | 0 | 0
11:30 | 2445 | 1186.65 | 876.5 | 0 | 114 | 1041.715 | 46 | 3527.5 | 530.5 | 52 | 408.8 | 0 | 0 | 0 | 0
12:00 | 2466 | 1206.8 | 876 | 0 | 116 | 1075.88 | 46 | 3643 | 577 | 52 | 428.6 | 0 | 0 | 0 | 0
12:30 | 2434 | 1245.4 | 875.5 | 0 | 119 | 1151.42 | 46 | 3710.5 | 571.515 | 52 | 575 | 0 | 0 | 0 | 0
13:00 | 2402 | 1284 | 875 | 0 | 122 | 1226.96 | 46 | 3778 | 566.03 | 52 | 721.4 | 0 | 0 | 0 | 0
13:30 | 2387 | 1224.5 | 876 | 0 | 120 | 1146.97 | 46 | 3682.5 | 510.625 | 52 | 775.2 | 0 | 0 | 2.5 | 0
14:00 | 2372 | 1165 | 877 | 0 | 118 | 1066.98 | 46 | 3587 | 455.22 | 52 | 829 | 0 | 0 | 5 | 0
14:30 | 2331 | 1194.1 | 877 | 0 | 116 | 1022.18 | 46 | 3517.5 | 397.07 | 52 | 770.25 | 0 | 0 | 3.5 | 0
15:00 | 2290 | 1223.2 | 877 | 0 | 114 | 977.38 | 46 | 3448 | 338.92 | 52 | 711.5 | 0 | 0 | 2 | 0
15:30 | 2297.5 | 1234.35 | 877 | 0 | 114 | 953.29 | 46 | 3418.5 | 241.9 | 52 | 662.75 | 0 | 0 | 1 | 0
16:00 | 2305 | 1245.5 | 877 | 0 | 114 | 929.2 | 46 | 3389 | 144.88 | 52 | 614 | 0 | 0 | 0 | 0
16:30 | 2275.5 | 1207.75 | 877 | 0 | 114 | 977.29 | 46 | 3406.5 | 86.585 | 52 | 722.5 | 0 | 0 | 0.5 | 0
17:00 | 2246 | 1170 | 877 | 0 | 114 | 1025.38 | 46 | 3424 | 28.29 | 52 | 831 | 0 | 0 | 1 | 0
17:30 | 2339 | 1181.25 | 877 | 0 | 116 | 1135.795 | 46 | 3624 | 14.145 | 78 | 1058.75 | 0 | 0 | 0.5 | 0
18:00 | 2432 | 1192.5 | 877 | 0 | 118 | 1246.21 | 46 | 3824 | 0 | 104 | 1286.5 | 0 | 0 | 0 | 0
18:30 | 2442 | 1241.75 | 876.5 | 0 | 117 | 1344.14 | 46 | 3932 | 0 | 86.5 | 1166.75 | 0 | 0 | 0 | 0
19:00 | 2452 | 1291 | 876 | 0 | 116 | 1442.07 | 46 | 4040 | 0 | 69 | 1047 | 0 | 0 | 0 | 0
19:30 | 2454 | 1329 | 876 | 0 | 114 | 1461.05 | 46 | 3981 | 0 | 69 | 743 | 0 | 0 | 0 | 0
20:00 | 2453 | 1305 | 877 | 0 | 108 | 1450.64 | 46 | 3992 | 0 | 69 | 731 | 0 | 0 | 0 | 0
20:30 | 2399.5 | 1331.5 | 877 | 0 | 110 | 1451.62 | 46 | 3992 | 0 | 60.5 | 724.25 | 0 | 0 | 0 | 0
21:00 | 2346 | 1358 | 877 | 0 | 112 | 1452.6 | 46 | 3992 | 0 | 52 | 717.5 | 0 | 0 | 0 | 0
21:30 | 2365.5 | 1325 | 877 | 0 | 107 | 1450.885 | 46 | 3968.5 | 0 | 26 | 487.75 | 0 | 0 | 0 | 0
22:00 | 2385 | 1292 | 877 | 0 | 102 | 1449.17 | 46 | 3945 | 0 | 0 | 258 | 0 | 0 | 0 | 0
22:30 | 2396 | 1287 | 876.5 | 0 | 105 | 1454.43 | 46 | 3885 | 0 | 0 | 151 | 0 | 0 | 0 | 0
23:00 | 2407 | 1282 | 876 | 0 | 108 | 1459.69 | 46 | 3825 | 0 | 0 | 44 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 11-01-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 424 | 05:00 | 400 | 12:00 | Meghnaghat | 427 | 04:00 | 403 | 12:00
Ashuganj | 423 | 05:00 | 402 | 12:00 | Payra | 424 | 04:00 | 416 | 08:00
Bhulta | 406 | 05:00 | 383 | 12:00 | Rahanpur | 420 | 04:00 | 396 | 13:00
Bibiana | 422 | 05:00 | 408 | 08:00 | Rampal | 418 | 05:00 | 400 | 12:00
BIPTC | 407 | 02:00 | 392 | 09:00
Bogura | 417 | 04:00 | 384 | 13:00
Gopalganj | 423 | 05:00 | 402 | 12:00
Kaliakoir | 421 | 05:00 | 398 | 12:00
Korerhat | 425 | 04:00 | 408 | 12:00
Madunaghat | 416 | 04:00 | 405 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 246 | 05:00 | 230 | 12:00 | Kachua | 241 | 04:00 | 233 | 12:00
AKSML | 239 | 05:00 | 230 | 12:00 | Kaliakoir | 245 | 04:00 | 232 | 08:00
Aminbazar | 246 | 06:00 | 231 | 12:00 | Keranigonj | 244 | 05:00 | 228 | 12:00
Ashuganj | 238 | 02:00 | 225 | 13:00 | Khulna(S) | 245 | 04:00 | 229 | 12:00
Ashuganj-400 | 238 | 02:00 | 225 | 13:00 | Korerhat | 241 | 03:00 | 231 | 12:00
Baghabari | 239 | 03:00 | 226 | 12:00 | Madunaghat | 238 | 05:00 | 231 | 12:00
Barapukuria | 230 | 03:00 | 204 | 08:00 | Madunaghat-400 | 239 | 05:00 | 232 | 12:00
Barapukuria-230 | 230 | 03:00 | 204 | 08:00 | Maniknagar | 241 | 06:00 | 228 | 12:00
Barishal | 239 | 04:00 | 229 | 12:00 | Meghnaghat | 247 | 22:00 | 234 | 12:00
Bheramara | 240 | 04:00 | 221 | 12:00 | Meghnaghat-400 | 243 | 04:00 | 228 | 12:00
Bhulta | 245 | 05:00 | 230 | 12:00 | Mirsorai | 242 | 05:00 | 231 | 12:00
Bibiana | 241 | 03:00 | 233 | 08:00 | Rajshahi | 240 | 05:00 | 220 | 08:00
BIPTC | 240 | 04:00 | 222 | 08:00 | Rampal | 242 | 05:00 | 228 | 13:00
Bogura | 245 | 05:00 | 225 | 08:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 244 | 04:00 | 224 | 08:00 | Rampura | 244 | 04:00 | 229 | 12:00
Borhanuddin | 240 | 03:00 | 235 | 19:00 | Shikalbaha | 235 | 02:00 | 227 | 12:00
BSRM | 241 | 05:00 | 230 | 12:00 | Shyampur | 243 | 05:00 | 227 | 12:00
Cumilla(N) | 238 | 04:00 | 228 | 12:00 | Siddhirganj | 241 | 03:00 | 235 | 18:30
Faridpur | 239 | 04:00 | 227 | 12:00 | Sirajgonj | 248 | 04:00 | 230 | 08:00
Fenchuganj | 243 | 06:00 | 236 | 12:00 | Sreepur | 239 | 05:00 | 221 | 08:00
Feni | 242 | 04:00 | 230 | 12:00 | Tongi | 240 | 21:00 | 227 | 12:00
Ghorashal | 244 | 05:00 | 230 | 12:00
Ghorashal-230 | 234 | 04:00 | 213 | 12:00
Gopalganj | 237 | 04:00 | 225 | 12:00
GPH | 239 | 04:00 | 230 | 12:00
Haripur | 244 | 05:00 | 230 | 12:00
Hasnabad | 239 | 01:00 | 228 | 13:00
Hathazari | 234 | 01:00 | 227 | 12:00
Ishurdi | 242 | 05:00 | 225 | 08:00
Jhenaidah | 242 | 04:00 | 221 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 05:00 | 127 | 12:00 | Laksam | 139 | 05:00 | 133 | 12:00 | UttaraNew | 140 | 04:00 | 129 | 12:00
Agargaon | 140 | 04:00 | 130 | 12:00 | Lakshmipur | 135 | 03:00 | 129 | 11:00 | Zigatola | 138 | 05:00 | 127 | 12:00
Agrabad | 138 | 01:00 | 133 | 12:00 | Lalbag | 134 | 03:00 | 127 | 12:00
AKS | 135 | 01:00 | 132 | 11:00 | Lalmonirhat | 130 | 00:00 | 119 | 08:00
Aminbazar | 139 | 05:00 | 131 | 12:00 | Madanganj | 137 | 01:00 | 133 | 12:00
Amnura | 139 | 04:00 | 127 | 13:00 | Madaripur | 142 | 05:00 | 135 | 12:00
Ashuganj | 139 | 04:00 | 135 | 08:00 | Madartek | 135 | 04:00 | 126 | 12:00
Bagerhat | 134 | 02:00 | 124 | 13:00 | Madunaghat | 139 | 03:00 | 135 | 11:00
Bajitpur | 135 | 05:00 | 128 | 12:00 | Magura | 139 | 03:00 | 124 | 12:00
Bakerganj | 138 | 06:00 | 135 | 18:00 | Mahasthangarh | 138 | 05:00 | 125 | 08:00
Bakulia | 139 | 04:00 | 134 | 12:00 | Maijdee | 135 | 03:00 | 129 | 12:00
Banani | 135 | 03:00 | 125 | 13:00 | Manikganj | 129 | 18:00 | 123 | 12:00
Bangabhaban | 140 | 05:00 | 131 | 12:00 | Maniknagar | 141 | 04:00 | 131 | 12:00
Barapukuria | 139 | 03:00 | 123 | 08:00 | Matarbari | 130 | 05:00 | 121 | 18:00
Barguna | 138 | 05:00 | 135 | 08:00 | Matuail | 140.5 | 05:00 | 115 | 00:00
Barishal | 141 | 03:00 | 133 | 12:00 | Metrorail_Motijheel | 141 | 03:00 | 131 | 12:00
Barishal-230 | 141 | 04:00 | 133 | 12:00 | Metrorail_Uttara | 140 | 04:00 | 132 | 08:00
Baroaulia | 138 | 06:00 | 134 | 10:00 | Millgate | 136 | 04:00 | 124 | 12:00
Baroirhat | 137 | 05:00 | 127 | 12:00 | Mirpur | 139 | 04:00 | 131 | 12:00
Bashundhara | 136 | 03:00 | 126 | 13:00 | Mirzapur | 137 | 04:00 | 128 | 08:00
BashundharaCement | 137 | 01:00 | 131 | 19:30 | Mithapukur | 137 | 04:00 | 122 | 08:00
Beanibazar | 134 | 03:00 | 131 | 12:00 | MI_Cement | 138 | 05:00 | 125 | 12:00
Benapole | 138 | 04:00 | 117 | 13:00 | Modern | 0 | 00:00 | 0 | 00:00
Bhaluka | 133 | 05:00 | 117 | 08:00 | Mogbazar | 137 | 03:00 | 127 | 13:00
Bhandaria | 136 | 00:00 | 131 | 14:00 | Mongla | 133 | 05:00 | 124 | 13:00
Bhangura | 141 | 04:00 | 130 | 13:00 | Motijheel | 140 | 05:00 | 131 | 12:00
Bheramara | 140 | 04:00 | 132 | 08:00 | Muktagacha | 133 | 06:00 | 125 | 23:00
Bheramara(GK) | 139 | 04:00 | 133 | 09:00 | Munshiganj | 138 | 02:00 | 131 | 16:00
Bhulta | 132 | 04:00 | 126 | 12:00 | Muradnagar | 137 | 05:00 | 127 | 12:00
Bog-Sherpur | 140 | 05:00 | 127 | 08:00 | Mymensingh | 134 | 10:00 | 111 | 08:00
Bogura | 140 | 05:00 | 127 | 13:00 | Naogaon | 136 | 03:00 | 123 | 13:00
Bogura-230 | 140 | 05:00 | 127 | 08:00 | Narail | 140 | 04:00 | 122 | 13:00
Brahmanbaria | 133 | 04:00 | 125 | 19:30 | Narinda | 141 | 04:00 | 131 | 12:00
Cantonment | 140 | 05:00 | 130 | 12:00 | Narshingdi | 138 | 04:00 | 120 | 11:00
Chandina | 140 | 05:00 | 132 | 12:00 | Natore | 138 | 03:00 | 127 | 13:00
Chandpur | 139 | 18:00 | 135 | 12:00 | Nawabganj | 138 | 04:00 | 127 | 11:00
Chandraghona | 139 | 05:00 | 136 | 11:00 | Netrakona | 125 | 01:00 | 107 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 138 | 03:00 | 131 | 09:00 | New | 134 | 03:00 | 126 | 12:00
Charsaidpur | 139 | 05:00 | 133 | 08:00 | Niamatpur | 140 | 02:00 | 131 | 08:00
Chauddagram | 137 | 03:00 | 130 | 12:00 | Noapara | 138 | 04:00 | 118 | 13:00
Chhatak | 135 | 04:00 | 129 | 13:00 | Pabna | 140 | 04:00 | 131 | 08:00
Chowmuhani | 135 | 06:00 | 129 | 16:00 | Palashbari | 135 | 03:00 | 121 | 08:00
Chuadanga | 139 | 03:00 | 122 | 13:00 | Panchagarh | 139 | 19:00 | 124 | 08:00
Coxsbazar | 129 | 08:00 | 122 | 18:00 | Patiya | 138 | 03:00 | 133 | 12:00
Cumilla(N) | 138 | 03:00 | 132 | 12:00 | Patuakhali | 137 | 04:00 | 134 | 00:00
Cumilla(S) | 137 | 04:00 | 125 | 13:00 | Payra | 139 | 03:00 | 136 | 08:00
Daganbhuiyan | 136 | 04:00 | 129 | 12:00 | PHP | 136 | 05:00 | 127 | 13:00
Daudkandi | 133 | 03:00 | 121 | 12:00 | Postogola | 139 | 03:00 | 127 | 12:00
DhakaUniversity | 136 | 04:00 | 126 | 12:00 | Purbachal | 136 | 03:00 | 126 | 12:00
Dhamrai | 139 | 04:00 | 130 | 12:00 | Purbasadipur | 135 | 19:00 | 123 | 08:00
Dhanmondi | 140 | 05:00 | 133.6 | 12:00 | Rahanpur | 140 | 04:00 | 133 | 08:00
Dohazari | 136 | 17:00 | 131 | 12:00 | Rahanpur-400 | 141 | 03:00 | 133 | 08:00
Faridpur | 138 | 03:00 | 132 | 12:00 | Rahim | 140 | 05:00 | 132 | 12:00
Fatullah | 140 | 04:00 | 126 | 12:00 | Rajbari | 139 | 05:00 | 131 | 12:00
Fenchuganj | 138 | 04:00 | 134 | 12:00 | Rajendrapur | 133 | 04:00 | 118 | 08:00
Feni | 133 | 06:00 | 126 | 12:00 | Rajshahi | 136 | 01:00 | 126 | 12:00
Feni-230 | 136 | 04:00 | 128 | 12:00 | Rajshahi-230 | 138 | 04:00 | 127 | 08:00
Ghatail | 132 | 02:00 | 122 | 17:00 | Ramganj | 135 | 01:00 | 131 | 08:00
Ghorashal | 133 | 04:00 | 127 | 13:00 | Rampur | 138 | 03:00 | 133 | 12:00
Goalpara | 138 | 04:00 | 128 | 13:00 | Rampura | 136 | 05:00 | 126 | 12:00
Gollamari | 137 | 04:00 | 128 | 12:00 | Rangamati | 139 | 05:00 | 133 | 12:00
Gopalganj | 141 | 04:00 | 132 | 12:00 | Rangpur | 133 | 19:00 | 123 | 08:00
Gopalganj-400 | 143 | 03:00 | 136 | 12:00 | Ruppur | 140 | 03:00 | 132 | 13:00
Gulshan | 134 | 03:00 | 126 | 12:00 | Saidpur | 135 | 02:00 | 121 | 08:00
Halishahar | 139 | 03:00 | 133 | 12:00 | Satkhira | 136 | 03:00 | 124 | 12:00
Haripur | 139 | 04:00 | 133 | 12:00 | Satmasjid | 140 | 04:00 | 130 | 12:00
HaripurSBU | 140 | 05:00 | 132 | 16:00 | Savar | 139 | 18:00 | 131 | 08:00
Hasnabad | 135 | 01:00 | 128 | 12:00 | SevenRings | 138 | 07:00 | 124 | 13:00
Hathazari | 138 | 02:00 | 134 | 12:00 | ShahCement | 139 | 05:00 | 133 | 08:00
Hatirjheel | 136 | 04:00 | 126 | 12:00 | Shahjadpur | 141 | 00:00 | 133 | 12:00
Ishurdi | 141 | 04:00 | 133 | 08:00 | Shahjibazar | 134 | 04:00 | 128 | 07:00
Jaldhaka | 135 | 05:00 | 119 | 08:00 | Shahmirpur | 139 | 17:00 | 134 | 12:00
Jamalpur | 131 | 10:00 | 123 | 23:00 | Shariatpur | 143 | 04:00 | 135 | 12:00
Jashore | 137 | 03:00 | 119 | 13:00 | Sherpur | 129 | 02:00 | 119 | 23:00
Jhenaidah | 138 | 00:00 | 115 | 08:00 | Shikalbaha | 126 | 06:00 | 124 | 00:00
Jhenaidah-230 | 141 | 04:00 | 126 | 13:00 | Shikalbaha-230 | 140 | 04:00 | 134 | 12:00
Joydebpur | 132 | 03:00 | 124 | 08:00 | Shitalakhya | 138 | 05:00 | 125 | 12:00
Joypurhat | 135 | 05:00 | 123 | 08:00 | Sholosohor | 138 | 00:00 | 134 | 12:00
Juldah | 138 | 05:00 | 133 | 12:00 | Shyampur | 138 | 03:00 | 133 | 09:00
Kabirpur | 139 | 21:00 | 122 | 12:00 | Shyampur-230 | 141 | 04:00 | 131 | 12:00
Kachua | 139 | 04:00 | 134 | 12:00 | Siddhirganj | 139 | 02:00 | 132 | 12:00
Kaliakoir | 141 | 03:00 | 132 | 08:00 | Sirajganj | 140 | 04:00 | 127 | 08:00
Kallyanpur | 138 | 02:00 | 130 | 12:00 | Sonargaon | 138 | 02:00 | 116 | 07:00
Kalurghat | 139 | 04:00 | 135 | 13:00 | Sreemongol | 134 | 03:00 | 130 | 12:00
Kamrangirchar | 138 | 05:00 | 127 | 12:00 | Sreepur | 134 | 05:00 | 121 | 08:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 138 | 05:00 | 127 | 12:00
Kasba | 136 | 03:00 | 128 | 12:00 | SSM | 141 | 04:00 | 140 | 00:00
Kazla | 140 | 04:00 | 130 | 13:00 | Sunamganj | 133 | 03:00 | 129 | 18:30
Keranigonj | 138 | 04:00 | 127 | 12:00 | Sylhet | 135 | 04:00 | 131 | 12:00
Khagrachori | 138 | 04:00 | 132 | 12:00 | Sylhet-132 | 134 | 01:00 | 132 | 11:00
Khulna | 136 | 04:00 | 127 | 08:00 | Tangail | 133 | 03:00 | 122 | 08:00
Khulna(S) | 138 | 04:00 | 128 | 12:00 | Taraganj | 135 | 02:00 | 121 | 08:00
Khulshi | 137 | 04:00 | 132 | 12:00 | Tasnim | 139 | 04:00 | 131 | 16:00
Kishoreganj | 132 | 15:00 | 123 | 07:00 | Thakurgaon | 139 | 19:00 | 122 | 08:00
Kodda | 137 | 21:00 | 127 | 12:00 | TK | 139 | 05:00 | 135 | 19:30
KSRM | 137 | 00:00 | 132 | 12:00 | Tongi | 137 | 03:00 | 128 | 12:00
Kulaura | 138 | 04:00 | 134 | 12:00 | Ullahpara | 139 | 03:00 | 128 | 08:00
Kurigram | 132 | 04:00 | 116 | 08:00 | Ullon | 136 | 05:00 | 126 | 12:00
Kushtia | 134 | 01:00 | 124 | 08:00 | Uttara | 160 | 15:00 | 125 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 11-01-2026 | [28 empty] | Date: | 11-01-2026 | [28 empty] | Date: | 11-01-2026 | [28 empty] | Date: | 11-01-2026 | [28 empty] | Date: | 11-01-2026 | [17 empty] | Date: | 11-01-2026
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [17 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 37 | 345 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1080 | 0 | 0 | 8 | 0 | 285 | 0 | 51 | 10 | 190 | 34 | 0 | 110 | 0 | 0 | 11 | 0 | 94 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 60 | 35 | 0 | 4 | 0 | 78 | 30 | 0 | 0 | 157 | 0 | 19 | 0 | 68 | 0 | 0 | 0 | 4288 | 871 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1038 | 0 | 0 | 0 | 1223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 136 | 180 | 0 | 423 | 535 | 0 | 4902 | 9190 | 94.93
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 37 | 345 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1100 | 0 | 0 | 8 | 10 | 295 | 0 | 51 | 10 | 194 | 34 | 0 | 110 | 0 | 0 | 10 | 0 | 84 | 0 | 0 | 0 | 305 | 0 | 0 | 41 | 60 | 35 | 0 | 0 | 0 | 78 | 30 | 0 | 0 | 157 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 4281 | 781 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 896 | 0 | 0 | 0 | 1026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 136 | 180 | 0 | 313 | 450 | 0 | 4279 | 8560 | 96.93
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 37 | 345 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1055 | 0 | 0 | 8 | 30 | 310 | 0 | 10 | 10 | 205 | 34 | 0 | 109 | 0 | 0 | 10 | 0 | 84 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 60 | 35 | 0 | 0 | 0 | 41 | 20 | 0 | 0 | 157 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 4215 | 688 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 786 | 0 | 0 | 0 | 855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 136 | 180 | 0 | 256 | 400 | 0 | 3805 | 8020 | 96.92
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 38 | 345 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1012 | 0 | 0 | 8 | 45 | 320 | 0 | 10 | 10 | 206 | 34 | 0 | 109 | 0 | 0 | 10 | 0 | 78 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 60 | 41 | 0 | 0 | 0 | 41 | 20 | 0 | 0 | 157 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 4228 | 428 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 798 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 136 | 180 | 0 | 256 | 400 | 0 | 3523 | 7751 | 96.92
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 38 | 345 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1000 | 0 | 0 | 8 | 105 | 300 | 0 | 10 | 10 | 197 | 34 | 0 | 110 | 0 | 0 | 10 | 0 | 76 | 0 | 0 | 0 | 320 | 0 | 0 | 41 | 60 | 73 | 0 | 0 | 0 | 41 | 20 | 0 | 0 | 157 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 4289 | 222 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 778 | 0 | 0 | 0 | 835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 136 | 180 | 0 | 256 | 400 | 0 | 3293 | 7582 | 96.91
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 34 | 345 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 953 | 0 | 0 | 8 | 145 | 310 | 0 | 10 | 10 | 199 | 34 | 0 | 110 | 0 | 0 | 10 | 0 | 84 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 60 | 152 | 0 | 0 | 0 | 42 | 20 | 0 | 0 | 157 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 4314 | 222 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 777 | 0 | 0 | 0 | 835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 120 | 180 | 0 | 256 | 350 | 0 | 3207 | 7521 | 96.91
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 34 | 345 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1025 | 0 | 0 | 8 | 250 | 320 | 0 | 10 | 10 | 206 | 34 | 0 | 109 | 0 | 0 | 10 | 0 | 80 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 60 | 145 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 157 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 4545 | 222 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 828 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 135 | 220 | 0 | 259 | 360 | 0 | 3375 | 7920 | 96.9
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36 | 46 | 0 | 34 | 345 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1100 | 1 | 0 | 8 | 350 | 325 | 0 | 39 | 0 | 208 | 34 | 0 | 109 | 0 | 0 | 10 | 0 | 88 | 0 | 2 | 0 | 320 | 0 | 0 | 41 | 60 | 148 | 0 | 0 | 0 | 75 | 20 | 0 | 0 | 157 | 0 | 19 | 16 | 71 | 0 | 0.48 | 0 | 4813.84 | 460 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 823 | 0 | 0 | 0 | 941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29 | 1 | 0 | 0 | 0.48 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 253 | 135 | 220 | 0 | 306 | 433 | 0 | 3912.82 | 8726.66 | 96.9
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 300 | 0 | 0 | 5 | 0 | 27 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38 | 46 | 0 | 12 | 345 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1175 | 2 | 0 | 0 | 280 | 318 | 0 | 44 | 0 | 189 | 0 | 0 | 110 | 0 | 0 | 12 | 0 | 100 | 0 | 6 | 0 | 315 | 0 | 0 | 41 | 60 | 160 | 1 | 0 | 0 | 75 | 20 | 0 | 0 | 157 | 0 | 19 | 56 | 71 | 0 | 9.24 | 0 | 4847.62 | 689 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 1037 | 0 | 0 | 0 | 1262.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.25 | 17 | 0 | 0 | 8.68 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 1 | 16 | 0.06 | 0 | 283 | 135 | 220 | 0 | 440 | 500 | 0 | 4997.93 | 9845.55 | 96.89
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 28 | 0 | 7 | 0 | 75 | 0 | 0 | 49 | 0 | 0 | 0 | 345 | 0 | 0 | 280 | 0 | 0 | 12 | 52 | 30.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 1 | 46 | 0 | 5 | 345 | 0 | 0 | 0 | 0 | 4 | 160 | 0 | 0 | 0 | 1126 | 0 | 0 | 0 | 245 | 280 | 0 | 44 | 0 | 185 | 0 | 0 | 110 | 21 | 0 | 12 | 0 | 106 | 0 | 18 | 0 | 310 | 0 | 0 | 41 | 60 | 156 | 4 | 0 | 0 | 75 | 30 | 0 | 0 | 160 | 0 | 19 | 56 | 64 | 1 | 6.95 | 0 | 4921.45 | 876 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 1107 | 0 | 0 | 0 | 1319.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.8 | 50 | 0 | 0 | 20.41 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.84 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 2.7 | 51 | 0.37 | 0 | 270 | 100 | 180 | 0 | 500 | 560 | 0 | 5475.34 | 10396.79 | 96.89
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 30.5 | 0 | 34 | 0 | 95 | 0 | 0 | 48 | 0 | 0 | 0 | 270 | 0 | 0 | 280 | 0 | 0 | 19 | 52 | 28.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 1.65 | 46 | 0 | 5 | 306 | 0 | 0 | 0 | 0 | 16 | 160 | 0 | 0 | 0 | 1027 | 0 | 0 | 0 | 230 | 280 | 0 | 44 | 0 | 177 | 0 | 0 | 108 | 50 | 0 | 13 | 0 | 104 | 0 | 19 | 0 | 310 | 0 | 0 | 41 | 60 | 152 | 8 | 0 | 0 | 77 | 30 | 0 | 0 | 160 | 0 | 19 | 56 | 63 | 1 | 24.23 | 0 | 4789.88 | 877 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 980 | 0 | 0 | 0 | 1113.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.71 | 77 | 0 | 0 | 33.79 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.97 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 66 | 0.22 | 0 | 244 | 100 | 180 | 0 | 400 | 560 | 0 | 5192.1 | 9981.98 | 96.88
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 42 | 0 | 34 | 0 | 95 | 0 | 0 | 51 | 0 | 0 | 0 | 290 | 0 | 0 | 290 | 0 | 0 | 24 | 52 | 27.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 1.97 | 46 | 0 | 5 | 310 | 0 | 0 | 0 | 0 | 15 | 160 | 0 | 0 | 0 | 1080 | 0 | 0 | 0 | 230 | 250 | 0 | 44 | 0 | 198 | 0 | 0 | 108 | 51 | 0 | 11 | 0 | 112 | 0 | 41 | 0 | 320 | 0 | 0 | 42 | 60 | 159 | 10 | 0 | 0 | 75 | 30 | 0 | 0 | 160 | 0 | 19 | 57 | 31 | 1 | 36.47 | 0 | 4928.94 | 877 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 900 | 0 | 0 | 0 | 1007.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.51 | 62 | 0 | 0 | 42.93 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.69 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 5.2 | 122 | 0.23 | 0 | 265 | 100 | 220 | 0 | 357 | 500 | 0 | 5041.11 | 9970.05 | 96.88
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 48.6 | 0 | 34 | 0 | 110 | 20 | 0 | 50 | 0 | 0 | 0 | 335 | 0 | 0 | 300 | 0 | 0 | 26 | 52 | 26.8 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 1.63 | 46 | 0 | 5 | 312 | 0 | 0 | 0 | 0 | 15 | 160 | 0 | 0 | 0 | 1187 | 17 | 0 | 0 | 230 | 226 | 0 | 44 | 0 | 209 | 0 | 0 | 106 | 49 | 0 | 13 | 0 | 116 | 0 | 38 | 0 | 315 | 0 | 0 | 42 | 60 | 157 | 10 | 0 | 0 | 77 | 30 | 0 | 0 | 160 | 0 | 19 | 58 | 32 | 2 | 38.27 | 0 | 5134.3 | 876 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 921 | 0 | 0 | 0 | 1075.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.82 | 102 | 0 | 0 | 47.24 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.17 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 5.4 | 127 | 0.47 | 0 | 289 | 132 | 220 | 0 | 429 | 505 | 0 | 5352.98 | 10487.28 | 96.87
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 50.4 | 0 | 43 | 0 | 195 | 30 | 35 | 101 | 0 | 0 | 0 | 400 | 0 | 35 | 300 | 0 | 0 | 25 | 52 | 22 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 2.42 | 46 | 0 | 8 | 312 | 0 | 0 | 0 | 0 | 54 | 160 | 0 | 0 | 0 | 1147 | 15 | 0 | 0 | 260 | 147 | 0 | 44 | 0 | 179 | 0 | 0 | 106 | 76 | 0 | 13 | 0 | 122 | 0 | 53 | 0 | 310 | 0 | 0 | 42 | 60 | 159 | 10 | 17 | 0 | 77 | 30 | 0 | 0 | 159 | 0 | 19 | 58 | 34 | 1 | 35.33 | 0 | 5407.15 | 875 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 1068 | 0 | 0 | 0 | 1226.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.01 | 98 | 0 | 0 | 46.5 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.07 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 5.2 | 123 | 0.5 | 0 | 272 | 132 | 220 | 0 | 436 | 543 | 0 | 5666.24 | 11073.39 | 96.87
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 47 | 0 | 70 | 0 | 195 | 30 | 35 | 100 | 0 | 0 | 0 | 330 | 0 | 35 | 300 | 0 | 0 | 21 | 52 | 27 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 12 | 2.07 | 46 | 0 | 2 | 312 | 0 | 0 | 0 | 0 | 80 | 161 | 0 | 0 | 0 | 1167 | 15 | 38 | 0 | 290 | 100 | 0 | 44 | 0 | 200 | 0 | 0 | 103 | 110 | 0 | 13 | 0 | 118 | 0 | 42 | 0 | 310 | 0 | 0 | 42 | 60 | 153 | 7 | 17 | 0 | 76 | 30 | 0 | 0 | 159 | 0 | 19 | 58 | 34 | 1 | 27.93 | 0 | 5416 | 877 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 1019 | 0 | 0 | 0 | 1066.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.72 | 87 | 0 | 0 | 36.19 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.43 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 4.5 | 110 | 0.38 | 0 | 276 | 130 | 180 | 0 | 363 | 450 | 0 | 5157.2 | 10573.2 | 96.86
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 49.5 | 0 | 70 | 0 | 195 | 30 | 17 | 105 | 0 | 0 | 0 | 335 | 0 | 55 | 270 | 0 | 0 | 13 | 52 | 25.2 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 12 | 1.69 | 46 | 0 | 2 | 313 | 0 | 0 | 0 | 0 | 17 | 161 | 0 | 0 | 0 | 1152 | 11 | 50 | 0 | 320 | 100 | 0 | 44 | 0 | 187 | 0 | 0 | 103 | 34 | 0 | 13 | 0 | 114 | 0 | 29 | 0 | 320 | 0 | 0 | 42 | 60 | 157 | 4 | 17 | 0 | 77 | 30 | 0 | 0 | 153 | 0 | 19 | 58 | 34 | 1 | 21.94 | 0 | 5270.33 | 877 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 918 | 0 | 0 | 0 | 977.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.79 | 63 | 0 | 0 | 26.61 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.42 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 3.2 | 72 | 0.27 | 0 | 275 | 100 | 220 | 0 | 300 | 490 | 0 | 4809.67 | 10080 | 96.86
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 33 | 0 | 82 | 0 | 160 | 15 | 17 | 104 | 0 | 0 | 0 | 355 | 0 | 55 | 260 | 0 | 0 | 7 | 52 | 24.5 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0.27 | 46 | 0 | 2 | 311 | 0 | 0 | 0 | 0 | 15 | 161 | 0 | 0 | 0 | 1127 | 3 | 12 | 0 | 325 | 65 | 0 | 51 | 0 | 203 | 0 | 0 | 104 | 33 | 0 | 13 | 0 | 114 | 0 | 9 | 0 | 315 | 0 | 0 | 42 | 60 | 158 | 1 | 17 | 0 | 77 | 30 | 0 | 0 | 153 | 0 | 19 | 57 | 32 | 0 | 10.47 | 0 | 5088.24 | 877 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 918 | 0 | 0 | 0 | 929.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.44 | 30 | 0 | 0 | 10.12 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 1.6 | 32 | 0.13 | 0 | 283 | 130 | 220 | 0 | 300 | 450 | 0 | 4628.34 | 9716.58 | 95.85
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 16 | 5 | 107 | 0 | 160 | 15 | 17 | 105 | 0 | 0 | 0 | 325 | 0 | 55 | 260 | 0 | 0 | 2 | 52 | 24 | 13 | 0 | 0 | 6 | 15 | 0 | 0 | 1 | 0 | 0 | 9 | 50 | 38 | 0.06 | 46 | 8 | 3 | 314 | 5 | 0 | 7 | 0 | 65 | 161 | 0 | 0 | 0 | 1161 | 0 | 12 | 0 | 330 | 20 | 0 | 51 | 0 | 195 | 0 | 1 | 104 | 58 | 0 | 13 | 0 | 114 | 0 | 3 | 0 | 315 | 0 | 0 | 42 | 60 | 149 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 153 | 0 | 19 | 58 | 32 | 0 | 1.87 | 0 | 5225.93 | 877 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 947 | 0 | 0 | 0 | 1025.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.11 | 6 | 0 | 0 | 1.82 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.3 | 6 | 0.02 | 0 | 250 | 110 | 180 | 0 | 312 | 440 | 0 | 4588.74 | 9814.67 | 96.85
18:00 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 16.5 | 17 | 149 | 0 | 300 | 0 | 36 | 143 | 0 | 0 | 0 | 315 | 0 | 55 | 335 | 0 | 0 | 0 | 52 | 23.5 | 14 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 17 | 24 | 0 | 50 | 38 | 0 | 46 | 16 | 8 | 315 | 0 | 0 | 18 | 0 | 99 | 161 | 0 | 0 | 0 | 1212 | 0 | 20 | 0 | 393 | 20 | 0 | 51 | 0 | 197 | 0 | 16 | 104 | 97 | 0 | 13 | 0 | 118 | 0 | 0 | 0 | 310 | 0 | 0 | 42 | 60 | 141 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 152 | 0 | 19 | 58 | 32 | 0 | 0 | 14 | 5812 | 877 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1042 | 0 | 0 | 0 | 1246.21 | 0 | 0 | 0 | 8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 448 | 500 | 0 | 5314.21 | 11126.21 | 96.84
19:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 48 | 0 | 149 | 0 | 195 | 0 | 17 | 151 | 0 | 0 | 0 | 395 | 0 | 17 | 335 | 0 | 0 | 0 | 35 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 38 | 0 | 46 | 0 | 10 | 315 | 0 | 0 | 0 | 0 | 51 | 161 | 0 | 0 | 0 | 1212 | 0 | 0 | 0 | 393 | 40 | 0 | 51 | 0 | 191 | 0 | 0 | 104 | 111 | 0 | 13 | 0 | 116 | 0 | 0 | 0 | 310 | 0 | 0 | 42 | 60 | 152 | 0 | 21 | 0 | 81 | 30 | 0 | 0 | 152 | 0 | 19 | 57 | 32 | 0 | 0 | 18 | 5556 | 876 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1113 | 0 | 0 | 0 | 1442.07 | 0 | 0 | 0 | 35 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 508 | 585 | 0 | 5823.07 | 11379.07 | 96.84
19:30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 35 | 0 | 149 | 0 | 95 | 0 | 0 | 126 | 0 | 0 | 0 | 425 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 38 | 0 | 46 | 0 | 4 | 315 | 0 | 0 | 0 | 0 | 17 | 161 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 335 | 50 | 0 | 51 | 0 | 213 | 0 | 0 | 104 | 120 | 0 | 13 | 0 | 114 | 0 | 0 | 0 | 325 | 0 | 0 | 42 | 60 | 150 | 0 | 21 | 0 | 82 | 30 | 0 | 0 | 152 | 0 | 19 | 57 | 32 | 0 | 0 | 18 | 5348 | 876 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1116 | 0 | 0 | 0 | 1461.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 130 | 220 | 0 | 508 | 600 | 0 | 5725.05 | 11073.05
20:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 25 | 0 | 149 | 0 | 95 | 0 | 0 | 126 | 0 | 0 | 0 | 400 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 25 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 38 | 0 | 46 | 0 | 2 | 315 | 0 | 0 | 0 | 0 | 17 | 161 | 0 | 0 | 0 | 1162 | 0 | 0 | 0 | 320 | 60 | 0 | 51 | 0 | 219 | 0 | 0 | 106 | 118 | 0 | 13 | 0 | 108 | 0 | 0 | 0 | 320 | 0 | 0 | 41 | 60 | 157 | 0 | 21 | 0 | 82 | 30 | 0 | 0 | 155 | 0 | 19 | 57 | 33 | 0 | 0 | 18 | 5300 | 877 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1129 | 0 | 0 | 0 | 1450.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 130 | 220 | 0 | 508 | 600 | 0 | 5731.64 | 11031.64 | 96.83
21:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 16.5 | 0 | 149 | 0 | 95 | 0 | 0 | 122 | 0 | 0 | 0 | 445 | 0 | 0 | 250 | 0 | 0 | 0 | 35 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 46 | 0 | 10 | 315 | 0 | 0 | 0 | 0 | 15 | 161 | 0 | 0 | 0 | 1163 | 0 | 0 | 0 | 310 | 75 | 0 | 51 | 0 | 224 | 0 | 0 | 107 | 118 | 0 | 13 | 0 | 112 | 0 | 0 | 0 | 320 | 0 | 0 | 41 | 60 | 161 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 155 | 0 | 19 | 58 | 33 | 0 | 0 | 18 | 5248.5 | 877 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1130 | 0 | 0 | 0 | 1452.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 130 | 220 | 0 | 506 | 600 | 0 | 5704.6 | 10953.1 | 96.83
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 395 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 12 | 315 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1162 | 0 | 0 | 0 | 310 | 145 | 0 | 51 | 0 | 215 | 0 | 0 | 108 | 51 | 0 | 13 | 0 | 102 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 60 | 153 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 155 | 0 | 19 | 58 | 33 | 0 | 0 | 0 | 4774 | 877 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 0 | 0 | 0 | 1449.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 130 | 220 | 0 | 509 | 560 | 0 | 5580.17 | 10354.17 | 96.82
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 18 | 315 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 245 | 249 | 0 | 51 | 0 | 206 | 0 | 0 | 109 | 0 | 0 | 13 | 0 | 108 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 60 | 147 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 155 | 0 | 19 | 8 | 33 | 0 | 0 | 0 | 4574 | 876 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1059 | 0 | 0 | 0 | 1459.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 135 | 220 | 0 | 474 | 545 | 0 | 5473.69 | 10047.69 | 96.82
Total KWH | 0 | 66240 | 0 | 0 | 0 | 0 | 0 | 0 | 7812000 | 0 | 0 | 462240 | 41040 | 1224432 | 0 | 1928989 | 170863 | 185313 | 1383840 | 0 | 0 | 0 | 8639091 | 0 | 301707 | 7178094 | 0 | 0 | 154132 | 651600 | 521400 | 336960 | 0 | 0 | 30109 | 37636 | 0 | 0 | 7680 | 47143 | 12518 | 28131 | 84480 | 374400 | 13922 | 1094880 | 34290 | 402240 | 7912727.27 | 3345 | 0 | 28800 | 0 | 557854 | 3814106 | 0 | 0 | 0 | 26558179 | 68040 | 192363 | 0 | 5847500 | 5139400 | 0 | 1024057 | 70560 | 4942000 | 253080 | 26880 | 2591228 | 1055520 | 0 | 301510 | 0 | 2496960 | 0 | 255091 | 0 | 7618000 | 0 | 0 | 986000 | 1446960 | 3249900 | 47620 | 233520 | 0 | 1687680 | 651168 | 0 | 0 | 3398920 | 0 | 337200 | 883200 | 1107840 | 9050 | 224840 | 84240 | 118330708.27 | 17915636 | 4948416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414720 | 23149100 | 0 | 0 | 0 | 27013494 | 0 | 0 | 0 | 35520 | 48576 | 0 | 0 | 0 | 0 | 281536 | 625440 | 0 | 0 | 271504 | 4516364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24300 | 0 | 0 | 179524 | 175356 | 191260 | 0 | 0 | 0 | 32183.76 | 753120 | 2649 | 0 | 6568000 | 3017000 | 5275920 | 0 | 9120000 | 12356363.64 | 0 | 116915982.4 | 235246690.67