## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 13-01-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 12-01-2026 | during | 13-01-2026 | during | 13-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 323 | 346 | 412 | 412 | 0 | 100 | Machine Problem
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 5 | 25 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 100 | 100 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 335 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 49.6 | 47 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 14 | 35 | 55 | 55 | 55 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 22 | 23 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 12 | 14 | 15.1 | 15.1 | 15.1 | 15.1 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 95 | 300 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 134 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 126 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 28 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 355 | 520 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 90 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1286.6 | 2067 | 5335.25 | 5307.25 | 2268.13 | 2340.13
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 37 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 | 46 | 46 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 160 | 161 | 150 | 150 | 150 | 150 | Plant availability less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 31 | 75 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 24 | 40 | 64 | 40 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 51 | 51 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 50 | 100 | 100 | 12 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 9 | 22 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.98 | 0 | 3.21 | 0 | 3.22 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 45 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 15 | 49 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 38 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 40 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 16 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1158 | 1210 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 2 | 0 | 8 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 316 | 315 | 315 | 315 | 355 | 355 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1807.98 | 2164 | 3084.07 | 3101.86 | 2639.72 | 2736.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 194 | 189 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 100 | 35 | 353.35 | 353.35 | 353.35 | 353.35 | STG Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 0 | 0 | Under maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 300 | 360 | 393 | 393 | 393 | 393 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 10 | 10 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 53 | 0 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | Gas shortage
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 12 | 137 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 24 | 24 | 24 | 24 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 105 | 105 | 163 | 163 | 115 | 115 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 16 | 167 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 118 | 110 | 84 | 82 | 122 | 122 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 13 | 24.5 | 24.5 | 24.5 | 24.5 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 16 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 60 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1022 | 1183 | 2409.75 | 2352.75 | 2168.05 | 2113.05
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 12-01-2026 | during | 13-01-2026 | during | 13-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 30 | 30 | 157.5 | 157.5 | 50 | 50 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 0 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 57 | 58 | 60 | 60 | 60 | 60 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 19 | 20 | 20 | 20 | 20 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 39.32 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 18 | 22 | 22 | 18 | 18 | To be dispatched 18 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 165.32 | 142 | 356 | 314 | 246.6 | 202.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 0 | 42 | 42 | 42 | 42 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 149 | 155 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 83 | 83 | 83 | 83 | 83 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 157 | 0 | 158 | 158 | 158 | 158 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 839 | 590 | 842 | 842 | 792 | 792
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 878 | 645 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 297 | 410 | 410 | 369 | 369 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 79 | 0 | 72 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1047 | 1104 | 0 | 0 | 1148 | 1148 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2254 | 2046 | 2344 | 2272 | 2699.1 | 2624.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 1 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 133 | 130 | 136 | 136 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 510 | 595 | 622 | 622 | 575 | 575 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 45 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 282 | 290 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.53 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1145.53 | 1281 | 1546 | 1545 | 1346 | 1345
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 47.61 | 0 | 0 | 0 | 47.32 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 206 | 185 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.71 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1393 | 1442.48 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 54.81 | 0 | 61 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 94 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1800.13 | 1767.48 | 2673.58 | 2507.08 | 2216.5 | 2013.68
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 100 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.1 | 0 | 4.8 | 0 | 4.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 90 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 140 | 0 | 136.84 | 0 | 136.85 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 176.1 | 190 | 433.64 | 262 | 399.65 | 228
System Total |  |  |  |  | 28823.2 | 28382.248 | 10496.66 | 11430.48 | 19024.29 | 18503.94 | 14775.75 | 14394.96
Forecast Scenario (13-01-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9008.18 |  | 374.1881 |  | 9400
|  |  |  | 1:00 | 8810 |  | 0 |  | 8810
|  |  |  | 2:00 | 8320 |  | 0 |  | 8320
|  |  |  | 3:00 | 8000 |  | 0 |  | 8000
|  |  |  | 4:00 | 7710 |  | 0 |  | 7710
|  |  |  | 5:00 | 7640 |  | 0 |  | 7640
|  |  |  | 6:00 | 8020 |  | 0 |  | 8020
|  |  |  | 7:00 | 8840 |  | 0 |  | 8840
|  |  |  | 8:00 | 9860 |  | 0 |  | 9860
|  |  |  | 9:00 | 10200 |  | 0 |  | 10200
|  |  |  | 10:00 | 9900 |  | 0 |  | 9900
|  |  |  | 11:00 | 9950 |  | 0 |  | 9950
|  |  |  | 12:00 | 10490 |  | 0 |  | 10490
|  |  |  | 13:00 | 10770 |  | 0 |  | 10770
|  |  |  | 14:00 | 10520 |  | 0 |  | 10520
|  |  |  | 15:00 | 9920 |  | 0 |  | 9920
|  |  |  | 16:00 | 9460 |  | 0 |  | 9460
|  |  |  | 17:00 | 9990 |  | 0 |  | 9990
|  |  |  | 18:00 | 11100 |  | 0 |  | 11100
|  |  |  | 18:30 | 11250 |  | 0 |  | 11250
|  |  |  | 19:00 | 11430 |  | 0 |  | 11430
|  |  |  | 19:30 | 11330 |  | 0 |  | 11330
|  |  |  | 20:00 | 11210 |  | 0 |  | 11210
|  |  |  | 21:00 | 11030 |  | 0 |  | 11030
|  |  |  | 22:00 | 10350 |  | 0 |  | 10350
|  |  |  | 23:00 | 10000 |  | 0 |  | 10000
Probable Maximum Temperature: |  |  | 24.00°C
Probable Maximum Demand at Day Peak: |  |  | 10490.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11430.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11430.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 232.52818 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:32 hrs on 13-01-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 12-01-2026 | [28 empty] | Date: | 12-01-2026 | [28 empty] | Date: | 12-01-2026 | [28 empty] | Date: | 12-01-2026 | [28 empty] | Date: | 12-01-2026 | [17 empty] | Date: | 12-01-2026
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [17 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 21 | 315 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1045 | 0 | 0 | 0 | 225 | 290 | 0 | 51 | 0 | 190 | 0 | 0 | 108 | 0 | 0 | 13 | 0 | 102 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 30 | 137 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 156 | 0 | 19 | 16 | 33 | 0 | 0 | 0 | 4371 | 877 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 977 | 0 | 0 | 0 | 1325.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 135 | 220 | 0 | 355 | 520 | 0 | 5106.18 | 9477.18 | 96.81
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 21 | 315 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 950 | 0 | 0 | 0 | 215 | 290 | 0 | 51 | 0 | 190 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 94 | 0 | 0 | 0 | 320 | 0 | 0 | 41 | 30 | 142 | 0 | 17 | 0 | 83 | 20 | 0 | 0 | 155 | 0 | 19 | 16 | 33 | 0 | 0 | 0 | 4276 | 764 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 847 | 0 | 0 | 0 | 1119.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 135 | 220 | 0 | 256 | 495 | 0 | 4540.23 | 8816.23 | 96.81
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 37 | 315 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 906 | 0 | 0 | 0 | 215 | 290 | 0 | 51 | 0 | 190 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 90 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 30 | 145 | 0 | 17 | 0 | 41 | 20 | 0 | 0 | 155 | 0 | 19 | 0 | 43 | 0 | 0 | 0 | 4182 | 691 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 788 | 0 | 0 | 0 | 1021.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 135 | 220 | 0 | 178 | 450 | 0 | 4141.45 | 8323.45 | 96.81
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 37 | 315 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 931 | 0 | 0 | 0 | 225 | 280 | 0 | 51 | 0 | 221 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 88 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 30 | 144 | 0 | 17 | 0 | 41 | 20 | 0 | 0 | 155 | 0 | 19 | 0 | 48 | 0 | 0 | 0 | 4264 | 471 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 778 | 0 | 0 | 0 | 1028.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 135 | 220 | 0 | 0 | 450 | 0 | 3741.96 | 8005.96 | 96.81
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 37 | 315 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 950 | 0 | 0 | 0 | 215 | 180 | 0 | 51 | 0 | 189 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 86 | 0 | 0 | 0 | 320 | 0 | 0 | 41 | 30 | 149 | 0 | 17 | 0 | 41 | 30 | 0 | 0 | 155 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 4198 | 225 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 795 | 0 | 0 | 0 | 1026.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 135 | 220 | 0 | 0 | 450 | 0 | 3512.8 | 7710.8 | 96.81
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 14.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 39 | 315 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 936 | 0 | 0 | 0 | 215 | 180 | 0 | 51 | 0 | 210 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 78 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 30 | 141 | 0 | 17 | 0 | 41 | 30 | 0 | 0 | 155 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 4160.5 | 225 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 775 | 0 | 0 | 0 | 1027.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226 | 135 | 220 | 0 | 0 | 450 | 0 | 3483.54 | 7644.04 | 96.81
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 14.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 40 | 315 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1088 | 0 | 0 | 0 | 260 | 160 | 0 | 51 | 0 | 215 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 88 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 30 | 153 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 155 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 4419.5 | 224 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 833 | 0 | 0 | 0 | 1021.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 135 | 220 | 0 | 0 | 455 | 0 | 3605.75 | 8025.25 | 96.81
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 14.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0.08 | 46 | 0 | 34 | 316 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1173 | 1 | 0 | 0 | 300 | 100 | 0 | 51 | 0 | 222 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 90 | 0 | 2 | 0 | 320 | 0 | 0 | 41 | 30 | 160 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 155 | 0 | 19 | 16 | 49 | 0 | 0.79 | 0 | 4537.37 | 441 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1032 | 0 | 0 | 0 | 1226.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53 | 1 | 0 | 0 | 0.65 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.01 | 0 | 281 | 135 | 220 | 0 | 0 | 515 | 0 | 4302.24 | 8839.61 | 96.81
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 35 | 0 | 21 | 0 | 120 | 0 | 17 | 101 | 0 | 0 | 0 | 400 | 0 | 17 | 250 | 0 | 0 | 5 | 0 | 15 | 14 | 0 | 0 | 0 | 15 | 0 | 0 | 7 | 0 | 0 | 0 | 7 | 25 | 0.46 | 46 | 2 | 5 | 315 | 0 | 0 | 0 | 0 | 29 | 160 | 0 | 0 | 0 | 1154 | 3 | 20 | 0 | 300 | 100 | 0 | 51 | 0 | 225 | 0 | 0 | 110 | 23 | 0 | 13 | 0 | 104 | 0 | 14 | 0 | 325 | 0 | 0 | 41 | 30 | 163 | 2 | 17 | 0 | 80 | 30 | 0 | 0 | 155 | 0 | 19 | 56 | 43 | 0 | 8.79 | 0 | 5036.25 | 575 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 1134 | 0 | 0 | 0 | 1385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.95 | 16 | 0 | 0 | 9.17 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89 | 0 | 0 | 0 | 5 | 15 | 0 | 0 | 0 | 0.9 | 28 | 0.11 | 0 | 280 | 135 | 220 | 0 | 0 | 550 | 0 | 4832.02 | 9868.27 | 96.8
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 47 | 0 | 85 | 0 | 195 | 0 | 35 | 141 | 0 | 0 | 0 | 390 | 0 | 35 | 250 | 0 | 0 | 14 | 35 | 24 | 14 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 1.44 | 46 | 15 | 3 | 315 | 0 | 0 | 0 | 0 | 75 | 160 | 0 | 0 | 0 | 1163 | 0 | 70 | 0 | 300 | 100 | 0 | 51 | 0 | 170 | 0 | 0 | 50 | 17 | 0 | 13 | 0 | 104 | 0 | 26 | 0 | 315 | 0 | 0 | 41 | 30 | 152 | 5 | 17 | 0 | 42 | 30 | 0 | 0 | 156 | 0 | 19 | 56 | 33 | 1 | 21.94 | 1 | 5233.38 | 691 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.21 | 1097 | 0 | 0 | 0 | 1375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.19 | 43 | 0 | 0 | 26.61 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.29 | 0 | 0 | 35 | 14 | 34 | 0 | 0 | 0 | 2.6 | 71 | 0.23 | 0 | 276 | 120 | 180 | 0 | 0 | 550 | 0 | 4970.13 | 10203.51 | 96.8
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 19 | 0 | 68 | 0 | 95 | 0 | 17 | 32 | 0 | 0 | 0 | 395 | 0 | 17 | 250 | 0 | 0 | 21 | 17 | 23 | 10 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 2.03 | 46 | 15 | 5 | 315 | 0 | 0 | 0 | 0 | 34 | 160 | 0 | 0 | 0 | 1163 | 15 | 12 | 0 | 335 | 100 | 0 | 51 | 0 | 170 | 0 | 0 | 50 | 17 | 0 | 13 | 0 | 104 | 0 | 47 | 0 | 315 | 0 | 0 | 41 | 30 | 145 | 7 | 17 | 0 | 42 | 20 | 0 | 0 | 156 | 0 | 19 | 56 | 30 | 1 | 32.78 | 15 | 4920.81 | 867 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 1101 | 0 | 0 | 0 | 1217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.44 | 71 | 0 | 0 | 36.65 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.44 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 4 | 108 | 0.36 | 0 | 265 | 100 | 180 | 0 | 0 | 530 | 0 | 4978.89 | 9899.7 | 96.8
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 49.6 | 0 | 34 | 0 | 45 | 0 | 17 | 33 | 0 | 0 | 0 | 335 | 0 | 17 | 250 | 0 | 0 | 27 | 17 | 23 | 14 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 2.68 | 46 | 15 | 5 | 316 | 0 | 0 | 0 | 0 | 32 | 160 | 0 | 0 | 0 | 1157 | 17 | 12 | 0 | 330 | 100 | 0 | 51 | 0 | 215 | 0 | 0 | 105 | 16 | 0 | 13 | 0 | 112 | 0 | 56 | 0 | 310 | 0 | 0 | 42 | 30 | 147 | 9 | 17 | 0 | 42 | 20 | 0 | 0 | 157 | 0 | 19 | 57 | 29 | 2 | 37.41 | 18 | 4933.69 | 879 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 1021 | 0 | 0 | 0 | 1219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.06 | 88 | 0 | 0 | 47.93 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 4.9 | 137 | 0.47 | 0 | 201 | 120 | 220 | 0 | 0 | 500 | 0 | 5016.46 | 9950.15 | 96.8
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 49.6 | 0 | 34 | 0 | 95 | 5 | 14 | 35 | 0 | 0 | 0 | 355 | 0 | 17 | 280 | 0 | 0 | 28 | 17 | 22 | 12 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 2.98 | 46 | 15 | 9 | 316 | 0 | 0 | 0 | 0 | 31 | 160 | 0 | 0 | 0 | 1158 | 18 | 12 | 53 | 300 | 100 | 0 | 51 | 0 | 194 | 0 | 0 | 105 | 16 | 0 | 13 | 0 | 118 | 0 | 60 | 0 | 325 | 0 | 0 | 42 | 30 | 149 | 9 | 17 | 0 | 80 | 30 | 0 | 0 | 157 | 0 | 19 | 57 | 30 | 2 | 39.32 | 18 | 5120.9 | 878 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 1047 | 0 | 0 | 0 | 1393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.61 | 94 | 0 | 0 | 54.81 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.71 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 5.1 | 140 | 0.53 | 0 | 282 | 133 | 220 | 0 | 0 | 510 | 0 | 5375.76 | 10496.66 | 96.8
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 51.8 | 0 | 54 | 0 | 95 | 15 | 47 | 145 | 0 | 0 | 0 | 375 | 0 | 35 | 280 | 0 | 0 | 27 | 17 | 19 | 14 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 2.84 | 46 | 16 | 9 | 316 | 0 | 0 | 0 | 0 | 53 | 160 | 0 | 0 | 0 | 1142 | 16 | 40 | 71 | 220 | 100 | 0 | 51 | 0 | 175 | 0 | 0 | 103 | 43 | 0 | 13 | 0 | 114 | 0 | 57 | 0 | 315 | 0 | 0 | 42 | 30 | 155 | 10 | 17 | 0 | 83 | 30 | 0 | 0 | 157 | 0 | 19 | 58 | 28 | 2 | 36.85 | 18 | 5304.49 | 878 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 1109 | 0 | 0 | 0 | 1418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.02 | 91 | 0 | 0 | 52.06 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.55 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 5 | 136 | 0.5 | 0 | 276 | 133 | 220 | 0 | 0 | 550 | 0 | 5470.13 | 10774.62 | 96.8
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 47.7 | 0 | 104 | 0 | 45 | 15 | 35 | 155 | 0 | 0 | 0 | 325 | 0 | 35 | 250 | 0 | 0 | 24 | 17 | 22 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 2.07 | 46 | 0 | 9 | 316 | 0 | 0 | 0 | 0 | 65 | 161 | 0 | 0 | 0 | 1130 | 14 | 100 | 3 | 240 | 50 | 0 | 51 | 0 | 210 | 0 | 0 | 102 | 80 | 0 | 13 | 0 | 120 | 0 | 46 | 0 | 310 | 0 | 0 | 42 | 30 | 151 | 7 | 17 | 0 | 82 | 30 | 0 | 0 | 157 | 0 | 19 | 58 | 29 | 2 | 32.02 | 18 | 5157.79 | 879 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 1070 | 0 | 0 | 0 | 1473.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.86 | 78 | 0 | 0 | 40.39 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.04 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 4.3 | 124 | 0.42 | 0 | 290 | 100 | 180 | 0 | 0 | 570 | 0 | 5367.41 | 10525.2 | 96.8
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 48 | 0 | 100 | 0 | 45 | 0 | 17 | 108 | 0 | 0 | 0 | 300 | 0 | 17 | 335 | 0 | 0 | 16 | 17 | 22 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1.47 | 46 | 0 | 5 | 316 | 0 | 0 | 0 | 0 | 17 | 161 | 0 | 0 | 0 | 1092 | 0 | 12 | 0 | 300 | 17 | 0 | 51 | 0 | 191 | 0 | 0 | 102 | 51 | 0 | 13 | 0 | 112 | 0 | 31 | 0 | 320 | 0 | 0 | 0 | 30 | 153 | 6 | 17 | 0 | 83 | 30 | 0 | 0 | 154 | 0 | 19 | 45 | 29 | 1 | 23.19 | 17 | 4814.66 | 878 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 1046 | 0 | 0 | 0 | 1279.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.63 | 57 | 0 | 0 | 32.57 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.01 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 3.3 | 90 | 0.3 | 0 | 290 | 82 | 220 | 0 | 0 | 600 | 0 | 5107.88 | 9922.54 | 96.79
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 16.7 | 0 | 72 | 0 | 45 | 0 | 17 | 90 | 0 | 0 | 0 | 330 | 0 | 17 | 335 | 0 | 0 | 8 | 17 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 12 | 0.73 | 46 | 0 | 2 | 316 | 0 | 0 | 0 | 0 | 16 | 161 | 0 | 0 | 0 | 1147 | 6 | 0 | 3 | 345 | 20 | 0 | 51 | 0 | 213 | 0 | 0 | 102 | 51 | 0 | 13 | 0 | 108 | 0 | 14 | 0 | 320 | 0 | 0 | 0 | 0 | 159 | 2 | 0 | 0 | 81 | 27 | 0 | 0 | 0 | 0 | 19 | 48 | 29 | 0 | 10.59 | 15 | 4661.02 | 879 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 960 | 0 | 0 | 0 | 1266.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.76 | 27 | 0 | 0 | 11.76 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 1.6 | 45 | 0.15 | 0 | 260 | 100 | 220 | 0 | 0 | 560 | 0 | 4803.22 | 9464.24 | 96.79
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 35.5 | 19 | 76 | 0 | 180 | 0 | 27 | 120 | 0 | 0 | 0 | 385 | 0 | 50 | 335 | 0 | 0 | 2 | 52 | 24 | 14 | 0 | 0 | 0 | 15 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 38 | 0.1 | 46 | 0 | 3 | 316 | 0 | 0 | 0 | 0 | 35 | 161 | 0 | 0 | 0 | 1143 | 1 | 0 | 3 | 393 | 29 | 0 | 51 | 0 | 197 | 0 | 0 | 105 | 81 | 0 | 13 | 0 | 106 | 0 | 2 | 0 | 315 | 0 | 0 | 0 | 0 | 149 | 0 | 17 | 0 | 82 | 27 | 0 | 0 | 0 | 0 | 19 | 58 | 29 | 0 | 1.78 | 18 | 5132.38 | 879 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 998 | 0 | 0 | 0 | 1355.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.01 | 6 | 0 | 0 | 1.81 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.3 | 5 | 0.03 | 0 | 290 | 100 | 220 | 0 | 0 | 560 | 0 | 4865.88 | 9998.26 | 96.79
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 48.8 | 54 | 121 | 0 | 265 | 10 | 55 | 153 | 0 | 0 | 0 | 380 | 0 | 55 | 335 | 0 | 0 | 0 | 52 | 22 | 14 | 0 | 0 | 13 | 15 | 0 | 0 | 2 | 17 | 24 | 14 | 36 | 38 | 0 | 46 | 10 | 5 | 313 | 20 | 0 | 13 | 0 | 96 | 161 | 0 | 0 | 0 | 1186 | 0 | 66 | 0 | 393 | 35 | 0 | 51 | 0 | 203 | 0 | 8 | 104 | 119 | 0 | 13 | 0 | 108 | 0 | 0 | 24 | 310 | 0 | 0 | 0 | 0 | 147 | 0 | 17 | 0 | 82 | 30 | 0 | 0 | 0 | 17 | 19 | 58 | 30 | 0 | 0 | 18 | 5798.8 | 878 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 0 | 0 | 0 | 1463.1 | 0 | 0 | 0 | 35 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 130 | 220 | 0 | 0 | 590 | 14 | 5310.1 | 11108.9 | 96.79
19:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 47 | 0 | 134 | 0 | 300 | 25 | 35 | 126 | 0 | 0 | 0 | 520 | 0 | 55 | 335 | 0 | 0 | 0 | 90 | 23 | 14 | 0 | 0 | 40 | 45 | 0 | 0 | 2 | 34 | 24 | 0 | 50 | 38 | 0 | 46 | 49 | 22 | 315 | 16 | 0 | 37 | 0 | 75 | 161 | 0 | 0 | 0 | 1210 | 0 | 137 | 0 | 360 | 35 | 0 | 51 | 0 | 189 | 0 | 16 | 105 | 167 | 0 | 13 | 0 | 110 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 155 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 0 | 17 | 19 | 58 | 30 | 0 | 0 | 18 | 6146 | 645 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1104 | 0 | 0 | 0 | 1442.48 | 0 | 0 | 0 | 70 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 290 | 130 | 220 | 0 | 0 | 595 | 45 | 5284.48 | 11430.48 | 96.78
19:30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 16 | 0 | 133 | 0 | 300 | 15 | 17 | 122 | 0 | 0 | 0 | 505 | 0 | 55 | 335 | 0 | 0 | 0 | 75 | 23 | 14 | 0 | 0 | 15 | 45 | 0 | 0 | 0 | 34 | 24 | 0 | 50 | 38 | 0 | 46 | 64 | 20 | 315 | 17 | 0 | 32 | 0 | 51 | 161 | 0 | 0 | 0 | 1210 | 0 | 141 | 0 | 360 | 35 | 0 | 51 | 0 | 194 | 0 | 0 | 105 | 172 | 0 | 13 | 0 | 110 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 155 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 0 | 17 | 22 | 58 | 30 | 0 | 0 | 18 | 6033 | 645 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1102 | 0 | 0 | 0 | 1442.31 | 0 | 0 | 0 | 70 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 290 | 130 | 220 | 0 | 0 | 605 | 27 | 5303.31 | 11336.31
20:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 16.8 | 0 | 133 | 0 | 277 | 0 | 17 | 119 | 0 | 0 | 0 | 495 | 0 | 55 | 335 | 0 | 0 | 0 | 35 | 23 | 14 | 0 | 0 | 15 | 45 | 0 | 0 | 0 | 34 | 24 | 0 | 50 | 38 | 0 | 46 | 64 | 32 | 315 | 0 | 0 | 32 | 0 | 51 | 161 | 0 | 0 | 0 | 1208 | 0 | 142 | 0 | 360 | 35 | 0 | 51 | 0 | 187 | 0 | 0 | 105 | 172 | 0 | 13 | 0 | 110 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 157 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 0 | 17 | 23 | 58 | 30 | 0 | 0 | 18 | 5919.8 | 645 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1111 | 0 | 0 | 0 | 1442.92 | 0 | 0 | 0 | 70 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 287 | 130 | 220 | 0 | 0 | 595 | 27 | 5289.92 | 11209.72 | 96.78
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 15.4 | 0 | 133 | 0 | 277 | 0 | 17 | 118 | 0 | 0 | 0 | 405 | 0 | 55 | 240 | 0 | 0 | 0 | 17 | 23 | 14 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 24 | 0 | 50 | 38 | 0 | 46 | 65 | 32 | 315 | 0 | 0 | 19 | 0 | 50 | 161 | 0 | 0 | 0 | 1209 | 0 | 142 | 0 | 375 | 105 | 0 | 51 | 0 | 196 | 0 | 0 | 105 | 172 | 0 | 13 | 0 | 108 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 20 | 158 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 24 | 58 | 31 | 0 | 0 | 18 | 5720.4 | 737 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1114 | 0 | 0 | 0 | 1443 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 607 | 45 | 5319 | 11039.4 | 96.78
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 15.4 | 0 | 133 | 0 | 195 | 0 | 17 | 115 | 0 | 0 | 0 | 370 | 0 | 55 | 240 | 0 | 0 | 0 | 0 | 23 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 38 | 0 | 46 | 34 | 35 | 315 | 0 | 0 | 0 | 0 | 47 | 161 | 0 | 0 | 0 | 1212 | 0 | 50 | 0 | 345 | 155 | 0 | 51 | 0 | 191 | 0 | 0 | 107 | 171 | 0 | 13 | 0 | 106 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 20 | 154 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 19 | 58 | 31 | 0 | 0 | 0 | 5305.4 | 737 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1101 | 0 | 0 | 0 | 1449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 622 | 0 | 5187 | 10492.4 | 96.77
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 15 | 0 | 83 | 0 | 15 | 0 | 17 | 35 | 0 | 0 | 0 | 350 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 12 | 0 | 46 | 0 | 36 | 315 | 0 | 0 | 0 | 0 | 17 | 161 | 0 | 0 | 0 | 1210 | 0 | 0 | 0 | 315 | 205 | 0 | 51 | 0 | 196 | 0 | 0 | 109 | 68 | 0 | 13 | 0 | 100 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 20 | 156 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 19 | 16 | 31 | 0 | 0 | 0 | 4664 | 878 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 0 | 0 | 0 | 1442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 130 | 220 | 0 | 0 | 622 | 0 | 5164 | 9828 | 96.77
Total KWH | 0 | 54720 | 0 | 0 | 0 | 0 | 0 | 0 | 8067600 | 0 | 0 | 547560 | 121680 | 1426896 | 0 | 2226316 | 106995 | 461979 | 1700640 | 0 | 0 | 0 | 9130455 | 0 | 560412 | 6552494 | 0 | 0 | 171889 | 423600 | 464400 | 322920 | 0 | 0 | 91582 | 301091 | 0 | 0 | 112320 | 93504 | 102240 | 29925 | 265920 | 444480 | 15824 | 1103580 | 355450 | 485760 | 7672727.27 | 35127 | 0 | 120000 | 0 | 827999 | 3869603 | 0 | 0 | 0 | 26716361 | 97875 | 993600 | 117091 | 7261000 | 3200000 | 0 | 1256507 | 0 | 4923000 | 0 | 29760 | 2462838 | 1470240 | 0 | 313340 | 0 | 2406720 | 0 | 361727 | 33008 | 7682500 | 0 | 0 | 611000 | 528720 | 3660136 | 57530 | 373872 | 0 | 1662720 | 658752 | 0 | 0 | 2513700 | 67680 | 397200 | 912000 | 787200 | 10850 | 245030 | 224640 | 120304285.27 | 16733090 | 6316416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 486720 | 24160000 | 0 | 0 | 0 | 29678039 | 0 | 0 | 0 | 205920 | 317952 | 0 | 0 | 0 | 0 | 279924 | 580010 | 0 | 0 | 315744 | 4499636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27300 | 0 | 0 | 495181 | 181390 | 574137 | 0 | 0 | 0 | 32008.32 | 894240 | 3043 | 16608 | 6545000 | 3159000 | 5491630 | 0 | 465454 | 13397818.18 | 148320 | 115004580.5 | 235308865.77

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 12-01-2026
Power Supply Scenario
| Day Peak Generation |  |  | 10496.66 | MW | 12:00 Hr. | Energy Generated |  |  | 235.3089 |  | MKWHr.
| Day Peak Demand |  |  | 10496.66 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11430.48 | MW | 19:00 Hr. | Energy Demand |  |  | 235.3089 |  | MKWHr.
| Evening Peak Demand |  |  | 11430.48 | MW | 19:00 Hr. | Maximum Temperature |  |  | 27 |  | °C
| Minimum Generation of the Day |  |  | 7644.04 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 633.39 |  | MMCFD
| Maximum Generation of the Day |  |  | 11430.48 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.1693 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 24.5379 | 0 | 7.6308 | 0 | 0 | 0.17189 | 0 | 0 | 32.3406 | Gas | 86.3723 | Gas | 306003242.64
| Chattogram Zone |  |  | 4.3554 | 34.3891 | 2.6673 | 0 | 1.1036 | 0.1137 | 0 | 0.11232 | 42.7414 | Coal | 78.9574 | Coal | 515704509.6875
| Cumilla Zone |  |  | 19.5338 | 0 | 2.5266 | 0 | 0 | 0.36173 | 2.4067 | 0 | 24.8288 | HFO | 16.1844 | HFO | 271955963.25
| Mymensingh Zone |  |  | 0.7872 | 0 | 1.6015 | 0 | 0 | 0.25588 | 0 | 0 | 2.6446 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 17.6914 | 0 | 0 | 0 | 0 | 0.05753 | 0 | 0 | 17.7489 | Hydro | 1.1036 | Hydro | 110358
| Khulna Zone |  |  | 6.3164 | 24.16 | 0 | 0 | 0 | 0.48672 | 16.7331 | 0 | 47.6962 | Solar | 3.7611 | Solar | 59403562.624
| Barishal Zone |  |  | 8.6506 | 20.4083 | 0.16493 | 0 | 0 | 0.003043 | 0 | 0 | 29.2269 | Import | 48.8178 | Import | 296853504.76
| Rajshahi Zone |  |  | 4.4996 | 0 | 0.52387 | 0 | 0 | 1.203 | 29.678 | 0 | 35.9045 | Wind | 0.11232 | Wind | 1652227.2
| Rangpur Zone |  |  | 0 | 0 | 1.0693 | 0 | 0 | 1.1076 | 0 | 0 | 2.177
| Total |  |  | 86.3723 | 78.9574 | 16.1844 | 0 | 1.1036 | 3.7611 | 48.8178 | 0.11232 | 235.3089
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 306003242.64 |  | Hydro | 110358
|  |  |  | Coal | 515704509.6875 |  | Solar | 59403562.624
|  |  |  | HFO | 271955963.25 |  | Import | 296853504.76
|  |  |  | HSD | 0 |  | Wind | 1652227.2
[5 empty] | Total: | 145,16,83,368 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 16.7331 | Peak Hr Flow | 645.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 33376509.09 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 29.678 | Peak Hr Flow | 1442.48 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1670 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.4067 | Peak Hr Flow | 110.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2297 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 48.8178 | Peak Hr Flow | 2197.48 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4124
|  |  |  | Chattogram |  | 0 |  | 1104
|  |  |  | Cumilla |  | 0 |  | 942
|  |  |  | Mymensingh |  | 0 |  | 913
|  |  |  | Sylhet |  | 0 |  | 414
|  |  |  | Khulna |  | 0 |  | 1308
|  |  |  | Barishal |  | 0 |  | 322
|  |  |  | Rajshahi |  | 0 |  | 1054
|  |  |  | Rangpur |  | 0 |  | 748
|  |  |  | Total |  | 0 |  | 10929
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:11 |  | Baroirhat-PHP 132 kV Ckt-1 Scheduled S/D from Baroirhat 132/33kV end Due to None
| 08:15 | 17:33 | Barishal-Bhola 230 kV Ckt-1 Scheduled S/D from Barishal 230/132kV end Due to Annual
Maintenance
| 08:20 | 17:01 | Kaliakoir 400/230/132kV S/S Bibiyana1 Scheduled S/D Due to Annual maintenance work.
| 08:21 | 17:02 | Chandraghona-Rangamati 132 kV Ckt-2 Scheduled S/D from Rangamati 132/33kV end Due to
Annual ROW.
| 08:22 | 16:31 | Dhamrai-Kaliakoir 132 kV Ckt-2 Scheduled S/D from Dhamrai 132/33kV end Due to Due to
annual maintenance.
| 08:27 | 17:59 | Aminbazar-Airport(Old) 230kV Ckt-1 Scheduled S/D from Agargaon 230/132kV end Due to
Annual maintenance
| 08:29 | 15:47 | Ramganj 132/33kV S/S Ramgonj-Desh Energy Ckt-02 Scheduled S/D Due to Annual Maintenance
| 08:30 | 15:24 | Magura-Narail 132kV Ckt-2 Scheduled S/D from Narail 132/33kV end Due to 132 kV Magura 2
Scheduled S/D due to Annual Maintenance work purpose and from Magura 132/33kV end Due to
Annual maintenance
| 08:34 | 18:45 | Feni-PHP 132kV Ckt-1 Scheduled S/D from Feni 132/33kV end Due to Annual maintenance work
| 08:36 | 16:30 | Dhamrai-Kaliakoir 132 kV Ckt-2 Forced S/D from Kaliakoir 400/230/132kV end Due to As per
the instructions of NLDC.
| 08:38 | 17:30 | Fenchuganj 230/132/33kV S/S 132 KV Bus-2 Scheduled S/D Due to Annual Maintenance.
| 08:40 | 16:22 | Brahmanbaria-Narsinghdi 132 kV Ckt-1 Scheduled S/D from Brahmanbaria 132/33kV end.
| 08:47 | 08:58 | Aggreko-keraniganj 132kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to
Annual Maintenance work
| 08:47 | 16:33 | Cox'sbazar-Dohazari 132 kV Ckt-1 Scheduled S/D from Dohazari 132/33kV end Due to Annual
Maintenance
| 08:51 | 19:00 | Sylhet 132/33kV S/S Sylhet-90MW P/S Project Work S/D Due to Operation Direction by NlDC
AE Desk
| 08:52 | 16:59 | Baghabari-Roppur 230kV Ckt-2 Scheduled S/D from Baghabari 230/132kV end Due to Annual
Maintenance
| 08:59 | 16:42 | Keranigonj 230/132/33kV S/S 132 kV Hasnabad Ckt. 1 Scheduled S/D Due to Annual work at
Hasnabad end.
| 09:05 | 12:48 | Fenchuganj-Kulaura 132 kV Ckt-1 Scheduled S/D from Kulaura 132/33kV end Due to Fenchuganj
Grid Annual maintenance.
| 09:08 | 15:32 | GPH 230/33kV S/S BSRM CKT-1 Scheduled S/D Due to Annual maintenance
| 09:15 | 16:56 | Dhamrai 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Due to annual maintenance.
| 09:15 | 16:55 | Dhamrai 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Due to annual maintenance.
| 09:22 | 18:56 | Fenchuganj-Fenchuganj 132 kV Ckt-4 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
OFCN Work.
| 09:26 | 16:49 | Mirpur 132/33kV S/S Reserve Bus Scheduled S/D Due to 132KV Buscoupler Reserve Bus Bay
Equipment Maintenance.
| 09:27 | 15:33 | BSRM 230/33kV S/S GPH Ispat Ckt. -01 Scheduled S/D Due to Annual Maintenance
| 09:29 | 17:14 | Kaliakoir-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end.
| 09:30 | 10:50 | Sherpur 132/33kV S/S Transformer- 01 LT Scheduled S/D Due to Maintenance
| 09:30 | 10:50 | Sherpur 132/33kV S/S Transformer- 01 HT Scheduled S/D Due to Maintenances
| 09:31 | 17:27 | Kodda-Rajendrapur 132kV Ckt-1 Scheduled S/D from Kodda 132/33kV end Due to Dead line
checking
| 09:34 | 15:41 | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) LT Scheduled S/D Due to Annual Maintenance.
| 09:35 | 15:40 | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) HT Scheduled S/D Due to Annual Maintenance.
| 09:37 | 13:52 | Khulna (S)-Rampal Ckt-1 Forced S/D from Rampal 400/230kV end Due to Khulna ALDC Demand
(Annual Maintenance) and from Khulna(S) 230/132kV end Due to Yearly Maintenance Work.
|  | 09:47 | Aminbazar 400/230/132kV S/S 230 kv Bus 01 is restored.
| 09:50 | 15:05 | Shahjadpur-Ullahpara 132kV Ckt-1 Scheduled S/D from Ullahpara 132/33kV end Due to Annual
Maintenance and from Shahjadpur 132/33kV end Due to Maintenance work
| 09:53 | 17:13 | Kaliakoir-Tongi 230kV Ckt-2 Forced S/D from Kaliakoir 400/230/132kV end Due to As per
the instructions of NLDC.
| 10:03 | 13:15 | BIPTC S/S 20DF32 Scheduled S/D Due to Annual Maintenance
| 10:17 | 16:42 | Aggreko-keraniganj 132kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to
Maintenance work at Hasnabad ss end
|  | 10:31 | Aminbazar-Keraniganj 230kV Ckt-2 is restored.
| 10:31 | 12:37 | Hasnabad-Keraniganj 230kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end.
| 10:40 | 13:45 | Narshingdi 132/33kV S/S T-3 LT Scheduled S/D Due to Oil leakage maintenance
| 10:40 | 13:45 | Narshingdi 132/33kV S/S T-3 HT Scheduled S/D Due to Oil leakage maintenance
| 10:42 | 13:26 | Ramganj 132/33kV S/S Transformer-01 LT Scheduled S/D Due to Annual aintenance
| 10:42 | 14:25 | Ramganj 132/33kV S/S Transformer -02 HT Scheduled S/D Due to Annual Maintenance
| 10:42 | 13:26 | Ramganj 132/33kV S/S Transformer-01 HT Scheduled S/D Due to Annual Maintenace ( SPMD)
| 11:02 | 15:41 | Rajshahi 230/132/33kV S/S 230 Kv BIPTC Ckt-02 Scheduled S/D
| 11:06 | 15:42 | HVDC Bheramera- Rajshahi 230kV Ckt-2 Scheduled S/D from BIPTC end Due to Annual
Maintenance
| 11:12 | 13:02 | Sherpur 132/33kV S/S Transformer- 04 HT Scheduled S/D Due to maintenances Works
| 11:12 | 13:02 | Sherpur 132/33kV S/S Transformer- 04 LT Scheduled S/D Due to maintenances Works
| 11:20 |  | Haripur-Haripur (360MW) 230kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to For
HPL end.
| 11:40 | 17:01 | Niamatpur 132/33kV S/S 132 kV Naogaon ckt-2 Project Work S/D Due to As per instruction of
ALDC Bogura.
| 11:49 | 14:00 | Haripur 230/132kV S/S Madanganj-2 Scheduled S/D Due to Annunciator replacement.
| 12:00 |  | Day Peak Generation: 10492 MW.
| 12:00 | 12:07 | Hasnabad-Keraniganj 230kV Ckt-2 Scheduled S/D from Keranigonj 230/132/33kV end.
| 12:07 | 17:19 | Aminbazar-Keraniganj 230kV Ckt-2 Scheduled S/D from Keranigonj 230/132/33kV end.
| 12:56 | 13:40 | Fenchuganj-Kulaura 132 kV Ckt-2 Scheduled S/D from Kulaura 132/33kV end Due to Fenchuganj
grid annual maintenance
| 13:15 | 17:36 | Fenchuganj-Sreemangal 132kV Ckt-2 Scheduled S/D from Sreemongol 132/33kV end Due to For
Bus maintenance at Fen SS.
| 13:29 | 14:25 | Ramganj 132/33kV S/S Transformer -02 LT Scheduled S/D Due to Annual Maintenance
| 13:41 | 14:33 | Gopalganj 400/132kV S/S ATR-04 HT Scheduled S/D
| 14:20 | 17:00 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Forced S/D Due to Termination kit installation
|  | 14:45 | Chandpur 132/33kV S/S Bus-B is restored.
| 14:54 | 15:29 | Fenchuganj 230/132/33kV S/S 132 KV Bus-1 Tripped showing REB 500 relays Due to Ground | [7 empty] | 20.0MW load
|  |  | Fault | [7 empty] | interrup.
| 14:54 | 15:35 | Fenchuganj 230/132/33kV S/S TR-01 HT Tripped showing REC 650 relays Due to 132 KV Bus -1 | [7 empty] | 20.0MW load
|  |  | Fail | [7 empty] | interrup.
| 14:54 |  | Full load interruption is occurring under Fenchuganj, Kulaura, Beanibazar, Sylhet(S),
Sylhet, Chattak, and Sunamganj grid S/S as Fenchuganj 132kV both buses and associated
132kV Ckts got tripped showing bus bar protection relay. Restoration process is going on.
| 14:57 | 17:36 | Fenchuganj-Sreemangal 132kV Ckt-1 Tripped from Sreemongol 132/33kV end showing Distance
Relay relays.
| 14:57 | 15:43 | Kulaura 132/33kV S/S TR-1 AB HT Forced S/D Due to Fenchuganj grid failure | [7 empty] | 17.0MW load
interrup.
| 14:57 | 15:44 | Kulaura 132/33kV S/S TR-2 LT Forced S/D Due to Fenchuganj grid failure | [7 empty] | 9.0MW load
interrup.
| 14:57 | 15:46 | Fenchuganj-Kulaura 132 kV Ckt-2 Forced S/D from Kulaura 132/33kV end Due to Fenchuganj | [7 empty] | 13.0MW load
|  |  | grid failure | [7 empty] | interrup. Kulaura
132/33kV end
| 14:57 | 15:41 | Fenchuganj-Kulaura 132 kV Ckt-1 Forced S/D from Kulaura 132/33kV end Due to Fenchuganj | [7 empty] | 13.0MW load
|  |  | grid failure | [7 empty] | interrup. Kulaura
132/33kV end
| 14:57 | 15:44 | Kulaura 132/33kV S/S TR-2 HT Forced S/D Due to Fenchuganj grid failure | [7 empty] | 9.0MW load
interrup.
| 14:57 | 15:43 | Kulaura 132/33kV S/S TR-1 AB LT Forced S/D Due to Fenchuganj grid failure | [7 empty] | 17.0MW load
interrup.
| 15:15 | 15:41 | Fenchuganj -Sylhet 132kV Ckt-1 Tripped from Beanibazar 132/33kV end showing REL 670 | [7 empty] | 40.0MW load
|  |  | relays Due to Undet Frequency Sylhet-Fenchuganj Line Trip | [7 empty] | interrup.
Beanibazar 132/33kV
end
| 15:15 | 15:42 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Tripped from Beanibazar 132/33kV end | [7 empty] | 40.0MW load
|  |  | showing No relays Due to Under Frequency | [7 empty] | interrup.
Beanibazar 132/33kV
end
| 16:07 |  | Entire Sylhet zone was restored.
| 16:18 | 19:22 | Kurigram-Lalmonirhat 132kV Ckt-1 Scheduled S/D from Kurigram 132/33kV end Due to Annual
maintenance
| 17:01 | 17:34 | Maijdee 132/33kV S/S TR-01 HT Scheduled S/D Due to Due to of 33KV Subornochor feeder | [7 empty] | 11.0MW load
|  |  | 33KV BUS load side DS insulator emergency maintenance. | [7 empty] | interrup.
|  | 17:21 | Aminbazar-Keraniganj 230kV Ckt-1 is restored.
|  | 17:38 | Chattak-Sylhet 132 kV Ckt-2 is restored.
|  | 18:01 | Gopalganj 400/132kV S/S 400kV Bus-02 is restored.
|  | 19:18 | Kurigram-Rangpur 132kV Ckt-1 is restored.
| 03:49 |  | Haripur 412 MW CCPP Shutdown with remarks:- ST
| 03:59 |  | Haripur 412 MW CCPP Shutdown with remarks:- GT
| 04:00 |  | Minimum Generation: 7660 MW.
| 07:15 |  | Haripur 230/132kV S/S EGCB 412MW Scheduled S/D Due to Loop replacement and clamp
replacement work.
| 07:28 |  | Keraniganj-Sreenagar (T at Powerpac 100MW) 132kV Ckt-2 Scheduled S/D from Srinagar
132/33kV end Due to Dead Line Checking. and from Keranigonj 230/132/33kV end Due to Dead
line checking
| 07:29 |  | Haripur 230/132kV S/S 132kV Main Bus Sec-1 Scheduled S/D Due to Loop replacement and
clamp replacement work at 132 kV 412 MW EGCB Bay.
| 07:32 |  | Aminbazar-Airport(Old) 230kV Ckt-1 Scheduled S/D from Agargaon 230/132kV end Due to Disc
replacement
| 07:35 |  | Barishal 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to To remove red hot at 33 kv Bus | [7 empty] | 10.0MW load
|  |  | section D/S. | [7 empty] | interrup.
| 07:37 |  | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to To remove red hot problem at 33 | [7 empty] | 10.0MW load
|  |  | kv bus section D/S. | [7 empty] | interrup.
| 07:52 |  | Keranigonj 230/132/33kV S/S 132 kV Hasnabad Ckt. 1 Scheduled S/D Due to Dead line
checking
| 07:57 |  | Barishal-Bhola 230 kV Ckt-2 Scheduled S/D from Barishal 230/132kV end Due to Annual
maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 12-01-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 346 | 8067600 | FGMO, Gas Shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 25 | 106995 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 6552494 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 47 | 547560 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 461979 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 560412 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 464400 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 322920 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 300 | 2226316 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 134 | 1426896 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 54720 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 1700640 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 171889 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 121680 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 520 | 9130455 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 90 | 423600 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 2067 | 32340556
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 97875 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 37 | 120000 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1103580 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 161 | 3869603 | Plant availability less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 75 | 827999 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 24 | 102240 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 93504 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 265920 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 22 | 485760 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 15824 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 45 | 301091 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 29925 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 49 | 355450 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 38 | 444480 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 40 | 91582 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 16 | 35127 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1210 | 26716361 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 2 | 112320 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 315 | 7672727.27 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4898.863 | 2164 | 42741368.27
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 189 | 4923000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 35 | 3200000 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Under maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 360 | 7261000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 117091 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1256507 | Gas shortage
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 137 | 993600 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 33008 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 105 | 2462838 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 167 | 1470240 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 110 | 2406720 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 313340 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 16 | 29760 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 361727 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1183 | 24828831
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 30 | 787200 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10850 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 912000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 397200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 245030 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 224640 | To be dispatched 18 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 67680 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 142 | 2644600
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 57530 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 611000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 528720 | machine problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3660136 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 658752 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1662720 | machine problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 2513700 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 373872 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7682500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 590 | 17748930
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 645 | 16733090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 297 | 6316416 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 486720 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1104 | 24160000 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2046 | 47696226
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 465454 | schedule outage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 1 | 16608 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 3159000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 595 | 13397818.18 | FGMO, U1 under maintenance
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5491630 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 45 | 148320 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 290 | 6545000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3043 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1281 | 29226873.18
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 279924 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 185 | 4499636 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 0 | 0 | -
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 317952 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 70 | 205920 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 27300 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1442.48 | 29678039 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 315744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 580010 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1767.48 | 35904525
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 100 | 574137 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 32008.32 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 90 | 495181 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 181390 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 894240 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 190 | 2176956.32
Eastern Grid Total |  |  |  |  | 17398.245 | 6146 | 120304285.27
Western Grid Total |  |  |  |  | 10984.003 | 5284.48 | 115004580.5
National Grid Total |  |  |  |  | 28382.248 | 11430.48 | 235308865.77
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 12-01-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7497.44 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3432.4 | MW
i) Dhaka area |  |  | 4124.04 |  | MW | i) Khulna area |  |  |  | 1308 | MW
ii) Chattogram area |  |  | 1104.4 |  | MW | ii) Barishal area |  |  |  | 322 | MW
iii) Cumilla area |  |  | 942 |  | MW | iii) Rajshahi area |  |  |  | 1054.4 | MW
iv) Mymensingh area |  |  | 913 |  | MW | iv) Rangpur area |  |  |  | 748 | MW
v) Sylhet area |  |  | 414 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10929.84 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 70 | 19:00 | 133 | Netrakona | 122 | 18:00
2 | AKSML | 116 | 17:00 | 68 | Hathazari | 72 | 13:00 | 134 | New | 54 | 12:00
3 | Aftabnagar | 26 | 14:00 | 69 | Hatirjheel | 29 | 15:00 | 135 | Niamatpur | 58 | 08:00
4 | Agargaon | 88 | 13:00 | 70 | Ishurdi | 53 | 18:30 | 136 | Noapara | 39 | 18:30
5 | Agrabad | 46 | 18:00 | 71 | Jaldhaka | 54 | 18:00 | 137 | PHP | 7 | 02:00
6 | Amnura | 26 | 08:00 | 72 | Jamalpur | 88 | 18:00 | 138 | Pabna | 77 | 18:00
7 | Ashuganj | 58 | 13:00 | 73 | Jashore | 104 | 13:00 | 139 | Palashbari | 87 | 18:00
8 | BSRM | 207 | 01:00 | 74 | Jhenaidah | 101 | 18:00 | 140 | Panchagarh | 43 | 18:00
9 | Bagerhat | 64 | 18:00 | 75 | Joydebpur | 110 | 18:30 | 141 | Patiya | 6.7 | 18:30
10 | Bajitpur | 63 | 18:00 | 76 | Joypurhat | 42 | 08:00 | 142 | Patuakhali | 40.5 | 21:00
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 14 | 11:00 | 143 | Payra | 28 | 18:00
12 | Bakulia | 65 | 18:00 | 78 | KSRM | 14 | 02:00 | 144 | Postogola | 40 | 12:00
13 | Banani | 32.8 | 13:00 | 79 | Kabirpur | 185 | 18:30 | 145 | Purbachal | 20 | 12:00
14 | Bangabhaban | 10 | 14:00 | 80 | Kachua | 68 | 23:00 | 146 | Purbasadipur | 120 | 18:30
15 | Barapukuria | 55 | 18:30 | 81 | Kallyanpur | 72 | 13:00 | 147 | Rahanpur | 23 | 18:30
16 | Barguna | 16 | 21:00 | 82 | Kalurghat | 34 | 11:00 | 148 | Rahim | 51 | 15:00
17 | Barishal | 85 | 13:00 | 83 | Kamrangirchar | 66 | 13:00 | 149 | Rajbari | 61 | 18:30
18 | Barishal-230 | 68 | 20:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 111 | 18:30
19 | Baroaulia | 58 | 18:00 | 85 | Kasba | 23 | 13:00 | 151 | Rajshahi | 73 | 20:00
20 | Baroirhat | 50 | 13:00 | 86 | Kazla | 98 | 13:00 | 152 | Rajshahi-230 | 81 | 13:00
21 | Bashundhara | 154 | 13:00 | 87 | Keranigonj | 72 | 12:00 | 153 | Ramganj | 67 | 20:00
22 | BashundharaCement | 7 | 22:00 | 88 | Khagrachori | 26 | 18:00 | 154 | Rampur | 28 | 12:00
23 | Beanibazar | 46 | 19:30 | 89 | Khulna | 50 | 13:00 | 155 | Rangamati | 13 | 18:30
24 | Benapole | 66 | 08:00 | 90 | Khulshi | 150 | 18:00 | 156 | Rangpur | 114 | 18:30
25 | Bhaluka | 139 | 18:00 | 91 | Kishoreganj | 97 | 20:00 | 157 | Ruppur | 2.4 | 09:00
26 | Bhandaria | 38 | 21:00 | 92 | Kodda | 265 | 18:00 | 158 | SSM | 2 | 01:00
27 | Bhangura | 25 | 18:00 | 93 | Kulaura | 31 | 16:00 | 159 | Saidpur | 94 | 18:00
28 | Bheramara(GK) | 44 | 18:00 | 94 | Kurigram | 53 | 08:00 | 160 | Satkhira | 103 | 08:00
29 | Bhulta | 196 | 12:00 | 95 | Kushtia | 128 | 13:00 | 161 | Satmasjid | 80 | 13:00
30 | Bog-Sherpur | 60 | 18:30 | 96 | Laksam | 23 | 13:00 | 162 | Savar | 194 | 12:00
31 | Bogura | 112 | 19:00 | 97 | Lakshmipur | 24 | 18:00 | 163 | SevenRings | 16.4 | 18:00
32 | Borhanuddin | 65 | 21:00 | 98 | Lalbag | 56 | 18:00 | 164 | ShahCement | 35 | 10:00
33 | Brahmanbaria | 92 | 19:00 | 99 | Lalmonirhat | 46 | 18:30 | 165 | Shahjadpur | 60 | 18:30
34 | Cantonment | 74 | 13:00 | 100 | MI_Cement | 16.1 | 03:00 | 166 | Shahjibazar | 105 | 18:00
35 | Chandina | 17 | 18:00 | 101 | Madanganj | 40 | 13:00 | 167 | Shahmirpur | 39 | 18:00
36 | Chandpur | 54 | 18:00 | 102 | Madaripur | 73 | 20:00 | 168 | Shariatpur | 57 | 21:00
37 | Chandraghona | 26 | 19:00 | 103 | Madartek | 52 | 13:00 | 169 | Sherpur | 118 | 18:30
38 | Chapai | 54 | 12:00 | 104 | Madunaghat | 37 | 21:00 | 170 | Shikalbaha | 16 | 00:00
39 | Charsaidpur | 39 | 09:00 | 105 | Magura | 50 | 18:00 | 171 | Shitalakhya | 65.3 | 12:00
40 | Chauddagram | 48 | 13:00 | 106 | Mahasthangarh | 50 | 18:30 | 172 | Sholosohor | 35 | 18:00
41 | Chhatak | 20 | 00:00 | 107 | Maijdee | 43 | 18:30 | 173 | Shyampur | 124 | 01:00
42 | Chowmuhani | 109 | 18:00 | 108 | Manikganj | 105 | 19:00 | 174 | Siddhirganj | 99 | 12:00
43 | Chuadanga | 81 | 18:30 | 109 | Maniknagar | 52 | 13:00 | 175 | Sirajganj | 86 | 18:30
44 | Coxsbazar | 112 | 18:00 | 110 | Matarbari | 48 | 18:00 | 176 | Sonargaon | 126 | 19:00
45 | Cumilla(N) | 107 | 18:30 | 111 | Matuail | 48 | 10:00 | 177 | Sreemongol | 53 | 18:00
46 | Cumilla(S) | 121 | 14:00 | 112 | Metrorail_Motijheel | 17 | 17:00 | 178 | Sreepur | 90 | 18:30
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 0 | 00:00 | 179 | Srinagar | 31.6 | 21:00
48 | Daudkandi | 100 | 00:00 | 114 | Millgate | 76 | 16:00 | 180 | Sunamganj | 40 | 19:00
49 | DhakaUniversity | 46 | 12:00 | 115 | Mirpur | 111 | 13:00 | 181 | Sylhet | 43 | 19:00
50 | Dhamrai | 84 | 19:00 | 116 | Mirsorai | 30 | 05:00 | 182 | Sylhet-132 | 79 | 18:00
51 | Dhanmondi | 75.8 | 13:00 | 117 | Mirzapur | 37 | 19:00 | 183 | TK | 15 | 13:00
52 | Dohazari | 71 | 19:30 | 118 | Mithapukur | 46 | 18:00 | 184 | Tangail | 128 | 18:00
53 | Faridpur | 119 | 18:30 | 119 | Modern | N/A | N/A | 185 | Taraganj | 16 | 08:00
54 | Fatullah | 92 | 12:00 | 120 | Mogbazar | 48.8 | 13:00 | 186 | Tasnim | 27 | 01:00
55 | Fenchuganj | 28 | 18:00 | 121 | Mongla | 36 | 13:00 | 187 | Thakurgaon | 76 | 18:30
56 | Feni | 78 | 18:00 | 122 | Motijheel | 30 | 18:00 | 188 | Tongi | 113 | 12:00
57 | GPH | 23 | 01:00 | 123 | Muktagacha | 31 | 08:00 | 189 | Ullahpara | 26 | 18:00
58 | Ghatail | 66 | 08:00 | 124 | Munshiganj | 74 | 13:00 | 190 | Ullon | 39 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 0 | 00:00 | 191 | Uttara | 62 | 12:00
60 | Ghorashal-230 | 85 | 19:30 | 126 | Mymensingh | 144 | 13:00 | 192 | UttaraNew | 30 | 13:00
61 | Goalpara | 33 | 13:00 | 127 | Naogaon | 100 | 13:00 | 193 | Zigatola | 68 | 13:00
62 | Gollamari | 74 | 13:00 | 128 | Narail | 43 | 19:00
63 | Gopalganj | 82 | 18:30 | 129 | Narinda | 60 | 13:00
64 | Gulshan | 72 | 13:00 | 130 | Narshingdi | 137 | 21:00
65 | Halishahar | 64 | 15:00 | 131 | Natore | 110 | 18:30
66 | HaripurSBU | 120 | 11:00 | 132 | Nawabganj | 31.4 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 12-01-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 9477.18 | 0 |  | 9477.18
1:00 | 8816.23 | 0 |  | 8816.23
2:00 | 8323.45 | 0 |  | 8323.45
3:00 | 8005.96 | 0 |  | 8005.96
4:00 | 7710.8 | 0 |  | 7710.8
5:00 | 7644.04 | 0 |  | 7644.04
6:00 | 8025.25 | 0 |  | 8025.25
7:00 | 8839.61 | 0 |  | 8839.61
8:00 | 9868.27 | 0 |  | 9868.27
9:00 | 10203.51 | 0 |  | 10203.51
10:00 | 9899.7 | 0 |  | 9899.7
11:00 | 9950.15 | 0 |  | 9950.15
12:00 | 10496.66 | 0 |  | 10496.66
13:00 | 10774.62 | 0 |  | 10774.62
14:00 | 10525.2 | 0 |  | 10525.2
15:00 | 9922.54 | 0 |  | 9922.54
16:00 | 9464.24 | 0 |  | 9464.24
17:00 | 9998.26 | 0 |  | 9998.26
18:00 | 11108.9 | 0 |  | 11108.9
19:00 | 11430.48 | 0 |  | 11430.48
19:30 | 11336.31 | 0 |  | 11336.31
20:00 | 11209.72 | 0 |  | 11209.72
21:00 | 11039.4 | 0 |  | 11039.4
22:00 | 10492.4 | 0 |  | 10492.4
23:00 | 9828 | 0 |  | 9828
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 12-01-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4371 | 5106.18 | 9477.18 | DAILY GENERATION CURVE
00:30 | 4323.5 | 4823.205 | 9146.705
01:00 | 4276 | 4540.23 | 8816.23 | 12-01-2026
01:30 | 4229 | 4340.84 | 8569.84
02:00 | 4182 | 4141.45 | 8323.45
02:30 | 4223 | 3941.705 | 8164.705
03:00 | 4264 | 3741.96 | 8005.96
03:30 | 4231 | 3627.38 | 7858.38
04:00 | 4198 | 3512.8 | 7710.8
04:30 | 4179.25 | 3498.17 | 7677.42
05:00 | 4160.5 | 3483.54 | 7644.04
05:30 | 4290 | 3544.645 | 7834.645
06:00 | 4419.5 | 3605.75 | 8025.25
06:30 | 4478.435 | 3953.995 | 8432.43
07:00 | 4537.37 | 4302.24 | 8839.61
07:30 | 4786.81 | 4567.13 | 9353.94
08:00 | 5036.25 | 4832.02 | 9868.27
08:30 | 5134.815 | 4901.075 | 10035.89
09:00 | 5233.38 | 4970.13 | 10203.51
09:30 | 5077.095 | 4974.51 | 10051.605
10:00 | 4920.81 | 4978.89 | 9899.7
10:30 | 4927.25 | 4997.675 | 9924.925
11:00 | 4933.69 | 5016.46 | 9950.15
11:30 | 5027.295 | 5196.11 | 10223.405
12:00 | 5120.9 | 5375.76 | 10496.66
12:30 | 5212.695 | 5422.945 | 10635.64
13:00 | 5304.49 | 5470.13 | 10774.62
13:30 | 5231.14 | 5418.77 | 10649.91
14:00 | 5157.79 | 5367.41 | 10525.2
14:30 | 4986.225 | 5237.645 | 10223.87
15:00 | 4814.66 | 5107.88 | 9922.54
15:30 | 4737.84 | 4955.55 | 9693.39
16:00 | 4661.02 | 4803.22 | 9464.24
16:30 | 4896.7 | 4834.55 | 9731.25
17:00 | 5132.38 | 4865.88 | 9998.26
17:30 | 5465.59 | 5087.99 | 10553.58
18:00 | 5798.8 | 5310.1 | 11108.9
18:30 | 5972.4 | 5297.29 | 11269.69
19:00 | 6146 | 5284.48 | 11430.48
19:30 | 6033 | 5303.31 | 11336.31
20:00 | 5919.8 | 5289.92 | 11209.72
20:30 | 5820.1 | 5304.46 | 11124.56 |  | Executive Engineer
21:00 | 5720.4 | 5319 | 11039.4 |  | Network Operation Division
21:30 | 5512.9 | 5253 | 10765.9
22:00 | 5305.4 | 5187 | 10492.4
22:30 | 4984.7 | 5175.5 | 10160.2
23:00 | 4664 | 5164 | 9828

## En-Curve
QF-LDC-12
Date | 12-01-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2377 | 1228 | 877 | 0 | 102 | 1325.18 | 46 | 3487 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2375 | 1236 | 820.5 | 0 | 98 | 1222.205 | 46 | 3314 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 12-01-2026
01:00 | 2373 | 1244 | 764 | 0 | 94 | 1119.23 | 46 | 3141 | 0 | 0 | 35 | 0 | 0 | 0 | 0
01:30 | 2381 | 1220 | 727.5 | 0 | 92 | 1070.34 | 46 | 3004 | 0 | 0 | 27 | 0 | 0 | 2 | 0 | Energy Generated | 235.3089 |  | MKWHr
02:00 | 2389 | 1196 | 691 | 0 | 90 | 1021.45 | 46 | 2867 | 0 | 0 | 19 | 0 | 0 | 4 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2406 | 1205.5 | 581 | 0 | 89 | 1025.205 | 46 | 2786.5 | 0 | 0 | 19 | 0 | 0 | 6.5 | 0 | Total Energy Requirement | 235.3089 |  | MKWHr
03:00 | 2423 | 1215 | 471 | 0 | 88 | 1028.96 | 46 | 2706 | 0 | 0 | 19 | 0 | 0 | 9 | 0
03:30 | 2365.5 | 1242.5 | 348 | 0 | 87 | 1027.88 | 46 | 2722.5 | 0 | 0 | 9.5 | 0 | 0 | 9.5 | 0
04:00 | 2308 | 1270 | 225 | 0 | 86 | 1026.8 | 46 | 2739 | 0 | 0 | 0 | 0 | 0 | 10 | 0
04:30 | 2306.5 | 1254.25 | 225 | 0 | 82 | 1027.17 | 46 | 2720.5 | 0 | 0 | 0 | 0 | 0 | 16 | 0
05:00 | 2305 | 1238.5 | 225 | 0 | 78 | 1027.54 | 46 | 2702 | 0 | 0 | 0 | 0 | 0 | 22 | 0
05:30 | 2331 | 1272 | 224.5 | 0 | 83 | 1024.645 | 46 | 2836.5 | 0 | 0 | 0 | 0 | 0 | 17 | 0
06:00 | 2357 | 1305.5 | 224 | 0 | 88 | 1021.75 | 46 | 2971 | 0 | 0 | 0 | 0 | 0 | 12 | 0
06:30 | 2354.5 | 1308.5 | 332.5 | 0 | 89 | 1124.365 | 46 | 3144 | 4.565 | 0 | 17.5 | 0 | 0 | 11.5 | 0
07:00 | 2352 | 1311.5 | 441 | 0 | 90 | 1226.98 | 46 | 3317 | 9.13 | 0 | 35 | 0 | 0 | 11 | 0
07:30 | 2364 | 1307.25 | 508 | 0 | 97 | 1305.99 | 46 | 3375 | 63.2 | 0 | 278.5 | 0 | 0 | 9 | 0
08:00 | 2376 | 1303 | 575 | 0 | 104 | 1385 | 46 | 3433 | 117.27 | 0 | 522 | 0 | 0 | 7 | 0
08:30 | 2260.5 | 1252 | 633 | 0 | 104 | 1380 | 46 | 3417 | 205.39 | 17.5 | 717 | 0 | 0 | 3.5 | 0
09:00 | 2145 | 1201 | 691 | 0 | 104 | 1375 | 46 | 3401 | 293.51 | 35 | 912 | 0 | 0 | 0 | 0
09:30 | 2143.5 | 1198.5 | 779 | 0 | 104 | 1296 | 46 | 3387.5 | 381.105 | 26 | 690 | 0 | 0 | 0 | 0
10:00 | 2142 | 1196 | 867 | 0 | 104 | 1217 | 46 | 3374 | 468.7 | 17 | 468 | 0 | 0 | 0 | 0
10:30 | 2227.5 | 1186.5 | 873 | 0 | 108 | 1218 | 46 | 3284.5 | 522.125 | 17 | 442.3 | 0 | 0 | 0 | 0
11:00 | 2313 | 1177 | 879 | 0 | 112 | 1219 | 46 | 3195 | 575.55 | 17 | 416.6 | 0 | 0 | 0 | 0
11:30 | 2326.5 | 1241.5 | 878.5 | 0 | 115 | 1306 | 46 | 3254 | 595.805 | 17 | 443.1 | 0 | 0 | 0 | 0
12:00 | 2340 | 1306 | 878 | 0 | 118 | 1393 | 46 | 3313 | 616.06 | 17 | 469.6 | 0 | 0 | 0 | 0
12:30 | 2288 | 1324 | 878 | 0 | 116 | 1405.5 | 46 | 3353 | 602.44 | 17 | 605.7 | 0 | 0 | 0 | 0
13:00 | 2236 | 1342 | 878 | 0 | 114 | 1418 | 46 | 3393 | 588.82 | 17 | 741.8 | 0 | 0 | 0 | 0
13:30 | 2192 | 1259.5 | 878.5 | 0 | 117 | 1445.7 | 46 | 3384.5 | 544.46 | 17 | 765.25 | 0 | 0 | 0 | 0
14:00 | 2148 | 1177 | 879 | 0 | 120 | 1473.4 | 46 | 3376 | 500.1 | 17 | 788.7 | 0 | 0 | 0 | 0
14:30 | 2163 | 1187.5 | 878.5 | 0 | 116 | 1376.235 | 46 | 3360 | 431.285 | 17 | 648.35 | 0 | 0 | 0 | 0
15:00 | 2178 | 1198 | 878 | 0 | 112 | 1279.07 | 46 | 3344 | 362.47 | 17 | 508 | 0 | 0 | 0 | 0
15:30 | 2137.5 | 1207.5 | 878.5 | 0 | 110 | 1272.56 | 46 | 3293.5 | 266.98 | 17 | 463.35 | 0 | 0 | 0.5 | 0
16:00 | 2097 | 1217 | 879 | 0 | 108 | 1266.05 | 46 | 3243 | 171.49 | 17 | 418.7 | 0 | 0 | 1 | 0
16:30 | 2136 | 1246.5 | 879 | 0 | 107 | 1310.81 | 46 | 3275 | 100.34 | 34.5 | 595.1 | 0 | 0 | 1 | 0
17:00 | 2175 | 1276 | 879 | 0 | 106 | 1355.57 | 46 | 3307 | 29.19 | 52 | 771.5 | 0 | 0 | 1 | 0
17:30 | 2227 | 1268.5 | 878.5 | 0 | 107 | 1409.335 | 46 | 3373 | 14.595 | 84.5 | 1143.65 | 0 | 0 | 1.5 | 0
18:00 | 2279 | 1261 | 878 | 0 | 108 | 1463.1 | 46 | 3439 | 0 | 117 | 1515.8 | 0 | 0 | 2 | 0
18:30 | 2241 | 1342 | 761.5 | 0 | 109 | 1452.79 | 46 | 3476.5 | 0 | 141 | 1697.9 | 0 | 0 | 2 | 0
19:00 | 2203 | 1423 | 645 | 0 | 110 | 1442.48 | 46 | 3514 | 0 | 165 | 1880 | 0 | 0 | 2 | 0
19:30 | 2222 | 1416 | 645 | 0 | 110 | 1442.31 | 46 | 3522 | 0 | 150 | 1783 | 0 | 0 | 0 | 0
20:00 | 2206 | 1415 | 645 | 0 | 110 | 1442.92 | 46 | 3516 | 0 | 110 | 1718.8 | 0 | 0 | 0 | 0
20:30 | 2185.5 | 1370.5 | 691 | 0 | 109 | 1442.96 | 46 | 3534 | 0 | 75.5 | 1670.1 | 0 | 0 | 0 | 0
21:00 | 2165 | 1326 | 737 | 0 | 108 | 1443 | 46 | 3552 | 0 | 41 | 1621.4 | 0 | 0 | 0 | 0
21:30 | 2167 | 1305.5 | 737 | 0 | 107 | 1446 | 46 | 3554.5 | 0 | 20.5 | 1378.9 | 0 | 0 | 3.5 | 0
22:00 | 2169 | 1285 | 737 | 0 | 106 | 1449 | 46 | 3557 | 0 | 0 | 1136.4 | 0 | 0 | 7 | 0
22:30 | 2186.5 | 1273.5 | 807.5 | 0 | 103 | 1445.5 | 46 | 3548 | 0 | 0 | 739.2 | 0 | 0 | 11 | 0
23:00 | 2204 | 1262 | 878 | 0 | 100 | 1442 | 46 | 3539 | 0 | 0 | 342 | 0 | 0 | 15 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 12-01-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 426 | 05:00 | 396 | 12:00 | Meghnaghat | 428 | 05:00 | 401 | 12:00
Ashuganj | 409 | 5:00 | 382 | 12:00 | Payra | 427 | 05:00 | 413 | 12:00
Bhulta | 402 | 02:00 | 375 | 12:00 | Rahanpur | 417 | 05:00 | 395 | 12:00
Bibiana | 424 | 05:00 | 407 | 12:00 | Rampal | 418 | 05:00 | 399 | 12:00
BIPTC | 407 | 02:00 | 390 | 11:00
Bogura | 414 | 05:00 | 383 | 13:00
Gopalganj | 424 | 04:00 | 400 | 12:00
Kaliakoir | 422 | 05:00 | 392 | 12:00
Korerhat | 426 | 05:00 | 406 | 12:00
Madunaghat | 417 | 05:00 | 405 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 249 | 04:00 | 227 | 12:00 | Kachua | 242 | 18:30 | 231 | 12:00
AKSML | 238 | 04:00 | 230 | 14:00 | Kaliakoir | 247 | 05:00 | 229 | 11:00
Aminbazar | 248 | 03:00 | 233 | 12:00 | Keranigonj | 248 | 05:00 | 221 | 13:00
Ashuganj | 238 | 04:00 | 223 | 12:00 | Khulna(S) | 246 | 04:00 | 229 | 12:00
Ashuganj-400 | 238 | 04:00 | 223 | 12:00 | Korerhat | 242 | 05:00 | 231 | 12:00
Baghabari | 239 | 04:00 | 223 | 12:00 | Madunaghat | 247 | 19:30 | 231 | 12:00
Barapukuria | 226 | 19:00 | 209 | 12:00 | Madunaghat-400 | 239 | 05:00 | 232 | 12:00
Barapukuria-230 | 226 | 19:00 | 209 | 12:00 | Maniknagar | 241 | 04:00 | 222 | 12:00
Barishal | 239 | 04:00 | 227 | 12:00 | Meghnaghat | 247 | 05:00 | 237 | 09:00
Bheramara | 240 | 05:00 | 221 | 12:00 | Meghnaghat-400 | 242 | 05:00 | 226 | 12:00
Bhulta | 243 | 05:00 | 225 | 12:00 | Mirsorai | 242 | 04:00 | 231 | 12:00
Bibiana | 244 | 04:00 | 232 | 12:00 | Rajshahi | 238 | 06:00 | 219 | 12:00
BIPTC | 241 | 05:00 | 222 | 08:00 | Rampal | 241 | 02:00 | 228 | 12:00
Bogura | 242 | 04:00 | 225 | 08:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 242 | 05:00 | 223 | 13:00 | Rampura | 243 | 05:00 | 225 | 12:00
Borhanuddin | 241 | 06:00 | 236 | 12:00 | Shikalbaha | 237 | 18:00 | 229 | 15:00
BSRM | 241 | 04:00 | 230 | 12:00 | Shyampur | 240 | 04:00 | 223 | 14:00
Cumilla(N) | 236 | 02:00 | 226 | 11:00 | Siddhirganj | 242 | 03:00 | 225 | 12:00
Faridpur | 240 | 04:00 | 225 | 12:00 | Sirajgonj | 246 | 05:00 | 229 | 12:00
Fenchuganj | 244 | 05:00 | 233 | 16:00 | Sreepur | 237 | 05:00 | 219 | 12:00
Feni | 243 | 05:00 | 229 | 12:00 | Tongi | 244 | 19:30 | 220 | 12:00
Ghorashal | 240 | 01:00 | 225 | 13:00
Ghorashal-230 | 234 | 05:00 | 212 | 12:00
Gopalganj | 238 | 04:00 | 224 | 12:00
GPH | 238 | 19:00 | 230 | 04:00
Haripur | 242 | 04:00 | 227 | 12:00
Hasnabad | 239 | 20:00 | 220 | 12:00
Hathazari | 237 | 18:30 | 229 | 12:00
Ishurdi | 242 | 05:00 | 224 | 12:00
Jhenaidah | 243 | 05:00 | 222 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 02:00 | 124 | 12:00 | Laksam | 139 | 04:00 | 132 | 12:00
Agargaon | 142 | 04:00 | 128 | 12:00 | Lakshmipur | 135 | 04:00 | 129 | 12:00
Agrabad | 139 | 18:30 | 133 | 12:00 | Lalbag | 138 | 06:00 | 122 | 14:00
AKS | 136 | 19:00 | 131 | 13:00 | Lalmonirhat | 133 | 19:30 | 120 | 23:00
Aminbazar | 141 | 03:00 | 132 | 12:00 | Madanganj | 135 | 00:00 | 132 | 07:00
Amnura | 138 | 03:00 | 127 | 12:00 | Madaripur | 140 | 01:00 | 136 | 11:00
Ashuganj | 139 | 04:00 | 133 | 12:00 | Madartek | 134 | 04:00 | 124 | 12:00
Bagerhat | 135 | 04:00 | 125 | 12:00 | Madunaghat | 139 | 18:30 | 134 | 14:00
Bajitpur | 136 | 05:00 | 127 | 14:00 | Magura | 138 | 02:00 | 125 | 12:00
Bakerganj | 141 | 19:00 | 134 | 14:00 | Mahasthangarh | 136 | 04:00 | 125 | 12:00
Bakulia | 138 | 04:00 | 133 | 16:00 | Maijdee | 136 | 05:00 | 129 | 12:00
Banani | 134 | 02:00 | 124 | 12:00 | Manikganj | 132 | 05:00 | 118 | 12:00
Bangabhaban | 141 | 05:00 | 124 | 12:00 | Maniknagar | 140 | 05:00 | 124 | 12:00
Barapukuria | 137 | 19:00 | 126 | 12:00 | Matarbari | 131 | 02:00 | 123 | 18:00
Barguna | 140 | 19:00 | 135 | 12:00 | Matuail | 138 | 02:00 | 131 | 12:00
Barishal | 140 | 04:00 | 132 | 12:00 | Metrorail_Motijheel | 140 | 05:00 | 124 | 12:00
Barishal-230 | 141 | 04:00 | 133 | 12:00 | Metrorail_Uttara | 139 | 04:00 | 129 | 12:00
Baroaulia | 138 | 03:00 | 134 | 14:00 | Millgate | 137 | 01:00 | 120 | 12:00
Baroirhat | 137 | 05:00 | 129 | 12:00 | Mirpur | 140 | 01:00 | 129 | 12:00
Bashundhara | 135 | 03:00 | 124 | 12:00 | Mirzapur | 137 | 04:00 | 127 | 12:00
BashundharaCement | 135 | 00:00 | 132 | 07:00 | Mithapukur | 136 | 04:00 | 122 | 08:00
Beanibazar | 135 | 05:00 | 121 | 16:00 | MI_Cement | 136.4 | 06:00 | 124 | 12:00
Benapole | 137 | 03:00 | 118 | 08:00 | Modern | N/A | N/A | N/A | N/A
Bhaluka | 129 | 00:00 | 122 | 12:00 | Mogbazar | 136 | 02:00 | 125 | 13:00
Bhandaria | 140 | 06:00 | 132 | 12:00 | Mongla | 132 | 01:00 | 125 | 12:00
Bhangura | 139 | 04:00 | 129 | 12:00 | Motijheel | 141 | 04:00 | 124 | 12:00
Bheramara | 141 | 04:00 | 133 | 08:00 | Muktagacha | 132 | 10:00 | 124 | 23:00
Bheramara(GK) | 141 | 04:00 | 133 | 12:00 | Munshiganj | 136 | 02:00 | 128 | 12:00
Bhulta | 130 | 00:00 | 124 | 12:00 | Muradnagar | 139 | 04:00 | 130 | 12:00
Bog-Sherpur | 138 | 04:00 | 126 | 12:00 | Mymensingh | 133 | 10:00 | 118 | 08:00
Bogura | 137 | 19:00 | 124 | 13:00 | Naogaon | 135 | 04:00 | 122 | 13:00
Bogura-230 | 138 | 04:00 | 127 | 12:00 | Narail | 138 | 05:00 | 123 | 12:00
Brahmanbaria | 133 | 05:00 | 122 | 16:00 | Narinda | 140 | 05:00 | 124 | 12:00
Cantonment | 141 | 03:00 | 129 | 12:00 | Narshingdi | 134 | 18:00 | 114 | 13:00
Chandina | 140 | 04:00 | 132 | 12:00 | Natore | 136 | 04:00 | 128 | 12:00
Chandpur | 139 | 05:00 | 134 | 11:00 | Nawabganj | 139 | 03:00 | 122 | 13:00
Chandraghona | 140 | 05:00 | 135 | 12:00 | Netrakona | 125 | 05:00 | 112 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 139 | 03:00 | 130 | 12:00 | New | 136 | 21:00 | 122 | 12:00
Charsaidpur | 138 | 04:00 | 130 | 11:00 | Niamatpur | 138 | 03:00 | 130 | 12:00
Chauddagram | 137 | 02:00 | 129 | 12:00 | Noapara | 137 | 02:00 | 121 | 08:00
Chhatak | 136 | 03:00 | 121 | 17:00 | Pabna | 140 | 04:00 | 131 | 08:00
Chowmuhani | 134 | 18:00 | 129 | 06:00 | Palashbari | 134 | 04:00 | 121 | 08:00
Chuadanga | 139 | 05:00 | 124 | 12:00 | Panchagarh | 141 | 19:00 | 125 | 08:00
Coxsbazar | 132 | 09:00 | 123 | 13:00 | Patiya | 139 | 05:00 | 134 | 12:00
Cumilla(N) | 138 | 02:00 | 132 | 11:00 | Patuakhali | 139 | 18:30 | 133 | 12:00
Cumilla(S) | 137 | 00:00 | 125 | 11:00 | Payra | 140 | 05:00 | 135 | 12:00
Daganbhuiyan | 136 | 04:00 | 129 | 12:00 | PHP | 136 | 05:00 | 133 | 00:00
Daudkandi | 136 | 04:00 | 128 | 12:00 | Postogola | 136 | 06:00 | 125 | 14:00
DhakaUniversity | 135 | 03:00 | 124 | 12:00 | Purbachal | 135 | 03:00 | 124 | 12:00
Dhamrai | 138 | 02:00 | 131 | 15:00 | Purbasadipur | 139 | 19:00 | 123 | 08:00
Dhanmondi | 139 | 04:00 | 131.5 | 12:00 | Rahanpur | 139 | 04:00 | 132 | 13:00
Dohazari | 135 | 04:00 | 132 | 00:00 | Rahanpur-400 | 140 | 04:00 | 132 | 12:00
Faridpur | 139 | 04:00 | 131 | 12:00 | Rahim | 139 | 05:00 | 130 | 12:00
Fatullah | 139 | 05:00 | 124 | 12:00 | Rajbari | 139 | 04:00 | 130 | 12:00
Fenchuganj | 138 | 03:00 | 129 | 16:00 | Rajendrapur | 134 | 05:00 | 122 | 12:00
Feni | 134 | 22:00 | 127 | 12:00 | Rajshahi | 137 | 02:00 | 126 | 13:00
Feni-230 | 136 | 04:00 | 129 | 12:00 | Rajshahi-230 | 137 | 04:00 | 126 | 13:00
Ghatail | 131 | 10:00 | 123 | 23:00 | Ramganj | 137 | 20:00 | 125 | 13:00
Ghorashal | 132 | 08:00 | 125 | 11:00 | Rampur | 138 | 03:00 | 132 | 14:00
Goalpara | 136 | 04:00 | 128 | 12:00 | Rampura | 135 | 04:00 | 124 | 12:00
Gollamari | 138 | 03:00 | 128 | 12:00 | Rangamati | 138 | 03:00 | 133 | 12:00
Gopalganj | 141 | 04:00 | 131 | 12:00 | Rangpur | 136 | 04:00 | 125 | 08:00
Gopalganj-400 | 144 | 05:00 | 135 | 12:00 | Ruppur | 140 | 04:00 | 132 | 08:00
Gulshan | 134 | 03:00 | 124 | 11:00 | Saidpur | 135 | 19:00 | 120 | 08:00
Halishahar | 140 | 18:30 | 134 | 12:00 | Satkhira | 136 | 04:00 | 123 | 19:30
Haripur | 139 | 04:00 | 130 | 12:00 | Satmasjid | 141 | 05:00 | 125 | 13:00
HaripurSBU | 139 | 04:00 | 131 | 13:00 | Savar | 140 | 04:00 | 130 | 11:00
Hasnabad | 135 | 03:00 | 125 | 12:00 | SevenRings | 134 | 05:00 | 125 | 12:00
Hathazari | 139 | 18:30 | 135 | 13:00 | ShahCement | 138 | 04:00 | 130 | 12:00
Hatirjheel | 135 | 04:00 | 124 | 12:00 | Shahjadpur | 142 | 04:00 | 133 | 12:00
Ishurdi | 142 | 04:00 | 133 | 08:00 | Shahjibazar | 133 | 05:00 | 121 | 16:00
Jaldhaka | 133 | 05:00 | 124 | 12:00 | Shahmirpur | 139 | 19:00 | 134 | 12:00
Jamalpur | 132 | 10:00 | 116 | 07:00 | Shariatpur | 142 | 03:00 | 134 | 12:00
Jashore | 136 | 03:00 | 120 | 13:00 | Sherpur | 129 | 10:00 | 114 | 07:00
Jhenaidah | 139 | 04:00 | 116 | 14:00 | Shikalbaha | 128 | 05:00 | 123 | 14:00
Jhenaidah-230 | 142 | 05:00 | 125 | 13:00 | Shikalbaha-230 | 141 | 18:30 | 135 | 13:00
Joydebpur | 132 | 05:00 | 122 | 12:00 | Shitalakhya | 136.3 | 05:00 | 124 | 12:00
Joypurhat | 135 | 03:00 | 124 | 13:00 | Sholosohor | 139 | 04:00 | 134 | 12:00
Juldah | 140 | 18:30 | 134 | 12:00 | Shyampur | 138 | 19:30 | 127 | 13:00
Kabirpur | 139 | 19:00 | 120 | 11:00 | Shyampur-230 | 139 | 04:00 | 129 | 13:00
Kachua | 139 | 04:00 | 133 | 12:00 | Siddhirganj | 139 | 20:00 | 130 | 12:00
Kaliakoir | 142 | 04:00 | 131 | 12:00 | Sirajganj | 139 | 04:00 | 125 | 12:00
Kallyanpur | 141 | 08:00 | 129 | 12:00 | Sonargaon | 135 | 18:00 | 129 | 12:00
Kalurghat | 139 | 04:00 | 134 | 12:00 | Sreemongol | 133 | 01:00 | 124 | 13:00
Kamrangirchar | 140 | 05:00 | 121 | 13:00 | Sreepur | 135 | 04:00 | 124 | 12:00
Kaptai | 137 | 03:00 | 132 | 13:00 | Srinagar | 139 | 03:00 | 121 | 12:00
Kasba | 139 | 05:00 | 129 | 12:00 | SSM | 142 | 03:00 | 140 | 00:00
Kazla | 140 | 04:00 | 123 | 13:00 | Sunamganj | 133 | 03:00 | 117 | 16:00
Keranigonj | 140 | 05:00 | 123 | 14:00 | Sylhet | 136 | 16:00 | 123 | 18:00
Khagrachori | 138 | 03:00 | 133 | 12:00 | Sylhet-132 | 135 | 06:00 | 123 | 16:00
Khulna | 136 | 03:00 | 127 | 12:00 | Tangail | 131 | 05:00 | 125 | 12:00
Khulna(S) | 138 | 04:00 | 125 | 13:00 | Taraganj | 135 | 19:00 | 124 | 08:00
Khulshi | 138 | 18:30 | 132 | 12:00 | Tasnim | 138 | 04:00 | 129 | 12:00
Kishoreganj | 134 | 04:00 | 127 | 12:00 | Thakurgaon | 142 | 19:00 | 123 | 08:00
Kodda | 136 | 19:30 | 124 | 12:00 | TK | 137 | 00:00 | 135 | 08:00
KSRM | 139 | 18:30 | 133 | 13:00 | Tongi | 136 | 19:30 | 120 | 12:00
Kulaura | 138 | 04:00 | 127 | 16:00 | Ullahpara | 140 | 03:00 | 124 | 12:00
Kurigram | 132 | 19:30 | 116 | 08:00 | Ullon | 134 | 04:00 | 124 | 12:00
Kushtia | 136 | 04:00 | 124 | 13:00 | Uttara | 135 | 04:00 | 121 | 11:00
UttaraNew | 139 | 04:00 | 129 | 12:00 | Zigatola | 139 | 04:00 | 120 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division