## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 13-01-2026 | [28 empty] | Date: | 13-01-2026 | [28 empty] | Date: | 13-01-2026 | [28 empty] | Date: | 13-01-2026 | [28 empty] | Date: | 13-01-2026 | [17 empty] | Date: | 13-01-2026
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [17 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 37 | 315 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 240 | 280 | 0 | 51 | 0 | 194 | 0 | 0 | 109 | 0 | 0 | 13 | 0 | 100 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 20 | 159 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 0 | 0 | 19 | 0 | 31 | 0 | 0 | 0 | 4345 | 879 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1098 | 0 | 0 | 0 | 1389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 130 | 180 | 0 | 0 | 540 | 0 | 4929 | 9274 | 96.77
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 37 | 315 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1088 | 0 | 0 | 0 | 240 | 280 | 0 | 51 | 0 | 194 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 92 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 30 | 158 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 4248 | 765 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1009 | 0 | 0 | 0 | 1149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 130 | 180 | 0 | 0 | 500 | 0 | 4446 | 8694 | 96.76
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 37 | 315 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1004 | 0 | 0 | 0 | 240 | 280 | 0 | 51 | 0 | 194 | 0 | 0 | 108 | 0 | 0 | 11 | 0 | 88 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 30 | 160 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 4199 | 691 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 987 | 0 | 0 | 0 | 1017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 130 | 180 | 0 | 0 | 500 | 0 | 4117 | 8316 | 96.76
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 37 | 315 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1002 | 0 | 0 | 0 | 240 | 280 | 0 | 51 | 0 | 196 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 82 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 30 | 142 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 4189 | 465 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 896 | 0 | 0 | 0 | 1027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 130 | 180 | 0 | 0 | 495 | 0 | 3794 | 7983 | 96.75
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 38 | 315 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1003 | 0 | 0 | 0 | 240 | 280 | 0 | 51 | 0 | 202 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 78 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 30 | 158 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 4014 | 225 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 915 | 0 | 0 | 0 | 1023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 130 | 220 | 0 | 0 | 494 | 0 | 3646 | 7660 | 96.75
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475 | 0 | 0 | 335 | 40 | 0 | 0 | 0 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 38 | 315 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1033 | 0 | 0 | 0 | 240 | 280 | 0 | 51 | 0 | 196 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 84 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 30 | 162 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 4121 | 225 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 878 | 0 | 0 | 0 | 1014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 130 | 220 | 0 | 0 | 495 | 0 | 3600 | 7721 | 96.74
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 515 | 0 | 0 | 335 | 106 | 0 | 0 | 0 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 40 | 315 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1162 | 0 | 0 | 0 | 235 | 280 | 0 | 51 | 0 | 198 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 86 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 30 | 163 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 4366 | 225 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 873 | 0 | 0 | 0 | 1033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 130 | 220 | 0 | 0 | 490 | 0 | 3671 | 8037 | 96.74
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 15 | 0 | 4 | 17 | 0 | 0 | 0 | 565 | 0 | 17 | 335 | 106 | 0 | 1 | 0 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 35 | 315 | 0 | 0 | 0 | 0 | 5 | 160 | 0 | 0 | 0 | 1175 | 1 | 5 | 0 | 235 | 280 | 0 | 51 | 0 | 199 | 0 | 0 | 109 | 8 | 0 | 11 | 0 | 90 | 0 | 2 | 0 | 320 | 0 | 0 | 0 | 30 | 163 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 19 | 16 | 49 | 0 | 0.8 | 0 | 4551.8 | 482 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1011 | 0 | 0 | 0 | 1227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0 | 0 | 0 | 0.65 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.01 | 0 | 288 | 130 | 220 | 0 | 0 | 547 | 0 | 4388.38 | 8940.18 | 96.73
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 95 | 0 | 54 | 102 | 0 | 0 | 0 | 560 | 0 | 40 | 335 | 105 | 0 | 6 | 7 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0.37 | 46 | 0 | 10 | 315 | 0 | 0 | 0 | 0 | 45 | 160 | 0 | 0 | 0 | 1184 | 3 | 55 | 0 | 235 | 280 | 0 | 51 | 0 | 194 | 0 | 0 | 110 | 36 | 0 | 11 | 0 | 96 | 0 | 17 | 0 | 320 | 0 | 0 | 0 | 30 | 163 | 2 | 17 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 19 | 56 | 33 | 0 | 9.08 | 2 | 5011.45 | 527 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 1112 | 0 | 0 | 0 | 1428.42 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 8.78 | 19 | 0 | 0 | 9.41 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99 | 0 | 0 | 70 | 5 | 70 | 0 | 0 | 0 | 0.9 | 29 | 0.1 | 0 | 286 | 130 | 220 | 0 | 0 | 585 | 0 | 5025.6 | 10037.05 | 96.73
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.5 | 0 | 6 | 0 | 145 | 0 | 55 | 142 | 0 | 0 | 0 | 510 | 0 | 55 | 335 | 80 | 0 | 14 | 44 | 23 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 1.11 | 46 | 0 | 6 | 315 | 0 | 0 | 0 | 0 | 82 | 160 | 0 | 0 | 0 | 1126 | 11 | 80 | 0 | 230 | 280 | 0 | 51 | 0 | 190 | 0 | 0 | 110 | 89 | 0 | 11 | 0 | 110 | 0 | 35 | 0 | 310 | 0 | 0 | 0 | 30 | 161 | 6 | 17 | 0 | 80 | 30 | 0 | 0 | 0 | 0 | 19 | 56 | 32 | 1 | 21.91 | 17 | 5210.52 | 659 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 1120 | 0 | 0 | 0 | 1430.59 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 23.84 | 45 | 0 | 0 | 28.12 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.56 | 0 | 0 | 70 | 14 | 70 | 0 | 0 | 0 | 2.5 | 74 | 0.23 | 0 | 272 | 130 | 180 | 0 | 0 | 570 | 0 | 5203.84 | 10414.36 | 96.72
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.1 | 0 | 33 | 0 | 95 | 0 | 55 | 141 | 0 | 0 | 0 | 385 | 0 | 35 | 335 | 80 | 0 | 22 | 62 | 22 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 2.41 | 46 | 0 | 7 | 315 | 0 | 0 | 0 | 0 | 62 | 160 | 0 | 0 | 0 | 1107 | 0 | 50 | 0 | 230 | 280 | 0 | 44 | 0 | 188 | 0 | 0 | 109 | 81 | 0 | 11 | 0 | 112 | 0 | 50 | 0 | 305 | 0 | 0 | 0 | 30 | 151 | 8 | 17 | 0 | 80 | 30 | 0 | 0 | 0 | 0 | 19 | 58 | 32 | 2 | 31.77 | 18 | 4974.28 | 760 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.31 | 1036 | 0 | 0 | 0 | 1311.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 73 | 0 | 0 | 42.54 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.84 | 0 | 0 | 35 | 22 | 34 | 0 | 0 | 0 | 4.1 | 115 | 0.36 | 0 | 269 | 130 | 180 | 0 | 0 | 545 | 0 | 5065.32 | 10039.6 | 96.72
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.2 | 0 | 43 | 0 | 95 | 0 | 55 | 147 | 0 | 0 | 0 | 345 | 0 | 35 | 270 | 80 | 0 | 27 | 17 | 21 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 2.91 | 46 | 0 | 6 | 315 | 0 | 0 | 0 | 0 | 61 | 160 | 0 | 0 | 0 | 1100 | 17 | 50 | 0 | 225 | 280 | 0 | 44 | 0 | 188 | 0 | 0 | 106 | 76 | 0 | 13 | 0 | 108 | 0 | 58 | 0 | 310 | 0 | 0 | 0 | 30 | 136 | 10 | 17 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 19 | 58 | 30 | 2 | 37.93 | 18 | 4841.04 | 905 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.58 | 942 | 0 | 0 | 0 | 1334.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.42 | 90 | 0 | 0 | 49.16 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.32 | 0 | 0 | 35 | 29 | 34 | 0 | 0 | 0 | 5.1 | 137 | 0.46 | 0 | 278 | 130 | 180 | 0 | 0 | 500 | 0 | 5180.95 | 10021.99 | 96.71
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 43 | 0 | 95 | 0 | 55 | 156 | 0 | 0 | 0 | 450 | 0 | 35 | 335 | 80 | 0 | 29 | 17 | 21 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3.12 | 46 | 0 | 7 | 315 | 0 | 0 | 0 | 0 | 65 | 161 | 0 | 0 | 0 | 1171 | 18 | 50 | 0 | 225 | 280 | 0 | 44 | 0 | 192 | 0 | 0 | 102 | 81 | 0 | 7 | 0 | 120 | 0 | 61 | 0 | 315 | 0 | 0 | 0 | 60 | 153 | 10 | 17 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 27 | 58 | 30 | 2 | 39.24 | 18 | 5178.36 | 905 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.05 | 960 | 0 | 0 | 0 | 1328.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.31 | 95 | 0 | 0 | 52.71 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.49 | 0 | 0 | 35 | 30 | 34 | 0 | 0 | 0 | 5.4 | 145 | 0.49 | 0 | 280 | 130 | 220 | 0 | 0 | 500 | 0 | 5280.18 | 10458.54 | 96.71
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 53 | 0 | 95 | 0 | 55 | 158 | 0 | 0 | 0 | 510 | 0 | 35 | 335 | 140 | 0 | 27 | 17 | 18 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 2.96 | 46 | 0 | 14 | 315 | 0 | 0 | 0 | 0 | 83 | 161 | 0 | 0 | 0 | 1217 | 17 | 73 | 0 | 225 | 280 | 0 | 44 | 0 | 195 | 0 | 0 | 102 | 89 | 0 | 13 | 0 | 126 | 0 | 60 | 0 | 320 | 0 | 0 | 0 | 60 | 162 | 10 | 17 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 23 | 58 | 29 | 2 | 39.28 | 19 | 5444.24 | 905 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.3 | 1108 | 0 | 0 | 0 | 1380.05 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 46.52 | 95 | 0 | 0 | 49.91 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.14 | 0 | 0 | 35 | 29 | 34 | 0 | 0 | 0 | 5.2 | 138 | 0.47 | 0 | 277 | 130 | 220 | 0 | 0 | 565 | 0 | 5562.59 | 11006.83 | 96.7
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.7 | 0 | 77 | 0 | 45 | 0 | 55 | 154 | 0 | 0 | 0 | 500 | 0 | 35 | 335 | 80 | 0 | 24 | 17 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 2.43 | 46 | 0 | 2 | 315 | 0 | 0 | 0 | 0 | 51 | 161 | 0 | 0 | 0 | 1158 | 15 | 40 | 0 | 225 | 280 | 0 | 51 | 0 | 196 | 0 | 0 | 101 | 111 | 6 | 13 | 0 | 120 | 0 | 51 | 0 | 325 | 0 | 0 | 0 | 58 | 143 | 8 | 17 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 28 | 58 | 29 | 2 | 33.16 | 19 | 5183.29 | 879 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.94 | 1111 | 0 | 0 | 0 | 1281 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 38.79 | 81 | 0 | 0 | 41.9 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.77 | 0 | 0 | 35 | 24 | 15 | 0 | 0 | 0 | 4.3 | 115 | 0.39 | 0 | 278 | 130 | 220 | 0 | 0 | 560 | 0 | 5337.09 | 10520.38 | 96.7
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.8 | 0 | 77 | 0 | 45 | 0 | 50 | 155 | 0 | 0 | 0 | 505 | 0 | 35 | 335 | 80 | 0 | 18 | 17 | 16 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 25 | 1.7 | 46 | 0 | 2 | 315 | 0 | 0 | 0 | 0 | 50 | 161 | 0 | 0 | 0 | 1176 | 11 | 20 | 0 | 225 | 280 | 0 | 51 | 0 | 188 | 0 | 0 | 50 | 112 | 9 | 13 | 0 | 114 | 0 | 38 | 0 | 315 | 0 | 0 | 0 | 59 | 143 | 5 | 17 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 19 | 58 | 29 | 1 | 25.44 | 20 | 5088.94 | 878 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.2 | 1090 | 0 | 0 | 0 | 1178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.89 | 61 | 0 | 0 | 27.35 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.61 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 2.9 | 80 | 0.27 | 0 | 240 | 130 | 220 | 0 | 0 | 520 | 0 | 4943.22 | 10032.16 | 96.69
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 77 | 0 | 45 | 0 | 46 | 159 | 0 | 0 | 0 | 540 | 0 | 35 | 335 | 140 | 0 | 10 | 17 | 22 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0.73 | 46 | 0 | 6 | 315 | 0 | 0 | 0 | 0 | 50 | 161 | 0 | 0 | 0 | 1162 | 6 | 20 | 0 | 225 | 280 | 0 | 51 | 0 | 182 | 0 | 0 | 50 | 117 | 9 | 13 | 0 | 108 | 0 | 17 | 0 | 320 | 0 | 0 | 30 | 59 | 158 | 2 | 17 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 19 | 58 | 29 | 0 | 10.58 | 18 | 5166.31 | 879 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.89 | 1008 | 0 | 0 | 0 | 1179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.24 | 28 | 0 | 0 | 10.94 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 1.6 | 38 | 0.13 | 0 | 200 | 130 | 220 | 0 | 0 | 500 | 0 | 4674.76 | 9841.07 | 96.69
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 77 | 0 | 145 | 0 | 55 | 160 | 0 | 0 | 0 | 545 | 0 | 35 | 335 | 140 | 0 | 2 | 20 | 22 | 13 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 25 | 0.09 | 46 | 2 | 8 | 318 | 0 | 0 | 2 | 0 | 49 | 161 | 0 | 0 | 0 | 1160 | 1 | 20 | 0 | 225 | 280 | 0 | 51 | 0 | 180 | 0 | 1 | 50 | 117 | 0 | 13 | 0 | 108 | 0 | 3 | 0 | 315 | 0 | 0 | 30 | 60 | 159 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 19 | 58 | 29 | 0 | 1.97 | 24 | 5284.06 | 878 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.35 | 1016 | 0 | 0 | 0 | 1313 | 0 | 0 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 2.25 | 6 | 0 | 0 | 2.19 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 0 | 35 | 2 | 34 | 0 | 0 | 0 | 0 | 5 | 0.03 | 0 | 199 | 130 | 220 | 0 | 0 | 500 | 10 | 4845.03 | 10129.09 | 96.69
18:00 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 15 | 77 | 0 | 275 | 0 | 48 | 156 | 0 | 0 | 0 | 520 | 0 | 55 | 335 | 140 | 0 | 0 | 70 | 22 | 13 | 0 | 0 | 4 | 49 | 0 | 0 | 0 | 34 | 23 | 3 | 50 | 38 | 0 | 46 | 18 | 12 | 318 | 5 | 0 | 20 | 0 | 61 | 161 | 0 | 0 | 0 | 1161 | 0 | 61 | 0 | 225 | 280 | 0 | 51 | 0 | 180 | 0 | 13 | 50 | 115 | 0 | 13 | 0 | 120 | 0 | 0 | 24 | 315 | 0 | 0 | 30 | 60 | 159 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 65 | 0 | 19 | 58 | 30 | 0 | 0 | 24 | 5808 | 879 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1030 | 0 | 0 | 0 | 1436 | 0 | 0 | 0 | 70 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 279 | 130 | 220 | 0 | 0 | 520 | 36 | 5307 | 11115 | 96.69
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.7 | 54 | 122 | 0 | 297 | 12 | 55 | 152 | 0 | 0 | 0 | 485 | 0 | 55 | 280 | 80 | 0 | 0 | 70 | 23 | 13 | 0 | 0 | 30 | 60 | 0 | 0 | 0 | 51 | 23 | 17 | 60 | 38 | 0 | 46 | 65 | 9 | 316 | 10 | 0 | 32 | 0 | 94 | 161 | 0 | 0 | 0 | 1153 | 0 | 140 | 0 | 225 | 280 | 0 | 51 | 0 | 194 | 0 | 16 | 50 | 139 | 0 | 13 | 0 | 112 | 0 | 0 | 16 | 310 | 0 | 0 | 30 | 60 | 145 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 16 | 19 | 58 | 31 | 0 | 0 | 24 | 6068.7 | 879 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 0 | 0 | 0 | 1446 | 0 | 0 | 0 | 70 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 275 | 130 | 220 | 0 | 0 | 545 | 54 | 5463 | 11531.7 | 96.68
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.7 | 0 | 133 | 0 | 297 | 0 | 55 | 155 | 0 | 0 | 0 | 540 | 0 | 55 | 335 | 81 | 0 | 0 | 52 | 23 | 13 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 51 | 23 | 0 | 24 | 38 | 0 | 46 | 65 | 12 | 315 | 0 | 0 | 19 | 0 | 104 | 161 | 0 | 0 | 0 | 1175 | 0 | 143 | 0 | 225 | 280 | 0 | 51 | 0 | 196 | 0 | 16 | 50 | 68 | 0 | 13 | 0 | 118 | 0 | 0 | 0 | 325 | 0 | 0 | 30 | 60 | 146 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 17 | 19 | 58 | 31 | 0 | 0 | 24 | 5978.7 | 757 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1104 | 0 | 0 | 0 | 1439 | 0 | 0 | 0 | 70 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 130 | 220 | 0 | 0 | 550 | 54 | 5347 | 11325.7
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.5 | 0 | 134 | 0 | 297 | 0 | 55 | 156 | 0 | 0 | 0 | 505 | 0 | 55 | 335 | 141 | 0 | 0 | 52 | 26 | 13 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 51 | 23 | 0 | 24 | 38 | 0 | 46 | 71 | 12 | 315 | 0 | 0 | 19 | 0 | 99 | 161 | 0 | 0 | 0 | 1160 | 0 | 142 | 0 | 225 | 280 | 0 | 51 | 0 | 195 | 0 | 17 | 50 | 68 | 0 | 13 | 0 | 116 | 0 | 0 | 0 | 315 | 0 | 0 | 30 | 60 | 154 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 17 | 19 | 58 | 31 | 0 | 0 | 24 | 5992.5 | 644 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1125 | 0 | 0 | 0 | 1450 | 0 | 0 | 0 | 70 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 130 | 220 | 0 | 0 | 550 | 54 | 5264 | 11256.5 | 96.68
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.5 | 0 | 149 | 0 | 297 | 0 | 55 | 157 | 0 | 0 | 0 | 525 | 0 | 55 | 335 | 142 | 0 | 0 | 35 | 25 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 46 | 0 | 17 | 316 | 0 | 0 | 0 | 0 | 99 | 161 | 0 | 0 | 0 | 1170 | 0 | 80 | 0 | 225 | 280 | 0 | 51 | 0 | 191 | 0 | 0 | 50 | 66 | 0 | 13 | 0 | 108 | 0 | 0 | 0 | 310 | 0 | 0 | 30 | 60 | 163 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 19 | 58 | 35 | 0 | 0 | 24 | 5676.5 | 878 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1128 | 0 | 0 | 0 | 1448.06 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 130 | 220 | 0 | 0 | 550 | 0 | 5239.06 | 10915.56 | 96.67
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 49.8 | 0 | 149 | 0 | 95 | 0 | 55 | 159 | 0 | 0 | 0 | 520 | 0 | 55 | 335 | 82 | 0 | 0 | 35 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 46 | 0 | 12 | 315 | 0 | 0 | 0 | 0 | 99 | 161 | 0 | 0 | 0 | 1148 | 0 | 20 | 0 | 225 | 280 | 0 | 51 | 0 | 181 | 0 | 0 | 80 | 68 | 0 | 13 | 0 | 108 | 0 | 0 | 0 | 315 | 0 | 0 | 30 | 60 | 162 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 19 | 58 | 35 | 0 | 0 | 24 | 5361.8 | 878 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1123 | 0 | 0 | 0 | 1443.86 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 130 | 220 | 0 | 0 | 555 | 0 | 5227.86 | 10589.66 | 96.67
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 45.2 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 505 | 0 | 0 | 335 | 82 | 0 | 0 | 0 | 19 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 46 | 0 | 16 | 315 | 0 | 0 | 0 | 0 | 34 | 160 | 0 | 0 | 0 | 1150 | 0 | 0 | 0 | 225 | 280 | 0 | 51 | 0 | 176 | 0 | 0 | 80 | 63 | 0 | 13 | 0 | 98 | 0 | 0 | 0 | 305 | 0 | 0 | 30 | 60 | 155 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 19 | 45 | 35 | 0 | 0 | 0 | 4760.2 | 878 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 0 | 0 | 0 | 1441.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 130 | 220 | 0 | 0 | 545 | 0 | 5066.76 | 9826.96 | 96.67
Total KWH | 0 | 25920 | 0 | 0 | 0 | 0 | 0 | 0 | 1328400 | 0 | 0 | 745560 | 84600 | 1233216 | 0 | 2150542 | 22379 | 823485 | 2515680 | 0 | 0 | 0 | 11519860 | 0 | 687278 | 7753303 | 2094000 | 0 | 179753 | 532800 | 423600 | 312840 | 0 | 0 | 141764 | 178145 | 0 | 0 | 76800 | 126155 | 80688 | 24764 | 144960 | 450240 | 17039 | 1098000 | 200730 | 479040 | 7650909.09 | 1673 | 0 | 82080 | 0 | 1225272 | 3755586 | 0 | 0 | 0 | 27098179 | 104220 | 1122400 | 0 | 5549500 | 7062100 | 0 | 1214726 | 0 | 4695000 | 0 | 60480 | 2123928 | 1490400 | 31080 | 295250 | 0 | 2492160 | 0 | 391627 | 42328 | 7662500 | 0 | 0 | 258000 | 1083000 | 3742936 | 62340 | 401904 | 0 | 1954560 | 717984 | 0 | 0 | 614200 | 39600 | 367200 | 950400 | 736320 | 11800 | 251130 | 312720 | 121107033.09 | 17289455 | 6484608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459360 | 24778200 | 0 | 0 | 0 | 30811204 | 0 | 0 | 0 | 255072 | 535776 | 0 | 0 | 0 | 0 | 288976 | 608710 | 0 | 0 | 315760 | 4443182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27840 | 0 | 0 | 740408 | 185823 | 866803 | 0 | 0 | 0 | 32297.52 | 879120 | 2950 | 54144 | 6153000 | 3116000 | 5315800 | 0 | 0 | 13018181.82 | 158400 | 116821070.34 | 237928103.43

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 14-01-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-01-2026 | during | 14-01-2026 | during | 14-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 412 | 412 | 100 | 100 | Under Maintenance
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 12 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 80 | 80 | 208.13 | 208.13 | 100 | 100 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 280 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 33 | 46.7 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 23 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 13 | 15.1 | 15.1 | 15.1 | 15.1 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 95 | 297 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 43 | 122 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 156 | 152 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 29 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 54 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 450 | 485 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 70 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1363 | 1744.7 | 5335.25 | 5307.25 | 2350.13 | 2340.13
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 17 | 0 | 17 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 32 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 | 46 | 46 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 161 | 161 | 150 | 150 | 150 | 150 | Plant availability less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 65 | 94 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 23 | 24 | 32 | 24 | 32 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 60 | 100 | 100 | 12 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 7 | 9 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.12 | 0 | 3 | 0 | 3 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 60 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 17 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 65 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 38 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 30 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 10 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1171 | 1153 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 315 | 316 | 315 | 315 | 355 | 355 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1811.12 | 2165 | 3066.86 | 3061.86 | 2621.5 | 2704.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 192 | 194 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 280 | 280 | 353.35 | 353.35 | 353.35 | 353.35 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 0 | 0 | Under maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 225 | 225 | 393 | 393 | 393 | 393 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 10 | 10 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 51 | 51 | 51 | 51 | 51 | Gas shortage
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 50 | 140 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 16 | 24 | 24 | 24 | 24 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 102 | 50 | 163 | 163 | 115 | 115 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 81 | 139 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 120 | 112 | 84 | 82 | 126 | 126 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 7 | 13 | 24.5 | 24.5 | 24.5 | 24.5 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 16 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 61 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1162 | 1236 | 2409.75 | 2352.75 | 2172.05 | 2117.05
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-01-2026 | during | 14-01-2026 | during | 14-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 30 | 31 | 157.5 | 157.5 | 50 | 50 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 58 | 60 | 60 | 60 | 60 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 27 | 19 | 20 | 20 | 20 | 20 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 39.24 | 0 | 39.32 | 0 | 39.32 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 24 | 22 | 22 | 18 | 18 | To be dispatched 18 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 16 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 174.24 | 148 | 355.42 | 314 | 243.92 | 202.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 30 | 0 | 0 | 42 | 42 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 60 | 60 | 0 | 0 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 153 | 145 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 83 | 83 | 83 | 83 | 83 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 100 | 100 | 100 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 668 | 775 | 802 | 802 | 734 | 734
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 905 | 879 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 280 | 410 | 410 | 369 | 369 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 74.05 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 960 | 1088 | 0 | 0 | 1148 | 1148 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2189.05 | 2247 | 2347 | 2272 | 2699.1 | 2624.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 26 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 130 | 130 | 136 | 136 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 500 | 545 | 622 | 622 | 575 | 575 | FGMO & #01 under maint.
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 280 | 275 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.49 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1130.49 | 1250 | 1546 | 1545 | 1346 | 1345
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 48.31 | 0 | 45 | 0 | 45 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 182 | 170 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.49 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1328.73 | 1446 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 52.71 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 95 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1711.24 | 1756 | 2718.78 | 2507.08 | 2225.38 | 2013.68
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 100 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.4 | 0 | 3.2 | 0 | 3.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 110 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 145 | 0 | 143.69 | 0 | 143.69 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 249.4 | 210 | 438.89 | 262 | 404.89 | 228
System Total |  |  |  |  | 28823.2 | 28382.248 | 10458.54 | 11531.7 | 19019.95 | 18423.94 | 14796.97 | 14308.96
Forecast Scenario (14-01-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9270 |  | 0 |  | 9270
|  |  |  | 1:00 | 8690 |  | 0 |  | 8690
|  |  |  | 2:00 | 8310 |  | 0 |  | 8310
|  |  |  | 3:00 | 7980 |  | 0 |  | 7980
|  |  |  | 4:00 | 7660 |  | 0 |  | 7660
|  |  |  | 5:00 | 7720 |  | 0 |  | 7720
|  |  |  | 6:00 | 8030 |  | 0 |  | 8030
|  |  |  | 7:00 | 8940 |  | 0 |  | 8940
|  |  |  | 8:00 | 10030 |  | 0 |  | 10030
|  |  |  | 9:00 | 10410 |  | 0 |  | 10410
|  |  |  | 10:00 | 10040 |  | 0 |  | 10040
|  |  |  | 11:00 | 10020 |  | 0 |  | 10020
|  |  |  | 12:00 | 10450 |  | 0 |  | 10450
|  |  |  | 13:00 | 11000 |  | 0 |  | 11000
|  |  |  | 14:00 | 10520 |  | 0 |  | 10520
|  |  |  | 15:00 | 10030 |  | 0 |  | 10030
|  |  |  | 16:00 | 9840 |  | 0 |  | 9840
|  |  |  | 17:00 | 10120 |  | 0 |  | 10120
|  |  |  | 18:00 | 11110 |  | 0 |  | 11110
|  |  |  | 18:30 | 11250 |  | 0 |  | 11250
|  |  |  | 19:00 | 11530 |  | 0 |  | 11530
|  |  |  | 19:30 | 11320 |  | 0 |  | 11320
|  |  |  | 20:00 | 11250 |  | 0 |  | 11250
|  |  |  | 21:00 | 10910 |  | 0 |  | 10910
|  |  |  | 22:00 | 10590 |  | 0 |  | 10590
|  |  |  | 23:00 | 9900 |  | 0 |  | 9900
Probable Maximum Temperature: |  |  | 23.10°C
Probable Maximum Demand at Day Peak: |  |  | 10450.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11530.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11530.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 234.35 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:26 hrs on 14-01-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 13-01-2026
Power Supply Scenario
| Day Peak Generation |  |  | 10458.54 | MW | 12:00 Hr. | Energy Generated |  |  | 237.9281 |  | MKWHr.
| Day Peak Demand |  |  | 10458.54 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11531.7 | MW | 19:00 Hr. | Energy Demand |  |  | 237.9281 |  | MKWHr.
| Evening Peak Demand |  |  | 11531.7 | MW | 19:00 Hr. | Maximum Temperature |  |  | 26.3 |  | °C
| Minimum Generation of the Day |  |  | 7660 | MW | 04:00 Hr. | Total Gas Supplied |  |  | 665.64 |  | MMCFD
| Maximum Generation of the Day |  |  | 11531.7 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.2998 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 23.432 | 0 | 8.8215 | 0 | 0 | 0.17975 | 0 | 0 | 32.4332 | Gas | 85.1381 | Gas | 307392057.72
| Chattogram Zone |  |  | 4.2346 | 34.7491 | 2.6565 | 0 | 1.098 | 0.12126 | 0 | 0.0768 | 42.9362 | Coal | 78.6985 | Coal | 513531126.8433
| Cumilla Zone |  |  | 20.9405 | 0 | 2.7467 | 0 | 0 | 0.39163 | 2.4922 | 0 | 26.571 | HFO | 18.5051 | HFO | 308933311.85
| Mymensingh Zone |  |  | 0.73632 | 0 | 1.6699 | 0 | 0 | 0.26293 | 0 | 0 | 2.6692 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 16.4351 | 0 | 0 | 0 | 0 | 0.06234 | 0 | 0 | 16.4974 | Hydro | 1.098 | Hydro | 109800
| Khulna Zone |  |  | 6.4846 | 24.7782 | 0 | 0 | 0 | 0.45936 | 17.2895 | 0 | 49.0116 | Solar | 3.8187 | Solar | 60028063.894
| Barishal Zone |  |  | 8.4318 | 19.1712 | 0.21254 | 0 | 0 | 0.00295 | 0 | 0 | 27.8185 | Import | 50.5928 | Import | 307775061.16
| Rajshahi Zone |  |  | 4.4432 | 0 | 0.79085 | 0 | 0 | 1.2413 | 30.8112 | 0 | 37.2865 | Wind | 0.0768 | Wind | 1129728
| Rangpur Zone |  |  | 0 | 0 | 1.6072 | 0 | 0 | 1.0972 | 0 | 0 | 2.7045
| Total |  |  | 85.1381 | 78.6985 | 18.5051 | 0 | 1.098 | 3.8187 | 50.5928 | 0.0768 | 237.9281
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 307392057.72 |  | Hydro | 109800
|  |  |  | Coal | 513531126.8433 |  | Solar | 60028063.894
|  |  |  | HFO | 308933311.85 |  | Import | 307775061.16
|  |  |  | HSD | 0 |  | Wind | 1129728
[5 empty] | Total: | 149,88,99,149 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 17.2895 | Peak Hr Flow | 879.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 38966090.92 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 30.8112 | Peak Hr Flow | 1446.00 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1818 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.4922 | Peak Hr Flow | 112.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2260 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.5928 | Peak Hr Flow | 2437.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4182
|  |  |  | Chattogram |  | 0 |  | 1177
|  |  |  | Cumilla |  | 0 |  | 910
|  |  |  | Mymensingh |  | 0 |  | 941
|  |  |  | Sylhet |  | 0 |  | 422
|  |  |  | Khulna |  | 0 |  | 1314
|  |  |  | Barishal |  | 0 |  | 321
|  |  |  | Rajshahi |  | 0 |  | 1058
|  |  |  | Rangpur |  | 0 |  | 739
|  |  |  | Total |  | 0 |  | 11064
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:18 | 15:25 | AKSML-Khulshi 132kV Ckt-1 Scheduled S/D from Khulshi 132/33kV end Due to Annual
maintenance (Deadline checking) and from AKS 132/33kV end Due to Khulshi to AKSPL 132 KV
Line Checking & Annual Maintenance.
| 08:18 | 21:25 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 LT Scheduled S/D Due to Annual maintenance
| 08:19 | 21:22 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 HT Scheduled S/D Due to Annual maintenance
| 08:27 | 17:29 | Sirajganj-Ullahpara 132KV Ckt-1 Scheduled S/D from Sirajganj 132/33kV end Due to Annual
Maintenance Work and from Ullahpara 132/33kV end Due to Annual Maintenance.
| 08:28 | 17:08 | Gopalganj-Madhumati 132kV Ckt-1 Scheduled S/D from Gopalganj 132/33kV end Due to Yearly
maintenance
| 08:39 |  | Siddhirganj 2*120 MW GT-1 was sync.
| 08:39 | 16:50 | Bagerhat-Goalpara 132 kV Ckt-1 Scheduled S/D from Bagerhat 132/33kV end Due to Annual
Maintenance
| 08:40 | 16:34 | Pabna 132/33kV S/S T-2 LT Scheduled S/D Due to Annual Maintenance
| 08:42 | 16:34 | Pabna 132/33kV S/S T-2 HT Scheduled S/D Due to Annual Maintenance
| 08:43 | 17:22 | Cox'sbazar-Dohazari 132 kV Ckt-1 Scheduled S/D from Coxsbazar 132/33kV end Due to Annual
maintenance and from Dohazari 132/33kV end Due to Annual Maintenance
| 08:45 | 18:41 | Fenchuganj-Fenchuganj 132 kV Ckt-4 Project Work S/D from Fenchuganj 230/132/33kV end Due
to OPCN Work
| 08:49 | 16:46 | Rangpur-Saidpur 132kV Ckt-2 Scheduled S/D from Saidpur 132/33kV end Due to Annual
maintenance
| 08:50 | 16:45 | Taraganj 132/33kV S/S Taraganj-Saidpur CKT-02 Scheduled S/D Due to Annual Maintenance
| 08:51 | 20:00 | Lalmonirhat-Rangpur 132 kV Ckt-2 Project Work S/D from Rangpur 132/33kV end Due to
Grantly piling
| 08:56 | 17:53 | Chattak-Sylhet 132 kV Ckt-2 Scheduled S/D from Chhatak 132/33kV end Due to Dead Line | [7 empty] | 6.0MW load
|  |  | Cheacking. and from Sylhet 132/33kV end Due to Deadline Checking Purpose. | [7 empty] | interrup. Chhatak
132/33kV end
| 08:58 | 15:51 | Khagrachari-Rangamati 132kV Ckt-1 Scheduled S/D from Rangamati 132/33kV end Due to For
Row maintenance
| 09:00 | 16:05 | Brahmanbaria-Narsinghdi 132 kV Ckt-1 Scheduled S/D from Brahmanbaria 132/33kV end. and
from Narshingdi 132/33kV end Due to For annual maintenance Work.
| 09:03 | 16:50 | Bagerhat-Goalpara 132 kV Ckt-1 Scheduled S/D from Goalpara 132/33kV end Due to Annual
maintenance
| 09:04 | 16:11 | Daudkandi-Sonargaon 132 kV Ckt-1 Scheduled S/D from Sonargaon 132/33kV end Due to Annual
maintenance and from Daudkandi 132/33kV end Due to Annual Maintenance
| 09:04 | 20:28 | Fenchuganj 230/132/33kV S/S TR-02 LT Scheduled S/D Due to 132 KV Bus-02 Maintenance
| 09:05 | 14:46 | Baroirhat-Feni 132 kV Ckt-2 Scheduled S/D from Baroirhat 132/33kV end.
| 09:07 | 15:51 | Dhamrai-Kaliakoir 132 kV Ckt-2 Scheduled S/D from Dhamrai 132/33kV end Due to Annual
maintenance and from Kaliakoir 400/230/132kV end Due to By NLDC
| 09:07 | 20:28 | Fenchuganj 230/132/33kV S/S TR-02 HT Scheduled S/D Due to 132kv Bus-02 Maintenance
| 09:12 | 16:05 | Khulna (S)-Rampal Ckt-2 Scheduled S/D from Khulna(S) 230/132kV end. and from Rampal
400/230kV end Due to Khulna ALDC Requirement.
|  | 09:19 | Aminbazar-Kaliakoir 230kV Ckt-1 is restored.
| 09:19 | 18:01 | Sylhet 132/33kV S/S Sylhet-90MW P/S Scheduled S/D Due to OPGW Change purpose.
| 09:19 | 20:21 | Fenchuganj 230/132/33kV S/S 132 KV Bus-2 Scheduled S/D Due to Annual Maintenance
| 09:20 | 14:45 | Baroirhat-Feni 132 kV Ckt-2 Scheduled S/D from Feni 132/33kV end Due to S/D taken for
AMS-2025-26
| 09:20 | 12:09 | Bhaluka 132/33kV S/S 02. Transformer- 02 LT Scheduled S/D Due to Annual maintenance
purpose.
| 09:20 |  | Muradnagar 132/33kV S/S 132KV Transformar-01 HT Scheduled S/D Due to Shutdown for 33 kv
switching station connection for pbs
| 09:21 | 12:08 | Bhaluka 132/33kV S/S 02. Transformer- 02 HT Scheduled S/D Due to Annual maintenance
purpose.
| 09:22 | 17:00 | Chandraghona-Madunaghat 132 kV Ckt-1 Scheduled S/D from Chandraghona 132/33kV end. and
from Madunaghat 132/33kV end Due to insulator disk change.
| 09:24 |  | Aminbazar 400/230/132kV S/S ATR-03 LT Scheduled S/D Due to Annual Maintenace
| 09:25 |  | Aminbazar 400/230/132kV S/S ATR-03 HT Scheduled S/D Due to Annual Maintenace
| 09:25 | 19:40 | Taraganj 132/33kV S/S Taraganj-Rangpur CKT-01 Scheduled S/D Due to Annual Maintenance
| 09:25 |  | Rangpur-Saidpur 132kV Ckt-1 Project Work S/D from Rangpur 132/33kV end.
| 09:25 |  | Bibiyana-Kaliakoir 400 kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to
Disc Cleaning
| 09:29 | 16:07 | Kabirpur 132/33kV S/S XFR, T-3 LT Scheduled S/D Due to Annual maintenance
| 09:30 | 16:06 | Kabirpur 132/33kV S/S XFR, T-3 HT Scheduled S/D Due to Annual maintenance
| 09:30 |  | Tangail 132/33kV S/S Kaliakair-2 Scheduled S/D Due to Annual Maintenance
| 09:32 | 14:52 | GPH 230/33kV S/S HATHAZARI Scheduled S/D Due to Annual maintenance
| 09:33 | 16:16 | Mirzapur 132/33kV S/S Mirzapur-Tangail-ckt-2B(E03) Scheduled S/D Due to By NLDC
| 09:33 | 16:16 | Mirzapur 132/33kV S/S Mirzapur-Tangail-ckt-2A(E04) Scheduled S/D Due to By NLDC
| 09:47 | 17:07 | Mirpur 132/33kV S/S Main Bus Scheduled S/D Due to Annual Maintenance work
| 09:47 | 17:07 | Mirpur 132/33kV S/S Main Bus Scheduled S/D Due to Annual Maintenance work
|  | 09:49 | Barishal 132/33kV S/S T-2 (415T) HT is restored.
| 09:50 | 15:51 | Meghnaghat 400/230kV S/S ATR-1 HT Scheduled S/D Due to For annual Maintenanace work
| 09:50 | 15:51 | Meghnaghat 400/230kV S/S ATR-1 LT Scheduled S/D Due to For annual maintenance work
|  | 09:50 | Barishal 132/33kV S/S T-2 (415T) LT is restored.
| 10:03 | 16:08 | Aggreko-keraniganj 132kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to
Deadline Checking
| 10:03 | 16:39 | Fenchuganj-Fenchuganj 132 kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
132kv Bus-02 Maintenance
| 10:06 |  | Aminbazar 400/230/132kV S/S 230 kv Bus 01 Scheduled S/D Due to Annual maintenance
| 10:14 | 13:55 | Kodda 132/33kV S/S RPCL 100 MW PS Scheduled S/D Due to Maintenance Work
| 10:28 | 13:31 | BIPTC S/S 20DF41 Scheduled S/D Due to Shutdown is taken for annual maintenance
|  | 11:00 | Haripur-Haripur (360MW) 230kV Ckt-1 is restored.
| 11:08 | 16:13 | AKSML-Baroaulia 132kV Ckt-1 Scheduled S/D from AKS 132/33kV end Due to Baraulia 132 KV
Line Shutdown due to Baraulia 132/33 KV Sub-station Annual Maintenance. and from
Baroaulia 132/33kV end Due to Maintenance for ground fault
|  | 11:58 | Madanganj-Munsiganj 132 kV Ckt-1 is restored.
| 12:00 |  | Day Peak Generation: 10455 MW.
| 12:09 | 16:56 | Madanganj-Munsiganj 132 kV Ckt-2 Scheduled S/D from Munshiganj 132/33kV end Due to Annual
maintenance and from Madanganj 132/33kV end Due to Annual Maintenance
| 14:14 | 14:55 | Sylhet (South) S/S Trafo-2 LT Project Work S/D Due to 132 kv Transformer -2 is taken | [7 empty] | 10.0MW load
|  |  | shutdown by simense due to replacement of 132 kv transformer -1. | [7 empty] | interrup.
| 14:14 |  | Sylhet (South) S/S Trafo-2 HT Project Work S/D Due to 132 kv Transformer -2 is taken | [7 empty] | 10.0MW load
|  |  | shutdown by simense due to replacement of 132 kv transformer -1. | [7 empty] | interrup.
| 14:19 | 17:10 | Bogura 400/230kV S/S ATR-02 LT Scheduled S/D Due to Oil leakage maintenance
| 14:20 | 17:09 | Bogura 400/230kV S/S ATR-02 HT Scheduled S/D
| 14:54 | 16:01 | Fenchuganj-Sreemangal 132kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Annual maintenance and from Sreemongol 132/33kV end Due to Order by NLDC.
|  | 14:55 | Sylhet (South) S/S Trafo-1 HT is restored.
|  | 15:55 | Aminbazar-Airport(Old) 230kV Ckt-1 is restored.
|  | 16:07 | Keranigonj 230/132/33kV S/S 132 kV Hasnabad Ckt. 1 is restored.
| 16:19 | 17:41 | Fenchuganj 230/132/33kV S/S AT-02 HT Scheduled S/D Due to 132kv Bus-02 Maintenance
| 16:21 | 17:41 | Fenchuganj 230/132/33kV S/S AT-02 LT Scheduled S/D Due to 132kv Bus-02 Annual Maintenance
| 16:48 | 18:13 | Fenchuganj-Fenchuganj 132 kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
132kv Bus-02 Maintenance
|  | 16:58 | Mymensingh RPCL -Mymensingh 132kV Ckt-1 is restored.
|  | 17:02 | Barishal-Bhola 230 kV Ckt-2 is restored.
| 17:02 | 19:52 | Niamatpur 132/33kV S/S 132 kV Naogaon ckt-2 Project Work S/D Due to as per instruction of
ALDC, Bogura
|  | 17:10 | Keraniganj-Sreenagar (T at Powerpac 100MW) 132kV Ckt-2 is restored.
|  | 17:18 | Khulna(C )-Noapara 132kV Ckt-2 is restored.
|  | 17:18 | Khulna(C )-Noapara 132kV Ckt-1 is restored.
| 17:35 |  | Sylhet 225MW CCPP GT was sync .
|  | 17:41 | Patuakhali-Payra 132kV Ckt-2 is restored.
|  | 17:41 | Patuakhali-Payra 132kV Ckt-2 is restored.
|  | 18:24 | Haripur 230/132kV S/S EGCB 412MW is restored.
|  | 18:58 | Chowmuhani-Ramganj 132 kV Ckt-2 is restored.
|  | 19:13 | Haripur 230/132kV S/S 132kV Main Bus Sec-1 is restored.
|  | 19:52 | Naogaon-Niyamatpur 132kV Ckt-1 is restored.
|  | 19:52 | Naogaon-Niyamatpur 132kV Ckt-1 is restored.
| 21:11 |  | Sirajgonj 225MW CCPP Unit-1, FGMO is ON with remarks:-
| 21:16 |  | Haripur 412 MW CCPP Synchronized with remarks:- GT
| 21:16 |  | Haripur EGCB 412 MW CCPP GT was sync. at 21:16 hrs.
| 02:36 |  | Haripur 412 MW CCPP Synchronized with remarks:- ST
| 04:00 |  | Minimum Generation: 7763 MW.
| 07:07 |  | Sylhet 132/33kV S/S Sylhet-90MW P/S Scheduled S/D Due to OPGW change
| 07:13 |  | Jashore 132/33kV S/S JH-2(L1) Project Work S/D Due to shutdown is taken by g2g project
| 07:13 |  | Jashore 132/33kV S/S JH-1(L2) Project Work S/D Due to shutdown is taken by g2g project
| 07:14 |  | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-1 Project Work S/D Due to Shutdown for
kaliganj grid line work
| 07:14 |  | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-2 Project Work S/D Due to Shutdown for
Kaliganj grid line work
| 07:26 |  | Rampura-Ullon-2 132kV Ckt-2 Scheduled S/D from Rampura 230/132kV end Due to Annual
Maintenance
| 07:28 |  | Moghbazar-Rampura 132kV Ckt-2 Scheduled S/D from Mogbazar 132/33kV end.
| 07:33 |  | Keraniganj-Sreenagar (T at Powerpac 100MW) 132kV Ckt-2 Tripped from Keranigonj
230/132/33kV end showing distance relay & 86.1 relays Due to zone-01 trip
| 07:48 |  | Bhulta-Ghorasal 230 kV Ckt-2 Scheduled S/D from Bhulta 400/230kV end.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 13-01-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 1328400 | Machine Problem
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 12 | 22379 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 80 | 2094000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 7753303 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 46.7 | 745560 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 823485 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 687278 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 423600 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 13 | 312840 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 297 | 2150542 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 122 | 1233216 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 25920 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 152 | 2515680 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 179753 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 84600 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 485 | 11519860 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 70 | 532800 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1744.7 | 32433216
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 104220 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 32 | 82080 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1098000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 161 | 3755586 | Plant availability less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 94 | 1225272 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 23 | 80688 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 126155 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 60 | 144960 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 9 | 479040 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 17039 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 60 | 178145 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 17 | 24764 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 65 | 200730 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 38 | 450240 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 30 | 141764 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 10 | 1673 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1153 | 27098179 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 76800 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 316 | 7650909.09 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4898.863 | 2165 | 42936244.09
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 194 | 4695000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 280 | 7062100 | STG Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Under maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 225 | 5549500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1214726 | Gas shortage
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 140 | 1122400 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 16 | 42328 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 2123928 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 139 | 1490400 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 112 | 2492160 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 295250 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 31080 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 16 | 60480 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 391627 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1236 | 26570979
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 31 | 736320 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 950400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 367200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 251130 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 312720 | To be dispatched 18 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 16 | 39600 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 148 | 2669170
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 62340 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 258000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1083000 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 145 | 3742936 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 717984 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1954560 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 614200 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 401904 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7662500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 775 | 16497424
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 879 | 17289455 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 280 | 6484608 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 459360 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1088 | 24778200 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2247 | 49011623
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 26 | 54144 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 3116000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 545 | 13018181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5315800 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 158400 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 275 | 6153000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2950 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1250 | 27818475.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 288976 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 170 | 4443182 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 0 | 0 | Under Maintenance
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 535776 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 70 | 255072 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 27840 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1446 | 30811204 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 315760 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 608710 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1756 | 37286520
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 100 | 866803 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 32297.52 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 110 | 740408 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 185823 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 879120 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 210 | 2704451.52
Eastern Grid Total |  |  |  |  | 17398.245 | 6068.7 | 121107033.09
Western Grid Total |  |  |  |  | 10984.003 | 5463 | 116821070.34
National Grid Total |  |  |  |  | 28382.248 | 11531.7 | 237928103.43
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 13-01-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7632.66 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3432.8 | MW
i) Dhaka area |  |  | 4182.26 |  | MW | i) Khulna area |  |  |  | 1314 | MW
ii) Chattogram area |  |  | 1177.4 |  | MW | ii) Barishal area |  |  |  | 321.4 | MW
iii) Cumilla area |  |  | 910 |  | MW | iii) Rajshahi area |  |  |  | 1058.4 | MW
iv) Mymensingh area |  |  | 941 |  | MW | iv) Rangpur area |  |  |  | 739 | MW
v) Sylhet area |  |  | 422 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11065.46 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 80 | 13:00 | 133 | Netrakona | 122 | 19:00
2 | AKSML | 122.1 | 13:00 | 68 | Hathazari | 62 | 18:00 | 134 | New | 57 | 12:00
3 | Aftabnagar | 28 | 13:00 | 69 | Hatirjheel | 22 | 15:00 | 135 | Niamatpur | 62 | 18:30
4 | Agargaon | 87 | 13:00 | 70 | Ishurdi | 53 | 18:30 | 136 | Noapara | 39 | 18:30
5 | Agrabad | 48 | 18:00 | 71 | Jaldhaka | 60 | 18:00 | 137 | PHP | 8 | 21:00
6 | Amnura | 46 | 13:00 | 72 | Jamalpur | 100 | 08:00 | 138 | Pabna | 80 | 18:00
7 | Ashuganj | 66 | 13:00 | 73 | Jashore | 104 | 13:00 | 139 | Palashbari | 84 | 18:30
8 | BSRM | 205 | 10:00 | 74 | Jhenaidah | 101 | 18:00 | 140 | Panchagarh | 39 | 18:00
9 | Bagerhat | 64 | 18:00 | 75 | Joydebpur | 115 | 18:00 | 141 | Patiya | 6 | 21:00
10 | Bajitpur | 64 | 19:00 | 76 | Joypurhat | 42 | 20:00 | 142 | Patuakhali | 38.9 | 20:00
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 17.5 | 14:00 | 143 | Payra | 28 | 19:00
12 | Bakulia | 66 | 18:00 | 78 | KSRM | 13 | 12:00 | 144 | Postogola | 37 | 18:00
13 | Banani | 32.8 | 13:00 | 79 | Kabirpur | 192 | 18:00 | 145 | Purbachal | 20 | 12:00
14 | Bangabhaban | 10 | 11:00 | 80 | Kachua | 60 | 18:00 | 146 | Purbasadipur | 119 | 18:30
15 | Barapukuria | 55 | 18:30 | 81 | Kallyanpur | 75 | 13:00 | 147 | Rahanpur | 20 | 08:00
16 | Barguna | 14 | 18:30 | 82 | Kalurghat | 32 | 11:00 | 148 | Rahim | 49 | 14:00
17 | Barishal | 91 | 13:00 | 83 | Kamrangirchar | 63 | 13:00 | 149 | Rajbari | 63 | 18:30
18 | Barishal-230 | 68 | 18:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 114 | 18:30
19 | Baroaulia | 59 | 11:00 | 85 | Kasba | 24 | 18:00 | 151 | Rajshahi | 78 | 18:00
20 | Baroirhat | 40 | 18:00 | 86 | Kazla | 100 | 13:00 | 152 | Rajshahi-230 | 84 | 13:00
21 | Bashundhara | 155 | 13:00 | 87 | Keranigonj | 66 | 13:00 | 153 | Ramganj | 68 | 20:00
22 | BashundharaCement | 9 | 14:00 | 88 | Khagrachori | 24 | 18:00 | 154 | Rampur | 27 | 13:00
23 | Beanibazar | 48 | 18:00 | 89 | Khulna | 51 | 13:00 | 155 | Rangamati | 13 | 19:00
24 | Benapole | 66 | 08:00 | 90 | Khulshi | 150 | 15:00 | 156 | Rangpur | 111 | 18:30
25 | Bhaluka | 146 | 18:00 | 91 | Kishoreganj | 96 | 18:30 | 157 | Ruppur | 2.6 | 09:00
26 | Bhandaria | 38 | 21:00 | 92 | Kodda | 259 | 18:00 | 158 | SSM | 9 | 23:00
27 | Bhangura | 25 | 18:00 | 93 | Kulaura | 27 | 18:00 | 159 | Saidpur | 92 | 09:00
28 | Bheramara(GK) | 44 | 18:00 | 94 | Kurigram | 50 | 18:00 | 160 | Satkhira | 99 | 08:00
29 | Bhulta | 204 | 12:00 | 95 | Kushtia | 121 | 13:00 | 161 | Satmasjid | 80 | 13:00
30 | Bog-Sherpur | 56 | 18:00 | 96 | Laksam | 21 | 20:00 | 162 | Savar | 189 | 12:00
31 | Bogura | 113 | 19:00 | 97 | Lakshmipur | 18 | 19:30 | 163 | SevenRings | 15.96 | 16:00
32 | Borhanuddin | 64 | 20:00 | 98 | Lalbag | 54 | 13:00 | 164 | ShahCement | 34 | 00:00
33 | Brahmanbaria | 94 | 19:30 | 99 | Lalmonirhat | 48 | 18:30 | 165 | Shahjadpur | 59 | 18:30
34 | Cantonment | 74 | 13:00 | 100 | MI_Cement | 16.4 | 00:00 | 166 | Shahjibazar | 93 | 18:00
35 | Chandina | 12 | 12:00 | 101 | Madanganj | 39 | 11:00 | 167 | Shahmirpur | 39 | 18:00
36 | Chandpur | 52 | 21:00 | 102 | Madaripur | 73 | 21:00 | 168 | Shariatpur | 57 | 20:00
37 | Chandraghona | 26 | 18:00 | 103 | Madartek | 50 | 13:00 | 169 | Sherpur | 124 | 19:00
38 | Chapai | 40 | 00:00 | 104 | Madunaghat | 37 | 18:00 | 170 | Shikalbaha | 22 | 17:00
39 | Charsaidpur | 38 | 16:00 | 105 | Magura | 51 | 18:30 | 171 | Shitalakhya | 59.5 | 15:00
40 | Chauddagram | 51 | 13:00 | 106 | Mahasthangarh | 54 | 09:00 | 172 | Sholosohor | 34 | 12:00
41 | Chhatak | 24 | 18:30 | 107 | Maijdee | 42 | 21:00 | 173 | Shyampur | 136 | 11:00
42 | Chowmuhani | 110 | 18:00 | 108 | Manikganj | 106 | 18:00 | 174 | Siddhirganj | 105 | 12:00
43 | Chuadanga | 78 | 18:00 | 109 | Maniknagar | 48 | 13:00 | 175 | Sirajganj | 84 | 19:00
44 | Coxsbazar | 107 | 18:00 | 110 | Matarbari | 46 | 18:30 | 176 | Sonargaon | 125 | 18:30
45 | Cumilla(N) | 99 | 08:00 | 111 | Matuail | 50 | 09:00 | 177 | Sreemongol | 58 | 18:00
46 | Cumilla(S) | 126 | 13:00 | 112 | Metrorail_Motijheel | 22 | 17:00 | 178 | Sreepur | 92 | 16:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 0 | 00:00 | 179 | Srinagar | 31 | 20:00
48 | Daudkandi | 94 | 00:00 | 114 | Millgate | 76 | 15:00 | 180 | Sunamganj | 44 | 18:30
49 | DhakaUniversity | 48 | 13:00 | 115 | Mirpur | 106 | 13:00 | 181 | Sylhet | 42 | 18:30
50 | Dhamrai | 98 | 17:00 | 116 | Mirsorai | 42 | 19:00 | 182 | Sylhet-132 | 83 | 14:00
51 | Dhanmondi | 67 | 13:00 | 117 | Mirzapur | 40 | 18:00 | 183 | TK | 18 | 18:00
52 | Dohazari | 67 | 18:00 | 118 | Mithapukur | 46 | 18:00 | 184 | Tangail | 126 | 08:00
53 | Faridpur | 118 | 19:00 | 119 | Modern | N/A | N/A | 185 | Taraganj | 16 | 08:00
54 | Fatullah | 96 | 12:00 | 120 | Mogbazar | 49.8 | 18:00 | 186 | Tasnim | 27 | 04:00
55 | Fenchuganj | 37 | 10:00 | 121 | Mongla | 37 | 14:00 | 187 | Thakurgaon | 77 | 18:30
56 | Feni | 80 | 18:00 | 122 | Motijheel | 32 | 13:00 | 188 | Tongi | 111 | 11:00
57 | GPH | 31 | 13:00 | 123 | Muktagacha | 29 | 18:00 | 189 | Ullahpara | 27 | 18:30
58 | Ghatail | 64 | 07:00 | 124 | Munshiganj | 72 | 09:00 | 190 | Ullon | 40 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 0 | 00:00 | 191 | Uttara | 56 | 18:00
60 | Ghorashal-230 | 89 | 18:30 | 126 | Mymensingh | 147 | 18:00 | 192 | UttaraNew | 26 | 19:30
61 | Goalpara | 30 | 13:00 | 127 | Naogaon | 95 | 08:00 | 193 | Zigatola | 71 | 14:00
62 | Gollamari | 84 | 13:00 | 128 | Narail | 44 | 18:30
63 | Gopalganj | 84 | 18:30 | 129 | Narinda | 62 | 13:00
64 | Gulshan | 72 | 13:00 | 130 | Narshingdi | 142 | 19:00
65 | Halishahar | 57.5 | 16:00 | 131 | Natore | 109 | 18:30
66 | HaripurSBU | 120 | 17:00 | 132 | Nawabganj | 31.6 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 13-01-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 9274 | 0 |  | 9274
1:00 | 8694 | 0 |  | 8694
2:00 | 8316 | 0 |  | 8316
3:00 | 7983 | 0 |  | 7983
4:00 | 7660 | 0 |  | 7660
5:00 | 7721 | 0 |  | 7721
6:00 | 8037 | 0 |  | 8037
7:00 | 8940.18 | 0 |  | 8940.18
8:00 | 10037.05 | 0 |  | 10037.05
9:00 | 10414.36 | 0 |  | 10414.36
10:00 | 10039.6 | 0 |  | 10039.6
11:00 | 10021.99 | 0 |  | 10021.99
12:00 | 10458.54 | 0 |  | 10458.54
13:00 | 11006.83 | 0 |  | 11006.83
14:00 | 10520.38 | 0 |  | 10520.38
15:00 | 10032.16 | 0 |  | 10032.16
16:00 | 9841.07 | 0 |  | 9841.07
17:00 | 10129.09 | 0 |  | 10129.09
18:00 | 11115 | 0 |  | 11115
19:00 | 11531.7 | 0 |  | 11531.7
19:30 | 11325.7 | 0 |  | 11325.7
20:00 | 11256.5 | 0 |  | 11256.5
21:00 | 10915.56 | 0 |  | 10915.56
22:00 | 10589.66 | 0 |  | 10589.66
23:00 | 9826.96 | 0 |  | 9826.96
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 13-01-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4345 | 4929 | 9274 | DAILY GENERATION CURVE
00:30 | 4296.5 | 4687.5 | 8984
01:00 | 4248 | 4446 | 8694 | 13-01-2026
01:30 | 4223.5 | 4281.5 | 8505
02:00 | 4199 | 4117 | 8316
02:30 | 4194 | 3955.5 | 8149.5
03:00 | 4189 | 3794 | 7983
03:30 | 4101.5 | 3720 | 7821.5
04:00 | 4014 | 3646 | 7660
04:30 | 4067.5 | 3623 | 7690.5
05:00 | 4121 | 3600 | 7721
05:30 | 4243.5 | 3635.5 | 7879
06:00 | 4366 | 3671 | 8037
06:30 | 4458.9 | 4029.69 | 8488.59
07:00 | 4551.8 | 4388.38 | 8940.18
07:30 | 4781.625 | 4706.99 | 9488.615
08:00 | 5011.45 | 5025.6 | 10037.05
08:30 | 5110.985 | 5114.72 | 10225.705
09:00 | 5210.52 | 5203.84 | 10414.36
09:30 | 5092.4 | 5134.58 | 10226.98
10:00 | 4974.28 | 5065.32 | 10039.6
10:30 | 4907.66 | 5123.135 | 10030.795
11:00 | 4841.04 | 5180.95 | 10021.99
11:30 | 5009.7 | 5230.565 | 10240.265
12:00 | 5178.36 | 5280.18 | 10458.54
12:30 | 5311.3 | 5421.385 | 10732.685
13:00 | 5444.24 | 5562.59 | 11006.83
13:30 | 5313.765 | 5449.84 | 10763.605
14:00 | 5183.29 | 5337.09 | 10520.38
14:30 | 5136.115 | 5140.155 | 10276.27
15:00 | 5088.94 | 4943.22 | 10032.16
15:30 | 5127.625 | 4808.99 | 9936.615
16:00 | 5166.31 | 4674.76 | 9841.07
16:30 | 5225.185 | 4759.895 | 9985.08
17:00 | 5284.06 | 4845.03 | 10129.09
17:30 | 5546.03 | 5076.015 | 10622.045
18:00 | 5808 | 5307 | 11115
18:30 | 5938.35 | 5385 | 11323.35
19:00 | 6068.7 | 5463 | 11531.7
19:30 | 5978.7 | 5347 | 11325.7
20:00 | 5992.5 | 5264 | 11256.5
20:30 | 5834.5 | 5251.53 | 11086.03 |  | Executive Engineer
21:00 | 5676.5 | 5239.06 | 10915.56 |  | Network Operation Division
21:30 | 5519.15 | 5233.46 | 10752.61
22:00 | 5361.8 | 5227.86 | 10589.66
22:30 | 5061 | 5147.31 | 10208.31
23:00 | 4760.2 | 5066.76 | 9826.96

## En-Curve
QF-LDC-12
Date | 13-01-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2206 | 1224 | 879 | 0 | 100 | 1389 | 46 | 3389 | 0 | 0 | 19 | 0 | 0 | 22 | 0 | DAILY ENERGY CURVE
00:30 | 2210 | 1226.5 | 822 | 0 | 96 | 1269 | 46 | 3289 | 0 | 0 | 9.5 | 0 | 0 | 16 | 0 | 13-01-2026
01:00 | 2214 | 1229 | 765 | 0 | 92 | 1149 | 46 | 3189 | 0 | 0 | 0 | 0 | 0 | 10 | 0
01:30 | 2237 | 1230 | 728 | 0 | 90 | 1083 | 46 | 3083.5 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | Energy Generated | 237.9281 |  | MKWHr
02:00 | 2260 | 1231 | 691 | 0 | 88 | 1017 | 46 | 2978 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2257 | 1224.5 | 578 | 0 | 85 | 1022 | 46 | 2929.5 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | Total Energy Requirement | 237.9281 |  | MKWHr
03:00 | 2254 | 1218 | 465 | 0 | 82 | 1027 | 46 | 2881 | 0 | 0 | 0 | 0 | 0 | 10 | 0
03:30 | 2120.5 | 1286.5 | 345 | 0 | 80 | 1025 | 46 | 2905 | 0 | 0 | 0 | 0 | 0 | 13.5 | 0
04:00 | 1987 | 1355 | 225 | 0 | 78 | 1023 | 46 | 2929 | 0 | 0 | 0 | 0 | 0 | 17 | 0
04:30 | 2006.5 | 1374.5 | 225 | 0 | 81 | 1018.5 | 46 | 2923.5 | 0 | 0 | 0 | 0 | 0 | 15.5 | 0
05:00 | 2026 | 1394 | 225 | 0 | 84 | 1014 | 46 | 2918 | 0 | 0 | 0 | 0 | 0 | 14 | 0
05:30 | 2066.5 | 1418 | 225 | 0 | 85 | 1023.5 | 46 | 3007 | 0 | 0 | 0 | 0 | 0 | 8 | 0
06:00 | 2107 | 1442 | 225 | 0 | 86 | 1033 | 46 | 3096 | 0 | 0 | 0 | 0 | 0 | 2 | 0
06:30 | 2124.5 | 1467.5 | 353.5 | 0 | 88 | 1130 | 46 | 3216 | 4.59 | 0 | 57.5 | 0 | 0 | 1 | 0
07:00 | 2142 | 1493 | 482 | 0 | 90 | 1227 | 46 | 3336 | 9.18 | 0 | 115 | 0 | 0 | 0 | 0
07:30 | 2138.5 | 1483 | 504.5 | 0 | 93 | 1327.71 | 46 | 3409 | 67.905 | 3.5 | 415.5 | 0 | 0 | 0 | 0
08:00 | 2135 | 1473 | 527 | 0 | 96 | 1428.42 | 46 | 3482 | 126.63 | 7 | 716 | 0 | 0 | 0 | 0
08:30 | 2091 | 1418 | 593 | 0 | 103 | 1429.505 | 46 | 3442.5 | 221.95 | 25.5 | 855.25 | 0 | 0 | 0 | 0
09:00 | 2047 | 1363 | 659 | 0 | 110 | 1430.59 | 46 | 3403 | 317.27 | 44 | 994.5 | 0 | 0 | 0 | 0
09:30 | 2031 | 1289.5 | 709.5 | 0 | 111 | 1370.88 | 46 | 3337.5 | 393.8 | 53 | 884.8 | 0 | 0 | 0 | 0
10:00 | 2015 | 1216 | 760 | 0 | 112 | 1311.17 | 46 | 3272 | 470.33 | 62 | 775.1 | 0 | 0 | 0 | 0
10:30 | 1978 | 1192.5 | 832.5 | 0 | 110 | 1323.04 | 46 | 3203.5 | 527.605 | 39.5 | 778.15 | 0 | 0 | 0 | 0
11:00 | 1941 | 1169 | 905 | 0 | 108 | 1334.91 | 46 | 3135 | 584.88 | 17 | 781.2 | 0 | 0 | 0 | 0
11:30 | 1999 | 1250 | 905 | 0 | 114 | 1331.82 | 46 | 3180.5 | 601.345 | 17 | 795.6 | 0 | 0 | 0 | 0
12:00 | 2057 | 1331 | 905 | 0 | 120 | 1328.73 | 46 | 3226 | 617.81 | 17 | 810 | 0 | 0 | 0 | 0
12:30 | 2094.5 | 1372.5 | 905 | 0 | 123 | 1354.39 | 46 | 3354 | 607.295 | 17 | 859 | 0 | 0 | 0 | 0
13:00 | 2132 | 1414 | 905 | 0 | 126 | 1380.05 | 46 | 3482 | 596.78 | 17 | 908 | 0 | 0 | 0 | 0
13:30 | 2089.5 | 1390.5 | 892 | 0 | 123 | 1330.525 | 46 | 3452 | 551.73 | 17 | 871.35 | 0 | 0 | 0 | 0
14:00 | 2047 | 1367 | 879 | 0 | 120 | 1281 | 46 | 3422 | 506.68 | 17 | 834.7 | 0 | 0 | 0 | 0
14:30 | 2018.5 | 1372.5 | 878.5 | 0 | 117 | 1229.5 | 46 | 3381.5 | 435.52 | 17 | 779.25 | 0 | 0 | 1 | 0
15:00 | 1990 | 1378 | 878 | 0 | 114 | 1178 | 46 | 3341 | 364.36 | 17 | 723.8 | 0 | 0 | 2 | 0
15:30 | 2038 | 1410.5 | 878.5 | 0 | 111 | 1178.5 | 46 | 3263 | 267.215 | 17 | 725.9 | 0 | 0 | 1 | 0
16:00 | 2086 | 1443 | 879 | 0 | 108 | 1179 | 46 | 3185 | 170.07 | 17 | 728 | 0 | 0 | 0 | 0
16:30 | 2086 | 1444.5 | 878.5 | 0 | 108 | 1246 | 46 | 3189 | 100.58 | 18.5 | 868 | 0 | 0 | 0 | 0
17:00 | 2086 | 1446 | 878 | 0 | 108 | 1313 | 46 | 3193 | 31.09 | 20 | 1008 | 0 | 0 | 0 | 0
17:30 | 2132 | 1435.5 | 878.5 | 0 | 114 | 1374.5 | 46 | 3250.5 | 15.545 | 89.5 | 1286 | 0 | 0 | 0 | 0
18:00 | 2178 | 1425 | 879 | 0 | 120 | 1436 | 46 | 3308 | 0 | 159 | 1564 | 0 | 0 | 0 | 0
18:30 | 2139.5 | 1397 | 879 | 0 | 116 | 1441 | 46 | 3342.5 | 0 | 159.5 | 1802.85 | 0 | 0 | 0 | 0
19:00 | 2101 | 1369 | 879 | 0 | 112 | 1446 | 46 | 3377 | 0 | 160 | 2041.7 | 0 | 0 | 0 | 0
19:30 | 2166 | 1443 | 757 | 0 | 118 | 1439 | 46 | 3425 | 0 | 126 | 1805.7 | 0 | 0 | 0 | 0
20:00 | 2229 | 1409 | 644 | 0 | 116 | 1450 | 46 | 3427 | 0 | 126 | 1809.5 | 0 | 0 | 0 | 0
20:30 | 2216 | 1423 | 761 | 0 | 112 | 1449.03 | 46 | 3436 | 0 | 80.5 | 1562.5 | 0 | 0 | 0 | 0
21:00 | 2203 | 1437 | 878 | 0 | 108 | 1448.06 | 46 | 3445 | 0 | 35 | 1315.5 | 0 | 0 | 0 | 0
21:30 | 2189.5 | 1432 | 878 | 0 | 108 | 1445.96 | 46 | 3431.5 | 0 | 35 | 1186.65 | 0 | 0 | 0 | 0
22:00 | 2176 | 1427 | 878 | 0 | 108 | 1443.86 | 46 | 3418 | 0 | 35 | 1057.8 | 0 | 0 | 0 | 0
22:30 | 2176.5 | 1409 | 878 | 0 | 103 | 1442.81 | 46 | 3405 | 0 | 17.5 | 730.5 | 0 | 0 | 0 | 0
23:00 | 2177 | 1391 | 878 | 0 | 98 | 1441.76 | 46 | 3392 | 0 | 0 | 403.2 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 13-01-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 423 | 05:00 | 413 | 8:00 | Meghnaghat | 427 | 05:00 | 401 | 11:00
Ashuganj | 410 | 03:000 | 386 | 12:00 | Payra | 426 | 05:00 | 414 | 13:00
Bhulta | 403 | 03:00 | 378 | 12:00 | Rahanpur | 417 | 05:00 | 398 | 12:00
Bibiana | 421 | 21:00 | 404 | 12:00 | Rampal | 417 | 04:00 | 401 | 13:00
BIPTC | 407 | 04:00 | 389 | 11:00
Bogura | 413 | 05:00 | 387 | 13:00
Gopalganj | 422 | 05:00 | 402 | 13:00
Kaliakoir | 419 | 05:00 | 391 | 12:00
Korerhat | 425 | 05:00 | 406 | 12:00
Madunaghat | 416 | 04:00 | 403 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 245 | 05:00 | 228 | 12:00 | Kachua | 242 | 04:00 | 232 | 12:00
AKSML | 241 | 20:00 | 229 | 13:00 | Kaliakoir | 245 | 20:00 | 229 | 12:00
Aminbazar | 245 | 05:00 | 228 | 12:00 | Keranigonj | 243 | 04:00 | 226 | 12:00
Ashuganj | 239 | 05:00 | 225 | 12:00 | Khulna(S) | 245 | 04:00 | 229 | 13:00
Ashuganj-400 | 239 | 05:00 | 225 | 12:00 | Korerhat | 242 | 05:00 | 230 | 12:00
Baghabari | 238 | 11:00 | 225 | 12:00 | Madunaghat | 240 | 19:00 | 230 | 18:00
Barapukuria | 228 | 05:00 | 212 | 12:00 | Madunaghat-400 | 239 | 19:00 | 230 | 13:00
Barapukuria-230 | 228 | 05:00 | 212 | 12:00 | Maniknagar | 240 | 03:00 | 223 | 12:00
Barishal | 239 | 05:00 | 228 | 12:00 | Meghnaghat | 243 | 20:00 | 232 | 13:00
Bheramara | 241 | 05:00 | 222 | 12:00 | Meghnaghat-400 | 242 | 05:00 | 224 | 11:00
Bhulta | 243 | 05:00 | 225 | 12:00 | Mirsorai | 241 | 05:00 | 232 | 12:00
Bibiana | 242 | 05:00 | 229 | 12:00 | Rajshahi | 240 | 05:00 | 221 | 12:00
BIPTC | 242 | 05:00 | 222 | 12:00 | Rampal | 241 | 02:00 | 229 | 13:00
Bogura | 242 | 05:00 | 227 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 241 | 05:00 | 226 | 12:00 | Rampura | 242 | 05:00 | 225 | 12:00
Borhanuddin | 268 | 07:00 | 236 | 10:00 | Shikalbaha | 239 | 18:30 | 229 | 12:00
BSRM | 242 | 05:00 | 231 | 12:00 | Shyampur | 242 | 05:00 | 225 | 12:00
Cumilla(N) | 239 | 03:00 | 225 | 12:00 | Siddhirganj | 239 | 20:00 | 225 | 13:00
Faridpur | 239 | 05:00 | 225 | 12:00 | Sirajgonj | 244 | 02:00 | 230 | 12:00
Fenchuganj | 243 | 04:00 | 232 | 13:00 | Sreepur | 237 | 05:00 | 218 | 12:00
Feni | 242 | 05:00 | 230 | 12:00 | Tongi | 244 | 19:30 | 227 | 11:00
Ghorashal | 245 | 01:00 | 230 | 11:00
Ghorashal-230 | 234 | 05:00 | 211 | 12:00
Gopalganj | 237 | 05:00 | 225 | 12:00
GPH | 239 | 18:30 | 231 | 13:00
Haripur | 242 | 05:00 | 226 | 12:00
Hasnabad | 240 | 06:00 | 226 | 12:00
Hathazari | 237 | 19:00 | 229 | 11:00
Ishurdi | 243 | 05:00 | 225 | 12:00
Jhenaidah | 243 | 05:00 | 221 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 03:00 | 125 | 12:00 | Laksam | 139 | 04:00 | 133 | 12:00 | UttaraNew | 139 | 19:30 | 130 | 12:00
Agargaon | 139 | 04:00 | 129 | 12:00 | Lakshmipur | 136 | 05:00 | 129 | 12:00 | Zigatola | 137 | 04:00 | 125 | 13:00
Agrabad | 139 | 18:30 | 133 | 12:00 | Lalbag | 135 | 02:00 | 127 | 13:00
AKS | 135 | 03:00 | 132 | 11:00 | Lalmonirhat | 130 | 04:00 | 122 | 12:00
Aminbazar | 140 | 19:30 | 130 | 18:00 | Madanganj | 136 | 04:00 | 133 | 00:00
Amnura | 138 | 04:00 | 128 | 12:00 | Madaripur | 142 | 02:00 | 136 | 10:00
Ashuganj | 139 | 05:00 | 133 | 12:00 | Madartek | 134 | 19:00 | 124 | 12:00
Bagerhat | 135 | 04:00 | 120 | 13:00 | Madunaghat | 140 | 18:30 | 134 | 11:00
Bajitpur | 136 | 04:00 | 127 | 13:00 | Magura | 137 | 05:00 | 124 | 12:00
Bakerganj | 140 | 19:00 | 135 | 11:00 | Mahasthangarh | 136 | 04:00 | 128 | 12:00
Bakulia | 140 | 18:30 | 133 | 13:00 | Maijdee | 135 | 04:00 | 129 | 12:00
Banani | 135 | 04:00 | 124 | 12:00 | Manikganj | 130 | 19:00 | 122 | 12:00
Bangabhaban | 139 | 04:00 | 123 | 12:00 | Maniknagar | 140 | 05:00 | 123 | 13:00
Barapukuria | 138 | 05:00 | 128 | 07:00 | Matarbari | 129 | 00:00 | 126 | 22:00
Barguna | 140 | 18:30 | 135 | 12:00 | Matuail | 139 | 04:00 | 128.5 | 12:00
Barishal | 140 | 04:00 | 133 | 12:00 | Metrorail_Motijheel | 140 | 05:00 | 123 | 13:00
Barishal-230 | 140 | 02:00 | 133 | 12:00 | Metrorail_Uttara | 139 | 22:00 | 130 | 12:00
Baroaulia | 139 | 18:30 | 133 | 12:00 | Millgate | 135 | 03:00 | 124 | 12:00
Baroirhat | 137 | 04:00 | 130 | 13:00 | Mirpur | 140 | 21:00 | 130 | 12:00
Bashundhara | 134 | 03:00 | 123 | 13:00 | Mirzapur | 136 | 04:00 | 129 | 07:00
BashundharaCement | 136 | 06:00 | 133 | 00:00 | Mithapukur | 136 | 05:00 | 127 | 12:00
Beanibazar | 135 | 03:00 | 123 | 12:00 | MI_Cement | 137 | 04:00 | 125.5 | 13:00
Benapole | 135 | 01:00 | 116 | 12:00 | Modern | N/A | N/A | N/A | N/A
Bhaluka | 134 | 03:00 | 122 | 12:00 | Mogbazar | 136 | 03:00 | 125 | 12:00
Bhandaria | 139 | 03:00 | 131 | 13:00 | Mongla | 135 | 04:00 | 120 | 12:00
Bhangura | 141 | 05:00 | 129 | 12:00 | Motijheel | 139 | 04:00 | 123 | 12:00
Bheramara | 142 | 05:00 | 133 | 12:00 | Muktagacha | 134 | 10:00 | 123 | 18:00
Bheramara(GK) | 141 | 02:00 | 134 | 12:00 | Munshiganj | 137 | 03:00 | 127 | 12:00
Bhulta | 130 | 23:00 | 122 | 12:00 | Muradnagar | 139 | 04:00 | 129 | 13:00
Bog-Sherpur | 138 | 05:00 | 129 | 12:00 | Mymensingh | 134 | 10:00 | 118 | 07:00
Bogura | 137 | 06:00 | 130 | 12:00 | Naogaon | 135 | 01:00 | 125 | 12:00
Bogura-230 | 138 | 04:00 | 129 | 12:00 | Narail | 139 | 03:00 | 123 | 10:00
Brahmanbaria | 131 | 03:00 | 123 | 12:00 | Narinda | 140 | 05:00 | 123 | 13:00
Cantonment | 139 | 04:00 | 128 | 12:00 | Narshingdi | 136 | 05:00 | 116 | 12:00
Chandina | 140 | 04:00 | 132 | 12:00 | Natore | 137 | 06:00 | 129 | 12:00
Chandpur | 140 | 18:00 | 135 | 12:00 | Nawabganj | 138 | 04:00 | 126 | 12:00
Chandraghona | 140 | 19:00 | 134 | 12:00 | Netrakona | 129 | 06:00 | 113 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 139 | 05:00 | 131 | 13:00 | New | 135 | 04:00 | 125 | 12:00
Charsaidpur | 137 | 05:00 | 127 | 13:00 | Niamatpur | 140 | 03:00 | 130 | 13:00
Chauddagram | 137 | 04:00 | 130 | 12:00 | Noapara | 137 | 03:00 | 117 | 12:00
Chhatak | 133 | 02:00 | 120 | 12:00 | Pabna | 140 | 05:00 | 131 | 12:00
Chowmuhani | 134 | 05:00 | 129 | 12:00 | Palashbari | 133 | 20:00 | 125 | 12:00
Chuadanga | 139 | 03:00 | 123 | 12:00 | Panchagarh | 140 | 19:30 | 128 | 12:00
Coxsbazar | 130 | 02:00 | 124 | 15:00 | Patiya | 138 | 00:00 | 134 | 12:00
Cumilla(N) | 139 | 02:00 | 131 | 12:00 | Patuakhali | 138 | 19:00 | 133 | 13:00
Cumilla(S) | 140 | 04:00 | 125 | 09:00 | Payra | 139 | 02:00 | 136 | 08:00
Daganbhuiyan | 136 | 05:00 | 129 | 12:00 | PHP | 136 | 04:00 | 129 | 13:00
Daudkandi | 136 | 02:00 | 127 | 12:00 | Postogola | 138 | 04:00 | 127 | 12:00
DhakaUniversity | 133 | 01:00 | 124 | 12:00 | Purbachal | 135 | 02:00 | 124 | 12:00
Dhamrai | 139 | 22:00 | 127 | 12:00 | Purbasadipur | 138 | 05:00 | 129 | 00:00
Dhanmondi | 140 | 04:00 | 129 | 12:00 | Rahanpur | 139 | 03:00 | 133 | 12:00
Dohazari | 136 | 19:00 | 131 | 12:00 | Rahanpur-400 | 140 | 03:00 | 133 | 12:00
Faridpur | 138 | 04:00 | 132 | 11:00 | Rahim | 138 | 06:00 | 127 | 13:00
Fatullah | 140 | 04:00 | 125 | 12:00 | Rajbari | 139 | 05:00 | 130 | 13:00
Fenchuganj | 138 | 04:00 | 131 | 13:00 | Rajendrapur | 134 | 05:00 | 122 | 12:00
Feni | 135 | 05:00 | 128 | 12:00 | Rajshahi | 137 | 01:00 | 128 | 12:00
Feni-230 | 136 | 05:00 | 129 | 12:00 | Rajshahi-230 | 137 | 04:00 | 127 | 12:00
Ghatail | 131 | 10:00 | 120 | 07:00 | Ramganj | 137 | 18:30 | 133 | 11:00
Ghorashal | 134 | 01:00 | 125 | 10:00 | Rampur | 138 | 18:30 | 133 | 12:00
Goalpara | 139 | 05:00 | 128 | 12:00 | Rampura | 135 | 05:00 | 124 | 12:00
Gollamari | 138 | 05:00 | 128 | 12:00 | Rangamati | 139 | 18:30 | 133 | 12:00
Gopalganj | 141 | 04:00 | 131 | 13:00 | Rangpur | 135 | 04:00 | 125 | 13:00
Gopalganj-400 | 144 | 05:00 | 136 | 12:00 | Ruppur | 140 | 04:00 | 133 | 12:00
Gulshan | 133 | 05:00 | 124 | 12:00 | Saidpur | 135 | 05:00 | 125 | 12:00
Halishahar | 141 | 19:00 | 134 | 12:00 | Satkhira | 136 | 04:00 | 124 | 13:00
Haripur | 139 | 05:00 | 128 | 12:00 | Satmasjid | 139 | 04:00 | 128 | 13:00
HaripurSBU | 139 | 05:00 | 128 | 12:00 | Savar | 140 | 20:00 | 131 | 12:00
Hasnabad | 137 | 03:00 | 127 | 12:00 | SevenRings | 134 | 04:00 | 123 | 13:00
Hathazari | 139 | 18:30 | 133 | 11:00 | ShahCement | 137 | 06:00 | 127 | 13:00
Hatirjheel | 135 | 05:00 | 124 | 12:00 | Shahjadpur | 140 | 01:00 | 135 | 10:00
Ishurdi | 143 | 05:00 | 134 | 12:00 | Shahjibazar | 134 | 04:00 | 125 | 12:00
Jaldhaka | 132 | 05:00 | 124 | 12:00 | Shahmirpur | 140 | 19:00 | 132 | 08:00
Jamalpur | 134 | 10:00 | 118 | 07:00 | Shariatpur | 142 | 04:00 | 134 | 12:00
Jashore | 138 | 01:00 | 117 | 12:00 | Sherpur | 133 | 10:00 | 116 | 00:00
Jhenaidah | 141 | 05:00 | 118 | 13:00 | Shikalbaha | 129 | 19:00 | 123 | 12:00
Jhenaidah-230 | 138 | 05:00 | 124 | 13:00 | Shikalbaha-230 | 141 | 18:30 | 135 | 09:00
Joydebpur | 130 | 03:00 | 122 | 12:00 | Shitalakhya | 137.5 | 05:00 | 125.5 | 13:00
Joypurhat | 135 | 03:00 | 125 | 12:00 | Sholosohor | 140 | 19:00 | 134 | 12:00
Juldah | 140 | 19:00 | 134 | 12:00 | Shyampur | 136 | 08:00 | 133 | 10:00
Kabirpur | 139 | 21:00 | 123 | 12:00 | Shyampur-230 | 140 | 05:00 | 130 | 12:00
Kachua | 140 | 04:00 | 134 | 12:00 | Siddhirganj | 138 | 02:00 | 128 | 12:00
Kaliakoir | 141 | 04:00 | 130 | 12:00 | Sirajganj | 139 | 05:00 | 127 | 12:00
Kallyanpur | 139 | 19:00 | 132 | 12:00 | Sonargaon | 137 | 05:00 | 127 | 12:00
Kalurghat | 140 | 18:30 | 135 | 11:00 | Sreemongol | 134 | 04:00 | 126 | 12:00
Kamrangirchar | 137 | 03:00 | 125 | 12:00 | Sreepur | 136 | 05:00 | 124 | 12:00
Kaptai | 140 | 5:00 | 136 | 13:00 | Srinagar | 136 | 04:00 | 126 | 12:00
Kasba | 139 | 04:00 | 128 | 13:00 | SSM | 142 | 18:00 | 138 | 12:00
Kazla | 138 | 04:00 | 122 | 13:00 | Sunamganj | 132 | 03:00 | 118 | 12:00
Keranigonj | 138 | 05:00 | 126 | 12:00 | Sylhet | 135 | 04:00 | 122 | 13:00
Khagrachori | 138 | 18:30 | 131 | 13:00 | Sylhet-132 | 133 | 01:00 | 123 | 12:00
Khulna | 136 | 04:00 | 126 | 13:00 | Tangail | 131 | 04:00 | 124 | 07:00
Khulna(S) | 138 | 04:00 | 128 | 13:00 | Taraganj | 134 | 05:00 | 126 | 12:00
Khulshi | 137 | 18:30 | 132 | 11:00 | Tasnim | 137 | 05:00 | 127 | 12:00
Kishoreganj | 134 | 04:00 | 126 | 12:00 | Thakurgaon | 140 | 19:30 | 128 | 12:00
Kodda | 138 | 22:00 | 124 | 12:00 | TK | 139 | 06:00 | 134 | 12:00
KSRM | 139 | 19:30 | 134 | 12:00 | Tongi | 136 | 19:30 | 127 | 11:00
Kulaura | 137 | 03:00 | 130 | 12:00 | Ullahpara | 139 | 06:00 | 129 | 12:00
Kurigram | 132 | 19:30 | 124 | 11:00 | Ullon | 134 | 02:00 | 125 | 12:00
Kushtia | 136 | 01:00 | 126 | 07:00 | Uttara | 134 | 04:00 | 124 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division