## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 18-01-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-01-2026 | during | 18-01-2026 | during | 18-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 376 | 336 | 412 | 412 | 392 | 392 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 240 | 240 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 16.6 | 48.8 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23.4 | 25 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 7 | 15.1 | 15.1 | 15.1 | 15.1 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 50 | 278 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 156 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 26 | 0 | 27 | 0 | 27 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 365 | 380 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 125 | 52 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1361 | 1816.8 | 5349.45 | 5322.45 | 2579.13 | 2552.13
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 39 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 | 46 | 46 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 203 | 187 | 150 | 150 | 150 | 150 | Plant availability less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 95 | 105 | 105 | 95 | 95 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 16 | 0 | 0 | 24 | 32 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 51 | 51 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 90 | 100 | 100 | 12 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 8 | 17 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.14 | 0 | 2.97 | 0 | 2.97 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 100 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 93 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 50 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1110 | 1162 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 12 | 0 | 12 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 355 | 355 | 355 | 355 | 355 | 355 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1789.14 | 2267 | 3083.83 | 3081.86 | 2622.47 | 2716.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 201 | 196 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 300 | 305 | 353.35 | 353.35 | 353.35 | 353.35 | STG Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 230 | 220 | 393 | 393 | 250 | 250 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 10 | 10 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 25 | 51 | 51 | 51 | 51 | 51 | Gas shortage
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 12 | 142 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 14 | 24 | 24 | 24 | 24 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 80 | 163 | 163 | 115 | 115 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 128 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 108 | 114 | 84 | 82 | 128 | 128 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 13 | 24.5 | 24.5 | 24.5 | 24.5 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 9 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 16 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 59 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1044 | 1288 | 2409.75 | 2352.75 | 1836.05 | 1781.05
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-01-2026 | during | 18-01-2026 | during | 18-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 67 | 72 | 157.5 | 157.5 | 50 | 50 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 19 | 20 | 20 | 60 | 60 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 59 | 60 | 60 | 20 | 20 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 39.78 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 24 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 186.78 | 174 | 358.1 | 314 | 250.6 | 206.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 42 | 42 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 52 | 52 | 60 | 60 | 0 | 0 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 162 | 154 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 80 | 83 | 83 | 83 | 83 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 99 | 100 | 100 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 330 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 826 | 789 | 844 | 844 | 734 | 734
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 878 | 905 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 339 | 343 | 410 | 410 | 369 | 369 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 72 | 0 | 72 | 0 | 72 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 830 | 1098 | 0 | 0 | 1148 | 1148 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2119 | 2346 | 2344 | 2272 | 2696.1 | 2624.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 130 | 130 | 136 | 136 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 330 | 560 | 622 | 622 | 575 | 575 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 51 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 256 | 307 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.46 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 936.46 | 1268 | 1546 | 1545 | 1346 | 1345
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 46.14 | 0 | 44.45 | 0 | 44.45 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 197 | 187 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.48 | 0 | 5 | 0 | 5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 770 | 764.19 | 748 | 748 | 748 | 748 | U#1 Under AOH
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 51.14 | 0 | 60 | 0 | 60 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 98 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1166.76 | 1134.19 | 2021.65 | 1812.2 | 1535.25 | 1325.8
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 56 | 56 | 57 | 57 | 58 | 58 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 107 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.4 | 0 | 4.8 | 0 | 4.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 142 | 0 | 136.85 | 0 | 136.85 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 233.4 | 278 | 490.65 | 319 | 457.65 | 286
System Total |  |  |  |  | 28823.2 | 28382.248 | 9662.54 | 11360.99 | 18447.43 | 17863.26 | 14057.25 | 13571.08
Forecast Scenario (18-01-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9190 |  | 0 |  | 9190
|  |  |  | 1:00 | 8560 |  | 0 |  | 8560
|  |  |  | 2:00 | 8020 |  | 0 |  | 8020
|  |  |  | 3:00 | 7751 |  | 0 |  | 7751
|  |  |  | 4:00 | 7582 |  | 0 |  | 7582
|  |  |  | 5:00 | 7521 |  | 0 |  | 7521
|  |  |  | 6:00 | 7920 |  | 0 |  | 7920
|  |  |  | 7:00 | 8727 |  | 0 |  | 8727
|  |  |  | 8:00 | 9846 |  | 0 |  | 9846
|  |  |  | 9:00 | 10397 |  | 0 |  | 10397
|  |  |  | 10:00 | 9982 |  | 0 |  | 9982
|  |  |  | 11:00 | 9970 |  | 0 |  | 9970
|  |  |  | 12:00 | 10487 |  | 0 |  | 10487
|  |  |  | 13:00 | 11073 |  | 0 |  | 11073
|  |  |  | 14:00 | 10573 |  | 0 |  | 10573
|  |  |  | 15:00 | 10080 |  | 0 |  | 10080
|  |  |  | 16:00 | 9717 |  | 0 |  | 9717
|  |  |  | 17:00 | 9815 |  | 0 |  | 9815
|  |  |  | 18:00 | 11126 |  | 0 |  | 11126
|  |  |  | 18:30 | 11200 |  | 0 |  | 11200
|  |  |  | 19:00 | 11379 |  | 0 |  | 11379
|  |  |  | 19:30 | 11073 |  | 0 |  | 11073
|  |  |  | 20:00 | 11032 |  | 0 |  | 11032
|  |  |  | 21:00 | 10953 |  | 0 |  | 10953
|  |  |  | 22:00 | 10354 |  | 0 |  | 10354
|  |  |  | 23:00 | 10048 |  | 0 |  | 10048
Probable Maximum Temperature: |  |  | 24.70°C
Probable Maximum Demand at Day Peak: |  |  | 10487.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11379.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11379.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 232.103 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:13 hrs on 18-01-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 17-01-2026 | [28 empty] | Date: | 17-01-2026 | [28 empty] | Date: | 17-01-2026 | [28 empty] | Date: | 17-01-2026 | [28 empty] | Date: | 17-01-2026 | [17 empty] | Date: | 17-01-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 10 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 30 | 155 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1117 | 0 | 0 | 0 | 215 | 300 | 0 | 51 | 0 | 170 | 0 | 0 | 80 | 0 | 0 | 13 | 0 | 82 | 0 | 0 | 0 | 310 | 0 | 0 | 42 | 52 | 154 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 4307 | 879 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1102 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 130 | 220 | 0 | 0 | 525 | 0 | 4529 | 8836 | 96.41
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 10 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 32 | 155 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1002 | 0 | 0 | 0 | 230 | 300 | 0 | 51 | 0 | 170 | 0 | 0 | 80 | 0 | 0 | 12 | 0 | 90 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 52 | 144 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 59 | 0 | 107 | 0 | 0 | 0 | 4268 | 878 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 928 | 0 | 0 | 0 | 633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 130 | 220 | 0 | 0 | 450 | 0 | 4105 | 8373 | 96.41
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 8 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 32 | 158 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 910 | 0 | 0 | 0 | 230 | 300 | 0 | 51 | 0 | 170 | 0 | 0 | 80 | 0 | 0 | 12 | 0 | 78 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 52 | 137 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 4094 | 879 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802 | 0 | 0 | 0 | 479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 130 | 220 | 0 | 0 | 350 | 0 | 3676 | 7770 | 96.4
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 8 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 40 | 158 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 850 | 0 | 0 | 0 | 230 | 300 | 0 | 5 | 0 | 170 | 0 | 0 | 80 | 0 | 0 | 12 | 0 | 82 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 52 | 142 | 0 | 17 | 0 | 31 | 20 | 0 | 0 | 100 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 3982 | 879 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 807 | 0 | 0 | 0 | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 130 | 220 | 0 | 0 | 300 | 0 | 3582 | 7564 | 96.4
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 8 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 37 | 158 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 718 | 0 | 0 | 0 | 230 | 300 | 0 | 5 | 0 | 170 | 0 | 0 | 80 | 0 | 0 | 12 | 0 | 72 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 52 | 145 | 0 | 17 | 0 | 31 | 20 | 0 | 0 | 100 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 3791 | 879 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 806 | 0 | 0 | 0 | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 130 | 180 | 0 | 0 | 300 | 0 | 3495 | 7286 | 96.4
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 8 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 40 | 158 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 711 | 0 | 0 | 0 | 280 | 300 | 0 | 5 | 0 | 170 | 0 | 0 | 80 | 0 | 0 | 12 | 0 | 80 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 52 | 141 | 0 | 17 | 0 | 31 | 20 | 0 | 0 | 100 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 3830 | 879 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802 | 0 | 0 | 0 | 439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 130 | 180 | 0 | 0 | 300 | 0 | 3483 | 7313 | 96.39
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 8 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 40 | 158 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 800 | 0 | 0 | 0 | 340 | 300 | 0 | 8 | 0 | 170 | 0 | 0 | 80 | 0 | 0 | 12 | 0 | 84 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 52 | 149 | 0 | 17 | 0 | 65 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 4066 | 879 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 815 | 0 | 0 | 0 | 434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 130 | 220 | 0 | 0 | 310 | 0 | 3591 | 7657 | 96.39
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 240 | 0 | 0 | 1 | 0 | 8 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0.03 | 46 | 0 | 36 | 158 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1088 | 1 | 0 | 0 | 330 | 300 | 0 | 25 | 0 | 170 | 0 | 0 | 80 | 0 | 0 | 12 | 0 | 86 | 0 | 2 | 0 | 325 | 0 | 0 | 42 | 52 | 163 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 107 | 0 | 0.78 | 0 | 4468.81 | 878 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.55 | 866 | 0 | 0 | 0 | 530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53 | 0 | 0 | 0 | 0.41 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.01 | 0 | 294 | 130 | 220 | 0 | 0 | 383 | 0 | 3914.55 | 8383.36 | 96.39
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 30 | 0 | 22 | 0 | 45 | 0 | 23 | 33 | 0 | 0 | 0 | 420 | 0 | 20 | 240 | 0 | 0 | 5 | 17 | 4 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 10 | 0.44 | 46 | 0 | 17 | 155 | 0 | 0 | 0 | 0 | 37 | 160 | 0 | 0 | 0 | 1160 | 4 | 6 | 0 | 230 | 300 | 0 | 51 | 0 | 170 | 0 | 0 | 80 | 0 | 0 | 12 | 0 | 94 | 0 | 14 | 0 | 320 | 0 | 0 | 42 | 52 | 163 | 2 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 47 | 19 | 106 | 0 | 9.44 | 0 | 4774.88 | 878 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1096 | 0 | 0 | 0 | 694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.84 | 17 | 0 | 0 | 8.48 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85 | 0 | 57 | 35 | 5 | 34 | 0 | 0 | 0 | 0.9 | 29 | 0.09 | 0 | 275 | 130 | 220 | 0 | 0 | 458 | 0 | 4565.16 | 9340.04 | 96.38
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 31.4 | 0 | 52 | 5 | 45 | 0 | 35 | 35 | 0 | 0 | 0 | 365 | 0 | 35 | 240 | 0 | 0 | 13 | 108 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 25 | 1.73 | 46 | 0 | 8 | 155 | 0 | 0 | 0 | 0 | 64 | 160 | 0 | 0 | 0 | 1043 | 11 | 30 | 0 | 230 | 300 | 0 | 51 | 0 | 170 | 0 | 0 | 80 | 28 | 0 | 5 | 0 | 90 | 0 | 33 | 0 | 305 | 0 | 0 | 42 | 52 | 145 | 4 | 17 | 0 | 80 | 20 | 0 | 0 | 100 | 0 | 57 | 19 | 107 | 1 | 23.23 | 0 | 4825.36 | 878 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 1068 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5 | 45 | 0 | 0 | 24.57 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.23 | 0 | 56 | 35 | 13 | 34 | 0 | 0 | 0 | 2.9 | 71 | 0.21 | 0 | 198 | 115 | 180 | 0 | 0 | 500 | 0 | 4627.41 | 9452.77 | 96.38
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 20.6 | 0 | 110 | 15 | 45 | 0 | 35 | 35 | 0 | 0 | 0 | 305 | 0 | 35 | 240 | 0 | 0 | 19 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 2.55 | 46 | 0 | 7 | 210 | 0 | 0 | 0 | 0 | 34 | 160 | 0 | 0 | 0 | 850 | 15 | 12 | 0 | 275 | 300 | 0 | 10 | 0 | 140 | 0 | 0 | 80 | 17 | 0 | 5 | 0 | 90 | 0 | 47 | 0 | 305 | 0 | 0 | 42 | 32 | 134 | 7 | 17 | 0 | 45 | 20 | 0 | 0 | 100 | 0 | 57 | 19 | 69 | 1 | 32.87 | 0 | 4509.02 | 878 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 919 | 0 | 0 | 0 | 762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.72 | 70 | 0 | 0 | 38.48 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.37 | 0 | 56 | 0 | 21 | 0 | 0 | 0 | 0 | 3.8 | 108 | 0.32 | 0 | 159 | 115 | 180 | 0 | 0 | 400 | 0 | 4222.69 | 8731.71 | 96.38
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 16.6 | 0 | 34 | 0 | 45 | 0 | 35 | 35 | 0 | 0 | 0 | 340 | 0 | 35 | 240 | 0 | 0 | 24 | 125 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 3.01 | 46 | 0 | 8 | 355 | 0 | 0 | 0 | 0 | 33 | 184 | 0 | 0 | 0 | 860 | 17 | 12 | 0 | 250 | 300 | 0 | 10 | 0 | 199 | 0 | 0 | 80 | 16 | 0 | 12 | 0 | 96 | 0 | 55 | 0 | 320 | 0 | 0 | 42 | 32 | 155 | 9 | 17 | 0 | 45 | 20 | 0 | 0 | 100 | 0 | 47 | 19 | 67 | 1 | 38.96 | 0 | 4771.57 | 879 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 799 | 0 | 0 | 0 | 768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.35 | 87 | 0 | 0 | 48.14 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.17 | 0 | 56 | 0 | 29 | 0 | 0 | 0 | 0 | 5 | 135 | 0.42 | 0 | 171 | 130 | 220 | 0 | 0 | 300 | 0 | 4227.08 | 8998.65 | 96.37
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 16.6 | 0 | 34 | 0 | 50 | 0 | 35 | 35 | 0 | 0 | 0 | 365 | 0 | 35 | 240 | 0 | 0 | 26 | 125 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 3.14 | 46 | 0 | 8 | 355 | 0 | 0 | 0 | 0 | 34 | 203 | 0 | 0 | 0 | 1110 | 18 | 12 | 0 | 230 | 300 | 0 | 25 | 0 | 201 | 0 | 0 | 80 | 17 | 0 | 12 | 0 | 108 | 0 | 59 | 0 | 330 | 0 | 0 | 42 | 52 | 162 | 10 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 59 | 19 | 67 | 2 | 39.78 | 0 | 5206.92 | 878 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 830 | 0 | 0 | 0 | 770 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.14 | 98 | 0 | 0 | 51.14 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.48 | 0 | 56 | 0 | 30 | 0 | 0 | 0 | 0 | 5.4 | 142 | 0.46 | 0 | 256 | 130 | 220 | 0 | 0 | 330 | 0 | 4455.62 | 9662.54 | 96.37
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 40 | 0 | 50 | 0 | 145 | 0 | 55 | 35 | 0 | 0 | 0 | 380 | 0 | 35 | 240 | 0 | 0 | 25 | 142 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 3.05 | 46 | 0 | 9 | 355 | 0 | 0 | 0 | 0 | 60 | 203 | 0 | 0 | 0 | 1160 | 17 | 55 | 0 | 230 | 300 | 0 | 44 | 0 | 170 | 0 | 0 | 81 | 38 | 0 | 12 | 0 | 110 | 0 | 61 | 0 | 315 | 0 | 0 | 42 | 52 | 155 | 10 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 60 | 19 | 69 | 2 | 38.79 | 0 | 5505.84 | 879 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 1042 | 0 | 0 | 0 | 763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.96 | 88 | 0 | 0 | 48.52 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.49 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1 | 137 | 0.44 | 0 | 278 | 130 | 220 | 0 | 0 | 430 | 0 | 4728.51 | 10234.35 | 96.37
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 47.2 | 0 | 68 | 0 | 95 | 0 | 55 | 35 | 0 | 0 | 0 | 365 | 0 | 17 | 240 | 0 | 0 | 22 | 142 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 12 | 2.58 | 46 | 0 | 11 | 355 | 0 | 0 | 0 | 0 | 38 | 187 | 0 | 0 | 0 | 1135 | 15 | 20 | 0 | 230 | 300 | 0 | 44 | 0 | 170 | 0 | 0 | 81 | 17 | 0 | 12 | 0 | 102 | 0 | 54 | 0 | 310 | 0 | 0 | 42 | 52 | 144 | 8 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 59 | 19 | 69 | 1 | 31.87 | 0 | 5242.65 | 878 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 1092 | 0 | 0 | 0 | 765.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.2 | 77 | 0 | 0 | 34.87 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.46 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6 | 115 | 0.36 | 0 | 226 | 130 | 180 | 0 | 0 | 460 | 0 | 4608.37 | 9851.02 | 96.37
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 15.8 | 0 | 32 | 0 | 45 | 0 | 48 | 35 | 0 | 0 | 0 | 345 | 0 | 17 | 240 | 0 | 0 | 16 | 142 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 12 | 0 | 46 | 0 | 2 | 355 | 0 | 0 | 0 | 0 | 27 | 187 | 0 | 0 | 0 | 1100 | 11 | 20 | 0 | 230 | 300 | 0 | 44 | 0 | 170 | 0 | 0 | 80 | 17 | 0 | 12 | 0 | 106 | 0 | 40 | 0 | 310 | 0 | 0 | 42 | 52 | 157 | 6 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 59 | 19 | 71 | 1 | 25.74 | 0 | 5051.54 | 879 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 1013 | 0 | 0 | 0 | 770.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.59 | 54 | 0 | 0 | 28.84 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.66 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 88 | 0.24 | 0 | 189 | 130 | 220 | 0 | 0 | 438 | 0 | 4469.98 | 9521.52 | 96.36
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 15.8 | 0 | 17 | 0 | 45 | 0 | 17 | 34 | 0 | 0 | 0 | 355 | 0 | 17 | 240 | 0 | 0 | 8 | 142 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0.92 | 46 | 0 | 6 | 355 | 0 | 0 | 0 | 0 | 17 | 187 | 0 | 0 | 0 | 1103 | 6 | 20 | 0 | 230 | 300 | 0 | 44 | 0 | 170 | 0 | 0 | 80 | 17 | 0 | 12 | 0 | 108 | 0 | 20 | 0 | 310 | 0 | 0 | 42 | 52 | 159 | 2 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 67 | 19 | 71 | 0 | 11.27 | 0 | 4976.99 | 888 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 858 | 0 | 0 | 0 | 764.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.75 | 26 | 0 | 0 | 11.9 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.13 | 0 | 56 | 0 | 9 | 0 | 0 | 0 | 0 | 1.6 | 43 | 0.12 | 0 | 175 | 115 | 220 | 0 | 0 | 350 | 0 | 4089.82 | 9066.81 | 96.36
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 40 | 4 | 31 | 0 | 95 | 0 | 17 | 78 | 0 | 0 | 0 | 395 | 0 | 17 | 240 | 0 | 0 | 2 | 142 | 24 | 0 | 0 | 0 | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 38 | 0.11 | 46 | 8 | 12 | 355 | 0 | 0 | 5 | 0 | 38 | 187 | 0 | 0 | 0 | 1135 | 1 | 50 | 0 | 230 | 300 | 0 | 44 | 0 | 170 | 0 | 6 | 80 | 33 | 6 | 12 | 0 | 104 | 0 | 3 | 0 | 325 | 0 | 0 | 42 | 52 | 156 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 99 | 0 | 59 | 19 | 71 | 0 | 2.2 | 0 | 5311.31 | 893 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 854 | 0 | 0 | 0 | 767.31 | 0 | 0 | 0 | 25 | 15 | 0 | 0 | 0 | 0 | 2.19 | 6 | 0 | 0 | 2.52 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | 56 | 35 | 2 | 34 | 0 | 0 | 0 | 0.3 | 8 | 0.02 | 0 | 188 | 115 | 180 | 0 | 0 | 364 | 0 | 4065.56 | 9376.87 | 96.36
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 50.5 | 21 | 146 | 0 | 175 | 0 | 40 | 162 | 0 | 0 | 0 | 370 | 0 | 55 | 240 | 0 | 0 | 0 | 142 | 25 | 0 | 0 | 0 | 17 | 45 | 0 | 0 | 0 | 0 | 16 | 17 | 50 | 50 | 0 | 46 | 19 | 16 | 355 | 0 | 0 | 20 | 0 | 97 | 187 | 0 | 0 | 0 | 1175 | 0 | 115 | 0 | 245 | 325 | 0 | 51 | 0 | 202 | 0 | 16 | 80 | 102 | 9 | 12 | 0 | 114 | 0 | 0 | 9 | 320 | 0 | 0 | 42 | 52 | 152 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 99 | 5 | 59 | 18 | 71 | 0 | 0 | 0 | 6124.5 | 905 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995 | 0 | 0 | 0 | 765.67 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 110 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283 | 130 | 220 | 0 | 0 | 420 | 10 | 4611.67 | 10736.17 | 96.36
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 48.8 | 35 | 149 | 0 | 260 | 0 | 55 | 162 | 0 | 0 | 0 | 370 | 0 | 55 | 240 | 0 | 0 | 0 | 108 | 25 | 0 | 0 | 0 | 33 | 70 | 0 | 0 | 0 | 7 | 16 | 17 | 90 | 50 | 0 | 46 | 54 | 17 | 355 | 0 | 0 | 29 | 0 | 100 | 187 | 0 | 0 | 0 | 1160 | 0 | 142 | 0 | 230 | 295 | 0 | 51 | 0 | 198 | 0 | 15 | 80 | 114 | 9 | 13 | 0 | 114 | 0 | 0 | 9 | 315 | 0 | 0 | 42 | 52 | 157 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 99 | 17 | 59 | 18 | 73 | 0 | 0 | 13 | 6324.8 | 904 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1108 | 0 | 0 | 0 | 766.74 | 0 | 0 | 0 | 60 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 485 | 49 | 4951.74 | 11276.54 | 96.35
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 48.8 | 35 | 149 | 0 | 278 | 0 | 55 | 156 | 0 | 0 | 0 | 380 | 0 | 55 | 240 | 0 | 0 | 0 | 52 | 25 | 7 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 17 | 16 | 0 | 90 | 50 | 0 | 46 | 93 | 17 | 355 | 0 | 0 | 39 | 0 | 95 | 187 | 0 | 0 | 0 | 1162 | 0 | 142 | 0 | 220 | 305 | 0 | 51 | 0 | 196 | 0 | 16 | 80 | 128 | 9 | 13 | 0 | 114 | 0 | 0 | 14 | 315 | 0 | 0 | 42 | 52 | 154 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 99 | 0 | 59 | 19 | 72 | 0 | 0 | 24 | 6334.8 | 905 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1098 | 0 | 0 | 0 | 764.19 | 0 | 0 | 0 | 70 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 560 | 51 | 5026.19 | 11360.99
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 46 | 17 | 149 | 0 | 278 | 0 | 55 | 152 | 0 | 0 | 0 | 375 | 0 | 55 | 240 | 0 | 0 | 0 | 52 | 25 | 7 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 17 | 16 | 0 | 90 | 50 | 0 | 46 | 87 | 20 | 355 | 0 | 0 | 39 | 0 | 95 | 187 | 0 | 0 | 0 | 1153 | 0 | 142 | 0 | 220 | 290 | 0 | 51 | 0 | 180 | 0 | 16 | 80 | 128 | 0 | 13 | 0 | 112 | 0 | 0 | 16 | 310 | 0 | 0 | 42 | 52 | 153 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 99 | 0 | 59 | 19 | 73 | 0 | 0 | 24 | 6188 | 905 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 752.68 | 0 | 0 | 0 | 35 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 570 | 49 | 4989.68 | 11177.68 | 96.35
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 47 | 17 | 149 | 0 | 278 | 0 | 55 | 150 | 0 | 0 | 0 | 395 | 0 | 55 | 240 | 0 | 0 | 0 | 52 | 25 | 7 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 17 | 16 | 0 | 60 | 50 | 0 | 46 | 49 | 22 | 355 | 0 | 0 | 39 | 0 | 96 | 187 | 0 | 0 | 0 | 1165 | 0 | 143 | 0 | 220 | 300 | 0 | 51 | 0 | 180 | 0 | 16 | 80 | 129 | 0 | 13 | 0 | 108 | 0 | 0 | 17 | 310 | 0 | 0 | 42 | 52 | 155 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 99 | 0 | 59 | 18 | 73 | 0 | 0 | 24 | 6166 | 905 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 0 | 0 | 757.23 | 0 | 0 | 0 | 35 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 622 | 50 | 5057.23 | 11223.23 | 96.35
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 46 | 0 | 149 | 0 | 230 | 0 | 55 | 147 | 0 | 0 | 0 | 385 | 0 | 35 | 240 | 0 | 0 | 0 | 34 | 18 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 46 | 0 | 25 | 355 | 0 | 0 | 0 | 0 | 93 | 186 | 0 | 0 | 0 | 1160 | 0 | 100 | 0 | 220 | 290 | 0 | 51 | 0 | 180 | 0 | 15 | 80 | 126 | 0 | 13 | 0 | 104 | 0 | 0 | 0 | 310 | 0 | 0 | 42 | 52 | 151 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 99 | 0 | 59 | 18 | 73 | 0 | 0 | 0 | 5693 | 905 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 770.33 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 70 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 622 | 28 | 4906.33 | 10599.33 | 96.35
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 45.5 | 0 | 149 | 0 | 145 | 0 | 17 | 107 | 0 | 0 | 0 | 390 | 0 | 35 | 240 | 0 | 0 | 0 | 0 | 12 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 50 | 0 | 46 | 0 | 27 | 355 | 0 | 0 | 0 | 0 | 94 | 182 | 0 | 0 | 0 | 1165 | 0 | 30 | 0 | 220 | 290 | 0 | 51 | 0 | 187 | 0 | 0 | 80 | 51 | 0 | 13 | 0 | 100 | 0 | 0 | 0 | 310 | 0 | 0 | 42 | 52 | 153 | 0 | 17 | 0 | 81 | 30 | 0 | 0 | 99 | 0 | 59 | 18 | 73 | 0 | 0 | 0 | 5349.5 | 905 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 0 | 0 | 762.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 35 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 622 | 0 | 4706.65 | 10056.15 | 96.34
Total KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8384400 | 0 | 0 | 559080 | 124920 | 1485504 | 6720 | 2112153 | 0 | 624117 | 1249920 | 0 | 0 | 0 | 9097609 | 0 | 582084 | 5819421 | 0 | 0 | 160417 | 1586400 | 381000 | 183600 | 0 | 0 | 72764 | 265964 | 0 | 0 | 87360 | 39862 | 70808 | 47326 | 339840 | 496320 | 18145 | 1102920 | 263455 | 779520 | 6523636.36 | 0 | 0 | 151680 | 0 | 1149164 | 4114528 | 0 | 0 | 0 | 24834543 | 116235 | 1080581 | 0 | 5939500 | 7517800 | 0 | 947951 | 0 | 4400000 | 0 | 94080 | 1909446 | 1048800 | 32760 | 313920 | 0 | 2328000 | 0 | 389955 | 47168 | 7661500 | 0 | 0 | 994000 | 1257840 | 3652609 | 58532 | 403680 | 0 | 1645440 | 655488 | 0 | 0 | 2396500 | 33120 | 946800 | 302400 | 1949760 | 11050 | 257220 | 70080 | 121177395.36 | 21445090 | 8466048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 434160 | 23076400 | 0 | 0 | 0 | 16298182 | 0 | 0 | 0 | 226368 | 561024 | 0 | 0 | 0 | 0 | 273264 | 577420 | 0 | 0 | 306000 | 4650182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26160 | 0 | 1314673 | 637896 | 108514 | 650707 | 0 | 0 | 0 | 32870.04 | 873000 | 2676 | 0 | 5673000 | 3039000 | 5387680 | 0 | 0 | 10884363.64 | 184800 | 105129477.68 | 226306873.04

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 17-01-2026
Power Supply Scenario
| Day Peak Generation |  |  | 9662.54 | MW | 12:00 Hr. | Energy Generated |  |  | 226.3069 |  | MKWHr.
| Day Peak Demand |  |  | 9662.54 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11360.99 | MW | 19:30 Hr. | Energy Demand |  |  | 226.3069 |  | MKWHr.
| Evening Peak Demand |  |  | 11360.99 | MW | 19:30 Hr. | Maximum Temperature |  |  | 27.8 |  | °C
| Minimum Generation of the Day |  |  | 7286 | MW | 04:00 Hr. | Total Gas Supplied |  |  | 682.34 |  | MMCFD
| Maximum Generation of the Day |  |  | 11360.99 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.0664 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 23.866 | 0 | 8.3309 | 0 | 0 | 0.16042 | 0 | 0 | 32.3573 | Gas | 91.9484 | Gas | 325970831.63
| Chattogram Zone |  |  | 4.894 | 31.3582 | 2.8972 | 0 | 1.1029 | 0.13438 | 0 | 0.08736 | 40.4741 | Coal | 72.3066 | Coal | 473747086.482
| Cumilla Zone |  |  | 21.0286 | 0 | 2.3034 | 0 | 0 | 0.38995 | 2.328 | 0 | 26.05 | HFO | 17.1447 | HFO | 289836955.71
| Mymensingh Zone |  |  | 1.9498 | 0 | 1.3524 | 0 | 0 | 0.26827 | 0 | 0 | 3.5704 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 18.6671 | 0 | 0 | 0 | 0 | 0.058532 | 0 | 0 | 18.7256 | Hydro | 1.1029 | Hydro | 110292
| Khulna Zone |  |  | 8.466 | 23.0764 | 0 | 0 | 0 | 0.43416 | 21.4451 | 0 | 53.4217 | Solar | 3.6456 | Solar | 57150112.098
| Barishal Zone |  |  | 8.4267 | 16.5574 | 0.1848 | 0 | 0 | 0.002676 | 0 | 0 | 25.1715 | Import | 40.0713 | Import | 224775270.08
| Rajshahi Zone |  |  | 4.6502 | 0 | 0.78739 | 0 | 0 | 1.1828 | 16.2982 | 0 | 22.9186 | Wind | 0.08736 | Wind | 1285065.6
| Rangpur Zone |  |  | 0 | 1.3147 | 1.2886 | 0 | 0 | 1.0144 | 0 | 0 | 3.6177
| Total |  |  | 91.9484 | 72.3066 | 17.1447 | 0 | 1.1029 | 3.6456 | 40.0713 | 0.08736 | 226.3069
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 325970831.63 |  | Hydro | 110292
|  |  |  | Coal | 473747086.482 |  | Solar | 57150112.098
|  |  |  | HFO | 289836955.71 |  | Import | 224775270.08
|  |  |  | HSD | 0 |  | Wind | 1285065.6
[5 empty] | Total: | 137,28,75,613 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.4451 | Peak Hr Flow | 905.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 32461290 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 16.2982 | Peak Hr Flow | 764.19 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1574 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.328 | Peak Hr Flow | 114.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1753 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 40.0713 | Peak Hr Flow | 1783.19 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4118
|  |  |  | Chattogram |  | 0 |  | 1201
|  |  |  | Cumilla |  | 0 |  | 968
|  |  |  | Mymensingh |  | 0 |  | 965
|  |  |  | Sylhet |  | 0 |  | 422
|  |  |  | Khulna |  | 0 |  | 1220
|  |  |  | Barishal |  | 0 |  | 340
|  |  |  | Rajshahi |  | 0 |  | 1034
|  |  |  | Rangpur |  | 0 |  | 696
|  |  |  | Total |  | 0 |  | 10964
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:02 | 17:17 | Hathazari-Madunaghat 132kV Ckt-1 Scheduled S/D from Hathazari 230/132/33kV end.
| 08:10 | 18:08 | Bhaluka 132/33kV S/S 01. Transformer- 01 HT Scheduled S/D Due to Annual maintenance | [7 empty] | 48.0MW load
interrup.
| 08:10 | 10:16 | Bhaluka 132/33kV S/S 02. Transformer- 02 HT Scheduled S/D Due to Annual maintenance | [7 empty] | 48.0MW load
interrup.
| 08:10 | 18:09 | Bhaluka 132/33kV S/S 01. Transformer- 01 LT Scheduled S/D Due to Annual maintenance | [7 empty] | 48.0MW load
interrup.
| 08:10 | 10:18 | Bhaluka 132/33kV S/S 02. Transformer- 02 LT Scheduled S/D Due to Annual maintenance | [7 empty] | 48.0MW load
interrup.
| 08:16 | 12:12 | Jaldhaka 132/33kV S/S 406T-1 LT Scheduled S/D Due to New 33kV Feeder(Nilphamari PBS) | [7 empty] | 15.0MW load
|  |  | connection on 33kV Bus section-1 | [7 empty] | interrup.
| 08:16 | 12:11 | Jaldhaka 132/33kV S/S 406T-1 HT Scheduled S/D Due to New 33kV Feeder(Nilphamari PBS) | [7 empty] | 15.0MW load
|  |  | connection on 33kV Bus section-1 | [7 empty] | interrup.
| 08:18 | 15:45 | Mahasthangarh 132/33kV S/S 406T MTR1 LT Scheduled S/D Due to 33kv bus annual maintenance | [7 empty] | 14.0MW load
|  |  | work of PBS. | [7 empty] | interrup.
| 08:18 | 15:45 | Mahasthangarh 132/33kV S/S 406T MTR1 HT Scheduled S/D Due to 33kv bus annual maintenance | [7 empty] | 14.0MW load
|  |  | work of PBS. | [7 empty] | interrup.
| 08:18 | 13:05 | Mahasthangarh 132/33kV S/S 33KV Main bus T-1 Scheduled S/D Due to 33kv bus annual | [7 empty] | 14.0MW load
|  |  | maintenance work of PBS. | [7 empty] | interrup.
| 08:18 | 14:15 | Haripur-Meghnaghat 230kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to Annual
Maintenance
| 08:20 | 17:10 | Bogura-Rahanpur 400kV Ckt-1 Scheduled S/D from Bogura 400/230kV end Due to Annual
Maintenance. and from Rahanpur 400/132kV end Due to Annual maintenance
| 08:20 | 13:05 | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Scheduled S/D Due to 33kv bus annual maintenance | [7 empty] | 14.0MW load
|  |  | work of PBS. | [7 empty] | interrup.
| 08:20 | 13:05 | Mahasthangarh 132/33kV S/S 33KV Main bus T-2 Scheduled S/D Due to 33kv bus annual | [7 empty] | 14.0MW load
|  |  | maintenance work of PBS. | [7 empty] | interrup.
| 08:21 | 15:04 | Daudkandi-Sonargaon 132 kV Ckt-1 Scheduled S/D from Daudkandi 132/33kV end Due to
Maintenance work at Sonargaon Substation side and from Sonargaon 132/33kV end Due to
Annual maintenance on Sonargaon to Daudkandi line by Siddhirgonj 132/33KV grid Substation
| 08:21 | 13:04 | Mahasthangarh 132/33kV S/S 416T MTR 2 HT Scheduled S/D Due to 33kv bus annual maintenance | [7 empty] | 14.0MW load
|  |  | work of PBS. | [7 empty] | interrup.
| 08:30 | 15:49 | AKSML-Baroaulia 132kV Ckt-1 Scheduled S/D from AKS 132/33kV end Due to AKSPL to Baraulia
Deadline Checking and from Baroaulia 132/33kV end Due to Annual Maintenance for Dead line
check Baraulia to AKSPL line.
|  | 08:37 | Kodda-Rajendrapur 132kV Ckt-1 is restored.
| 08:37 | 17:27 | Kodda-Rajendrapur 132kV Ckt-2 Forced S/D from Rajendrapur 132/33kV end Due to Load
shifted from Sreepur to Kodda end.
| 08:40 | 16:04 | Brahmanbaria-Narsinghdi 132 kV Ckt-2 Scheduled S/D from Narshingdi 132/33kV end Due to
Annual maintenance and from Brahmanbaria 132/33kVend.
| 08:41 | 17:03 | Sirajganj-Ullahpara 132KV Ckt-2 Scheduled S/D from Sirajganj 132/33kV end Due to Annual
maintenance.
| 08:43 | 16:11 | Bagerhat-Labanchura 132 kV Ckt-2 Scheduled S/D from Bagerhat 132/33kV end Due to Yearly
maintenance work by Goalpara Grid S/S.
| 08:48 | 16:51 | Aminbazar-Kallyanpur 132kV Ckt-2 Scheduled S/D from Kallyanpur 132/33kV end.
| 08:50 | 20:58 | Faridpur 132/33kV S/S 132 KV Rajbari ckt-2 Scheduled S/D Due to Annual maintenance
| 08:50 | 11:23 | Thakurgaon 132/33kV S/S T-2(412T) LT Scheduled S/D Due to 33 kV Feeder Riser Maintenance
| 08:50 | 11:22 | Thakurgaon 132/33kV S/S T-2(412T) HT Scheduled S/D Due to 33 kV Feeder Riser Maintenance
| 08:50 | 20:59 | Rajbari 132/33kV S/S Faridpur - 2 Scheduled S/D Due to Annual maintenance
| 08:53 | 20:52 | Aminbazar-Keraniganj 230kV Ckt-2 Scheduled S/D from Keranigonj 230/132/33kV end Due to CT
maintenance work at aminbazar end. and from Aminbazar 400/230/132kV end Due to Schedule
shutdown
| 08:55 | 16:44 | Pabna 132/33kV S/S T-3 HT Scheduled S/D
| 08:55 | 16:44 | Pabna 132/33kV S/S T-3 LT Scheduled S/D
| 09:00 | 15:13 | Jhenaidah 132/33kV S/S Transformer T-2 LT Scheduled S/D Due to WZPDCL Jhenaidah Annual | [7 empty] | 12.0MW load
|  |  | Maintenance. | [7 empty] | interrup.
| 09:00 | 15:12 | Jhenaidah 132/33kV S/S Transformer T-2 HT Scheduled S/D Due to WZPDCL Jhenaidah Annual | [7 empty] | 12.0MW load
|  |  | Maintenance. | [7 empty] | interrup.
| 09:02 | 16:04 | BIPTC S/S Baharampur-1 Scheduled S/D Due to Annual Maintenance.
| 09:02 | 14:03 | Candpur- Kachua 132kV Ckt-2 Scheduled S/D from Kachua 230/132/33kV end Due to Annual
maintenance and from Chandpur 132/33kV end Due to Maintenance work
|  | 09:05 | Kishoreganj 132/33kV S/S Tr-2 (414T) HT is restored.
|  | 09:05 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT is restored.
|  | 09:06 | Kishoreganj 132/33kV S/S Tr-1 (404T) LT is restored.
|  | 09:06 | Kishoreganj 132/33kV S/S Tr-2 (414T) LT is restored.
| 09:07 | 13:43 | Ruppur 132/11kV S/S 132kv BUS-1 Scheduled S/D Due to Annual Maintenance
| 09:17 | 15:46 | Cantonment 132/33kV S/S Auxiliary Transformer, AT-2 LT Scheduled S/D Due to Annual
Maintenance
| 09:18 | 15:46 | Cantonment 132/33kV S/S Transformer-2 (T-2) LT Scheduled S/D Due to Annual Maintenance
| 09:19 | 15:44 | Cantonment 132/33kV S/S Transformer-2 (T-2) HT Scheduled S/D Due to Transformer-02 due to
Annual Maintenance .
| 09:20 | 17:22 | Sreepur 230/132/33kV S/S 230/132 kV T-1 HT Scheduled S/D Due to Annual Maintenance
| 09:20 | 17:22 | Sreepur 230/132/33kV S/S 230/132 kV T-1 LT Scheduled S/D Due to Annual Maintenance
| 09:24 | 17:00 | Gopalganj 400/132kV S/S 400kV Amtoli Ckt-1 Scheduled S/D
| 09:25 | 15:35 | Cantonment 132/33kV S/S Auxiliary Transformer, AT-2 HT Scheduled S/D Due to Annual
Maintenance
| 09:26 | 15:27 | Tangail 132/33kV S/S Main Bus Scheduled S/D Due to Annual Maintenance | [7 empty] | 100.0MW load
interrup.
| 09:26 | 17:15 | Kaliakoir-Kodda(300MW) 230kV Ckt-1 Scheduled S/D from Kaliakoir 400/230/132kV end Due to
Annual Maintenance.
| 09:34 | 12:49 | Mirzapur 132/33kV S/S Transformer-01(E05) LT Scheduled S/D Due to Tangail Grid | [7 empty] | 23.0MW load
|  |  | Maintenance work | [7 empty] | interrup.
| 09:34 | 12:47 | Mirzapur 132/33kV S/S Transformer-02(E07) LT Scheduled S/D Due to Tangail Grid | [7 empty] | 13.0MW load
|  |  | Maintenance work | [7 empty] | interrup.
| 09:36 | 17:26 | Barapukuria 230/132/33kV S/S 230/132KV T-06, 723T LT Scheduled S/D Due to Annual
Maintenance work
| 09:36 | 11:48 | Sylhet 132/33kV S/S T1 LT Scheduled S/D Due to 33KV cable test
| 09:36 | 11:48 | Sylhet 132/33kV S/S T1 HT Scheduled S/D Due to 33KV cable test
| 09:36 | 12:48 | Mirzapur 132/33kV S/S Transformer-01(E05) HT Scheduled S/D Due to Tangail Grid | [7 empty] | 23.0MW load
|  |  | Maintenance work | [7 empty] | interrup.
| 09:36 | 12:44 | Mirzapur 132/33kV S/S Mirzapur-Tangail-ckt-2B(E03) Scheduled S/D Due to Tangail Grid
Maintenance work
| 09:36 | 17:25 | Barapukuria 230/132/33kV S/S 230/132KV T-06, 723T HT Scheduled S/D Due to Annual
Maintenance work
| 09:37 | 12:47 | Mirzapur 132/33kV S/S Transformer-02(E07) HT Scheduled S/D Due to Tangail Grid | [7 empty] | 13.0MW load
|  |  | Maintenance work | [7 empty] | interrup.
| 09:40 | 16:39 | Gopalganj 400/132kV S/S 400kV Rooppur Scheduled S/D
| 09:42 | 15:38 | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-2 Scheduled S/D Due to Annual Maintenance
| 09:44 | 17:19 | Hathazari 230/132/33kV S/S AKSML-02 Scheduled S/D Due to dead line check
| 09:49 | 17:39 | Aminbazar-Meghnaghat 400kV Ckt-1 Scheduled S/D from Meghnaghat 400/230kV end Due to for
maintenance work
| 09:57 |  | Purbasadipur 132/33kV S/S T-3 Transformer (423T) LT Project Work S/D Due to T3 connection
work with GIS
| 09:57 |  | Purbasadipur 132/33kV S/S T-3 Transformer (423T) HT Project Work S/D Due to T3 connection
work with GIS
| 09:58 | 19:41 | Cumilla(N)-Meghnaghat 230 kV Ckt-1 Scheduled S/D from Meghnaghat 230/132kV end Due to As
per request of NLDC
| 10:10 |  | Baghbari 132 KV Bus 1 S/D Due to project works.
| 10:22 | 17:15 | Aminbazar-Kaliakoir 230kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to
Annual Maitenance.
| 10:55 | 11:42 | Kushtia 132/33kV S/S T-1 LT Forced S/D Due to 33kv Bus section isolator maintenance | [7 empty] | 24.0MW load
interrup.
| 10:56 | 11:41 | Kushtia 132/33kV S/S T-1 HT Forced S/D | [7 empty] | 24.0MW load
interrup.
| 11:21 |  | Khulna(S) 230/132kV S/S TR-2 HT Scheduled S/D Due to None
| 11:21 |  | Khulna(S) 230/132kV S/S TR-2 LT Scheduled S/D
| 12:00 |  | Day Peak Generation: 9659 MW.
|  | 12:09 | Haripur 230/132kV S/S Ullon (Maniknagar-2) is restored.
| 13:08 |  | Madanganj 132/33kV S/S GT-1 LT Scheduled S/D Due to Oil centrifuge
| 13:10 |  | Madanganj 132/33kV S/S GT-1 HT Scheduled S/D Due to Oil centrifuge
| 14:20 | 17:26 | Bog-Sherpur 132/33kV S/S Transformer-3 (424T) LT Scheduled S/D Due to Maintenance Work
| 14:21 | 17:16 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) LT Scheduled S/D Due to Maintenance Work | [7 empty] | 15.0MW load
interrup.
| 14:21 | 17:25 | Bog-Sherpur 132/33kV S/S Transformer-3 (424T) HT Scheduled S/D Due to Maintenance Work
| 14:22 | 17:16 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT Scheduled S/D Due to Maintenance Work | [7 empty] | 15.0MW load
interrup.
| 14:25 | 17:14 | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) LT Scheduled S/D Due to Maintenance Work | [7 empty] | 15.0MW load
interrup.
| 14:25 | 16:29 | Haripur-Meghnaghat 230kV Ckt-2 Scheduled S/D from Haripur 230/132kV end.
| 14:26 | 17:13 | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) HT Scheduled S/D Due to Maintenance Work | [7 empty] | 15.0MW load
interrup.
| 15:12 | 15:56 | Baghabari-Bangura 132 kV Ckt-1 Project Work S/D from Bhangura 132/33kV end Due to For | [7 empty] | 16.0MW load
|  |  | Bhagabari PDB work | [7 empty] | interrup. Bhangura
132/33kV end
| 15:47 | 17:48 | Mahasthangarh 132/33kV S/S 416T MTR 2 HT Scheduled S/D Due to Maintenance work done
| 15:47 | 17:49 | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Scheduled S/D Due to Maintenance work
| 15:58 |  | Ghorashal AIS-Ghorashal GIS 230kV Ckt-1 was switched on (loaded) for the first time after
the recent earthquake.
|  | 16:26 | Barishal 132/33kV S/S T-1 (405T) HT is restored.
|  | 16:27 | Barishal 132/33kV S/S T-1 (405T) LT is restored.
|  | 17:17 | Hathazari-Madunaghat 132kV Ckt-1 is restored.
| 17:27 |  | Kodda-Rajendrapur 132kV Ckt-1 Forced S/D from Rajendrapur 132/33kV end Due to Load
shifted from kodda-1 to sreepur end.
|  | 17:35 | Bibiyana-Fenchuganj 230 kV Ckt-2 is restored.
| 17:35 | 17:52 | Barishal-Bhandaria 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to Shutdown
by ALDC
|  | 17:41 | Rampura 230/132kV S/S 132 kV Busbar-2 is restored.
|  | 17:44 | Rampura 230/132kV S/S Auto Transformer - 02 HT is restored.
|  | 17:45 | Rampura 230/132kV S/S Auto Transformer - 02 LT is restored.
|  | 17:53 | Bhandaria 132/33kV S/S Main Bus Bar is restored.
|  | 17:53 | Barishal-Bhandaria 132 kV Ckt-1 is restored.
|  | 17:54 | Bhandaria 132/33kV S/S Transformer-1 HT is restored.
|  | 17:55 | Bhandaria 132/33kV S/S Transformer-1 LT is restored.
|  | 17:56 | Bhandaria 132/33kV S/S Transformer-2 HT is restored.
|  | 17:56 | Bhandaria 132/33kV S/S Transformer-2 LT is restored.
|  | 18:12 | Bagerhat-Bhandaria 132 kV Ckt-1 is restored.
|  | 18:12 | Sirajgonj 230 S/S SNWPCL (Unit-04) is restored.
|  | 18:12 | Bagerhat-Bhandaria 132 kV Ckt-1 is restored.
|  | 18:54 | Agargaon 230/132kV S/S 230kV Transformer-2 ( 715T2) HT is restored.
|  | 18:57 | Agargaon 230/132kV S/S 230kV Transformer-2 ( 715T2) LT is restored.
|  | 18:58 | Agargaon 230/132kV S/S Auxiliary Tr-2 HT is restored.
|  | 18:58 | Agargaon 230/132kV S/S Auxiliary Tr-2 LT is restored.
| 19:30 |  | Evening Peak Generation: 11360 MW.
| 20:17 | 21:19 | Chhatak 132/33kV S/S T-1 LT Scheduled S/D Due to Red Hot Maintenance. | [7 empty] | 11.0MW load
interrup.
| 20:17 | 21:19 | Chhatak 132/33kV S/S T-1 HT Scheduled S/D Due to Red Hot Maintenance. | [7 empty] | 11.0MW load
interrup.
| 04:00 |  | Minimum generation 7835 MW
| 07:30 |  | Sylhet 132/33kV S/S Sylhet-90MW P/S Scheduled S/D Due to OPGW Replacement
| 07:39 |  | Moghbazar-Rampura 132kV Ckt-1 Scheduled S/D from Rampura 230/132kV end Due to Annual
Annual Maintenance.
| 07:42 |  | Bibiyana-Fenchuganj 230 kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Deadline Cheacking
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 17-01-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 336 | 8384400 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 240 | 5819421 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 48.8 | 559080 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 6720 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 624117 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 582084 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 25 | 381000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 7 | 183600 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 278 | 2112153 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1485504 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 156 | 1249920 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 160417 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 124920 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 380 | 9097609 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 52 | 1586400 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1816.8 | 32357345
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 116235 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 39 | 151680 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1102920 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 187 | 4114528 | Plant availability less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 95 | 1149164 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 16 | 70808 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 39862 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 339840 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 17 | 779520 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 18145 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 100 | 265964 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 47326 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 93 | 263455 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 496320 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 72764 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1162 | 24834543 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 87360 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 355 | 6523636.36 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4898.863 | 2267 | 40474070.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 196 | 4400000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 305 | 7517800 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 220 | 5939500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 947951 | Gas shortage
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 142 | 1080581 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 14 | 47168 | Partial Shutdown due to maintenance
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1909446 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 128 | 1048800 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 114 | 2328000 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 313920 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 32760 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 16 | 94080 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 389955 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1288 | 26049961
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 72 | 1949760 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 302400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 946800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 257220 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 70080 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 33120 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 174 | 3570430
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 58532 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 994000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 52 | 1257840 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 154 | 3652609 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 655488 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1645440 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 99 | 2396500 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 403680 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7661500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 789 | 18725589
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 905 | 21445090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 343 | 8466048 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 434160 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1098 | 23076400 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2346 | 53421698
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 3039000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 560 | 10884363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5387680 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 51 | 184800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5673000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2676 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1268 | 25171519.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 273264 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 187 | 4650182 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 0 | 0 | Under Maintenance
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 561024 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 70 | 226368 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 26160 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 764.19 | 16298182 | U#1 Under AOH
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 306000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 577420 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1134.19 | 22918600
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 56 | 1314673 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 650707 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 32870.04 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 637896 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 108514 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 873000 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 278 | 3617660.04
Eastern Grid Total |  |  |  |  | 17398.245 | 6334.8 | 121177395.36
Western Grid Total |  |  |  |  | 10984.003 | 5026.19 | 105129477.68
National Grid Total |  |  |  |  | 28382.248 | 11360.99 | 226306873.04
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 17-01-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7674.1 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3290.4 | MW
i) Dhaka area |  |  | 4118.2 |  | MW | i) Khulna area |  |  |  | 1219.5 | MW
ii) Chattogram area |  |  | 1200.9 |  | MW | ii) Barishal area |  |  |  | 340.5 | MW
iii) Cumilla area |  |  | 968 |  | MW | iii) Rajshahi area |  |  |  | 1034.4 | MW
iv) Mymensingh area |  |  | 965 |  | MW | iv) Rangpur area |  |  |  | 696 | MW
v) Sylhet area |  |  | 422 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10964.5 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 75 | 13:00 | 133 | Netrakona | 128 | 18:00
2 | AKSML | 130 | 12:00 | 68 | Hathazari | 57 | 18:00 | 134 | New | 59.2 | 12:00
3 | Aftabnagar | 26 | 13:00 | 69 | Hatirjheel | 26 | 15:00 | 135 | Niamatpur | 71 | 08:00
4 | Agargaon | 88 | 13:00 | 70 | Ishurdi | 60 | 13:00 | 136 | Noapara | 52 | 13:00
5 | Agrabad | 48 | 18:00 | 71 | Jaldhaka | 60 | 18:30 | 137 | PHP | 8 | 00:00
6 | Amnura | 30 | 08:00 | 72 | Jamalpur | 99 | 18:00 | 138 | Pabna | 66 | 18:30
7 | Ashuganj | 53 | 23:00 | 73 | Jashore | 94 | 20:00 | 139 | Palashbari | 82 | 18:30
8 | BSRM | 194 | 14:00 | 74 | Jhenaidah | 98 | 08:00 | 140 | Panchagarh | 37 | 19:00
9 | Bagerhat | 61 | 20:00 | 75 | Joydebpur | 113 | 15:00 | 141 | Patiya | 6.7 | 13:00
10 | Bajitpur | 75 | 18:30 | 76 | Joypurhat | 43 | 09:00 | 142 | Patuakhali | 40.5 | 20:00
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 13 | 18:00 | 143 | Payra | 28 | 20:00
12 | Bakulia | 66 | 18:00 | 78 | KSRM | 17 | 06:00 | 144 | Postogola | 40 | 13:00
13 | Banani | 34 | 13:00 | 79 | Kabirpur | 194 | 15:00 | 145 | Purbachal | 22 | 12:00
14 | Bangabhaban | 5 | 10:00 | 80 | Kachua | 59 | 20:00 | 146 | Purbasadipur | 111 | 13:00
15 | Barapukuria | 50 | 21:00 | 81 | Kallyanpur | 75 | 13:00 | 147 | Rahanpur | 24 | 12:00
16 | Barguna | 16 | 19:30 | 82 | Kalurghat | 30 | 15:00 | 148 | Rahim | 38 | 23:00
17 | Barishal | 68 | 21:00 | 83 | Kamrangirchar | 68 | 13:00 | 149 | Rajbari | 60 | 18:30
18 | Barishal-230 | 84 | 18:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 111 | 19:00
19 | Baroaulia | 57 | 17:00 | 85 | Kasba | 26 | 13:00 | 151 | Rajshahi | 73 | 13:00
20 | Baroirhat | 41 | 18:30 | 86 | Kazla | 88 | 13:00 | 152 | Rajshahi-230 | 74 | 13:00
21 | Bashundhara | 153 | 13:00 | 87 | Keranigonj | 67 | 21:00 | 153 | Ramganj | 68 | 13:00
22 | BashundharaCement | 3 | 15:00 | 88 | Khagrachori | 26 | 18:30 | 154 | Rampur | 27 | 13:00
23 | Beanibazar | 48 | 19:00 | 89 | Khulna | 48 | 13:00 | 155 | Rangamati | 13 | 18:00
24 | Benapole | 74 | 09:00 | 90 | Khulshi | 151 | 11:00 | 156 | Rangpur | 112 | 18:30
25 | Bhaluka | 138 | 20:00 | 91 | Kishoreganj | 114 | 18:30 | 157 | Ruppur | 1.6 | 14:00
26 | Bhandaria | 52 | 18:30 | 92 | Kodda | 247 | 19:30 | 158 | SSM | 1 | 23:00
27 | Bhangura | 25 | 18:00 | 93 | Kulaura | 30 | 18:00 | 159 | Saidpur | 85 | 14:00
28 | Bheramara(GK) | 41 | 18:00 | 94 | Kurigram | 47 | 18:00 | 160 | Satkhira | 104 | 18:30
29 | Bhulta | 178 | 19:30 | 95 | Kushtia | 106 | 18:00 | 161 | Satmasjid | 75 | 13:00
30 | Bog-Sherpur | 58 | 18:00 | 96 | Laksam | 18 | 00:00 | 162 | Savar | 149 | 19:00
31 | Bogura | 115 | 19:30 | 97 | Lakshmipur | 23 | 19:30 | 163 | SevenRings | 14.92 | 19:00
32 | Borhanuddin | 64 | 19:30 | 98 | Lalbag | 54 | 12:00 | 164 | ShahCement | 33 | 19:30
33 | Brahmanbaria | 94 | 13:00 | 99 | Lalmonirhat | 38 | 18:30 | 165 | Shahjadpur | 54 | 12:00
34 | Cantonment | 68 | 13:00 | 100 | MI_Cement | 16 | 23:00 | 166 | Shahjibazar | 104 | 18:00
35 | Chandina | 14 | 18:00 | 101 | Madanganj | 37 | 13:00 | 167 | Shahmirpur | 40 | 19:00
36 | Chandpur | 52 | 21:00 | 102 | Madaripur | 68 | 20:00 | 168 | Shariatpur | 59 | 21:00
37 | Chandraghona | 28 | 18:00 | 103 | Madartek | 64 | 13:00 | 169 | Sherpur | 128 | 08:00
38 | Chapai | 50 | 19:30 | 104 | Madunaghat | 36 | 18:00 | 170 | Shikalbaha | 17 | 18:00
39 | Charsaidpur | 37 | 00:00 | 105 | Magura | 48 | 18:00 | 171 | Shitalakhya | 62.5 | 13:00
40 | Chauddagram | 50 | 13:00 | 106 | Mahasthangarh | 46 | 08:00 | 172 | Sholosohor | 38 | 15:00
41 | Chhatak | 33 | 18:00 | 107 | Maijdee | 33 | 18:30 | 173 | Shyampur | 136 | 12:00
42 | Chowmuhani | 111 | 18:00 | 108 | Manikganj | 101 | 20:00 | 174 | Siddhirganj | 105 | 12:00
43 | Chuadanga | 85 | 13:00 | 109 | Maniknagar | 46 | 13:00 | 175 | Sirajganj | 80 | 19:00
44 | Coxsbazar | 108 | 18:00 | 110 | Matarbari | 42 | 18:30 | 176 | Sonargaon | 128 | 19:30
45 | Cumilla(N) | 116 | 13:00 | 111 | Matuail | 56 | 12:00 | 177 | Sreemongol | 58 | 18:00
46 | Cumilla(S) | 117 | 18:00 | 112 | Metrorail_Motijheel | 20 | 12:00 | 178 | Sreepur | 76 | 20:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 0 | 00:00 | 179 | Srinagar | 33.2 | 13:00
48 | Daudkandi | 112 | 19:00 | 114 | Millgate | 70 | 11:00 | 180 | Sunamganj | 40 | 18:00
49 | DhakaUniversity | 48 | 14:00 | 115 | Mirpur | 107 | 13:00 | 181 | Sylhet | 40 | 13:00
50 | Dhamrai | 110 | 15:00 | 116 | Mirsorai | 38 | 05:00 | 182 | Sylhet-132 | 76 | 18:00
51 | Dhanmondi | 74.2 | 13:00 | 117 | Mirzapur | 44 | 19:30 | 183 | TK | 18 | 12:00
52 | Dohazari | 67 | 18:00 | 118 | Mithapukur | 40 | 08:00 | 184 | Tangail | 154 | 19:00
53 | Faridpur | 117 | 21:00 | 119 | Modern | N/A | N/A | 185 | Taraganj | 17 | 18:00
54 | Fatullah | 88 | 15:00 | 120 | Mogbazar | 47.6 | 14:00 | 186 | Tasnim | 30 | 05:00
55 | Fenchuganj | 25 | 17:00 | 121 | Mongla | 38 | 18:30 | 187 | Thakurgaon | 72 | 13:00
56 | Feni | 80 | 18:00 | 122 | Motijheel | 34 | 13:00 | 188 | Tongi | 113 | 17:00
57 | GPH | 94 | 22:00 | 123 | Muktagacha | 31 | 17:00 | 189 | Ullahpara | 25 | 18:30
58 | Ghatail | 74 | 08:00 | 124 | Munshiganj | 74 | 13:00 | 190 | Ullon | 40 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 0 | 00:00 | 191 | Uttara | 60 | 18:00
60 | Ghorashal-230 | 85 | 19:30 | 126 | Mymensingh | 163 | 18:00 | 192 | UttaraNew | 33 | 13:00
61 | Goalpara | 30 | 12:00 | 127 | Naogaon | 97 | 13:00 | 193 | Zigatola | 74 | 13:00
62 | Gollamari | 76 | 21:00 | 128 | Narail | 38.5 | 18:30
63 | Gopalganj | 75 | 21:00 | 129 | Narinda | 53 | 12:00
64 | Gulshan | 62 | 13:00 | 130 | Narshingdi | 143 | 19:00
65 | Halishahar | 59 | 18:00 | 131 | Natore | 104 | 21:00
66 | HaripurSBU | 125 | 17:00 | 132 | Nawabganj | 33.2 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 17-01-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 8836 | 0 |  | 8836
1:00 | 8373 | 0 |  | 8373
2:00 | 7770 | 0 |  | 7770
3:00 | 7564 | 0 |  | 7564
4:00 | 7286 | 0 |  | 7286
5:00 | 7313 | 0 |  | 7313
6:00 | 7657 | 0 |  | 7657
7:00 | 8383.36 | 0 |  | 8383.36
8:00 | 9340.04 | 0 |  | 9340.04
9:00 | 9452.77 | 0 |  | 9452.77
10:00 | 8731.71 | 0 |  | 8731.71
11:00 | 8998.65 | 0 |  | 8998.65
12:00 | 9662.54 | 0 |  | 9662.54
13:00 | 10234.35 | 0 |  | 10234.35
14:00 | 9851.02 | 0 |  | 9851.02
15:00 | 9521.52 | 0 |  | 9521.52
16:00 | 9066.81 | 0 |  | 9066.81
17:00 | 9376.87 | 0 |  | 9376.87
18:00 | 10736.17 | 0 |  | 10736.17
19:00 | 11276.54 | 0 |  | 11276.54
19:30 | 11360.99 | 0 |  | 11360.99
20:00 | 11177.68 | 0 |  | 11177.68
21:00 | 11223.23 | 0 |  | 11223.23
22:00 | 10599.33 | 0 |  | 10599.33
23:00 | 10056.15 | 0 |  | 10056.15
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 17-01-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4307 | 4529 | 8836 | DAILY GENERATION CURVE
00:30 | 4287.5 | 4317 | 8604.5
01:00 | 4268 | 4105 | 8373 | 17-01-2026
01:30 | 4181 | 3890.5 | 8071.5
02:00 | 4094 | 3676 | 7770
02:30 | 4038 | 3629 | 7667
03:00 | 3982 | 3582 | 7564
03:30 | 3886.5 | 3538.5 | 7425
04:00 | 3791 | 3495 | 7286
04:30 | 3810.5 | 3489 | 7299.5
05:00 | 3830 | 3483 | 7313
05:30 | 3948 | 3537 | 7485
06:00 | 4066 | 3591 | 7657
06:30 | 4267.405 | 3752.775 | 8020.18
07:00 | 4468.81 | 3914.55 | 8383.36
07:30 | 4621.845 | 4239.855 | 8861.7
08:00 | 4774.88 | 4565.16 | 9340.04
08:30 | 4800.12 | 4596.285 | 9396.405
09:00 | 4825.36 | 4627.41 | 9452.77
09:30 | 4667.19 | 4425.05 | 9092.24
10:00 | 4509.02 | 4222.69 | 8731.71
10:30 | 4640.295 | 4224.885 | 8865.18
11:00 | 4771.57 | 4227.08 | 8998.65
11:30 | 4989.245 | 4341.35 | 9330.595
12:00 | 5206.92 | 4455.62 | 9662.54
12:30 | 5356.38 | 4592.065 | 9948.445
13:00 | 5505.84 | 4728.51 | 10234.35
13:30 | 5374.245 | 4668.44 | 10042.685
14:00 | 5242.65 | 4608.37 | 9851.02
14:30 | 5147.095 | 4539.175 | 9686.27
15:00 | 5051.54 | 4469.98 | 9521.52
15:30 | 5014.265 | 4279.9 | 9294.165
16:00 | 4976.99 | 4089.82 | 9066.81
16:30 | 5144.15 | 4077.69 | 9221.84
17:00 | 5311.31 | 4065.56 | 9376.87
17:30 | 5717.905 | 4338.615 | 10056.52
18:00 | 6124.5 | 4611.67 | 10736.17
18:30 | 6224.65 | 4781.705 | 11006.355
19:00 | 6324.8 | 4951.74 | 11276.54
19:30 | 6334.8 | 5026.19 | 11360.99
20:00 | 6188 | 4989.68 | 11177.68
20:30 | 6177 | 5023.455 | 11200.455 |  | Executive Engineer
21:00 | 6166 | 5057.23 | 11223.23 |  | Network Operation Division
21:30 | 5929.5 | 4981.78 | 10911.28
22:00 | 5693 | 4906.33 | 10599.33
22:30 | 5521.25 | 4806.49 | 10327.74
23:00 | 5349.5 | 4706.65 | 10056.15

## En-Curve
QF-LDC-12
Date | 17-01-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2537 | 1302 | 879 | 0 | 82 | 758 | 46 | 3232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2545 | 1298 | 878.5 | 0 | 86 | 695.5 | 46 | 3026 | 0 | 0 | 29.5 | 0 | 0 | 0 | 0 | 17-01-2026
01:00 | 2553 | 1294 | 878 | 0 | 90 | 633 | 46 | 2820 | 0 | 0 | 59 | 0 | 0 | 0 | 0
01:30 | 2555 | 1289.5 | 878.5 | 0 | 84 | 556 | 46 | 2633 | 0 | 0 | 29.5 | 0 | 0 | 0 | 0 | Energy Generated | 226.3069 |  | MKWHr
02:00 | 2557 | 1285 | 879 | 0 | 78 | 479 | 46 | 2446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2558 | 1247.5 | 879 | 0 | 80 | 451.5 | 46 | 2394.5 | 0 | 0 | 0 | 0 | 0 | 10.5 | 0 | Total Energy Requirement | 226.3069 |  | MKWHr
03:00 | 2559 | 1210 | 879 | 0 | 82 | 424 | 46 | 2343 | 0 | 0 | 0 | 0 | 0 | 21 | 0
03:30 | 2538 | 1167.5 | 879 | 0 | 77 | 424.5 | 46 | 2277 | 0 | 0 | 0 | 0 | 0 | 16 | 0
04:00 | 2517 | 1125 | 879 | 0 | 72 | 425 | 46 | 2211 | 0 | 0 | 0 | 0 | 0 | 11 | 0
04:30 | 2527.5 | 1119.5 | 879 | 0 | 76 | 432 | 46 | 2205 | 0 | 0 | 0 | 0 | 0 | 14.5 | 0
05:00 | 2538 | 1114 | 879 | 0 | 80 | 439 | 46 | 2199 | 0 | 0 | 0 | 0 | 0 | 18 | 0
05:30 | 2580.5 | 1169 | 879 | 0 | 82 | 436.5 | 46 | 2276 | 0 | 0 | 0 | 0 | 0 | 16 | 0
06:00 | 2623 | 1224 | 879 | 0 | 84 | 434 | 46 | 2353 | 0 | 0 | 0 | 0 | 0 | 14 | 0
06:30 | 2637 | 1274 | 878.5 | 0 | 85 | 482 | 46 | 2599 | 4.68 | 0 | 0 | 0 | 0 | 14 | 0
07:00 | 2651 | 1324 | 878 | 0 | 86 | 530 | 46 | 2845 | 9.36 | 0 | 0 | 0 | 0 | 14 | 0
07:30 | 2625 | 1323 | 878 | 0 | 90 | 612 | 46 | 3023 | 64.2 | 8.5 | 180.5 | 0 | 0 | 11.5 | 0
08:00 | 2599 | 1322 | 878 | 0 | 94 | 694 | 46 | 3201 | 119.04 | 17 | 361 | 0 | 0 | 9 | 0
08:30 | 2566 | 1254.5 | 878 | 0 | 92 | 726 | 46 | 3110.5 | 209.705 | 65 | 443.2 | 0 | 0 | 5.5 | 0
09:00 | 2533 | 1187 | 878 | 0 | 90 | 758 | 46 | 3020 | 300.37 | 113 | 525.4 | 0 | 0 | 2 | 0
09:30 | 2423.5 | 1097.5 | 878 | 0 | 90 | 760 | 46 | 2807 | 377.74 | 133 | 478.5 | 0 | 0 | 1 | 0
10:00 | 2314 | 1008 | 878 | 0 | 90 | 762 | 46 | 2594 | 455.11 | 153 | 431.6 | 0 | 0 | 0 | 0
10:30 | 2400 | 1079.5 | 878.5 | 0 | 93 | 765 | 46 | 2567.5 | 511.08 | 139 | 385.6 | 0 | 0 | 0 | 0
11:00 | 2486 | 1151 | 879 | 0 | 96 | 768 | 46 | 2541 | 567.05 | 125 | 339.6 | 0 | 0 | 0 | 0
11:30 | 2536.5 | 1198.2 | 878.5 | 0 | 102 | 769 | 46 | 2739 | 587.295 | 125 | 349.1 | 0 | 0 | 0 | 0
12:00 | 2587 | 1245.4 | 878 | 0 | 108 | 770 | 46 | 2937 | 607.54 | 125 | 358.6 | 0 | 0 | 0 | 0
12:30 | 2560 | 1251.7 | 878.5 | 0 | 109 | 766.5 | 46 | 3129 | 579.945 | 133.5 | 494.3 | 0 | 0 | 0 | 0
13:00 | 2533 | 1258 | 879 | 0 | 110 | 763 | 46 | 3321 | 552.35 | 142 | 630 | 0 | 0 | 0 | 0
13:30 | 2496.5 | 1222.5 | 878.5 | 0 | 106 | 764.44 | 46 | 3322.5 | 507.645 | 142 | 556.1 | 0 | 0 | 0.5 | 0
14:00 | 2460 | 1187 | 878 | 0 | 102 | 765.88 | 46 | 3324 | 462.94 | 142 | 482.2 | 0 | 0 | 1 | 0
14:30 | 2493 | 1199 | 878.5 | 0 | 104 | 768.165 | 46 | 3237.5 | 402.105 | 142 | 414.5 | 0 | 0 | 1.5 | 0
15:00 | 2526 | 1211 | 879 | 0 | 106 | 770.45 | 46 | 3151 | 341.27 | 142 | 346.8 | 0 | 0 | 2 | 0
15:30 | 2525 | 1219 | 883.5 | 0 | 107 | 767.385 | 46 | 3024 | 256.98 | 142 | 322.3 | 0 | 0 | 1 | 0
16:00 | 2524 | 1227 | 888 | 0 | 108 | 764.32 | 46 | 2897 | 172.69 | 142 | 297.8 | 0 | 0 | 0 | 0
16:30 | 2513.5 | 1236 | 890.5 | 0 | 106 | 765.815 | 46 | 2924.5 | 103.625 | 142 | 493.9 | 0 | 0 | 0 | 0
17:00 | 2503 | 1245 | 893 | 0 | 104 | 767.31 | 46 | 2952 | 34.56 | 142 | 690 | 0 | 0 | 0 | 0
17:30 | 2553 | 1254 | 899 | 0 | 109 | 766.49 | 46 | 3118 | 17.28 | 154.5 | 1139.25 | 0 | 0 | 0 | 0
18:00 | 2603 | 1263 | 905 | 0 | 114 | 765.67 | 46 | 3284 | 0 | 167 | 1588.5 | 0 | 0 | 0 | 0
18:30 | 2568.5 | 1264 | 904.5 | 0 | 114 | 766.205 | 46 | 3377.5 | 0 | 153.5 | 1812.15 | 0 | 0 | 0 | 0
19:00 | 2534 | 1265 | 904 | 0 | 114 | 766.74 | 46 | 3471 | 0 | 140 | 2035.8 | 0 | 0 | 0 | 0
19:30 | 2519 | 1279 | 905 | 0 | 114 | 764.19 | 46 | 3538 | 0 | 99 | 2096.8 | 0 | 0 | 0 | 0
20:00 | 2484 | 1271 | 905 | 0 | 112 | 752.68 | 46 | 3541 | 0 | 101 | 1965 | 0 | 0 | 0 | 0
20:30 | 2489.5 | 1283 | 905 | 0 | 110 | 754.955 | 46 | 3578.5 | 0 | 101.5 | 1932 | 0 | 0 | 0 | 0
21:00 | 2495 | 1295 | 905 | 0 | 108 | 757.23 | 46 | 3616 | 0 | 102 | 1899 | 0 | 0 | 0 | 0
21:30 | 2481 | 1286 | 905 | 0 | 106 | 763.78 | 46 | 3607 | 0 | 68 | 1648.5 | 0 | 0 | 0 | 0
22:00 | 2467 | 1277 | 905 | 0 | 104 | 770.33 | 46 | 3598 | 0 | 34 | 1398 | 0 | 0 | 0 | 0
22:30 | 2473 | 1279 | 905 | 0 | 102 | 766.49 | 46 | 3607 | 0 | 17 | 1131.75 | 0 | 0 | 0.5 | 0
23:00 | 2479 | 1281 | 905 | 0 | 100 | 762.65 | 46 | 3616 | 0 | 0 | 865.5 | 0 | 0 | 1 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 17-01-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 426 | 03:00 | 396 | 12:00 | Madunaghat | 418 | 03:00 | 233 | 15:00
Amtali | 424 | 3:00 | 414 | 12:00 | Meghnaghat | 431 | 03:00 | 404 | 12:00
Ashuganj | 415 | 2:00 | 393 | 12:00 | Payra | 429 | 05:00 | 415 | 12:00
Bhulta | 408 | 02:00 | 385 | 12:00 | Rahanpur | 420 | 03:00 | 405 | 13:00
Bibiana | 424 | 01:00 | 408 | 12:00 | Rampal | 420 | 03:00 | 399 | 13:00
BIPTC | 400 | 00:00 | 386 | 10:00
Bogura | 418 | 03:00 | 397 | 12:00
Gopalganj | 425 | 03:00 | 404 | 12:00
Kaliakoir | 422 | 02:00 | 393 | 12:00
Korerhat | 426 | 02:00 | 410 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 248 | 03:00 | 229 | 12:00 | Kachua | 242 | 18:30 | 233 | 12:00
AKSML | 239 | 02:00 | 231 | 15:00 | Kaliakoir | 247 | 02:00 | 229 | 12:00
Aminbazar | 245 | 01:00 | 229 | 12:00 | Keranigonj | 245 | 02:00 | 226 | 12:00
Ashuganj | 240 | 03:00 | 230 | 12:00 | Khulna(S) | 248 | 03:00 | 232 | 12:00
Ashuganj-400 | 240 | 03:00 | 230 | 12:00 | Korerhat | 243 | 03:00 | 232 | 16:00
Baghabari | 240 | 04:00 | 231 | 12:00 | Madunaghat | 238 | 02:00 | 232 | 12:00
Barapukuria | 234 | 17:00 | 223 | 08:00 | Madunaghat-400 | 240 | 03:00 | 232 | 13:00
Barapukuria-230 | 234 | 17:00 | 223 | 08:00 | Maniknagar | 243 | 03:00 | 228 | 12:00
Barishal | 241 | 02:00 | 230 | 12:00 | Meghnaghat | 250 | 03:00 | 235 | 12:00
Bheramara | 239 | 05:00 | 225 | 13:00 | Meghnaghat-400 | 244 | 02:00 | 229 | 12:00
Bhulta | 245 | 02:00 | 230 | 12:00 | Mirsorai | 242 | 02:00 | 232 | 12:00
Bibiana | 244 | 04:00 | 234 | 12:00 | Rajshahi | 240 | 05:00 | 226 | 13:00
BIPTC | 243 | 03:00 | 227 | 13:00 | Rampal | 244 | 03:00 | 229 | 13:00
Bogura | 245 | 05:00 | 233 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 243 | 03:00 | 232 | 12:00 | Rampura | 245 | 03:00 | 230 | 12:00
Borhanuddin | 242 | 06:00 | 235 | 12:00 | Shikalbaha | 238 | 18:00 | 231 | 12:00
BSRM | 243 | 03:00 | 232 | 12:00 | Shyampur | 245 | 03:00 | 227 | 12:00
Cumilla(N) | 239 | 00:00 | 230 | 12:00 | Siddhirganj | 245 | 01:00 | 231 | 12:00
Faridpur | 240 | 02:00 | 228 | 12:00 | Sirajgonj | 247 | 04:00 | 237 | 12:00
Fenchuganj | 246 | 02:00 | 239 | 12:00 | Sreepur | 238 | 02:00 | 228 | 08:00
Feni | 243 | 03:00 | 232 | 12:00 | Tongi | 244 | 20:00 | 227 | 15:00
Ghorashal | 245 | 01:00 | 240 | 09:00
Ghorashal-230 | 238 | 18:30 | 216 | 12:00
Gopalganj | 238 | 02:00 | 227 | 12:00
GPH | 240 | 02:00 | 232 | 12:00
Haripur | 246 | 02:00 | 231 | 12:00
Hasnabad | 243 | 00:00 | 227 | 12:00
Hathazari | 237 | 05:00 | 228 | 16:00
Ishurdi | 245 | 03:00 | 231 | 13:00
Jhenaidah | 243 | 03:00 | 227 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 03:00 | 126 | 12:00 | Laksam | 140 | 03:00 | 134 | 12:00
Agargaon | 138 | 22:00 | 128 | 12:00 | Lakshmipur | 136 | 02:00 | 130 | 12:00
Agrabad | 139 | 02:00 | 133 | 15:00 | Lalbag | 139 | 04:00 | 126 | 12:00
AKS | 136 | 01:00 | 132 | 12:00 | Lalmonirhat | 132 | 01:00 | 122 | 13:00
Aminbazar | 140 | 00:00 | 130 | 12:00 | Madanganj | 137 | 18:00 | 133 | 13:00
Amnura | 139 | 02:00 | 131 | 12:00 | Madaripur | 141 | 04:00 | 136 | 12:00
Ashuganj | 140 | 01:00 | 135 | 10:00 | Madartek | 135 | 02:00 | 126 | 12:00
Bagerhat | 137 | 02:00 | 123 | 13:00 | Madunaghat | 139 | 02:00 | 135 | 12:00
Bajitpur | 135 | 01:00 | 130 | 12:00 | Magura | 140 | 02:00 | 128 | 13:00
Bakerganj | 140 | 18:30 | 135 | 12:00 | Mahasthangarh | 138 | 05:00 | 130 | 13:00
Bakulia | 140 | 04:00 | 134 | 12:00 | Maijdee | 136 | 02:00 | 130 | 12:00
Banani | 137 | 04:00 | 126 | 12:00 | Manikganj | 134 | 04:00 | 120 | 12:00
Bangabhaban | 141 | 03:00 | 128 | 12:00 | Maniknagar | 141 | 04:00 | 128 | 12:00
Barapukuria | 140 | 19:30 | 125 | 13:00 | Matarbari | 132 | 05:00 | 125 | 18:00
Barguna | 141 | 18:30 | 135 | 12:00 | Matuail | 140.5 | 02:00 | 132 | 12:00
Barishal | 141 | 04:00 | 135 | 15:00 | Metrorail_Motijheel | 141 | 04:00 | 128 | 12:00
Barishal-230 | 142 | 02:00 | 134 | 12:00 | Metrorail_Uttara | 140 | 03:00 | 129 | 12:00
Baroaulia | 140 | 09:00 | 134 | 12:00 | Millgate | 137 | 02:00 | 121 | 12:00
Baroirhat | 136 | 00:00 | 131 | 12:00 | Mirpur | 139 | 02:00 | 129 | 12:00
Bashundhara | 136 | 01:00 | 126 | 12:00 | Mirzapur | 139 | 03:00 | 130 | 07:00
BashundharaCement | 137 | 18:00 | 133 | 13:00 | Mithapukur | 138 | 05:00 | 126 | 13:00
Beanibazar | 134 | 02:00 | 129 | 12:00 | MI_Cement | 138 | 06:00 | 126 | 12:00
Benapole | 138 | 01:00 | 124 | 12:00 | Modern | N/A | N/A | N/A | N/A
Bhaluka | 137 | 09:00 | 120 | 22:00 | Mogbazar | 137 | 01:00 | 128 | 12:00
Bhandaria | 140 | 02:00 | 130 | 18:30 | Mongla | 138 | 03:00 | 123 | 12:00
Bhangura | 140 | 03:00 | 132 | 10:00 | Motijheel | 141 | 03:00 | 128 | 12:00
Bheramara | 141 | 03:00 | 136 | 12:00 | Muktagacha | 133 | 10:00 | 126 | 18:00
Bheramara(GK) | 142 | 05:00 | 135 | 12:00 | Munshiganj | 138 | 00:00 | 130 | 12:00
Bhulta | 135 | 03:00 | 130 | 12:00 | Muradnagar | 140 | 02:00 | 132 | 12:00
Bog-Sherpur | 140 | 05:00 | 131 | 13:00 | Mymensingh | 133 | 09:00 | 119 | 08:00
Bogura | 139 | 19:00 | 132 | 12:00 | Naogaon | 135 | 02:00 | 127 | 13:00
Bogura-230 | 139 | 03:00 | 132 | 13:00 | Narail | 140 | 01:00 | 128 | 13:00
Brahmanbaria | 133 | 03:00 | 126 | 12:00 | Narinda | 134 | 04:00 | 120 | 12:00
Cantonment | 140 | 02:00 | 127 | 12:00 | Narshingdi | 139 | 02:00 | 122 | 12:00
Chandina | 141 | 02:00 | 134 | 12:00 | Natore | 138 | 03:00 | 131 | 13:00
Chandpur | 140 | 21:00 | 133 | 12:00 | Nawabganj | 139 | 03:00 | 126 | 12:00
Chandraghona | 139 | 00:00 | 135 | 04:00 | Netrakona | 128 | 10:00 | 113 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 139 | 03:00 | 134 | 08:00 | New | 137 | 02:00 | 122 | 12:00
Charsaidpur | 140 | 05:00 | 131 | 12:00 | Niamatpur | 140 | 03:00 | 135 | 08:00
Chauddagram | 138 | 01:00 | 132 | 12:00 | Noapara | 139 | 05:00 | 126 | 13:00
Chhatak | 134 | 03:00 | 126 | 12:00 | Pabna | 141 | 03:00 | 134 | 12:00
Chowmuhani | 135 | 18:30 | 129 | 12:00 | Palashbari | 137 | 19:30 | 125 | 12:00
Chuadanga | 138 | 04:00 | 126 | 13:00 | Panchagarh | 140 | 17:00 | 128 | 12:00
Coxsbazar | 131 | 18:30 | 126 | 18:00 | Patiya | 139 | 03:00 | 134 | 12:00
Cumilla(N) | 140 | 00:00 | 134 | 12:00 | Patuakhali | 140 | 18:30 | 134 | 12:00
Cumilla(S) | 138 | 00:00 | 125 | 18:00 | Payra | 140 | 01:00 | 136 | 13:00
Daganbhuiyan | 137 | 03:00 | 131 | 12:00 | PHP | 136 | 01:00 | 130 | 12:00
Daudkandi | 137 | 02:00 | 129 | 12:00 | Postogola | 139 | 02:00 | 128 | 12:00
DhakaUniversity | 136 | 01:00 | 126 | 12:00 | Purbachal | 136 | 01:00 | 126 | 12:00
Dhamrai | 138 | 00:00 | 130 | 15:00 | Purbasadipur | 135 | 19:00 | 126 | 11:00
Dhanmondi | 141 | 04:00 | 133 | 12:00 | Rahanpur | 141 | 04:00 | 136 | 07:00
Dohazari | 136 | 08:00 | 132 | 15:00 | Rahanpur-400 | 141 | 02:00 | 135 | 13:00
Faridpur | 140 | 03:00 | 131 | 12:00 | Rahim | 139 | 01:00 | 132 | 09:00
Fatullah | 141 | 02:00 | 125 | 12:00 | Rajbari | 139 | 02:00 | 130 | 12:00
Fenchuganj | 139 | 03:00 | 135 | 13:00 | Rajendrapur | 135 | 05:00 | 124 | 15:00
Feni | 134 | 03:00 | 130 | 12:00 | Rajshahi | 138 | 01:00 | 131 | 13:00
Feni-230 | 137 | 03:00 | 130 | 12:00 | Rajshahi-230 | 139 | 05:00 | 130 | 13:00
Ghatail | 134 | 03:00 | 122 | 18:00 | Ramganj | 136 | 01:00 | 131 | 12:00
Ghorashal | 136 | 05:00 | 130 | 11:00 | Rampur | 139 | 02:00 | 133 | 11:00
Goalpara | 140 | 02:00 | 128 | 12:00 | Rampura | 136 | 02:00 | 126 | 12:00
Gollamari | 139 | 03:00 | 129 | 12:00 | Rangamati | 139 | 04:00 | 134 | 12:00
Gopalganj | 142 | 04:00 | 132 | 12:00 | Rangpur | 138 | 19:30 | 124 | 12:00
Gopalganj-400 | 144 | 02:00 | 137 | 12:00 | Ruppur | 142 | 03:00 | 136 | 12:00
Gulshan | 134 | 00:00 | 126 | 12:00 | Saidpur | 138 | 18:00 | 125 | 11:00
Halishahar | 141 | 18:30 | 134 | 12:00 | Satkhira | 137 | 02:00 | 125 | 13:00
Haripur | 140 | 01:00 | 132 | 12:00 | Satmasjid | 140 | 02:00 | 128 | 12:00
HaripurSBU | 140 | 01:00 | 133 | 13:00 | Savar | 141 | 22:00 | 129 | 12:00
Hasnabad | 138 | 01:00 | 128 | 12:00 | SevenRings | 134 | 02:00 | 128 | 12:00
Hathazari | 140 | 05:00 | 135 | 12:00 | ShahCement | 140 | 05:00 | 131 | 12:00
Hatirjheel | 136 | 01:00 | 126 | 12:00 | Shahjadpur | 140 | 00:00 | 135 | 12:00
Ishurdi | 144 | 05:00 | 137 | 12:00 | Shahjibazar | 133 | 01:00 | 129 | 12:00
Jaldhaka | 135 | 20:00 | 124 | 13:00 | Shahmirpur | 140 | 18:00 | 134 | 15:00
Jamalpur | 132 | 10:00 | 123 | 07:00 | Shariatpur | 142 | 02:00 | 134 | 13:00
Jashore | 137 | 00:00 | 127 | 13:00 | Sherpur | 129 | 09:00 | 120 | 00:00
Jhenaidah | 140 | 04:00 | 126 | 08:00 | Shikalbaha | 128 | 03:00 | 123 | 16:00
Jhenaidah-230 | 142 | 04:00 | 130 | 13:00 | Shikalbaha-230 | 140 | 01:00 | 135 | 16:00
Joydebpur | 132 | 01:00 | 124 | 12:00 | Shitalakhya | 139 | 02:00 | 126 | 12:00
Joypurhat | 135 | 04:00 | 126 | 13:00 | Sholosohor | 139 | 01:00 | 135 | 12:00
Juldah | 139 | 21:00 | 135 | 12:00 | Shyampur | 140 | 02:00 | 133 | 11:00
Kabirpur | 140 | 22:00 | 118 | 15:00 | Shyampur-230 | 142 | 03:00 | 131 | 12:00
Kachua | 139 | 00:00 | 134 | 12:00 | Siddhirganj | 140 | 01:00 | 132 | 12:00
Kaliakoir | 143 | 02:00 | 133 | 15:00 | Sirajganj | 138 | 04:00 | 131 | 12:00
Kallyanpur | 140 | 21:00 | 131 | 15:00 | Sonargaon | 136 | 00:00 | 131 | 12:00
Kalurghat | 139 | 02:00 | 135 | 12:00 | Sreemongol | 134 | 04:00 | 130 | 12:00
Kamrangirchar | 138 | 01:00 | 126 | 12:00 | Sreepur | 138 | 10:00 | 129 | 08:00
Kaptai | 141 | 6:00 | 137 | 13:00 | Srinagar | 139 | 03:00 | 126 | 12:00
Kasba | 140 | 02:00 | 132 | 12:00 | SSM | 142 | 00:00 | 140 | 08:00
Kazla | 140 | 02:00 | 127 | 13:00 | Sunamganj | 132 | 04:00 | 116 | 16:00
Keranigonj | 139 | 02:00 | 126 | 12:00 | Sylhet | 134 | 02:00 | 129 | 13:00
Khagrachori | 138 | 01:00 | 133 | 13:00 | Sylhet-132 | 133 | 00:00 | 129 | 12:00
Khulna | 137 | 03:00 | 126 | 13:00 | Tangail | 134 | 05:00 | 123 | 18:00
Khulna(S) | 140 | 03:00 | 129 | 12:00 | Taraganj | 137 | 19:30 | 126 | 10:00
Khulshi | 138 | 02:00 | 132 | 12:00 | Tasnim | 139 | 01:00 | 131 | 12:00
Kishoreganj | 135 | 17:00 | 127 | 08:00 | Thakurgaon | 140 | 20:00 | 126 | 12:00
Kodda | 138 | 02:00 | 126 | 12:00 | TK | 138 | 00:00 | 134 | 12:00
KSRM | 140 | 20:00 | 134 | 14:00 | Tongi | 137 | 01:00 | 127 | 15:00
Kulaura | 138 | 02:00 | 134 | 12:00 | Ullahpara | 139 | 01:00 | 133 | 08:00
Kurigram | 132 | 18:00 | 119 | 13:00 | Ullon | 136 | 02:00 | 126 | 12:00
Kushtia | 141 | 04:00 | 134 | 08:00 | Uttara | 136 | 01:00 | 120 | 12:00
Zigatola | 139 | 03:00 | 126 | 12:00 | UttaraNew | 140 | 03:00 | 129 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division