## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 18-01-2026 | [28 empty] | Date: | 18-01-2026 | [28 empty] | Date: | 18-01-2026 | [28 empty] | Date: | 18-01-2026 | [28 empty] | Date: | 18-01-2026 | [17 empty] | Date: | 18-01-2026
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [17 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 47.4 | 0 | 95 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 395 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 38 | 0 | 46 | 0 | 30 | 355 | 0 | 0 | 0 | 0 | 50 | 182 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 220 | 300 | 0 | 51 | 0 | 186 | 0 | 0 | 80 | 51 | 0 | 13 | 0 | 98 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 52 | 156 | 0 | 17 | 0 | 81 | 30 | 0 | 0 | 99 | 0 | 16 | 0 | 72 | 0 | 0 | 0 | 4936.4 | 905 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 0 | 0 | 760.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 130 | 220 | 0 | 0 | 622 | 0 | 4611.78 | 9548.18 | 96.34
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 27 | 355 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 978 | 0 | 0 | 0 | 220 | 310 | 0 | 51 | 0 | 191 | 0 | 0 | 80 | 0 | 0 | 13 | 0 | 86 | 0 | 0 | 0 | 305 | 0 | 0 | 42 | 52 | 158 | 0 | 17 | 0 | 81 | 30 | 0 | 0 | 99 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 4404 | 905 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 0 | 0 | 0 | 752.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 130 | 220 | 0 | 0 | 500 | 0 | 4431.34 | 8835.34 | 96.34
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 37 | 355 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 950 | 0 | 0 | 0 | 220 | 300 | 0 | 51 | 0 | 185 | 0 | 0 | 80 | 0 | 0 | 11 | 0 | 84 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 52 | 160 | 0 | 17 | 0 | 81 | 30 | 0 | 0 | 99 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 4380 | 905 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 830 | 0 | 0 | 0 | 761.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 130 | 220 | 0 | 0 | 400 | 0 | 4000.61 | 8380.61 | 96.34
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 32 | 355 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 898 | 0 | 0 | 0 | 220 | 310 | 0 | 51 | 0 | 189 | 0 | 0 | 80 | 0 | 0 | 11 | 0 | 86 | 0 | 0 | 0 | 320 | 0 | 0 | 42 | 52 | 159 | 0 | 17 | 0 | 81 | 30 | 0 | 0 | 99 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 4345 | 905 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 768 | 0 | 0 | 0 | 637.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 130 | 220 | 0 | 0 | 300 | 0 | 3719.99 | 8064.99 | 96.33
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 38 | 355 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 855 | 0 | 0 | 0 | 220 | 320 | 0 | 51 | 0 | 204 | 0 | 0 | 80 | 0 | 0 | 11 | 0 | 80 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 52 | 163 | 0 | 17 | 0 | 31 | 30 | 0 | 0 | 99 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 4281 | 905 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 0 | 0 | 0 | 453.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 130 | 220 | 0 | 0 | 300 | 0 | 3554.78 | 7835.78 | 96.33
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 37 | 355 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 950 | 0 | 0 | 0 | 230 | 300 | 0 | 51 | 0 | 189 | 0 | 0 | 80 | 0 | 0 | 11 | 0 | 74 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 52 | 161 | 0 | 17 | 0 | 31 | 30 | 0 | 0 | 98 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 4335 | 905 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 786 | 0 | 0 | 0 | 443.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 130 | 220 | 0 | 0 | 330 | 0 | 3572.09 | 7907.09 | 96.33
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 39 | 355 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 1072 | 0 | 0 | 0 | 230 | 305 | 0 | 51 | 0 | 196 | 0 | 0 | 80 | 0 | 0 | 11 | 0 | 84 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 52 | 158 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 4488 | 905 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 826 | 0 | 0 | 0 | 525.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 130 | 220 | 0 | 0 | 410 | 0 | 3823.28 | 8311.28 | 96.33
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 5 | 240 | 0 | 0 | 1 | 5 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0.06 | 46 | 0 | 37 | 355 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 1152 | 1 | 0 | 0 | 220 | 335 | 0 | 51 | 0 | 183 | 0 | 0 | 80 | 0 | 0 | 11 | 0 | 84 | 0 | 2 | 0 | 320 | 0 | 0 | 41 | 52 | 163 | 0 | 17 | 0 | 78 | 30 | 0 | 0 | 100 | 0 | 5 | 3 | 64 | 0 | 0.63 | 0 | 4660.69 | 905 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.61 | 1028 | 0 | 0 | 0 | 679.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51 | 0 | 0 | 0 | 0.48 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.01 | 0 | 295 | 130 | 220 | 0 | 0 | 496 | 0 | 4353.33 | 9014.02 | 96.32
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 30 | 0 | 44 | 0 | 145 | 0 | 52 | 147 | 0 | 0 | 0 | 465 | 0 | 55 | 240 | 0 | 0 | 5 | 70 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 38 | 0.81 | 46 | 0 | 12 | 355 | 0 | 0 | 1 | 0 | 57 | 182 | 0 | 0 | 0 | 1155 | 7 | 47 | 0 | 215 | 280 | 0 | 51 | 0 | 180 | 0 | 0 | 80 | 41 | 0 | 11 | 0 | 104 | 0 | 17 | 0 | 320 | 0 | 0 | 42 | 52 | 160 | 2 | 17 | 0 | 78 | 30 | 0 | 0 | 100 | 0 | 57 | 18 | 63 | 0 | 8.22 | 5 | 5495.03 | 905 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.43 | 1130 | 0 | 0 | 0 | 761.08 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 7.57 | 16 | 0 | 0 | 8.2 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83 | 0 | 55 | 50 | 5 | 49 | 0 | 0 | 0 | 0.9 | 27 | 0.09 | 0 | 307 | 130 | 220 | 0 | 0 | 575 | 0 | 4813.1 | 10308.13 | 96.32
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 49 | 0 | 140 | 0 | 195 | 4 | 55 | 146 | 0 | 0 | 0 | 385 | 0 | 55 | 280 | 0 | 0 | 13 | 35 | 21 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 38 | 1.79 | 46 | 0 | 7 | 355 | 0 | 0 | 18 | 0 | 103 | 182 | 0 | 0 | 0 | 1075 | 12 | 60 | 0 | 220 | 275 | 0 | 51 | 0 | 200 | 0 | 0 | 80 | 97 | 0 | 13 | 0 | 96 | 0 | 36 | 0 | 310 | 0 | 0 | 42 | 52 | 154 | 6 | 17 | 0 | 78 | 30 | 0 | 0 | 100 | 0 | 57 | 19 | 63 | 1 | 20.41 | 18 | 5686.2 | 905 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.82 | 1121 | 0 | 0 | 0 | 765.66 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 20.98 | 40 | 0 | 0 | 23.23 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.17 | 0 | 55 | 90 | 13 | 80 | 0 | 0 | 0 | 2.6 | 69 | 0.22 | 0 | 274 | 115 | 180 | 0 | 0 | 580 | 0 | 4950.68 | 10636.88 | 96.32
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 46.8 | 0 | 105 | 0 | 160 | 14 | 35 | 72 | 0 | 0 | 0 | 320 | 0 | 35 | 250 | 0 | 0 | 19 | 35 | 27 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 25 | 2.58 | 46 | 0 | 7 | 355 | 0 | 0 | 19 | 0 | 34 | 182 | 0 | 0 | 0 | 1065 | 16 | 40 | 0 | 220 | 280 | 0 | 51 | 0 | 183 | 0 | 0 | 80 | 64 | 0 | 13 | 0 | 101 | 0 | 51 | 0 | 310 | 0 | 0 | 42 | 52 | 138 | 8 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 57 | 19 | 64 | 1 | 31.24 | 18 | 5291.62 | 904 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 1091 | 0 | 0 | 0 | 761.08 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 32.83 | 63 | 0 | 0 | 36.75 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 54 | 50 | 21 | 70 | 0 | 0 | 0 | 3.9 | 109 | 0.34 | 0 | 268 | 115 | 220 | 0 | 0 | 520 | 17 | 4950.2 | 10241.82 | 96.32
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 49.6 | 0 | 88 | 0 | 130 | 15 | 35 | 67 | 0 | 0 | 0 | 385 | 0 | 35 | 250 | 0 | 0 | 23 | 35 | 27 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 24 | 25 | 3.06 | 46 | 0 | 7 | 355 | 0 | 0 | 19 | 0 | 34 | 183 | 0 | 0 | 0 | 1020 | 18 | 40 | 0 | 220 | 280 | 0 | 51 | 0 | 180 | 0 | 0 | 80 | 67 | 0 | 13 | 0 | 99 | 0 | 59 | 0 | 315 | 0 | 0 | 42 | 52 | 147 | 10 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 59 | 19 | 60 | 2 | 37.31 | 22 | 5318.97 | 905 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 1084 | 0 | 0 | 0 | 757.8 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 40.2 | 79 | 0 | 0 | 47.02 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.06 | 0 | 54 | 50 | 27 | 70 | 0 | 0 | 0 | 5 | 128 | 0.43 | 0 | 277 | 130 | 220 | 0 | 0 | 520 | 17 | 5047.51 | 10366.48 | 96.31
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 50 | 0 | 92 | 0 | 152 | 15 | 50 | 105 | 0 | 0 | 0 | 395 | 0 | 40 | 250 | 0 | 0 | 25 | 52 | 25.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 40 | 25 | 3.21 | 46 | 0 | 8 | 355 | 0 | 0 | 19 | 0 | 35 | 183 | 0 | 0 | 0 | 1170 | 19 | 55 | 0 | 220 | 280 | 0 | 51 | 0 | 200 | 0 | 0 | 80 | 72 | 0 | 13 | 0 | 102 | 0 | 63 | 0 | 320 | 0 | 0 | 42 | 52 | 163 | 10 | 17 | 0 | 78 | 30 | 0 | 0 | 100 | 0 | 59 | 19 | 29 | 2 | 39.54 | 24 | 5648.25 | 905 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 1108 | 0 | 0 | 0 | 764.29 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 43.82 | 86 | 0 | 0 | 50.12 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 0 | 0 | 50 | 30 | 70 | 0 | 0 | 0 | 5.2 | 143 | 0.49 | 0 | 277 | 130 | 220 | 0 | 0 | 570 | 42 | 5151.32 | 10799.57 | 96.31
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 50.5 | 0 | 110 | 0 | 175 | 25 | 54 | 120 | 0 | 0 | 0 | 410 | 0 | 55 | 250 | 0 | 0 | 25 | 52 | 17.5 | 14 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 60 | 25 | 3.09 | 46 | 0 | 10 | 355 | 0 | 0 | 19 | 0 | 57 | 183 | 0 | 0 | 0 | 1155 | 17 | 100 | 0 | 220 | 280 | 0 | 51 | 0 | 190 | 0 | 9 | 80 | 127 | 0 | 13 | 0 | 103 | 0 | 60 | 0 | 325 | 0 | 0 | 42 | 52 | 162 | 3 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 59 | 19 | 31 | 2 | 38.14 | 24 | 5868.23 | 905 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 1120 | 0 | 0 | 0 | 761.5 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 42.95 | 83 | 0 | 0 | 47.15 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 0 | 0 | 70 | 29 | 107 | 0 | 0 | 0 | 5 | 134 | 0.45 | 0 | 307 | 130 | 220 | 0 | 0 | 600 | 54 | 5289.25 | 11157.48 | 96.31
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 49 | 0 | 120 | 0 | 95 | 15 | 55 | 86 | 0 | 0 | 0 | 405 | 0 | 55 | 250 | 0 | 0 | 21 | 90 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 8 | 0 | 0 | 25 | 2.63 | 46 | 0 | 9 | 355 | 0 | 0 | 0 | 0 | 66 | 184 | 0 | 0 | 0 | 1195 | 16 | 10 | 0 | 220 | 280 | 0 | 51 | 0 | 190 | 0 | 12 | 80 | 100 | 0 | 13 | 0 | 109 | 0 | 52 | 0 | 315 | 0 | 0 | 42 | 52 | 159 | 8 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 60 | 19 | 31 | 1.2 | 32.32 | 24 | 5613.15 | 899 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 1112 | 0 | 0 | 0 | 763 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 34.75 | 68 | 0 | 0 | 35.41 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.07 | 0 | 0 | 70 | 25 | 107 | 0 | 0 | 0 | 4.2 | 112 | 0.4 | 0 | 307 | 130 | 220 | 0 | 0 | 622 | 0 | 5140.83 | 10753.98 | 96.31
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 50.2 | 0 | 120 | 0 | 95 | 15 | 55 | 88 | 0 | 0 | 0 | 410 | 0 | 55 | 250 | 0 | 0 | 16 | 90 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 8 | 0 | 0 | 25 | 1.77 | 46 | 0 | 3 | 355 | 0 | 0 | 0 | 0 | 17 | 187 | 0 | 0 | 0 | 1155 | 13 | 10 | 0 | 220 | 280 | 0 | 51 | 0 | 190 | 0 | 0 | 80 | 17 | 0 | 13 | 0 | 107 | 0 | 35 | 0 | 320 | 0 | 0 | 42 | 52 | 157 | 6 | 17 | 0 | 77 | 30 | 0 | 0 | 99 | 0 | 60 | 18 | 31 | 1 | 24.33 | 24 | 5403.3 | 874 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 1120 | 0 | 0 | 0 | 764 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 10 | 0 | 21.95 | 49 | 0 | 0 | 26.41 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.12 | 0 | 0 | 70 | 17 | 80 | 0 | 0 | 0 | 3 | 74 | 0.27 | 0 | 283 | 127 | 220 | 0 | 0 | 560 | 0 | 4910.75 | 10314.05 | 96.3
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 50.2 | 0 | 120 | 0 | 45 | 15 | 55 | 86 | 0 | 0 | 0 | 410 | 0 | 55 | 250 | 0 | 0 | 7 | 90 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 0 | 0 | 25 | 0.85 | 46 | 0 | 9 | 355 | 0 | 0 | 0 | 0 | 14 | 186 | 0 | 0 | 0 | 1190 | 7 | 10 | 0 | 220 | 280 | 0 | 51 | 0 | 190 | 0 | 0 | 80 | 17 | 0 | 13 | 0 | 110 | 0 | 19 | 0 | 320 | 0 | 0 | 42 | 52 | 158 | 2 | 17 | 0 | 74 | 30 | 0 | 0 | 99 | 0 | 59 | 18 | 31 | 0 | 12.06 | 20 | 5338.11 | 872 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 1075 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 15 | 0 | 9.71 | 22 | 0 | 0 | 12.38 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.25 | 0 | 0 | 35 | 10 | 49 | 0 | 0 | 0 | 1.6 | 35 | 0.13 | 0 | 281 | 127 | 220 | 0 | 0 | 554 | 0 | 4654.07 | 9992.18 | 96.3
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 50.2 | 0 | 120 | 0 | 90 | 15 | 55 | 121 | 0 | 0 | 0 | 415 | 0 | 55 | 250 | 0 | 0 | 2 | 90 | 24 | 14 | 0 | 0 | 0 | 15 | 0 | 0 | 4 | 0 | 8 | 0 | 12 | 25 | 0.1 | 46 | 1 | 15 | 355 | 0 | 0 | 9 | 0 | 28 | 186 | 0 | 0 | 0 | 1160 | 1 | 38 | 0 | 220 | 280 | 0 | 51 | 0 | 190 | 0 | 0 | 80 | 58 | 0 | 13 | 0 | 104 | 0 | 4 | 0 | 315 | 0 | 0 | 42 | 52 | 155 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 99 | 0 | 59 | 18 | 33 | 0 | 1.95 | 12 | 5488.25 | 873 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 1090 | 17 | 0 | 0 | 767 | 0 | 0 | 0 | 25 | 35 | 0 | 0 | 20 | 0 | 2.38 | 5 | 0 | 0 | 1.92 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19 | 0 | 0 | 35 | 2 | 70 | 0 | 0 | 0 | 0.3 | 8 | 0.03 | 0 | 278 | 127 | 180 | 0 | 0 | 545 | 16 | 4639.82 | 10128.07 | 96.3
18:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 50.6 | 16 | 128 | 0 | 295 | 15 | 55 | 150 | 0 | 0 | 0 | 420 | 0 | 55 | 300 | 0 | 0 | 0 | 90 | 23.5 | 14 | 0 | 0 | 12 | 15 | 0 | 0 | 3 | 29 | 8 | 7 | 12 | 38 | 0 | 46 | 16 | 7 | 355 | 16 | 0 | 18 | 0 | 104 | 185 | 0 | 0 | 0 | 1175 | 0 | 127 | 0 | 220 | 280 | 0 | 51 | 0 | 190 | 0 | 2 | 80 | 120 | 0 | 11 | 0 | 106 | 0 | 0 | 25 | 325 | 0 | 0 | 42 | 52 | 145 | 0 | 21 | 0 | 80 | 30 | 0 | 0 | 100 | 12 | 59 | 18 | 33 | 0 | 0 | 12 | 6174.1 | 873 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1121 | 17 | 0 | 0 | 766 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 530 | 53 | 4846 | 11020.1 | 96.3
19:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 51.3 | 17 | 149 | 0 | 298 | 15 | 55 | 154 | 0 | 0 | 0 | 465 | 0 | 55 | 300 | 0 | 0 | 0 | 90 | 23 | 14 | 0 | 0 | 17 | 15 | 0 | 0 | 4 | 51 | 8 | 17 | 50 | 38 | 0 | 46 | 16 | 16 | 355 | 16 | 0 | 19 | 0 | 101 | 186 | 0 | 0 | 0 | 1160 | 0 | 133 | 0 | 220 | 280 | 0 | 51 | 0 | 190 | 0 | 16 | 80 | 154 | 0 | 11 | 0 | 110 | 0 | 0 | 25 | 320 | 0 | 0 | 42 | 52 | 160 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 17 | 59 | 19 | 34 | 0 | 0 | 12 | 6381.3 | 873 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1129 | 17 | 0 | 0 | 754 | 0 | 0 | 0 | 35 | 70 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 307 | 130 | 220 | 0 | 0 | 528 | 54 | 4909 | 11290.3 | 96.3
19:30 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 51.3 | 17 | 149 | 0 | 298 | 15 | 55 | 145 | 0 | 0 | 0 | 460 | 0 | 55 | 300 | 0 | 0 | 0 | 90 | 23 | 14 | 0 | 0 | 15 | 15 | 0 | 0 | 5 | 51 | 8 | 17 | 50 | 38 | 0 | 46 | 17 | 19 | 355 | 16 | 0 | 19 | 0 | 100 | 185 | 0 | 0 | 0 | 1224 | 0 | 142 | 0 | 220 | 280 | 0 | 51 | 0 | 180 | 0 | 15 | 80 | 155 | 0 | 6 | 0 | 110 | 0 | 0 | 17 | 325 | 0 | 0 | 42 | 52 | 163 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 100 | 17 | 59 | 19 | 34 | 0 | 0 | 12 | 6460.3 | 872 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1136 | 17 | 0 | 0 | 756 | 0 | 0 | 0 | 35 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 130 | 220 | 0 | 0 | 531 | 54 | 4950 | 11410.3 | 96.3
20:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 50.7 | 17 | 149 | 0 | 298 | 15 | 55 | 143 | 0 | 0 | 0 | 465 | 0 | 55 | 300 | 0 | 0 | 0 | 90 | 23 | 14 | 0 | 0 | 17 | 15 | 0 | 0 | 6 | 51 | 8 | 17 | 50 | 38 | 0 | 46 | 15 | 23 | 355 | 16 | 0 | 19 | 0 | 103 | 185 | 0 | 0 | 0 | 1224 | 0 | 143 | 0 | 220 | 280 | 0 | 51 | 0 | 180 | 0 | 15 | 80 | 154 | 0 | 11 | 0 | 106 | 0 | 0 | 17 | 320 | 0 | 0 | 42 | 52 | 162 | 0 | 21 | 0 | 77 | 30 | 0 | 0 | 100 | 17 | 59 | 19 | 34 | 0 | 0 | 12 | 6490.7 | 873 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1125 | 17 | 0 | 0 | 763 | 0 | 0 | 0 | 35 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 130 | 220 | 0 | 0 | 531 | 54 | 4943 | 11433.7 | 96.29
21:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 50.2 | 17 | 149 | 0 | 298 | 15 | 55 | 157 | 0 | 0 | 0 | 440 | 0 | 55 | 270 | 0 | 0 | 0 | 52 | 23 | 14 | 0 | 0 | 16 | 15 | 0 | 0 | 3 | 51 | 8 | 0 | 50 | 38 | 0 | 46 | 15 | 25 | 355 | 0 | 0 | 19 | 0 | 102 | 186 | 0 | 0 | 0 | 1224 | 0 | 138 | 0 | 220 | 280 | 0 | 51 | 0 | 180 | 0 | 16 | 80 | 152 | 0 | 11 | 0 | 112 | 0 | 0 | 9 | 315 | 0 | 0 | 42 | 52 | 160 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 100 | 17 | 59 | 19 | 34 | 0 | 0 | 12 | 6304.2 | 873 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1121 | 17 | 0 | 0 | 762.56 | 0 | 0 | 0 | 35 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 530 | 53 | 4909.56 | 11213.76 | 96.29
22:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 48.8 | 0 | 149 | 0 | 298 | 0 | 55 | 156 | 0 | 0 | 0 | 400 | 0 | 55 | 270 | 0 | 0 | 0 | 35 | 23 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 38 | 0 | 46 | 0 | 30 | 355 | 0 | 0 | 0 | 0 | 96 | 186 | 0 | 0 | 0 | 1224 | 0 | 140 | 0 | 220 | 280 | 0 | 51 | 0 | 180 | 0 | 0 | 80 | 150 | 0 | 11 | 0 | 98 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 52 | 155 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 100 | 0 | 59 | 19 | 34 | 0 | 0 | 12 | 5953.8 | 872 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1113 | 0 | 0 | 0 | 759.44 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 527 | 49 | 4830.44 | 10784.24 | 96.29
23:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 47.4 | 0 | 149 | 0 | 260 | 0 | 35 | 150 | 0 | 0 | 0 | 395 | 0 | 35 | 270 | 0 | 0 | 0 | 0 | 17.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 38 | 0 | 46 | 0 | 24 | 355 | 0 | 0 | 0 | 0 | 94 | 185 | 0 | 0 | 0 | 1224 | 0 | 142 | 0 | 220 | 280 | 0 | 51 | 0 | 180 | 0 | 0 | 80 | 146 | 0 | 11 | 0 | 96 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 52 | 155 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 100 | 0 | 59 | 19 | 34 | 0 | 0 | 12 | 5802.9 | 452 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 0 | 0 | 0 | 756.08 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 525 | 48 | 4346.08 | 10148.98 | 96.28
Total KWH | 0 | 142080 | 45600 | 0 | 0 | 0 | 0 | 0 | 8445600 | 0 | 0 | 839160 | 0 | 2110464 | 0 | 3126578 | 222985 | 825791 | 2082240 | 0 | 0 | 0 | 9787273 | 0 | 833995 | 6211885 | 0 | 0 | 155970 | 1014000 | 488400 | 337320 | 0 | 0 | 71509 | 90327 | 0 | 0 | 72480 | 171428 | 91370 | 51583 | 390720 | 523200 | 20160 | 1100820 | 86981 | 494400 | 8581818.18 | 43491 | 0 | 194880 | 0 | 1244509 | 4428813 | 0 | 0 | 0 | 26585452 | 122445 | 1497090 | 0 | 5434000 | 7313000 | 0 | 1237211 | 0 | 4685000 | 0 | 101760 | 1935616 | 1756320 | 0 | 291540 | 0 | 2315520 | 0 | 400409 | 56160 | 7705000 | 0 | 0 | 995000 | 1300560 | 3784336.36 | 60564 | 434112 | 0 | 1715520 | 718656 | 0 | 0 | 2391950 | 73800 | 991200 | 312000 | 1153920 | 10350 | 246000 | 275040 | 130227361.54 | 20829090 | 8303904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 445680 | 25040000 | 84528 | 0 | 0 | 0 | 0 | 0 | 0 | 191808 | 1063392 | 0 | 0 | 56224 | 0 | 258092 | 521180 | 0 | 0 | 288000 | 4666909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25320 | 0 | 0 | 1285378 | 174199 | 1452681 | 0 | 0 | 0 | 31667.76 | 841680 | 2844 | 37248 | 6567000 | 3078000 | 5517150 | 0 | 0 | 12704000 | 495600 | 93961574.76 | 224188936.3

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 19-01-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-01-2026 | during | 19-01-2026 | during | 19-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 351 | 351 | 412 | 412 | 392 | 392 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 300 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 50 | 50.7 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 50 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 40 | 55 | 55 | 55 | 55 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 25.5 | 23 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 15.1 | 15.1 | 15.1 | 15.1 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 152 | 298 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 92 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 50 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 105 | 143 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 25 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 395 | 465 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 90 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1616.5 | 2100.7 | 5335.25 | 5307.25 | 2580.13 | 2552.13
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 | 46 | 46 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 183 | 185 | 150 | 150 | 150 | 150 | Plant availability less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 35 | 103 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 8 | 8 | 16 | 16 | 16 | 16 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 40 | 50 | 100 | 100 | 100 | 100 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 8 | 23 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.21 | 0 | 3.12 | 0 | 3.12 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 17 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 15 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 38 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 16 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1170 | 1224 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 6 | 0 | 1 | 0 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 355 | 355 | 355 | 355 | 355 | 355 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1911.21 | 2188 | 3099.98 | 3086.86 | 2702.62 | 2689.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 200 | 180 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 280 | 280 | 353.35 | 353.35 | 353.35 | 353.35 | STG Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 0 | 0 | Under maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 220 | 220 | 393 | 393 | 250 | 250 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 10 | 10 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | Gas shortage
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 55 | 143 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 17 | 32 | 32 | 24 | 24 | Partial Shutdown due to maintenance
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 80 | 163 | 163 | 115 | 115 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 72 | 154 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 102 | 106 | 84 | 82 | 114 | 114 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 11 | 24.5 | 24.5 | 24.5 | 24.5 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 15 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 63 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1136 | 1257 | 2427.75 | 2360.75 | 1832.05 | 1767.05
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-01-2026 | during | 19-01-2026 | during | 19-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 29 | 34 | 157.5 | 157.5 | 50 | 50 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 19 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 59 | 60 | 60 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 39.54 | 0 | 40.5 | 0 | 40.5 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 12 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 172.54 | 141 | 356.6 | 314 | 249.1 | 206.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 42 | 42 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 52 | 52 | 60 | 60 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 162 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 77 | 83 | 83 | 83 | 83 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 320 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 812 | 804 | 844 | 844 | 734 | 734
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 905 | 873 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 343 | 341 | 410 | 410 | 369 | 369 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 73 | 0 | 71 | 0 | 71 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1108 | 1125 | 0 | 0 | 1148 | 1148 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2429 | 2356 | 2343 | 2272 | 2800 | 2729
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 130 | 130 | 136 | 136 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 570 | 531 | 622 | 622 | 575 | 575 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 42 | 54 | 150 | 150 | 150 | 150 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 277 | 307 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.49 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1239.49 | 1258 | 1546 | 1545 | 1479 | 1478
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 43.82 | 0 | 46 | 0 | 46 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 201 | 196 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.4 | 0 | 5 | 0 | 5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 764.29 | 763 | 748 | 748 | 748 | 748 | U#1 Under AOH
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 50.12 | 0 | 60 | 0 | 60 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 86 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1184.63 | 1107 | 2028.2 | 1817.2 | 1536.8 | 1325.8
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 58 | 58 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 70 | 107 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.2 | 0 | 4.8 | 0 | 4.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 50 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 143 | 0 | 136.85 | 0 | 136.85 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 298.2 | 222 | 433.65 | 262 | 457.65 | 286
System Total |  |  |  |  | 28823.2 | 28382.248 | 10799.57 | 11433.7 | 18414.43 | 17809.06 | 14371.35 | 13767.98
Forecast Scenario (19-01-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9477 |  | 0 |  | 9477
|  |  |  | 1:00 | 8816 |  | 0 |  | 8816
|  |  |  | 2:00 | 8323 |  | 0 |  | 8323
|  |  |  | 3:00 | 8006 |  | 0 |  | 8006
|  |  |  | 4:00 | 7711 |  | 0 |  | 7711
|  |  |  | 5:00 | 7644 |  | 0 |  | 7644
|  |  |  | 6:00 | 8025 |  | 0 |  | 8025
|  |  |  | 7:00 | 8840 |  | 0 |  | 8840
|  |  |  | 8:00 | 9868 |  | 0 |  | 9868
|  |  |  | 9:00 | 10204 |  | 0 |  | 10204
|  |  |  | 10:00 | 9900 |  | 0 |  | 9900
|  |  |  | 11:00 | 9950 |  | 0 |  | 9950
|  |  |  | 12:00 | 10497 |  | 0 |  | 10497
|  |  |  | 13:00 | 10775 |  | 0 |  | 10775
|  |  |  | 14:00 | 10525 |  | 0 |  | 10525
|  |  |  | 15:00 | 9923 |  | 0 |  | 9923
|  |  |  | 16:00 | 9464 |  | 0 |  | 9464
|  |  |  | 17:00 | 9998 |  | 0 |  | 9998
|  |  |  | 18:00 | 11109 |  | 0 |  | 11109
|  |  |  | 18:30 | 11300 |  | 0 |  | 11300
|  |  |  | 19:00 | 11430 |  | 0 |  | 11430
|  |  |  | 19:30 | 11336 |  | 0 |  | 11336
|  |  |  | 20:00 | 11210 |  | 0 |  | 11210
|  |  |  | 21:00 | 11039 |  | 0 |  | 11039
|  |  |  | 22:00 | 10492 |  | 0 |  | 10492
|  |  |  | 23:00 | 9828 |  | 0 |  | 9828
Probable Maximum Temperature: |  |  | 27.00°C
Probable Maximum Demand at Day Peak: |  |  | 10497.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11430.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11430.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 233.054 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:18 hrs on 19-01-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 18-01-2026
Power Supply Scenario
| Day Peak Generation |  |  | 10799.57 | MW | 12:00 Hr. | Energy Generated |  |  | 242.0901 |  | MKWHr.
| Day Peak Demand |  |  | 10799.57 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11433.7 | MW | 20:00 Hr. | Energy Demand |  |  | 242.0901 |  | MKWHr.
| Evening Peak Demand |  |  | 11433.7 | MW | 20:00 Hr. | Maximum Temperature |  |  | 27.7 |  | °C
| Minimum Generation of the Day |  |  | 7835.78 | MW | 04:00 Hr. | Total Gas Supplied |  |  | 687.02 |  | MMCFD
| Maximum Generation of the Day |  |  | 11433.7 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 6.3633 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 25.2705 | 0 | 11.3261 | 0 | 0 | 0.15597 | 0 | 0 | 36.7525 | Gas | 92.8551 | Gas | 327974621.2576
| Chattogram Zone |  |  | 4.9232 | 35.1673 | 2.96 | 0 | 1.1008 | 0.14261 | 0 | 0.07248 | 44.3664 | Coal | 80.1206 | Coal | 524029111.9654
| Cumilla Zone |  |  | 20.8964 | 0 | 3.4113 | 0 | 0 | 0.40041 | 2.3155 | 0 | 27.0236 | HFO | 24.0163 | HFO | 402586399.43
| Mymensingh Zone |  |  | 1.1539 | 0 | 1.652 | 0 | 0 | 0.25635 | 0 | 0 | 3.0623 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 19.0451 | 0 | 0 | 0 | 0 | 0.060564 | 0 | 0 | 19.1057 | Hydro | 1.1008 | Hydro | 110082
| Khulna Zone |  |  | 8.3039 | 25.04 | 0.084528 | 0 | 0 | 0.44568 | 20.8291 | 0 | 54.7032 | Solar | 3.6046 | Solar | 56703328.982
| Barishal Zone |  |  | 8.5952 | 19.271 | 0.53285 | 0 | 0 | 0.002844 | 0 | 0 | 28.4018 | Import | 40.3203 | Import | 228025540.68
| Rajshahi Zone |  |  | 4.6669 | 0 | 1.3114 | 0 | 0 | 1.0926 | 17.1757 | 0 | 24.2466 | Wind | 0.07248 | Wind | 1066180.8
| Rangpur Zone |  |  | 0 | 0.64233 | 2.7381 | 0 | 0 | 1.0475 | 0 | 0 | 4.4279
| Total |  |  | 92.8551 | 80.1206 | 24.0163 | 0 | 1.1008 | 3.6046 | 40.3203 | 0.07248 | 242.0901
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 327974621.2576 |  | Hydro | 110082
|  |  |  | Coal | 524029111.9654 |  | Solar | 56703328.982
|  |  |  | HFO | 402586399.43 |  | Import | 228025540.68
|  |  |  | HSD | 0 |  | Wind | 1066180.8
[5 empty] | Total: | 154,04,95,265 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.8291 | Peak Hr Flow | 873.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 35238436.38 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 17.1757 | Peak Hr Flow | 763.00 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1372 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.3155 | Peak Hr Flow | 106.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2060 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 40.3203 | Peak Hr Flow | 1742.00 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4126
|  |  |  | Chattogram |  | 0 |  | 1146
|  |  |  | Cumilla |  | 0 |  | 977
|  |  |  | Mymensingh |  | 0 |  | 916
|  |  |  | Sylhet |  | 0 |  | 419
|  |  |  | Khulna |  | 0 |  | 1289
|  |  |  | Barishal |  | 0 |  | 338
|  |  |  | Rajshahi |  | 0 |  | 1051
|  |  |  | Rangpur |  | 0 |  | 701
|  |  |  | Total |  | 0 |  | 10963
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:20 | 17:25 | Bogura-Rahanpur 400kV Ckt-1 Scheduled S/D from Bogura 400/230kV end Due to Annual
maintenance and from Rahanpur 400/132kV end Due to Due to Annual maintenance work.
| 08:22 | 17:34 | Taraganj 132/33kV S/S Taraganj-Saidpur CKT-01 Scheduled S/D Due to Annual maintenance
| 08:22 | 17:00 | Daudkandi-Sonargaon 132 kV Ckt-2 Scheduled S/D from Daudkandi 132/33kV end Due to
Maintenance work at Sonargaon SS side
| 08:24 | 17:59 | Taraganj 132/33kV S/S Taraganj-Rangpur CKT-02 Scheduled S/D Due to Annual maintenance
| 08:25 | 17:34 | Rangpur-Saidpur 132kV Ckt-1 Scheduled S/D from Saidpur 132/33kV end Due to Annual
maintenance
| 08:26 | 17:58 | Rangpur-Saidpur 132kV Ckt-2 Scheduled S/D from Rangpur 132/33kV end Due to Annual
Maintenance ⛑.
| 08:28 | 16:09 | Bagerhat-Labanchura 132 kV Ckt-2 Scheduled S/D from Bagerhat 132/33kV end Due to Annual
maintenance
| 08:31 | 17:06 | Payra 400/132/33kV S/S 132/33 kV Transformer-03 LT Scheduled S/D Due to Maintenance
| 08:31 | 17:01 | Payra 400/132/33kV S/S 132/33 kV Transformer-03 HT Scheduled S/D Due to Maintenance
| 08:32 | 23:25 | Fatullah 132/33kV S/S 132 kV Hasnabad Scheduled S/D Due to Shutdown For Annual
Maintenance
| 08:32 | 17:20 | Sirajgonj 230 S/S SNWPCL (Unit-04) Scheduled S/D Due to Annual Maintenance work.
| 08:34 | 16:58 | Daudkandi-Sonargaon 132 kV Ckt-2 Scheduled S/D from Sonargaon 132/33kV end Due to Annual
maintenance
| 08:35 | 23:21 | Hasnabad 132/33kV S/S Fatulla (Pre-Brahmongaon) Scheduled S/D Due to Deadline checking
| 08:36 | 16:01 | Brahmanbaria-Narsinghdi 132 kV Ckt-2 Scheduled S/D from Brahmanbaria 132/33kV end Due to
ANNUAL MAINTENANCE
| 08:39 | 16:24 | Hasnabad-Keraniganj 230kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to
Maintenance work at Hasnabad end. and from Hasnabad 230/132kV end Due to
Hasnabad-Keraniganj 230KV circuit shutdown has been requested from Hasnabad 132KV
substation for work on Hasnabad-Fatullah 132KV line.
| 08:44 | 18:04 | KSRM 132/33kV S/S Transformer-02 HT Scheduled S/D Due to for schedule maintenance
| 08:48 | 16:21 | Gopalganj 400/132kV S/S 400kV Rampal Ckt-1 Scheduled S/D Due to Annual Maintenance
| 08:55 | 16:37 | BIPTC S/S Baharampur-1 Scheduled S/D Due to Annual Maintenance
| 08:55 | 18:20 | Aminbazar 400/230/132kV S/S ATR-01 HT Scheduled S/D Due to Annual maintenance
| 08:55 | 18:23 | Aminbazar 400/230/132kV S/S ATR-01 LT Scheduled S/D Due to Annual maintenance
| 08:57 | 16:20 | Gopalganj(N)-Rampal Ckt-1 Forced S/D from Rampal 400/230kV end Due to Annual Maintenance
| 09:03 | 18:03 | Ashuganj-Bhulta 400 kV Ckt-1 Scheduled S/D from Bhulta 400/230kV end Due to Annual
Maintenance Work
| 09:07 | 16:16 | Gopalganj 400/132kV S/S 400kV Amtoli Ckt-1 Scheduled S/D Due to Annual Maintenance
| 09:09 | 17:57 | Kallyanpur 132/33kV S/S GT-3 (132kV) HT Scheduled S/D
| 09:09 | 12:30 | Ruppur 132/11kV S/S 132kv BUS-2 Scheduled S/D Due to annual maintenance work
| 09:19 | 16:37 | Sirajganj-Ullahpara 132KV Ckt-2 Scheduled S/D from Sirajganj 132/33kV end Due to Annual
Maintenance
| 09:22 | 16:47 | Aminbazar-Kaliakoir 230kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to
Annual Maintenance.
| 09:36 | 15:56 | Kabirpur -Kodda 132kV Ckt-2 Scheduled S/D from Kabirpur 132/33kV end Due to Annual
Maintenance Work.
| 09:48 | 15:57 | Cumilla(S) 132/33kV S/S Tripura Ckt-2 Scheduled S/D Due to Annual Bay maintenance
| 09:53 | 16:44 | Kaliakoir-Kodda(300MW) 230kV Ckt-1 Scheduled S/D from Kaliakoir 400/230/132kV end Due to
Annual Maintenance Deadline Checking & Disk Cleaning
| 09:58 | 16:05 | Barapukuria S/S-P/S 230 kV Ckt-1 Scheduled S/D from Barapukuria 230/132/33kV end Due to
Annual maintenance work.
| 10:21 |  | Aminbazar 400/230/132kV S/S 230 kv Bus 01 Scheduled S/D Due to DS changing
| 10:26 | 12:03 | Joydebpur 132/33kV S/S GT-3 HT Scheduled S/D Due to Oil leakage maintenance of B-Phase
C.T.
| 11:02 |  | Tongi 230/132/33kV S/S T-1 LT Scheduled S/D Due to signal shifting work
| 11:02 |  | Tongi 230/132/33kV S/S T-1 HT Scheduled S/D Due to Signal shifting work
| 12:07 | 13:35 | Pabna- Shahjadpur 132kV Ckt-1 Forced S/D from Pabna 132/33kV end.
| 12:21 | 13:50 | Shahjadpur 132/33kV S/S Main Bus Forced S/D Due to Maintenance Work | [7 empty] | 25.0MW load
interrup.
| 12:28 | 14:42 | Kurigram-Lalmonirhat 132kV Ckt-1 Project Work S/D from Kurigram 132/33kV end.
|  | 13:19 | Ghorasal-Tongi 230kV Ckt-1 is restored.
| 13:32 | 15:55 | Sreepur 230/132/33kV S/S 230/132 kV T-2 LT Scheduled S/D Due to Annual maintenance &
works of Protection team for SPS
| 13:34 | 15:56 | Sreepur 230/132/33kV S/S Auxiliary Transformer - 2 HT Scheduled S/D Due to Annual
maintenance & works of Protection team for SPS
| 13:34 | 15:53 | Sreepur 230/132/33kV S/S 230/132 kV T-2 HT Scheduled S/D Due to Annual maintenance &
works of Protection team for SPS
|  | 14:40 | Kurigram-Rangpur 132kV Ckt-1 is restored.
|  | 14:40 | Kurigram-Rangpur 132kV Ckt-1 is restored.
| 14:54 | 21:10 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-2 Project Work S/D from Thakurgaon 132/33kV end
Due to STEGEP Project Reconductoring work
|  | 15:57 | Moghbazar-Rampura 132kV Ckt-1 is restored.
| 16:05 | 16:36 | Shahjibazar 132/33kV S/S TR-04 LT Forced S/D Due to Shutdown for Emergency. | [7 empty] | 62.0MW load
interrup.
| 16:06 | 16:35 | Shahjibazar 132/33kV S/S TR-04 HT Forced S/D Due to Shutdown for Emergency. | [7 empty] | 62.0MW load
interrup.
|  | 16:11 | Rajshahi-Rajshahi(New) 132kV Ckt-1 is restored.
|  | 16:21 | Rampal 400/230kV S/S Gopalganj Line-1 Reactor is restored.
|  | 16:29 | Bibiyana-Fenchuganj 230 kV Ckt-2 is restored.
| 16:53 | 16:53 | Hasnabad-Postogola 132kV ckt-1 Scheduled S/D from Postogola 132/33kV end Due to Yearly
maintenance
| 17:08 |  | Postogola 132/33kV S/S GT-1 HT Scheduled S/D Due to Yearly maintenance
|  | 18:35 | Sylhet 132/33kV S/S Sylhet-90MW P/S is restored.
| 21:25 |  | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 Scheduled S/D from Thakurgaon 132/33kV end Due
to Temperature Rise at Thakurgaon-EPV Ckt-1 R-Phase LA. Need to Maintenance
|  | 23:24 | Korerhat 400/230/132kV S/S 400kV BUS-1 is restored.
| 23:25 |  | Fatullah-Madanganj 132 kV Ckt-2 Forced S/D from Fatullah 132/33kV end.
| 05:00 |  | Minimum Generation: 7911 MW.
| 07:00 |  | Korerhat 400/230/132kV S/S 400kV BUS-2 Project Work S/D Due to Busbur internal testing
| 07:10 |  | Moghbazar-Rampura 132kV Ckt-1 Scheduled S/D from Rampura 230/132kV end Due to Annual
Maintenance and Line PT(Y) Phase Replacement.
| 07:19 |  | Shahjadpur 132/33kV S/S Main Bus Forced S/D Due to Maintenance work | [7 empty] | 20.0MW load
interrup.
| 07:21 |  | Sylhet 132/33kV S/S Sylhet-90MW P/S Project Work S/D Due to OPGW wire change
| 07:25 |  | Ashuganj-Bhulta 400 kV Ckt-1 Scheduled S/D from Bhulta 400/230kV end Due to Dead Line
Checking.
| 07:47 |  | Patuakhali-Payra 132kV Ckt-1 Scheduled S/D from Payra 400/132/33kV end Due to
Maintenance and from Patuakhali 132/33kV end Due to Annual Maintenance-2026
| 07:50 |  | Kachua 230/132/33kV S/S TR-1 HT Project Work S/D Due to For flood light setting.
| 07:52 |  | Purbasadipur-Thakurgaon-EPV 132kV Ckt-2 Scheduled S/D from Purbasadipur 132/33kV end.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 18-01-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 351 | 8445600 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 222985 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 6211885 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 50.7 | 839160 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 825791 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 833995 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 488400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 337320 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 45600 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 298 | 3126578 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2110464 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 50 | 142080 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 143 | 2082240 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 155970 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 83160 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 465 | 9787273 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 90 | 1014000 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 2100.7 | 36752501
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 122445 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 194880 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1100820 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 185 | 4428813 | Plant availability less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 103 | 1244509 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 8 | 91370 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 171428 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 390720 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 23 | 494400 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20160 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 90327 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 17 | 51583 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 15 | 86981 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 38 | 523200 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 71509 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 16 | 43491 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 26585452 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 6 | 72480 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 355 | 8581818.18 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4898.863 | 2188 | 44366386.18
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 180 | 4685000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 280 | 7313000 | STG Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 220 | 5434000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1237211 | Gas shortage
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 143 | 1497090 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 17 | 56160 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1935616 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 154 | 1756320 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 106 | 2315520 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 11 | 291540 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 15 | 101760 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 400409 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1257 | 27023626
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 34 | 1153920 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10350 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 312000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 991200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 246000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 275040 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 73800 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 141 | 3062310
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 60564 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 995000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 52 | 1300560 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 162 | 3784336.36 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 718656 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 77 | 1715520 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2391950 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 434112 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7705000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 804 | 19105698.36
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 873 | 20829090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 341 | 8303904 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 84528 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 445680 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1125 | 25040000 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2356 | 54703202
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 37248 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 3078000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 531 | 12704000 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5517150 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 495600 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6567000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2844 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1258 | 28401842
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 258092 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 56224 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 196 | 4666909 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 0 | 0 | Under Maintenance
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1063392 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 191808 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 25320 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 763 | 17175677 | U#1 Under AOH
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 288000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 521180 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1107 | 24246602
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 642327 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 1452681 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 31667.76 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1285378 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 174199 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 841680 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 222 | 4427932.76
Eastern Grid Total |  |  |  |  | 17398.245 | 6490.7 | 130310521.54
Western Grid Total |  |  |  |  | 10984.003 | 4943 | 111779578.76
National Grid Total |  |  |  |  | 28382.248 | 11433.7 | 242090100.3
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 18-01-2026
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7583.32 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3379.2 | MW
i) Dhaka area |  |  | 4125.82 |  | MW | i) Khulna area |  |  |  | 1289 | MW
ii) Chattogram area |  |  | 1145.5 |  | MW | ii) Barishal area |  |  |  | 337.8 | MW
iii) Cumilla area |  |  | 977 |  | MW | iii) Rajshahi area |  |  |  | 1051.4 | MW
iv) Mymensingh area |  |  | 916 |  | MW | iv) Rangpur area |  |  |  | 701 | MW
v) Sylhet area |  |  | 419 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10962.52 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 65 | 13:00 | 133 | Netrakona | 129 | 19:00
2 | AKSML | 147 | 08:00 | 68 | Hathazari | 59 | 13:00 | 134 | New | 60 | 12:00
3 | Aftabnagar | 28 | 13:00 | 69 | Hatirjheel | 29 | 14:00 | 135 | Niamatpur | 73 | 13:00
4 | Agargaon | 88 | 13:00 | 70 | Ishurdi | 48 | 21:00 | 136 | Noapara | 43 | 08:00
5 | Agrabad | 48 | 18:00 | 71 | Jaldhaka | 57 | 19:00 | 137 | PHP | 9 | 08:00
6 | Amnura | 32 | 08:00 | 72 | Jamalpur | 95 | 08:00 | 138 | Pabna | 79 | 20:00
7 | Ashuganj | 66 | 13:00 | 73 | Jashore | 106 | 12:00 | 139 | Palashbari | 87 | 19:00
8 | BSRM | 204 | 08:00 | 74 | Jhenaidah | 102 | 08:00 | 140 | Panchagarh | 44 | 18:30
9 | Bagerhat | 67 | 19:00 | 75 | Joydebpur | 115 | 18:00 | 141 | Patiya | 6 | 19:30
10 | Bajitpur | 59 | 08:00 | 76 | Joypurhat | 42 | 08:00 | 142 | Patuakhali | 39.8 | 20:00
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 15.5 | 12:00 | 143 | Payra | 46 | 11:00
12 | Bakulia | 65 | 18:30 | 78 | KSRM | 16 | 05:00 | 144 | Postogola | 42 | 13:00
13 | Banani | 37 | 13:00 | 79 | Kabirpur | 209 | 10:00 | 145 | Purbachal | 21 | 13:00
14 | Bangabhaban | 9 | 11:00 | 80 | Kachua | 60 | 18:00 | 146 | Purbasadipur | 118 | 13:00
15 | Barapukuria | 53 | 18:00 | 81 | Kallyanpur | 99 | 17:00 | 147 | Rahanpur | 24 | 18:30
16 | Barguna | 16 | 21:00 | 82 | Kalurghat | 36 | 18:00 | 148 | Rahim | 54 | 15:00
17 | Barishal | 83 | 21:00 | 83 | Kamrangirchar | 65 | 12:00 | 149 | Rajbari | 60 | 18:00
18 | Barishal-230 | 82 | 20:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 112 | 18:00
19 | Baroaulia | 47 | 18:00 | 85 | Kasba | 27 | 13:00 | 151 | Rajshahi | 73 | 21:00
20 | Baroirhat | 50 | 18:30 | 86 | Kazla | 67 | 19:00 | 152 | Rajshahi-230 | 70 | 13:00
21 | Bashundhara | 156 | 13:00 | 87 | Keranigonj | 75 | 13:00 | 153 | Ramganj | 66 | 13:00
22 | BashundharaCement | 7 | 08:00 | 88 | Khagrachori | 26 | 18:00 | 154 | Rampur | 28 | 18:00
23 | Beanibazar | 48 | 18:00 | 89 | Khulna | 42 | 18:30 | 155 | Rangamati | 13 | 18:00
24 | Benapole | 66 | 08:00 | 90 | Khulshi | 150 | 16:00 | 156 | Rangpur | 106 | 14:00
25 | Bhaluka | 144 | 08:00 | 91 | Kishoreganj | 103 | 19:00 | 157 | Ruppur | 2.6 | 15:00
26 | Bhandaria | 40 | 20:00 | 92 | Kodda | 256 | 09:00 | 158 | SSM | 10 | 23:00
27 | Bhangura | 23 | 08:00 | 93 | Kulaura | 28 | 18:00 | 159 | Saidpur | 95 | 18:30
28 | Bheramara(GK) | 43 | 18:30 | 94 | Kurigram | 56 | 08:00 | 160 | Satkhira | 107 | 08:00
29 | Bhulta | 178 | 04:00 | 95 | Kushtia | 112 | 08:00 | 161 | Satmasjid | 77 | 13:00
30 | Bog-Sherpur | 56 | 08:00 | 96 | Laksam | 14 | 21:00 | 162 | Savar | 176 | 12:00
31 | Bogura | 115 | 19:30 | 97 | Lakshmipur | 24 | 18:00 | 163 | SevenRings | 17.91 | 21:00
32 | Borhanuddin | 65 | 21:00 | 98 | Lalbag | 54 | 13:00 | 164 | ShahCement | 32 | 07:00
33 | Brahmanbaria | 94 | 18:00 | 99 | Lalmonirhat | 46 | 18:00 | 165 | Shahjadpur | 56 | 15:00
34 | Cantonment | 68 | 13:00 | 100 | MI_Cement | 16.5 | 00:00 | 166 | Shahjibazar | 104 | 21:00
35 | Chandina | 16 | 19:30 | 101 | Madanganj | 30 | 13:00 | 167 | Shahmirpur | 40 | 18:00
36 | Chandpur | 52 | 19:30 | 102 | Madaripur | 76 | 13:00 | 168 | Shariatpur | 58 | 19:30
37 | Chandraghona | 28 | 18:30 | 103 | Madartek | 60 | 13:00 | 169 | Sherpur | 114 | 09:00
38 | Chapai | 51 | 08:00 | 104 | Madunaghat | 41 | 18:00 | 170 | Shikalbaha | 16 | 12:00
39 | Charsaidpur | 38 | 11:00 | 105 | Magura | 49 | 18:30 | 171 | Shitalakhya | 66.6 | 12:00
40 | Chauddagram | 50 | 14:00 | 106 | Mahasthangarh | 54 | 08:00 | 172 | Sholosohor | 36 | 18:00
41 | Chhatak | 30 | 20:00 | 107 | Maijdee | 33 | 19:30 | 173 | Shyampur | 144 | 11:00
42 | Chowmuhani | 108 | 19:00 | 108 | Manikganj | 97 | 18:00 | 174 | Siddhirganj | 110 | 12:00
43 | Chuadanga | 82 | 08:00 | 109 | Maniknagar | 48 | 13:00 | 175 | Sirajganj | 86 | 18:30
44 | Coxsbazar | 108 | 18:30 | 110 | Matarbari | 40 | 18:00 | 176 | Sonargaon | 137 | 19:30
45 | Cumilla(N) | 127 | 18:00 | 111 | Matuail | 54 | 10:00 | 177 | Sreemongol | 54 | 18:30
46 | Cumilla(S) | 112 | 19:00 | 112 | Metrorail_Motijheel | 30 | 18:30 | 178 | Sreepur | 91 | 12:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 0 | 00:00 | 179 | Srinagar | 32 | 13:00
48 | Daudkandi | 118 | 19:00 | 114 | Millgate | 66 | 16:00 | 180 | Sunamganj | 40 | 18:00
49 | DhakaUniversity | 54 | 13:00 | 115 | Mirpur | 107 | 12:00 | 181 | Sylhet | 40 | 19:00
50 | Dhamrai | 110 | 18:00 | 116 | Mirsorai | 10 | 12:00 | 182 | Sylhet-132 | 78 | 13:00
51 | Dhanmondi | 79 | 13:00 | 117 | Mirzapur | 44 | 07:00 | 183 | TK | 17 | 18:00
52 | Dohazari | 77 | 18:30 | 118 | Mithapukur | 44 | 08:00 | 184 | Tangail | 126 | 18:00
53 | Faridpur | 117 | 19:00 | 119 | Modern | N/A | N/A | 185 | Taraganj | 17 | 18:00
54 | Fatullah | 91 | 12:00 | 120 | Mogbazar | 52 | 15:00 | 186 | Tasnim | 32 | 02:00
55 | Fenchuganj | 24 | 18:00 | 121 | Mongla | 39 | 18:30 | 187 | Thakurgaon | 79 | 19:00
56 | Feni | 75 | 18:00 | 122 | Motijheel | 36 | 13:00 | 188 | Tongi | 107 | 18:00
57 | GPH | 90 | 02:00 | 123 | Muktagacha | 30 | 08:00 | 189 | Ullahpara | 28 | 18:00
58 | Ghatail | 70 | 08:00 | 124 | Munshiganj | 72 | 13:00 | 190 | Ullon | 38 | 14:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 0 | 00:00 | 191 | Uttara | 71 | 11:00
60 | Ghorashal-230 | 97 | 19:00 | 126 | Mymensingh | 150 | 13:00 | 192 | UttaraNew | 32 | 13:00
61 | Goalpara | 30 | 13:00 | 127 | Naogaon | 97 | 20:00 | 193 | Zigatola | 72 | 14:00
62 | Gollamari | 92 | 13:00 | 128 | Narail | 42.5 | 08:00
63 | Gopalganj | 82 | 19:30 | 129 | Narinda | 56 | 13:00
64 | Gulshan | 72 | 13:00 | 130 | Narshingdi | 141 | 21:00
65 | Halishahar | 61.5 | 15:00 | 131 | Natore | 104 | 21:00
66 | HaripurSBU | 123 | 12:00 | 132 | Nawabganj | 31 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 18-01-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 9548.18 | 0 |  | 9548.18
1:00 | 8835.34 | 0 |  | 8835.34
2:00 | 8380.61 | 0 |  | 8380.61
3:00 | 8064.99 | 0 |  | 8064.99
4:00 | 7835.78 | 0 |  | 7835.78
5:00 | 7907.09 | 0 |  | 7907.09
6:00 | 8311.28 | 0 |  | 8311.28
7:00 | 9014.02 | 0 |  | 9014.02
8:00 | 10308.13 | 0 |  | 10308.13
9:00 | 10636.88 | 0 |  | 10636.88
10:00 | 10241.82 | 0 |  | 10241.82
11:00 | 10366.48 | 0 |  | 10366.48
12:00 | 10799.57 | 0 |  | 10799.57
13:00 | 11157.48 | 0 |  | 11157.48
14:00 | 10753.98 | 0 |  | 10753.98
15:00 | 10314.05 | 0 |  | 10314.05
16:00 | 9992.18 | 0 |  | 9992.18
17:00 | 10128.07 | 0 |  | 10128.07
18:00 | 11020.1 | 0 |  | 11020.1
19:00 | 11290.3 | 0 |  | 11290.3
19:30 | 11410.3 | 0 |  | 11410.3
20:00 | 11433.7 | 0 |  | 11433.7
21:00 | 11213.76 | 0 |  | 11213.76
22:00 | 10784.24 | 0 |  | 10784.24
23:00 | 10148.98 | 0 |  | 10148.98
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 18-01-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4936.4 | 4611.78 | 9548.18 | DAILY GENERATION CURVE
00:30 | 4670.2 | 4521.56 | 9191.76
01:00 | 4404 | 4431.34 | 8835.34 | 18-01-2026
01:30 | 4392 | 4215.975 | 8607.975
02:00 | 4380 | 4000.61 | 8380.61
02:30 | 4362.5 | 3860.3 | 8222.8
03:00 | 4345 | 3719.99 | 8064.99
03:30 | 4313 | 3637.385 | 7950.385
04:00 | 4281 | 3554.78 | 7835.78
04:30 | 4308 | 3563.435 | 7871.435
05:00 | 4335 | 3572.09 | 7907.09
05:30 | 4411.5 | 3697.685 | 8109.185
06:00 | 4488 | 3823.28 | 8311.28
06:30 | 4574.345 | 4088.305 | 8662.65
07:00 | 4660.69 | 4353.33 | 9014.02
07:30 | 5077.86 | 4583.215 | 9661.075
08:00 | 5495.03 | 4813.1 | 10308.13
08:30 | 5590.615 | 4881.89 | 10472.505
09:00 | 5686.2 | 4950.68 | 10636.88
09:30 | 5488.91 | 4950.44 | 10439.35
10:00 | 5291.62 | 4950.2 | 10241.82
10:30 | 5305.295 | 4998.855 | 10304.15
11:00 | 5318.97 | 5047.51 | 10366.48
11:30 | 5483.61 | 5099.415 | 10583.025
12:00 | 5648.25 | 5151.32 | 10799.57
12:30 | 5758.24 | 5220.285 | 10978.525
13:00 | 5868.23 | 5289.25 | 11157.48
13:30 | 5740.69 | 5215.04 | 10955.73
14:00 | 5613.15 | 5140.83 | 10753.98
14:30 | 5508.225 | 5025.79 | 10534.015
15:00 | 5403.3 | 4910.75 | 10314.05
15:30 | 5370.705 | 4782.41 | 10153.115
16:00 | 5338.11 | 4654.07 | 9992.18
16:30 | 5413.18 | 4646.945 | 10060.125
17:00 | 5488.25 | 4639.82 | 10128.07
17:30 | 5831.175 | 4742.91 | 10574.085
18:00 | 6174.1 | 4846 | 11020.1
18:30 | 6277.7 | 4877.5 | 11155.2
19:00 | 6381.3 | 4909 | 11290.3
19:30 | 6460.3 | 4950 | 11410.3
20:00 | 6490.7 | 4943 | 11433.7
20:30 | 6397.45 | 4926.28 | 11323.73 |  | Executive Engineer
21:00 | 6304.2 | 4909.56 | 11213.76 |  | Network Operation Division
21:30 | 6129 | 4870 | 10999
22:00 | 5953.8 | 4830.44 | 10784.24
22:30 | 5878.35 | 4588.26 | 10466.61
23:00 | 5802.9 | 4346.08 | 10148.98

## En-Curve
QF-LDC-12
Date | 18-01-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2497 | 1304 | 905 | 0 | 98 | 760.78 | 46 | 3581 | 0 | 0 | 349.4 | 0 | 0 | 7 | 0 | DAILY ENERGY CURVE
00:30 | 2505 | 1300 | 905 | 0 | 92 | 756.56 | 46 | 3404 | 0 | 0 | 174.7 | 0 | 0 | 8.5 | 0 | 18-01-2026
01:00 | 2513 | 1296 | 905 | 0 | 86 | 752.34 | 46 | 3227 | 0 | 0 | 0 | 0 | 0 | 10 | 0
01:30 | 2508 | 1304.5 | 905 | 0 | 85 | 756.975 | 46 | 2992.5 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | Energy Generated | 242.0901 |  | MKWHr
02:00 | 2503 | 1313 | 905 | 0 | 84 | 761.61 | 46 | 2758 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2508 | 1314.5 | 905 | 0 | 85 | 699.8 | 46 | 2653.5 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | Total Energy Requirement | 242.0901 |  | MKWHr
03:00 | 2513 | 1316 | 905 | 0 | 86 | 637.99 | 46 | 2549 | 0 | 0 | 0 | 0 | 0 | 12 | 0
03:30 | 2531.5 | 1296.5 | 905 | 0 | 83 | 545.885 | 46 | 2534.5 | 0 | 0 | 0 | 0 | 0 | 8 | 0
04:00 | 2550 | 1277 | 905 | 0 | 80 | 453.78 | 46 | 2520 | 0 | 0 | 0 | 0 | 0 | 4 | 0
04:30 | 2537 | 1273 | 905 | 0 | 77 | 448.435 | 46 | 2583 | 0 | 0 | 0 | 0 | 0 | 2 | 0
05:00 | 2524 | 1269 | 905 | 0 | 74 | 443.09 | 46 | 2646 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 2530 | 1273 | 905 | 0 | 79 | 484.43 | 46 | 2791.5 | 0.255 | 0 | 0 | 0 | 0 | 0 | 0
06:00 | 2536 | 1277 | 905 | 0 | 84 | 525.77 | 46 | 2937 | 0.51 | 0 | 0 | 0 | 0 | 0 | 0
06:30 | 2546.5 | 1296.5 | 905 | 0 | 84 | 602.715 | 46 | 3159 | 4.935 | 2.5 | 15.5 | 0 | 0 | 0 | 0
07:00 | 2557 | 1316 | 905 | 0 | 84 | 679.66 | 46 | 3381 | 9.36 | 5 | 31 | 0 | 0 | 0 | 0
07:30 | 2525.5 | 1338 | 905 | 0 | 94 | 720.37 | 46 | 3479 | 65.205 | 37.5 | 450.5 | 0 | 0 | 0 | 0
08:00 | 2494 | 1360 | 905 | 0 | 104 | 761.08 | 46 | 3577 | 121.05 | 70 | 870 | 0 | 0 | 0 | 0
08:30 | 2499 | 1295 | 905 | 0 | 100 | 763.37 | 46 | 3518.5 | 209.135 | 52.5 | 1084 | 0 | 0 | 0 | 0
09:00 | 2504 | 1230 | 905 | 0 | 96 | 765.66 | 46 | 3460 | 297.22 | 35 | 1298 | 0 | 0 | 0 | 0
09:30 | 2477 | 1213.5 | 904.5 | 0 | 98.5 | 763.37 | 46 | 3406.5 | 376.08 | 35 | 1118.9 | 0 | 0 | 0 | 0
10:00 | 2450 | 1197 | 904 | 0 | 101 | 761.08 | 46 | 3353 | 454.94 | 35 | 939.8 | 0 | 0 | 0 | 0
10:30 | 2463.5 | 1236.5 | 904.5 | 0 | 100 | 759.44 | 46 | 3331.5 | 503.51 | 39 | 920.2 | 0 | 0 | 0 | 0
11:00 | 2477 | 1276 | 905 | 0 | 99 | 757.8 | 46 | 3310 | 552.08 | 43 | 900.6 | 0 | 0 | 0 | 0
11:30 | 2484 | 1290.25 | 905 | 0 | 100.5 | 761.045 | 46 | 3395 | 574.93 | 51.5 | 974.8 | 0 | 0 | 0 | 0
12:00 | 2491 | 1304.5 | 905 | 0 | 102 | 764.29 | 46 | 3480 | 597.78 | 60 | 1049 | 0 | 0 | 0 | 0
12:30 | 2485 | 1312 | 905 | 0 | 102.5 | 762.895 | 46 | 3508.5 | 579.88 | 60 | 1216.75 | 0 | 0 | 0 | 0
13:00 | 2479 | 1319.5 | 905 | 0 | 103 | 761.5 | 46 | 3537 | 561.98 | 60 | 1384.5 | 0 | 0 | 0 | 0
13:30 | 2473.5 | 1311.25 | 902 | 0 | 106 | 762.25 | 46 | 3564 | 516.98 | 79 | 1193.75 | 0 | 0 | 1 | 0
14:00 | 2468 | 1303 | 899 | 0 | 109 | 763 | 46 | 3591 | 471.98 | 98 | 1003 | 0 | 0 | 2 | 0
14:30 | 2469 | 1302.5 | 886.5 | 0 | 108 | 763.5 | 46 | 3532 | 403.415 | 103 | 918.6 | 0 | 0 | 1.5 | 0
15:00 | 2470 | 1302 | 874 | 0 | 107 | 764 | 46 | 3473 | 334.85 | 108 | 834.2 | 0 | 0 | 1 | 0
15:30 | 2462.5 | 1306 | 873 | 0 | 108.5 | 761 | 46 | 3464 | 248.415 | 110.5 | 771.2 | 0 | 0 | 2 | 0
16:00 | 2455 | 1310 | 872 | 0 | 110 | 758 | 46 | 3455 | 161.98 | 113 | 708.2 | 0 | 0 | 3 | 0
16:30 | 2475.5 | 1294.5 | 872.5 | 0 | 107 | 762.5 | 46 | 3441.5 | 97.925 | 115.5 | 843.7 | 0 | 0 | 3.5 | 0
17:00 | 2496 | 1279 | 873 | 0 | 104 | 767 | 46 | 3428 | 33.87 | 118 | 979.2 | 0 | 0 | 4 | 0
17:30 | 2515.5 | 1298.25 | 873 | 0 | 105 | 766.5 | 46 | 3458 | 16.935 | 155 | 1336.4 | 0 | 0 | 3.5 | 0
18:00 | 2535 | 1317.5 | 873 | 0 | 106 | 766 | 46 | 3488 | 0 | 192 | 1693.6 | 0 | 0 | 3 | 0
18:30 | 2530 | 1347.25 | 873 | 0 | 108 | 760 | 46 | 3483.5 | 0 | 207 | 1796.95 | 0 | 0 | 3.5 | 0
19:00 | 2525 | 1377 | 873 | 0 | 110 | 754 | 46 | 3479 | 0 | 222 | 1900.3 | 0 | 0 | 4 | 0
19:30 | 2514 | 1380 | 872 | 0 | 110 | 756 | 46 | 3553 | 0 | 226 | 1948.3 | 0 | 0 | 5 | 0
20:00 | 2521 | 1387 | 873 | 0 | 106 | 763 | 46 | 3542 | 0 | 241 | 1948.7 | 0 | 0 | 6 | 0
20:30 | 2497 | 1372.5 | 873 | 0 | 109 | 762.78 | 46 | 3539.5 | 0 | 193 | 1926.45 | 0 | 0 | 4.5 | 0
21:00 | 2473 | 1358 | 873 | 0 | 112 | 762.56 | 46 | 3537 | 0 | 145 | 1904.2 | 0 | 0 | 3 | 0
21:30 | 2465.5 | 1334.5 | 872.5 | 0 | 105 | 761 | 46 | 3531.5 | 0 | 98.5 | 1782 | 0 | 0 | 2.5 | 0
22:00 | 2458 | 1311 | 872 | 0 | 98 | 759.44 | 46 | 3526 | 0 | 52 | 1659.8 | 0 | 0 | 2 | 0
22:30 | 2447.5 | 1302.75 | 662 | 0 | 97 | 757.76 | 46 | 3523.5 | 0 | 34.5 | 1593.1 | 0 | 0 | 2.5 | 0
23:00 | 2437 | 1294.5 | 452 | 0 | 96 | 756.08 | 46 | 3521 | 0 | 17 | 1526.4 | 0 | 0 | 3 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 18-01-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 423 | 04:00 | 412 | 18:30 | Madunaghat | 417 | 04:00 | 398 | 15:00
Amtali | 422 | 0:00 | 411 | 14:00 | Meghnaghat | 428 | 05:00 | 403 | 12:00
Ashuganj | 413 | 4:00 | 390 | 12:00 | Payra | 424 | 03:00 | 412 | 14:00
Bhulta | 406 | 04:00 | 376 | 12:00 | Rahanpur | 420 | 23:00 | 402 | 12:00
Bibiana | 423 | 03:00 | 409 | 11:00 | Rampal | 419 | 05:00 | 399 | 12:00
BIPTC | 406 | 23:00 | 385 | 10:00
Bogura | 417 | 05:00 | 394 | 12:00
Gopalganj | 422 | 04:00 | 401 | 12:00
Kaliakoir | 418 | 03:00 | 396 | 16:00
Korerhat | 425 | 03:00 | 410 | 14:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 245 | 04:00 | 230 | 12:00 | Kachua | 242 | 03:00 | 232 | 16:00
AKSML | 238 | 02:00 | 228 | 16:00 | Kaliakoir | 245 | 05:00 | 231 | 16:00
Aminbazar | 244 | 05:00 | 229 | 12:00 | Keranigonj | 244 | 05:00 | 228 | 12:00
Ashuganj | 240 | 23:00 | 227 | 12:00 | Khulna(S) | 245 | 02:00 | 231 | 12:00
Ashuganj-400 | 240 | 23:00 | 227 | 12:00 | Korerhat | 242 | 05:00 | 230 | 12:00
Baghabari | 242 | 23:00 | 229 | 11:00 | Madunaghat | 238 | 03:00 | 227 | 14:00
Barapukuria | 237 | 23:00 | 218 | 12:00 | Madunaghat-400 | 238 | 03:00 | 228 | 16:00
Barapukuria-230 | 237 | 23:00 | 218 | 12:00 | Maniknagar | 240 | 05:00 | 224 | 12:00
Barishal | 240 | 02:00 | 230 | 12:00 | Meghnaghat | 247 | 04:00 | 236 | 10:00
Bheramara | 239 | 05:00 | 225 | 12:00 | Meghnaghat-400 | 242 | 04:00 | 228 | 12:00
Bhulta | 244 | 05:00 | 226 | 12:00 | Mirsorai | 241 | 04:00 | 230 | 16:00
Bibiana | 243 | 02:00 | 235 | 12:00 | Rajshahi | 239 | 05:00 | 225 | 12:00
BIPTC | 243 | 05:00 | 226 | 12:00 | Rampal | 243 | 04:00 | 228 | 13:00
Bogura | 245 | 23:00 | 231 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 244 | 23:00 | 230 | 12:00 | Rampura | 243 | 05:00 | 227 | 12:00
Borhanuddin | 240 | 01:00 | 235 | 12:00 | Shikalbaha | 236 | 03:00 | 226 | 16:00
BSRM | 240 | 04:00 | 230 | 16:00 | Shyampur | 241 | 03:00 | 227 | 12:00
Cumilla(N) | 240 | 23:00 | 229 | 12:00 | Siddhirganj | 242 | 03:00 | 228 | 12:00
Faridpur | 239 | 04:00 | 226 | 12:00 | Sirajgonj | 247 | 23:00 | 234 | 12:00
Fenchuganj | 245 | 22:00 | 239 | 11:00 | Sreepur | 238 | 23:00 | 224 | 10:00
Feni | 241 | 03:00 | 231 | 12:00 | Tongi | 243 | 00:00 | 230 | 04:00
Ghorashal | 240 | 00:00 | 232 | 15:00
Ghorashal-230 | 242 | 23:00 | 226 | 12:00
Gopalganj | 237 | 04:00 | 226 | 12:00
GPH | 239 | 04:00 | 228 | 16:00
Haripur | 244 | 04:00 | 228 | 12:00
Hasnabad | 242 | 08:00 | 227 | 12:00
Hathazari | 233 | 03:00 | 226 | 11:00
Ishurdi | 245 | 05:00 | 231 | 12:00
Jhenaidah | 243 | 05:00 | 227 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 04:00 | 125 | 12:00 | Maijdee | 135 | 02:00 | 129 | 16:00
Agargaon | 139 | 03:00 | 129 | 12:00 | Manikganj | 132 | 04:00 | 121 | 16:00
Agrabad | 138 | 02:00 | 132 | 14:00 | Maniknagar | 139 | 04:00 | 126 | 12:00
AKS | 136 | 03:00 | 129 | 16:00 | Matarbari | 131 | 08:00 | 123 | 14:00
Aminbazar | 141 | 22:00 | 132 | 11:00 | Matuail | 138 | 02:00 | 130.3 | 12:00
Amnura | 138 | 04:00 | 130 | 13:00 | Metrorail_Motijheel | 139 | 04:00 | 126 | 12:00
Ashuganj | 139 | 23:00 | 135 | 09:00 | Metrorail_Uttara | 140 | 23:00 | 128 | 09:00
Bagerhat | 136 | 04:00 | 121 | 13:00 | Millgate | 135 | 03:00 | 124 | 16:00
Bajitpur | 134 | 23:00 | 129 | 09:00 | Mirpur | 140 | 07:00 | 130 | 12:00
Bakerganj | 140 | 18:00 | 135 | 14:00 | Mirzapur | 137 | 05:00 | 127 | 16:00
Bakulia | 138 | 04:00 | 132 | 12:00 | Mithapukur | 139 | 18:00 | 129 | 12:00
Banani | 135 | 04:00 | 124 | 12:00 | MI_Cement | 137 | 03:00 | 127 | 12:00
Bangabhaban | 138 | 02:00 | 126 | 12:00 | Modern | N/A | N/A | N/A | N/A
Barapukuria | 142 | 23:00 | 130 | 12:00 | Mogbazar | 137 | 03:00 | 120 | 09:00
Barguna | 140 | 18:00 | 135 | 14:00 | Mongla | 133 | 01:00 | 122 | 13:00
Barishal | 141 | 03:00 | 134 | 14:00 | Motijheel | 138 | 02:00 | 126 | 12:00
Barishal-230 | 140 | 02:00 | 134 | 12:00 | Muktagacha | 133 | 11:00 | 124 | 07:00
Baroaulia | 138 | 05:00 | 132 | 13:00 | Munshiganj | 136 | 01:00 | 128 | 10:00
Baroirhat | 136 | 04:00 | 130 | 12:00 | Muradnagar | 138 | 03:00 | 130 | 12:00
Bashundhara | 135 | 03:00 | 124 | 12:00 | Mymensingh | 134 | 11:00 | 118 | 12:00
BashundharaCement | 138 | 08:00 | 132 | 07:00 | Naogaon | 135 | 18:00 | 127 | 12:00
Beanibazar | 133 | 01:00 | 128 | 12:00 | Narail | 140 | 04:00 | 128 | 12:00
Benapole | 137 | 03:00 | 124 | 12:00 | Narinda | 139 | 04:00 | 126 | 12:00
Bhaluka | 135 | 23:00 | 125 | 05:00 | Narshingdi | 135 | 00:00 | 116 | 16:00
Bhandaria | 137 | 03:00 | 133 | 12:00 | Natore | 138 | 23:00 | 131 | 12:00
Bhangura | 137 | 00:00 | 132 | 14:00 | Nawabganj | 137 | 04:00 | 127 | 12:00
Bheramara | 141 | 02:00 | 135 | 12:00 | Netrakona | 125 | 22:00 | 114 | 12:00
Bheramara(GK) | 142 | 04:00 | 136 | 12:00 | New | 135 | 00:00 | 125 | 16:00
Bhulta | 135 | 23:00 | 126 | 13:00 | Niamatpur | 140 | 04:00 | 134 | 12:00
Bog-Sherpur | 139 | 05:00 | 130 | 12:00 | Noapara | 138 | 04:00 | 125 | 13:00
Bogura | 139 | 05:00 | 130 | 13:00 | Pabna | 141 | 05:00 | 134 | 12:00
Bogura-230 | 140 | 23:00 | 131 | 12:00 | Palashbari | 135 | 18:00 | 127 | 12:00
Brahmanbaria | 131 | 04:00 | 125 | 11:00 | Panchagarh | 140 | 23:00 | 126 | 12:00
Cantonment | 139 | 03:00 | 126 | 17:00 | Patiya | 138 | 04:00 | 132 | 12:00
Chandina | 140 | 04:00 | 133 | 12:00 | Patuakhali | 138 | 18:00 | 133 | 16:00
Chandpur | 141 | 23:00 | 133 | 16:00 | Payra | 139 | 00:00 | 135 | 14:00
Chandraghona | 140 | 04:00 | 133 | 14:00 | PHP | 136 | 03:00 | 129 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 139 | 02:00 | 133 | 12:00 | Postogola | 137 | 03:00 | 128 | 12:00
Charsaidpur | 138 | 04:00 | 129 | 12:00 | Purbachal | 136 | 04:00 | 124 | 12:00
Chauddagram | 137 | 03:00 | 130 | 16:00 | Purbasadipur | 136 | 23:00 | 125 | 12:00
Chhatak | 133 | 03:00 | 126 | 11:00 | Rahanpur | 140 | 03:00 | 135 | 11:00
Chowmuhani | 135 | 05:00 | 130 | 12:00 | Rahanpur-400 | 141 | 05:00 | 134 | 12:00
Chuadanga | 140 | 04:00 | 127 | 12:00 | Rahim | 139 | 03:00 | 130 | 12:00
Coxsbazar | 132 | 08:00 | 124 | 12:00 | Rajbari | 139 | 04:00 | 131 | 12:00
Cumilla(N) | 139 | 01:00 | 132 | 12:00 | Rajendrapur | 134 | 22:00 | 123 | 16:00
Cumilla(S) | 139 | 22:00 | 119 | 10:00 | Rajshahi | 138 | 23:00 | 130 | 12:00
Daganbhuiyan | 136 | 04:00 | 130 | 12:00 | Rajshahi-230 | 138 | 04:00 | 130 | 12:00
Daudkandi | 138 | 05:00 | 128 | 14:00 | Ramganj | 136 | 18:30 | 131 | 15:00
DhakaUniversity | 135 | 04:00 | 125 | 12:00 | Rampur | 137 | 02:00 | 131 | 12:00
Dhamrai | 138 | 00:00 | 129 | 16:00 | Rampura | 135 | 04:00 | 125 | 12:00
Dhanmondi | 140.4 | 05:00 | 131.5 | 12:00 | Rangamati | 138 | 07:00 | 132 | 16:00
Dohazari | 135 | 04:00 | 130 | 12:00 | Rangpur | 139 | 23:00 | 130 | 12:00
Faridpur | 138 | 03:00 | 130 | 12:00 | Ruppur | 142 | 03:00 | 135 | 12:00
Fatullah | 140 | 05:00 | 128 | 12:00 | Saidpur | 137 | 20:00 | 129 | 12:00
Fenchuganj | 138 | 23:00 | 135 | 13:00 | Satkhira | 136 | 04:00 | 123 | 13:00
Feni | 135 | 04:00 | 129 | 14:00 | Satmasjid | 139 | 03:00 | 129 | 12:00
Feni-230 | 136 | 04:00 | 129 | 12:00 | Savar | 141 | 08:00 | 131 | 12:00
Ghatail | 130 | 00:00 | 122 | 07:00 | SevenRings | 135 | 23:00 | 126 | 12:00
Ghorashal | 134 | 22:00 | 128 | 10:00 | ShahCement | 138 | 04:00 | 129 | 12:00
Goalpara | 139 | 05:00 | 127 | 13:00 | Shahjadpur | 142 | 03:00 | 135 | 16:00
Gollamari | 138 | 04:00 | 127 | 13:00 | Shahjibazar | 132 | 03:00 | 127 | 11:00
Gopalganj | 141 | 04:00 | 132 | 12:00 | Shahmirpur | 139 | 03:00 | 133 | 12:00
Gopalganj-400 | 143 | 03:00 | 136 | 12:00 | Shariatpur | 142 | 04:00 | 134 | 12:00
Gulshan | 134 | 04:00 | 124 | 12:00 | Sherpur | 129 | 11:00 | 116 | 02:00
Halishahar | 139 | 04:00 | 132 | 14:00 | Shikalbaha | 128 | 08:00 | 122 | 13:00
Haripur | 139 | 04:00 | 130 | 12:00 | Shikalbaha-230 | 140 | 06:00 | 133 | 16:00
HaripurSBU | 139 | 04:00 | 130 | 12:00 | Shitalakhya | 137 | 03:00 | 127 | 12:00
Hasnabad | 138 | 23:00 | 129 | 12:00 | Sholosohor | 139 | 04:00 | 132 | 16:00
Hathazari | 138 | 03:00 | 133 | 11:00 | Shyampur | 136 | 00:00 | 130 | 13:00
Hatirjheel | 135 | 05:00 | 125 | 12:00 | Shyampur-230 | 140 | 04:00 | 131 | 12:00
Ishurdi | 144 | 05:00 | 137 | 12:00 | Siddhirganj | 139 | 05:00 | 131 | 12:00
Jaldhaka | 135 | 22:00 | 125 | 12:00 | Sirajganj | 138 | 04:00 | 129 | 12:00
Jamalpur | 131 | 10:00 | 118 | 01:00 | Sonargaon | 137 | 04:00 | 129 | 14:00
Jashore | 138 | 03:00 | 126 | 12:00 | Sreemongol | 134 | 03:00 | 129 | 12:00
Jhenaidah | 141 | 05:00 | 126 | 07:00 | Sreepur | 136 | 19:00 | 127 | 12:00
Jhenaidah-230 | 140 | 02:00 | 128 | 08:00 | Srinagar | 138 | 05:00 | 126 | 12:00
Joydebpur | 131 | 23:00 | 123 | 12:00 | SSM | 140 | 00:00 | 135 | 16:00
Joypurhat | 134 | 18:00 | 125 | 12:00 | Sunamganj | 132 | 04:00 | 126 | 11:00
Juldah | 139 | 08:00 | 132 | 10:00 | Sylhet | 134 | 03:00 | 128 | 13:00
Kabirpur | 140 | 00:00 | 122 | 16:00 | Sylhet-132 | 133 | 02:00 | 128 | 12:00
Kachua | 139 | 03:00 | 133 | 16:00 | Tangail | 132 | 05:00 | 124 | 07:00
Kaliakoir | 141 | 23:00 | 132 | 16:00 | Taraganj | 137 | 22:00 | 127 | 12:00
Kallyanpur | 140 | 21:00 | 132 | 12:00 | Tasnim | 138 | 04:00 | 130 | 14:00
Kalurghat | 139 | 02:00 | 133 | 15:00 | Thakurgaon | 141 | 23:00 | 126 | 12:00
Kamrangirchar | 137 | 04:00 | 125 | 12:00 | TK | 138 | 08:00 | 133 | 12:00
Kaptai | 140 | 2:00 | 135 | 16:00 | Tongi | 136 | 00:00 | 128 | 15:00
Kasba | 138 | 03:00 | 130 | 12:00 | Ullahpara | 140 | 03:00 | 130 | 13:00
Kazla | 139 | 04:00 | 126 | 13:00 | Ullon | 135 | 05:00 | 124 | 12:00
Keranigonj | 137 | 04:00 | 127 | 12:00 | Uttara | 135 | 03:00 | 123 | 16:00
Khagrachori | 138 | 05:00 | 132 | 12:00 | UttaraNew | 140 | 23:00 | 131 | 12:00
Khulna | 136 | 04:00 | 125 | 13:00 | Zigatola | 136 | 02:00 | 126 | 13:00
Khulna(S) | 138 | 04:00 | 128 | 12:00
Khulshi | 137 | 08:00 | 127 | 10:00
Kishoreganj | 135 | 23:00 | 127 | 12:00
Kodda | 138 | 08:00 | 126 | 16:00
KSRM | 139 | 04:00 | 132 | 13:00
Kulaura | 137 | 01:00 | 134 | 12:00
Kurigram | 136 | 23:00 | 122 | 12:00
Kushtia | 139 | 06:00 | 133 | 12:00
Laksam | 139 | 03:00 | 133 | 16:00
Lakshmipur | 135 | 01:00 | 130 | 12:00
Lalbag | 137 | 04:00 | 126 | 12:00
Lalmonirhat | 135 | 22:00 | 125 | 12:00
Madanganj | 138 | 08:00 | 132 | 07:00
Madaripur | 140 | 00:00 | 135 | 12:00
Madartek | 135 | 05:00 | 123 | 12:00
Madunaghat | 138 | 03:00 | 132 | 11:00
Magura | 139 | 03:00 | 127 | 13:00
Mahasthangarh | 138 | 23:00 | 130 | 12:00
|  | Sub Assistant Engineer |  |  |  | Sub Divisional Engineer
|  | Network Operation Division |  |  |  | Network Operation Division