## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 20-01-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-01-2026 | during | 20-01-2026 | during | 20-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 336 | 347 | 412 | 412 | 392 | 392 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 45 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 260 | 260 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 51.2 | 51.3 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 48 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 24 | 23 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 0 | 15.1 | 15.1 | 15.1 | 15.1 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 34 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 278 | 260 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 147 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 72 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 142 | 143 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 28 | 0 | 27 | 0 | 27 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 54 | 54 | 55 | 55 | 55 | 55 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 350 | 465 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 142 | 125 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1929.2 | 2166.3 | 5334.25 | 5307.25 | 2617.13 | 2590.13
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 32 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 40 | 46 | 46 | 46 | 46 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 186 | 186 | 150 | 150 | 150 | 150 | Plant availability less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 16 | 103 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 16 | 16 | 16 | 16 | 16 | 16 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 51 | 51 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 60 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 3 | 13 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.28 | 0 | 3.22 | 0 | 3.22 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 45 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 48 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 84 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1205 | 1175 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 2 | 18 | 2 | 18 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 355 | 355 | 355 | 355 | 355 | 355 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1874.28 | 2233 | 3102.08 | 3103.86 | 2704.72 | 2706.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 191 | 197 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 280 | 280 | 353.35 | 353.35 | 353.35 | 353.35 | STG Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 0 | 0 | Under maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 220 | 220 | 393 | 393 | 250 | 250 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 10 | 10 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | Gas shortage
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 143 | 150 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 17 | 42 | 42 | 42 | 42 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 80 | 163 | 163 | 115 | 115 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 84 | 136 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 104 | 108 | 84 | 82 | 114 | 114 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 13 | 24.5 | 24.5 | 24.5 | 24.5 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 34 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 9 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 15 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 63 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1227 | 1318 | 2437.75 | 2370.75 | 1850.05 | 1785.05
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-01-2026 | during | 20-01-2026 | during | 20-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 34 | 34 | 157.5 | 157.5 | 50 | 50 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 18 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 59 | 60 | 60 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 40.79 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 166.79 | 158 | 358.1 | 314 | 240.6 | 196.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 42 | 42 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 52 | 52 | 60 | 60 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 163 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 83 | 83 | 83 | 83 | 83 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 20 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 325 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 808 | 816 | 844 | 844 | 734 | 734
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 452 | 452 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 323 | 302 | 410 | 410 | 369 | 369 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 33 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 70.39 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1130 | 1134 | 1148.28 | 1148.28 | 1148 | 1148 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1992.39 | 1921 | 3495.28 | 3420.28 | 2699.1 | 2624.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 77 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 130 | 130 | 136 | 136 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 597 | 596 | 622 | 622 | 575 | 575 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 35 | 70 | 150 | 150 | 150 | 150 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 286 | 307 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.5 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1268.5 | 1400 | 1546 | 1545 | 1479 | 1478
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 45.15 | 0 | 43 | 0 | 43 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 195 | 191 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 60 | 90 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 90 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.14 | 0 | 5 | 0 | 5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 768 | 765 | 748 | 748 | 748 | 748 | U#1 Under AOH
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 48.02 | 0 | 60 | 0 | 60 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 84 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1294.31 | 1184 | 2027.2 | 1819.2 | 1533.8 | 1325.8
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 58 | 58 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 107 | 107 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.3 | 0 | 4.8 | 0 | 4.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 140 | 0 | 136.85 | 0 | 136.85 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 397.3 | 222 | 433.65 | 262 | 457.65 | 286
System Total |  |  |  |  | 28823.2 | 28382.248 | 10957.77 | 11418.3 | 19578.31 | 18986.34 | 14316.05 | 13726.08
Forecast Scenario (20-01-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9270 |  | 0 |  | 9270
|  |  |  | 1:00 | 8690 |  | 0 |  | 8690
|  |  |  | 2:00 | 8310 |  | 0 |  | 8310
|  |  |  | 3:00 | 7980 |  | 0 |  | 7980
|  |  |  | 4:00 | 7660 |  | 0 |  | 7660
|  |  |  | 5:00 | 7720 |  | 0 |  | 7720
|  |  |  | 6:00 | 8030 |  | 0 |  | 8030
|  |  |  | 7:00 | 8940 |  | 0 |  | 8940
|  |  |  | 8:00 | 10030 |  | 0 |  | 10030
|  |  |  | 9:00 | 10410 |  | 0 |  | 10410
|  |  |  | 10:00 | 10040 |  | 0 |  | 10040
|  |  |  | 11:00 | 10020 |  | 0 |  | 10020
|  |  |  | 12:00 | 10450 |  | 0 |  | 10450
|  |  |  | 13:00 | 11000 |  | 0 |  | 11000
|  |  |  | 14:00 | 10520 |  | 0 |  | 10520
|  |  |  | 15:00 | 10030 |  | 0 |  | 10030
|  |  |  | 16:00 | 9840 |  | 0 |  | 9840
|  |  |  | 17:00 | 10120 |  | 0 |  | 10120
|  |  |  | 18:00 | 11110 |  | 0 |  | 11110
|  |  |  | 18:30 | 11300 |  | 0 |  | 11300
|  |  |  | 19:00 | 11530 |  | 0 |  | 11530
|  |  |  | 19:30 | 11320 |  | 0 |  | 11320
|  |  |  | 20:00 | 11250 |  | 0 |  | 11250
|  |  |  | 21:00 | 10910 |  | 0 |  | 10910
|  |  |  | 22:00 | 10590 |  | 0 |  | 10590
|  |  |  | 23:00 | 9820 |  | 0 |  | 9820
Probable Maximum Temperature: |  |  | 26.80°C
Probable Maximum Demand at Day Peak: |  |  | 10450.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11530.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11530.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 234.27 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:24 hrs on 20-01-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 19-01-2026
Power Supply Scenario
| Day Peak Generation |  |  | 10957.77 | MW | 12:00 Hr. | Energy Generated |  |  | 241.6321 |  | MKWHr.
| Day Peak Demand |  |  | 10967.77 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.282 |  | MKWHr.
| Evening Peak Generation |  |  | 11418.3 | MW | 19:00 Hr. | Energy Demand |  |  | 241.9141 |  | MKWHr.
| Evening Peak Demand |  |  | 11418.3 | MW | 19:00 Hr. | Maximum Temperature |  |  | 27.7 |  | °C
| Minimum Generation of the Day |  |  | 7911.76 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 680.12 |  | MMCFD
| Maximum Generation of the Day |  |  | 11418.3 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.8868 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 25.0723 | 0 | 14.5566 | 0 | 0 | 0.17089 | 0 | 0 | 39.7998 | Gas | 89.607 | Gas | 316694407.7052
| Chattogram Zone |  |  | 4.7318 | 36.4327 | 3.4289 | 0 | 1.0762 | 0.15147 | 0 | 0.01728 | 45.8384 | Coal | 83.9531 | Coal | 548125087.692
| Cumilla Zone |  |  | 18.9123 | 0 | 4.5496 | 0 | 0 | 0.40166 | 2.3261 | 0 | 26.1897 | HFO | 32.1917 | HFO | 551128286.422
| Mymensingh Zone |  |  | 0.87168 | 0 | 1.8556 | 0 | 0 | 0.25406 | 0 | 0 | 2.9813 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 19.2836 | 0 | 0 | 0 | 0 | 0.060888 | 0 | 0 | 19.3445 | Hydro | 1.0762 | Hydro | 107622
| Khulna Zone |  |  | 7.6954 | 26.0146 | 0.40512 | 0 | 0 | 0.45432 | 10.9462 | 0 | 45.5156 | Solar | 3.6393 | Solar | 57153435.256
| Barishal Zone |  |  | 8.4692 | 21.5057 | 1.1365 | 0 | 0 | 0.002886 | 0 | 0 | 31.1143 | Import | 31.1476 | Import | 190609877.4
| Rajshahi Zone |  |  | 4.5707 | 0 | 2.8026 | 0 | 0 | 1.1173 | 17.8753 | 0 | 26.366 | Wind | 0.01728 | Wind | 254188.8
| Rangpur Zone |  |  | 0 | 0 | 3.4568 | 0 | 0 | 1.0258 | 0 | 0 | 4.4826
| Total |  |  | 89.607 | 83.9531 | 32.1917 | 0 | 1.0762 | 3.6393 | 31.1476 | 0.01728 | 241.6321
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 316694407.7052 |  | Hydro | 107622
|  |  |  | Coal | 548125087.692 |  | Solar | 57153435.256
|  |  |  | HFO | 551128286.422 |  | Import | 190609877.4
|  |  |  | HSD | 0 |  | Wind | 254188.8
[5 empty] | Total: | 166,40,72,905 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 10.9462 | Peak Hr Flow | 452.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 31627091.57 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 17.8753 | Peak Hr Flow | 765.00 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1241 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.3261 | Peak Hr Flow | 108.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1904 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 31.1476 | Peak Hr Flow | 1325.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4302
|  |  |  | Chattogram |  | 0 |  | 1183
|  |  |  | Cumilla |  | 0 |  | 960
|  |  |  | Mymensingh |  | 0 |  | 906
|  |  |  | Sylhet |  | 0 |  | 423
|  |  |  | Khulna |  | 0 |  | 1267
|  |  |  | Barishal |  | 0 |  | 304
|  |  |  | Rajshahi |  | 0 |  | 1014
|  |  |  | Rangpur |  | 0 |  | 688
|  |  |  | Total |  | 0 |  | 11047
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:05 | 17:17 | Fenchuganj 230/132/33kV S/S TR-01 LT Scheduled S/D Due to 132 KV BUS-1 Shutdown for
Annual Maintenance
| 08:10 | 17:17 | Fenchuganj 230/132/33kV S/S TR-01 HT Scheduled S/D Due to 132 KV BUS -1 Shutdown
| 08:11 | 17:12 | Payra 400/132/33kV S/S 132/33 kV Transformer-03 LT Scheduled S/D Due to Maintenance
| 08:11 | 17:10 | Payra 400/132/33kV S/S 132/33 kV Transformer-03 HT Scheduled S/D Due to Maintenance
| 08:11 | 17:10 | Payra 400/132/33kV S/S 132/33 kV Transformer-03 HT Scheduled S/D Due to Maintenance
| 08:19 |  | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT Project Work S/D Due to Development Work.
| 08:20 |  | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT Project Work S/D Due to Development Work
| 08:22 | 15:32 | Daudkandi-Sonargaon 132 kV Ckt-2 Scheduled S/D from Daudkandi 132/33kV end Due to Annual
maintenance and from Sonargaon 132/33kV end Due to Annual maintenance deadline checking
&Bay maintenance..
| 08:22 | 16:42 | Kaliakoir-Tongi 230kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to Annual
Maintenance Disk Cleaning work and from Tongi 230/132/33kV end Due to Shutdown taken by
kalaikair ss
| 08:26 | 17:16 | Taraganj 132/33kV S/S Taraganj-Rangpur CKT-02 Scheduled S/D
| 08:26 | 16:55 | Taraganj 132/33kV S/S Taraganj-Saidpur CKT-01 Scheduled S/D Due to deadline checking
| 08:27 | 17:14 | Rangpur-Saidpur 132kV Ckt-2 Scheduled S/D from Rangpur 132/33kV end Due to Annual
Maintenance ⛑.
| 08:28 | 16:55 | Rangpur-Saidpur 132kV Ckt-1 Scheduled S/D from Saidpur 132/33kV end Due to Annual
maintenance
| 08:33 |  | Madunaghat-Meghnaghat 400kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end Due to
maintenance work
| 08:35 | 16:15 | Bogura-Rahanpur 400kV Ckt-1 Scheduled S/D from Bogura 400/230kV end Due to Annual
Maintenance and from Rahanpur 400/132kV end Due to Annual maintenance work
| 08:35 | 16:06 | Aminbazar-Kaliakoir 230kV Ckt-1 Scheduled S/D from Kaliakoir 400/230/132kV end Due to
Annual Maintenance Disk Cleaning work
| 08:35 | 17:09 | Fenchuganj 230/132/33kV S/S 132 KV Bus-1 Scheduled S/D Due to For Annual Maintenance
| 08:56 | 17:04 | Aminbazar 400/230/132kV S/S ATR-02 LT Scheduled S/D Due to Annual maintenance
| 08:59 | 17:02 | Aminbazar 400/230/132kV S/S ATR-02 HT Scheduled S/D Due to Annual maintenance
| 09:01 | 16:39 | Goalpara-Labanchura 132kV Ckt-2 Scheduled S/D from Goalpara 132/33kV end Due to Annual
Maintenance.
| 09:01 | 10:30 | Fenchuganj-Kulaura 132 kV Ckt-1 Scheduled S/D from Kulaura 132/33kV end Due to Fenchuganj
ckt-1 shutdown for maintenance by NLDC AE and from Fenchuganj 230/132/33kV end Due to
Annual Maintenance
|  | 09:15 | Shahjadpur 132/33kV S/S Main Bus is restored.
| 09:18 | 17:02 | Gopalganj 400/132kV S/S 400kV Rampal Ckt-1 Scheduled S/D Due to Annual maintenance
| 09:19 | 17:05 | Rampal 400/230kV S/S Gopalganj Line-1 Reactor Forced S/D Due to Khulna ALDC Demand(Annual
Maintenance)
| 09:20 | 17:02 | Gopalganj(N)-Rampal Ckt-1 Forced S/D from Rampal 400/230kV end Due to Khulna ALDC
Demand(Annual Maintenance)
| 09:22 | 16:47 | Mirpur 132/33kV S/S Main Bus Scheduled S/D Due to M/B Ds of Aminbazar Ckt-2 & Uttara old
ckt Annual Maintenance work.
| 09:23 | 20:01 | Shyampur-Shyampur(New) 132kV Ckt-2 Project Work S/D from Shyampur 230/132kV end Due to
Project work of DPDC.
| 09:24 | 16:49 | Kallyanpur 132/33kV S/S GT-1 (132kV) LT Scheduled S/D Due to DPDC 33kv bus shut down.
| 09:26 | 16:52 | Kallyanpur 132/33kV S/S GT-3 (132kV) LT Scheduled S/D Due to DPDC 33kv bus shut down.
| 09:30 |  | Kabirpur -Kodda 132kV Ckt-1 Scheduled S/D from Kabirpur 132/33kV end Due to Annual
maintenance (deadline checking)
| 09:34 | 15:38 | Sirajganj-Ullahpara 132KV Ckt-2 Scheduled S/D from Sirajganj 132/33kV end Due to Annual
Maintenance and from Ullahpara 132/33kV end Due to Annual maintenance Work
| 09:53 | 14:27 | Keranigonj 230/132/33kV S/S 132 kV Hasnabad Ckt. 1 Scheduled S/D Due to Dead line
checking at Hasnabad end.
| 09:53 | 15:49 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Cumilla(N) Ckt-01 Scheduled S/D Due to
maintenance work
| 10:02 | 14:28 | Aggreko-keraniganj 132kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to Dead
line checking at Hasnabad end.
| 10:02 | 14:28 | Aggreko-keraniganj 132kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to Dead
line checking at Hasnabad end.
| 10:10 | 18:01 | Sreepur 230/132/33kV S/S 230/132 kV T-2 LT Scheduled S/D Due to Annual Maintenance
| 10:10 | 18:00 | Sreepur 230/132/33kV S/S 230/132 kV T-2 HT Scheduled S/D Due to Annual Maintenance
|  | 10:19 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-2 is restored.
| 10:30 | 15:22 | Fenchuganj-Kulaura 132 kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Annual Maintenance and from Kulaura 132/33kV end Due to Fenchuganj ckt-2 shutdown for
maintenance by NLDC AE
|  | 10:58 | Kachua 230/132/33kV S/S TR-1 HT is restored.
| 11:07 |  | Purbasadipur-Thakurgaon-EPV 132kV Ckt-2 Project Work S/D from Thakurgaon 132/33kV end
Due to FOR RECONDUCTOING WORK
| 11:08 | 13:40 | AKSML-Baroaulia 132kV Ckt-1 Forced S/D from Baroaulia 132/33kV end Due to For maintenance | [7 empty] | 45.0MW load
|  |  | work of AKSPL's DS and from AKS 132/33kV end Due to AKSPL to Baraulia 132 KV Line | [7 empty] | interrup. Baroaulia
|  |  | Baraulia Line DS (104S) R-Phase spark (Flash) occurred. AKSPL-Baraulia & AKSPL-Khulshi | [7 empty] | 132/33kV end
Line forced S/D according to AKSPL S/S Demand for emergency maintenance.
| 11:18 | 12:35 | Ghorasal-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Shutdown
taken by Ghorashal ss
| 11:19 | 13:53 | Dohazari-Sikalbaha 132 kV Ckt-1 Scheduled S/D from Dohazari 132/33kV end Due to Loop
connection work from Line DS to newly installed CT (R-phase).
| 11:31 |  | Madunaghat 400/230kV S/S Madunaghat-Meghnaghat 400kV Ckt.-2 Scheduled S/D
| 11:31 | 20:25 | Tongi 230/132/33kV S/S Tongi-Tongi 80 MW PS Scheduled S/D Due to Kabirpur panel
instillation
| 11:31 | 16:15 | Tongi 230/132/33kV S/S Tongi-Dhaka Metro Rail Ckt Scheduled S/D Due to Kabirpur Panel
installation
| 11:52 | 13:30 | AKSML-Khulshi 132kV Ckt-1 Forced S/D from AKS 132/33kV end Due to AKSPL to Baraulia 132
KV Line Baraulia Line DS (104S) R-Phase spark (Flash) occurred. AKSPL-Baraulia &
AKSPL-Khulshi Line forced S/D according to AKSPL S/S Demand for emergency maintenance.
| 11:54 | 19:55 | Tongi 230/132/33kV S/S T-2 HT Scheduled S/D Due to Panel meter shifting
| 11:54 | 19:56 | Tongi 230/132/33kV S/S T-2 LT Scheduled S/D Due to Panel meter shifting
| 12:00 |  | Day Peak Generation: 10955 MW.
| 14:21 | 15:18 | Sirajganj 132/33kV S/S T4-(445) HT Forced S/D Due to S/D taken by Sirajgonj PBS-2 for | [7 empty] | 20.0MW load
|  |  | 33kV Economic Zone feeder BUS DS insulator replacement | [7 empty] | interrup.
| 14:21 | 15:18 | Sirajganj 132/33kV S/S T4-(445) LT Forced S/D Due to S/D taken by Sirajgonj PBS-2 for
33kV Economic Zone feeder BUS DS insulator replacement.
| 14:28 | 17:40 | Faridpur 132/33kV S/S 132 KV Rajbari ckt-2 Forced S/D Due to Circuit breaker maintenance
| 15:40 | 16:43 | Fenchuganj-Sreemangal 132kV Ckt-2 Scheduled S/D from Sreemongol 132/33kV end Due to
Annual Maintenance at Fenchuganj End and from Fenchuganj 230/132/33kV end Due to Annual
maintenance
|  | 16:11 | Ashuganj-Bhulta 400 kV Ckt-1 is restored.
|  | 16:47 | Mirpur 132/33kV S/S Main Bus is restored.
|  | 17:05 | Moghbazar-Rampura 132kV Ckt-1 is restored.
|  | 17:12 | Payra 400/132/33kV S/S 132/33 kV Transformer-03 LT is restored.
|  | 17:32 | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) HT is restored.
|  | 17:35 | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) LT is restored.
| 17:44 | 01:15 | Maniknagar-Siddhirganj 230kV Ckt-2 Tripped from Maniknagar 230/132kV end showing 1.RED670
2.REL-670 relays.
| 18:35 | 01:13 | Maniknagar-Siddhirganj 230kV Ckt-2 Scheduled S/D from Siddhirganj 230/132kV end Due to
Replace LA
| 19:00 |  | Evening peak Generation is 11418 MW
|  | 19:59 | Sylhet 132/33kV S/S Sylhet-90MW P/S is restored.
| 05:00 |  | Minimum Generation: 7911 MW.
| 07:12 |  | Ashuganj-Bhulta 400 kV Ckt-1 Scheduled S/D from Bhulta 400/230kV end.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 19-01-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 347 | 8258400 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 45 | 248157 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 260 | 6516948 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 51.3 | 907560 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 48 | 139680 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 580545 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 838003 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 461400 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 0 | 316440 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 34 | 289920 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 260 | 3467815 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2572992 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 72 | 493440 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 143 | 2600640 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 170894 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 649080 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 465 | 9519091 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 125 | 1768800 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 2166.3 | 39799805
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 8247.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 130950 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 32 | 186720 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 1076220 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 186 | 4281118 | Plant availability less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 103 | 1067199 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 16 | 183268 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 148506 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 60 | 309120 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 13 | 450720 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20520 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 45 | 323673 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 48 | 234180 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 476160 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 65236 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 84 | 426545 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1175 | 27850906 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 17280 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 355 | 8581818.18 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4898.863 | 2233 | 45838386.78
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 197 | 4745000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 280 | 7251600 | STG Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Under maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 220 | 5344500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1291685 | Gas shortage
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 2164509 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 17 | 96416 | Partial Shutdown due to maintenance
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1905.02 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 136 | 1902720 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 108 | 2326080 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 72946 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 277630 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 158460 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 33600 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 15 | 120960 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 401664 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1318 | 26189675.02
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 34 | 871680 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10650 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 18 | 326400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 1100400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 243410 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 223920 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 204840 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 158 | 2981300
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 60888 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 993000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 52 | 1274160 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3799391 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 715200 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1892160 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2407950 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 474240 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 325 | 7727500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 816 | 19344489
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 452 | 10946181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 302 | 7695360 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 33 | 405120 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 454320 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1134 | 26014600 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1921 | 45515581
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 77 | 403296 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 3053000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 596 | 14392727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5416220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 70 | 733200 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7113000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2886 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1400 | 31114329.27
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 276924 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 45000 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 115404 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 191 | 4570727 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 0 | 0 | Under Maintenance
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 90 | 1412832 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1229376 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 24720 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 765 | 17875328 | U#1 Under AOH
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 285744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 529910 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1184 | 26365965
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 1719398 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 32213.28 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1737422 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 173500 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 820080 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 222 | 4482613.28
Eastern Grid Total |  |  |  |  | 17398.245 | 6691.3 | 134153655.8
Western Grid Total |  |  |  |  | 10984.003 | 4727 | 107478488.55
National Grid Total |  |  |  |  | 28382.248 | 11418.3 | 241632144.35
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 19-01-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7773.72 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3272.8 | MW
i) Dhaka area |  |  | 4302.12 |  | MW | i) Khulna area |  |  |  | 1267 | MW
ii) Chattogram area |  |  | 1183.1 |  | MW | ii) Barishal area |  |  |  | 304.2 | MW
iii) Cumilla area |  |  | 959.5 |  | MW | iii) Rajshahi area |  |  |  | 1013.6 | MW
iv) Mymensingh area |  |  | 906 |  | MW | iv) Rangpur area |  |  |  | 688 | MW
v) Sylhet area |  |  | 423 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11046.52 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 13 | 18:00 | 67 | Hasnabad | 65 | 12:00 | 133 | Netrakona | 125 | 10:00
2 | AKSML | 113 | 02:00 | 68 | Hathazari | 58 | 18:00 | 134 | New | 61 | 12:00
3 | Aftabnagar | 26 | 13:00 | 69 | Hatirjheel | 29 | 16:00 | 135 | Niamatpur | 74 | 08:00
4 | Agargaon | 91 | 13:00 | 70 | Ishurdi | 48 | 18:30 | 136 | Noapara | 38 | 18:30
5 | Agrabad | 48 | 18:00 | 71 | Jaldhaka | 58 | 18:30 | 137 | PHP | 8 | 21:00
6 | Amnura | 31 | 08:00 | 72 | Jamalpur | 91 | 07:00 | 138 | Pabna | 76 | 19:30
7 | Ashuganj | 72 | 13:00 | 73 | Jashore | 104 | 09:00 | 139 | Palashbari | 82 | 08:00
8 | BSRM | 202 | 18:00 | 74 | Jhenaidah | 108 | 08:00 | 140 | Panchagarh | 41 | 18:00
9 | Bagerhat | 67 | 18:30 | 75 | Joydebpur | 118 | 19:00 | 141 | Patiya | 6.5 | 18:00
10 | Bajitpur | 58 | 19:00 | 76 | Joypurhat | 42 | 08:00 | 142 | Patuakhali | 38 | 19:30
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 17.5 | 13:00 | 143 | Payra | 28 | 18:30
12 | Bakulia | 65 | 13:00 | 78 | KSRM | 14 | 02:00 | 144 | Postogola | 40 | 12:00
13 | Banani | 38 | 12:00 | 79 | Kabirpur | 204 | 18:30 | 145 | Purbachal | 22 | 13:00
14 | Bangabhaban | 9 | 11:00 | 80 | Kachua | 64 | 18:00 | 146 | Purbasadipur | 108 | 09:00
15 | Barapukuria | 52 | 18:30 | 81 | Kallyanpur | 75 | 18:00 | 147 | Rahanpur | 24 | 20:00
16 | Barguna | 14 | 18:30 | 82 | Kalurghat | 34 | 12:00 | 148 | Rahim | 51 | 11:00
17 | Barishal | 90 | 13:00 | 83 | Kamrangirchar | 70 | 13:00 | 149 | Rajbari | 60 | 18:30
18 | Barishal-230 | 68 | 21:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 111 | 18:30
19 | Baroaulia | 59 | 11:00 | 85 | Kasba | 25 | 19:30 | 151 | Rajshahi | 78 | 18:30
20 | Baroirhat | 49 | 18:00 | 86 | Kazla | 93 | 13:00 | 152 | Rajshahi-230 | 57 | 21:00
21 | Bashundhara | 157 | 13:00 | 87 | Keranigonj | 79 | 13:00 | 153 | Ramganj | 68 | 18:00
22 | BashundharaCement | 7 | 00:00 | 88 | Khagrachori | 26 | 18:00 | 154 | Rampur | 28 | 13:00
23 | Beanibazar | 46 | 18:00 | 89 | Khulna | 47 | 19:00 | 155 | Rangamati | 13 | 18:00
24 | Benapole | 66 | 08:00 | 90 | Khulshi | 151 | 16:00 | 156 | Rangpur | 108 | 08:00
25 | Bhaluka | 138 | 08:00 | 91 | Kishoreganj | 98 | 21:00 | 157 | Ruppur | 2.6 | 15:00
26 | Bhandaria | 38 | 21:00 | 92 | Kodda | 262 | 18:30 | 158 | SSM | 13 | 00:00
27 | Bhangura | 25 | 18:00 | 93 | Kulaura | 29 | 18:00 | 159 | Saidpur | 90 | 09:00
28 | Bheramara(GK) | 42 | 18:00 | 94 | Kurigram | 52 | 18:30 | 160 | Satkhira | 106 | 08:00
29 | Bhulta | 205 | 22:00 | 95 | Kushtia | 110 | 12:00 | 161 | Satmasjid | 86 | 13:00
30 | Bog-Sherpur | 58 | 18:00 | 96 | Laksam | 14 | 21:00 | 162 | Savar | 174 | 09:00
31 | Bogura | 118 | 12:00 | 97 | Lakshmipur | 25 | 20:00 | 163 | SevenRings | 16.69 | 04:00
32 | Borhanuddin | 65 | 21:00 | 98 | Lalbag | 54 | 12:00 | 164 | ShahCement | 35 | 23:00
33 | Brahmanbaria | 90 | 13:00 | 99 | Lalmonirhat | 46 | 18:30 | 165 | Shahjadpur | 58 | 10:00
34 | Cantonment | 72 | 13:00 | 100 | MI_Cement | 10 | 23:00 | 166 | Shahjibazar | 99 | 21:00
35 | Chandina | 14 | 12:00 | 101 | Madanganj | 29 | 13:00 | 167 | Shahmirpur | 40 | 18:00
36 | Chandpur | 54 | 19:30 | 102 | Madaripur | 71 | 19:30 | 168 | Shariatpur | 57 | 22:00
37 | Chandraghona | 28 | 18:00 | 103 | Madartek | 61 | 13:00 | 169 | Sherpur | 120 | 21:00
38 | Chapai | 56 | 12:00 | 104 | Madunaghat | 39 | 18:00 | 170 | Shikalbaha | 21 | 20:00
39 | Charsaidpur | 43 | 23:00 | 105 | Magura | 50 | 18:30 | 171 | Shitalakhya | 69 | 12:00
40 | Chauddagram | 55 | 13:00 | 106 | Mahasthangarh | 50 | 18:30 | 172 | Sholosohor | 33 | 15:00
41 | Chhatak | 30 | 18:00 | 107 | Maijdee | 33 | 19:00 | 173 | Shyampur | 124 | 23:00
42 | Chowmuhani | 113 | 18:00 | 108 | Manikganj | 96 | 18:00 | 174 | Siddhirganj | 111 | 12:00
43 | Chuadanga | 79 | 08:00 | 109 | Maniknagar | 48 | 13:00 | 175 | Sirajganj | 92 | 18:00
44 | Coxsbazar | 106 | 18:00 | 110 | Matarbari | 41 | 18:00 | 176 | Sonargaon | 147 | 18:00
45 | Cumilla(N) | 121 | 21:00 | 111 | Matuail | 55 | 17:00 | 177 | Sreemongol | 62 | 18:30
46 | Cumilla(S) | 114 | 18:00 | 112 | Metrorail_Motijheel | 22 | 17:00 | 178 | Sreepur | 88 | 11:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 8 | 09:00 | 179 | Srinagar | 32.9 | 14:00
48 | Daudkandi | 120 | 20:00 | 114 | Millgate | 74 | 15:00 | 180 | Sunamganj | 40 | 18:00
49 | DhakaUniversity | 56 | 13:00 | 115 | Mirpur | 109 | 19:00 | 181 | Sylhet | 42 | 14:00
50 | Dhamrai | 110 | 12:00 | 116 | Mirsorai | 10 | 18:00 | 182 | Sylhet-132 | 71 | 18:30
51 | Dhanmondi | 81.7 | 13:00 | 117 | Mirzapur | 39 | 21:00 | 183 | TK | 17 | 18:30
52 | Dohazari | 76 | 19:30 | 118 | Mithapukur | 45 | 18:00 | 184 | Tangail | 130 | 07:00
53 | Faridpur | 119 | 19:30 | 119 | Modern | N/A | N/A | 185 | Taraganj | 17 | 08:00
54 | Fatullah | 91 | 12:00 | 120 | Mogbazar | 53.6 | 14:00 | 186 | Tasnim | 36 | 08:00
55 | Fenchuganj | 21 | 13:00 | 121 | Mongla | 36 | 08:00 | 187 | Thakurgaon | 75 | 08:00
56 | Feni | 71 | 18:00 | 122 | Motijheel | 36 | 13:00 | 188 | Tongi | 122 | 12:00
57 | GPH | 100 | 10:00 | 123 | Muktagacha | 31 | 08:00 | 189 | Ullahpara | 27 | 18:30
58 | Ghatail | 64 | 07:00 | 124 | Munshiganj | 75 | 22:00 | 190 | Ullon | 38 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 0 | 00:00 | 191 | Uttara | 60 | 13:00
60 | Ghorashal-230 | 92 | 17:00 | 126 | Mymensingh | 148 | 13:00 | 192 | UttaraNew | 30 | 13:00
61 | Goalpara | 27 | 08:00 | 127 | Naogaon | 97 | 08:00 | 193 | Zigatola | 76 | 14:00
62 | Gollamari | 80 | 12:00 | 128 | Narail | 46 | 18:30
63 | Gopalganj | 84 | 18:30 | 129 | Narinda | 58 | 13:00
64 | Gulshan | 76 | 13:00 | 130 | Narshingdi | 141 | 19:00
65 | Halishahar | 61 | 16:00 | 131 | Natore | 102 | 22:00
66 | HaripurSBU | 111 | 23:00 | 132 | Nawabganj | 32.4 | 14:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 19-01-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 9632.6 | 0 |  | 9632.6
1:00 | 8892.45 | 0 |  | 8892.45
2:00 | 8464.87 | 0 |  | 8464.87
3:00 | 8254.85 | 0 |  | 8254.85
4:00 | 8055.58 | 0 |  | 8055.58
5:00 | 7911.76 | 0 |  | 7911.76
6:00 | 8243.75 | 0 |  | 8243.75
7:00 | 9075.08 | 0 |  | 9075.08
8:00 | 10177.24 | 26 |  | 10204.24
9:00 | 10667.24 | 0 |  | 10667.24
10:00 | 10361.98 | 0 |  | 10361.98
11:00 | 10370.05 | 0 |  | 10370.05
12:00 | 10957.77 | 10 |  | 10967.77
13:00 | 11104.7 | 246 |  | 11361.7
14:00 | 10700.49 | 0 |  | 10700.49
15:00 | 10333.64 | 0 |  | 10333.64
16:00 | 10191.22 | 0 |  | 10191.22
17:00 | 10423.13 | 0 |  | 10423.13
18:00 | 11078.6 | 0 |  | 11078.6
19:00 | 11418.3 | 0 |  | 11418.3
19:30 | 11399.3 | 0 |  | 11399.3
20:00 | 11324.6 | 0 |  | 11324.6
21:00 | 11345.2 | 0 |  | 11345.2
22:00 | 10957 | 0 |  | 10957
23:00 | 10164.1 | 0 |  | 10164.1
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 19-01-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5519.6 | 4113 | 9632.6 | DAILY GENERATION CURVE
00:30 | 5191.05 | 4071.475 | 9262.525
01:00 | 4862.5 | 4029.95 | 8892.45 | 19-01-2026
01:30 | 4662 | 4016.66 | 8678.66
02:00 | 4461.5 | 4003.37 | 8464.87
02:30 | 4480.5 | 3879.36 | 8359.86
03:00 | 4499.5 | 3755.35 | 8254.85
03:30 | 4464.5 | 3690.715 | 8155.215
04:00 | 4429.5 | 3626.08 | 8055.58
04:30 | 4418.75 | 3564.92 | 7983.67
05:00 | 4408 | 3503.76 | 7911.76
05:30 | 4497 | 3580.755 | 8077.755
06:00 | 4586 | 3657.75 | 8243.75
06:30 | 4764.81 | 3894.605 | 8659.415
07:00 | 4943.62 | 4131.46 | 9075.08
07:30 | 5290.295 | 4335.865 | 9626.16
08:00 | 5636.97 | 4540.27 | 10177.24
08:30 | 5770.1 | 4652.14 | 10422.24
09:00 | 5903.23 | 4764.01 | 10667.24
09:30 | 5868.17 | 4646.44 | 10514.61
10:00 | 5833.11 | 4528.87 | 10361.98
10:30 | 5807.275 | 4558.74 | 10366.015
11:00 | 5781.44 | 4588.61 | 10370.05
11:30 | 5893.355 | 4770.555 | 10663.91
12:00 | 6005.27 | 4952.5 | 10957.77
12:30 | 6046.425 | 4984.81 | 11031.235
13:00 | 6087.58 | 5017.12 | 11104.7
13:30 | 5982.72 | 4919.875 | 10902.595
14:00 | 5877.86 | 4822.63 | 10700.49
14:30 | 5736.11 | 4780.955 | 10517.065
15:00 | 5594.36 | 4739.28 | 10333.64
15:30 | 5589.595 | 4672.835 | 10262.43
16:00 | 5584.83 | 4606.39 | 10191.22
16:30 | 5742.905 | 4564.27 | 10307.175
17:00 | 5900.98 | 4522.15 | 10423.13
17:30 | 6183.29 | 4567.575 | 10750.865
18:00 | 6465.6 | 4613 | 11078.6
18:30 | 6578.45 | 4670 | 11248.45
19:00 | 6691.3 | 4727 | 11418.3
19:30 | 6633.3 | 4766 | 11399.3
20:00 | 6554.6 | 4770 | 11324.6
20:30 | 6548.4 | 4786.5 | 11334.9 |  | Executive Engineer
21:00 | 6542.2 | 4803 | 11345.2 |  | Network Operation Division
21:30 | 6414.6 | 4736.5 | 11151.1
22:00 | 6287 | 4670 | 10957
22:30 | 6041.55 | 4519 | 10560.55
23:00 | 5796.1 | 4368 | 10164.1

## En-Curve
QF-LDC-12
Date | 19-01-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2446 | 1286 | 451 | 0 | 88 | 759 | 46 | 3523 | 0 | 0 | 1031.6 | 0 | 0 | 2 | 0 | DAILY ENERGY CURVE
00:30 | 2452.5 | 1279.25 | 451.5 | 0 | 86 | 758.975 | 46 | 3529.5 | 0 | 0 | 656.8 | 0 | 0 | 2 | 0 | 19-01-2026
01:00 | 2459 | 1272.5 | 452 | 0 | 84 | 758.95 | 46 | 3536 | 0 | 0 | 282 | 0 | 0 | 2 | 0
01:30 | 2460 | 1269 | 452 | 0 | 83 | 760.66 | 46 | 3466 | 0 | 0 | 141 | 0 | 0 | 1 | 0 | Energy Generated | 241.6321 |  | MKWHr
02:00 | 2461 | 1265.5 | 452 | 0 | 82 | 762.37 | 46 | 3396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy not Served | 0.282 |  | MKWHr
02:30 | 2476 | 1272.5 | 452 | 0 | 80 | 697.86 | 46 | 3335.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total Energy Requirement | 241.9141 |  | MKWHr
03:00 | 2491 | 1279.5 | 452 | 0 | 78 | 633.35 | 46 | 3275 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2485.5 | 1273.5 | 452 | 0 | 78 | 631.215 | 46 | 3188 | 0 | 0 | 0 | 0 | 0 | 1 | 0
04:00 | 2480 | 1267.5 | 452 | 0 | 78 | 629.08 | 46 | 3101 | 0 | 0 | 0 | 0 | 0 | 2 | 0
04:30 | 2466 | 1240.75 | 452 | 0 | 77 | 625.92 | 46 | 3074.5 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0
05:00 | 2452 | 1214 | 452 | 0 | 76 | 622.76 | 46 | 3048 | 0 | 0 | 0 | 0 | 0 | 1 | 0
05:30 | 2481.5 | 1245.5 | 452.5 | 0 | 80 | 627.255 | 46 | 3144 | 0 | 0 | 0 | 0 | 0 | 1 | 0
06:00 | 2511 | 1277 | 453 | 0 | 84 | 631.75 | 46 | 3240 | 0 | 0 | 0 | 0 | 0 | 1 | 0
06:30 | 2570 | 1280.5 | 452.5 | 0 | 85 | 694.865 | 46 | 3379.5 | 4.05 | 17.5 | 126 | 0 | 0 | 3.5 | 0
07:00 | 2629 | 1284 | 452 | 0 | 86 | 757.98 | 46 | 3519 | 8.1 | 35 | 252 | 0 | 0 | 6 | 0
07:30 | 2602.5 | 1295 | 452.5 | 0 | 90 | 760.99 | 46 | 3530 | 62.67 | 52.5 | 730.5 | 0 | 0 | 3.5 | 13
08:00 | 2576 | 1306 | 453 | 0 | 94 | 764 | 46 | 3541 | 117.24 | 70 | 1209 | 0 | 0 | 1 | 26
08:30 | 2547.5 | 1285.5 | 452.5 | 0 | 96 | 760 | 46 | 3531.5 | 208.94 | 82.5 | 1411.3 | 0 | 0 | 0.5 | 13
09:00 | 2519 | 1265 | 452 | 0 | 98 | 756 | 46 | 3522 | 300.64 | 95 | 1613.6 | 0 | 0 | 0 | 0
09:30 | 2490 | 1217 | 452 | 0 | 98 | 754 | 46 | 3497.5 | 376.81 | 126.5 | 1456.8 | 0 | 0 | 0 | 0
10:00 | 2461 | 1169 | 452 | 0 | 98 | 752 | 46 | 3473 | 452.98 | 158 | 1300 | 0 | 0 | 0 | 0
10:30 | 2419 | 1142.5 | 452 | 0 | 99 | 755.5 | 46 | 3476.5 | 503.115 | 164 | 1308.4 | 0 | 0 | 0 | 0
11:00 | 2377 | 1116 | 452 | 0 | 100 | 759 | 46 | 3480 | 553.25 | 170 | 1316.8 | 0 | 0 | 0 | 0
11:30 | 2418 | 1181.5 | 452 | 0 | 102 | 763.5 | 46 | 3526.5 | 573.41 | 180.5 | 1420.5 | 0 | 0 | 0 | 5
12:00 | 2459 | 1247 | 452 | 0 | 104 | 768 | 46 | 3573 | 593.57 | 191 | 1524.2 | 0 | 0 | 0 | 10
12:30 | 2470 | 1272.5 | 452 | 0 | 107 | 766.5 | 57 | 3566.5 | 584.635 | 182.5 | 1572.6 | 0 | 0 | 0 | 128
13:00 | 2481 | 1298 | 452 | 0 | 110 | 765 | 68 | 3560 | 575.7 | 174 | 1621 | 0 | 0 | 0 | 246
13:30 | 2469.5 | 1309 | 452.5 | 0 | 111 | 765.5 | 68 | 3567.5 | 530.495 | 174 | 1455.1 | 0 | 0 | 0 | 123
14:00 | 2458 | 1320 | 453 | 0 | 112 | 766 | 68 | 3575 | 485.29 | 174 | 1289.2 | 0 | 0 | 0 | 0
14:30 | 2451 | 1315 | 452.5 | 0 | 111 | 764 | 54 | 3564 | 416.215 | 174 | 1215.35 | 0 | 0 | 0 | 0
15:00 | 2444 | 1310 | 452 | 0 | 110 | 762 | 40 | 3553 | 347.14 | 174 | 1141.5 | 0 | 0 | 0 | 0
15:30 | 2437 | 1305 | 452.5 | 0 | 106 | 764.5 | 40 | 3547.5 | 254.98 | 170 | 1183.45 | 0 | 0 | 1.5 | 0
16:00 | 2430 | 1300 | 453 | 0 | 102 | 767 | 40 | 3542 | 162.82 | 166 | 1225.4 | 0 | 0 | 3 | 0
16:30 | 2428.5 | 1303 | 452.5 | 0 | 103 | 764 | 40 | 3524.5 | 98.925 | 182.5 | 1408.25 | 0 | 0 | 2 | 0
17:00 | 2427 | 1306 | 452 | 0 | 104 | 761 | 40 | 3507 | 35.03 | 199 | 1591.1 | 0 | 0 | 1 | 0
17:30 | 2435.5 | 1303.5 | 452 | 0 | 109 | 763 | 40 | 3540.5 | 17.515 | 268 | 1820.35 | 0 | 0 | 1.5 | 0
18:00 | 2444 | 1301 | 452 | 0 | 114 | 765 | 40 | 3574 | 0 | 337 | 2049.6 | 0 | 0 | 2 | 0
18:30 | 2447.5 | 1339 | 452 | 0 | 111 | 765 | 40 | 3570.5 | 0 | 354 | 2168.45 | 0 | 0 | 1 | 0
19:00 | 2451 | 1377 | 452 | 0 | 108 | 765 | 40 | 3567 | 0 | 371 | 2287.3 | 0 | 0 | 0 | 0
19:30 | 2448 | 1382 | 452 | 0 | 110 | 771 | 40 | 3556 | 0 | 370 | 2270.3 | 0 | 0 | 0 | 0
20:00 | 2445 | 1377 | 452 | 0 | 110 | 767 | 40 | 3581 | 0 | 365 | 2187.6 | 0 | 0 | 0 | 0
20:30 | 2444 | 1387.5 | 452.5 | 0 | 111 | 768.5 | 40 | 3585 | 0 | 365 | 2181.4 | 0 | 0 | 0 | 0
21:00 | 2443 | 1398 | 453 | 0 | 112 | 770 | 40 | 3589 | 0 | 365 | 2175.2 | 0 | 0 | 0 | 0
21:30 | 2434.5 | 1399 | 452.5 | 0 | 108 | 768 | 40 | 3576.5 | 0 | 296 | 2076.6 | 0 | 0 | 0 | 0
22:00 | 2426 | 1400 | 452 | 0 | 104 | 766 | 40 | 3564 | 0 | 227 | 1978 | 0 | 0 | 0 | 0
22:30 | 2412.5 | 1364.5 | 452 | 0 | 99 | 766 | 40 | 3571.5 | 0 | 146 | 1709.05 | 0 | 0 | 0 | 0
23:00 | 2399 | 1329 | 452 | 0 | 94 | 766 | 40 | 3579 | 0 | 65 | 1440.1 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 19-01-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 422 | 19:30 | 407 | 12:00 | Madunaghat | 424 | 05:00 | 398 | 13:00
Amtali | N/A | N/A | N/A | N/A | Meghnaghat | 428 | 22:00 | 410 | 12:00
Ashuganj | 421 | 04:00 | 409 | 12:00 | Payra | 426 | 05:00 | 418 | 12:00
Bhulta | 406 | 05:00 | 384 | 12:00 | Rahanpur | 420 | 04:00 | 409 | 10:00
Bibiana | 425 | 22:00 | 411 | 12:00 | Rampal | 417 | 03:00 | 404 | 12:00
BIPTC | 409 | 03:00 | 398 | 08:00
Bogura | 418 | 21:00 | 404 | 10:00
Gopalganj | 421 | 04:00 | 409 | 12:00
Kaliakoir | 418 | 20:00 | 401 | 16:00
Korerhat | 428 | 22:00 | 417 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 246 | 22:00 | 232 | 12:00 | Kachua | 243 | 18:00 | 235 | 12:00
AKSML | 238 | 17:00 | 229 | 12:00 | Kaliakoir | 247 | 22:00 | 234 | 15:00
Aminbazar | 246 | 21:00 | 231 | 12:00 | Keranigonj | 243 | 22:00 | 231 | 12:00
Ashuganj | 241 | 20:00 | 233 | 13:00 | Khulna(S) | 246 | 04:00 | 236 | 12:00
Ashuganj-400 | 241 | 20:00 | 233 | 13:00 | Korerhat | 242 | 20:00 | 235 | 12:00
Baghabari | 243 | 21:00 | 236 | 09:00 | Madunaghat | 235 | 11:00 | 228 | 12:00
Barapukuria | 238 | 21:00 | 225 | 01:00 | Madunaghat-400 | 235 | 19:00 | 229 | 13:00
Barapukuria-230 | 238 | 21:00 | 225 | 01:00 | Maniknagar | 241 | 03:00 | 229 | 12:00
Barishal | 239 | 05:00 | 233 | 12:00 | Meghnaghat | 246 | 21:00 | 235 | 05:00
Bheramara | 242 | 04:00 | 233 | 12:00 | Meghnaghat-400 | 242 | 22:00 | 231 | 12:00
Bhulta | 243 | 04:00 | 231 | 12:00 | Mirsorai | 242 | 19:30 | 235 | 12:00
Bibiana | 243 | 17:00 | 237 | 12:00 | Rajshahi | 243 | 05:00 | 233 | 12:00
BIPTC | 244 | 04:00 | 233 | 12:00 | Rampal | 242 | 04:00 | 232 | 12:00
Bogura | 247 | 22:00 | 238 | 10:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 245 | 22:00 | 235 | 03:00 | Rampura | 242 | 04:00 | 231 | 12:00
Borhanuddin | 240 | 06:00 | 236 | 14:00 | Shikalbaha | 234 | 18:00 | 227 | 12:00
BSRM | 241 | 20:00 | 233 | 12:00 | Shyampur | 242 | 22:00 | 231 | 12:00
Cumilla(N) | 242 | 22:00 | 232 | 12:00 | Siddhirganj | 242 | 19:00 | 238 | 17:00
Faridpur | 239 | 04:00 | 231 | 12:00 | Sirajgonj | 249 | 22:00 | 242 | 13:00
Fenchuganj | 246 | 05:00 | 241 | 15:00 | Sreepur | 240 | 21:00 | 233 | 12:00
Feni | 243 | 22:00 | 234 | 12:00 | Tongi | 244 | 00:00 | 228 | 15:00
Ghorashal | 245 | 19:30 | 142 | 01:00
Ghorashal-230 | 243 | 22:00 | 230 | 16:00
Gopalganj | 237 | 04:00 | 229 | 12:00
GPH | 237 | 18:30 | 223 | 01:00
Haripur | 243 | 22:00 | 232 | 12:00
Hasnabad | 243 | 08:00 | 232 | 12:00
Hathazari | 234 | 18:30 | 226 | 16:00
Ishurdi | 245 | 04:00 | 236 | 12:00
Jhenaidah | 244 | 04:00 | 233 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 05:00 | 126 | 13:00 | Laksam | 139 | 00:00 | 135 | 12:00
Agargaon | 139 | 04:00 | 131 | 12:00 | Lakshmipur | 136 | 20:00 | 132 | 12:00
Agrabad | 137 | 19:00 | 130 | 12:00 | Lalbag | 137 | 04:00 | 128 | 13:00
AKS | 134 | 04:00 | 130 | 11:00 | Lalmonirhat | 135 | 17:00 | 131 | 05:00
Aminbazar | 142 | 00:00 | 135 | 12:00 | Madanganj | 137 | 23:00 | 135 | 00:00
Amnura | 140 | 04:00 | 134 | 10:00 | Madaripur | 141 | 03:00 | 137 | 14:00
Ashuganj | 140 | 03:00 | 137 | 08:00 | Madartek | 134 | 02:00 | 126 | 12:00
Bagerhat | 136 | 04:00 | 128 | 08:00 | Madunaghat | 138 | 18:30 | 133 | 12:00
Bajitpur | 136 | 03:00 | 131 | 12:00 | Magura | 140 | 04:00 | 130 | 18:30
Bakerganj | 140 | 17:00 | 138 | 00:00 | Mahasthangarh | 139 | 20:00 | 134 | 07:00
Bakulia | 138 | 18:00 | 132 | 12:00 | Maijdee | 136 | 20:00 | 132 | 12:00
Banani | 135 | 02:00 | 126 | 12:00 | Manikganj | 131 | 03:00 | 122 | 15:00
Bangabhaban | 138 | 04:00 | 126 | 14:00 | Maniknagar | 139 | 05:00 | 127 | 12:00
Barapukuria | 142 | 20:00 | 133 | 01:00 | Matarbari | 130 | 06:00 | 123 | 12:00
Barguna | 140 | 01:00 | 137 | 12:00 | Matuail | 139 | 20:00 | 133 | 12:00
Barishal | 141 | 18:00 | 135 | 12:00 | Metrorail_Motijheel | 139 | 05:00 | 127 | 12:00
Barishal-230 | 141 | 20:00 | 135 | 12:00 | Metrorail_Uttara | 141 | 22:00 | 134 | 12:00
Baroaulia | 137 | 20:00 | 132 | 12:00 | Millgate | 135 | 23:00 | 124 | 16:00
Baroirhat | 135 | 19:30 | 131 | 12:00 | Mirpur | 141 | 22:00 | 134 | 12:00
Bashundhara | 135 | 03:00 | 126 | 13:00 | Mirzapur | 135 | 19:30 | 130 | 07:00
BashundharaCement | 137 | 23:00 | 135 | 00:00 | Mithapukur | 139 | 19:30 | 133 | 01:00
Beanibazar | 133 | 01:00 | 129 | 12:00 | MI_Cement | 136.6 | 06:00 | 128 | 12:00
Benapole | 137 | 03:00 | 127 | 08:00 | Modern | 0 | 00:00 | 0 | 00:00
Bhaluka | 137 | 20:00 | 131 | 12:00 | Mogbazar | 136 | 02:00 | 123 | 16:00
Bhandaria | 140 | 19:00 | 134 | 09:00 | Mongla | 135 | 04:00 | 128 | 09:00
Bhangura | 141 | 04:00 | 136 | 00:00 | Motijheel | 138 | 04:00 | 126 | 14:00
Bheramara | 142 | 04:00 | 138 | 08:00 | Muktagacha | 131 | 10:00 | 124 | 08:00
Bheramara(GK) | 142 | 03:00 | 10 | 18:00 | Munshiganj | 139 | 22:00 | 132 | 12:00
Bhulta | 135 | 00:00 | 130 | 12:00 | Muradnagar | 139 | 04:00 | 130 | 12:00
Bog-Sherpur | 140 | 05:00 | 135 | 08:00 | Mymensingh | 132 | 10:00 | 123 | 08:00
Bogura | 140 | 19:30 | 135 | 07:00 | Naogaon | 136 | 21:00 | 131 | 07:00
Bogura-230 | 141 | 22:00 | 136 | 07:00 | Narail | 140 | 05:00 | 131 | 12:00
Brahmanbaria | 132 | 03:00 | 127 | 12:00 | Narinda | 131 | 03:00 | 122 | 15:00
Cantonment | 139 | 04:00 | 131 | 12:00 | Narshingdi | 138 | 05:00 | 125 | 12:00
Chandina | 140 | 04:00 | 134 | 12:00 | Natore | 139 | 21:00 | 135 | 10:00
Chandpur | 141 | 22:00 | 137 | 13:00 | Nawabganj | 137 | 05:00 | 128 | 12:00
Chandraghona | 138 | 19:00 | 132 | 12:00 | Netrakona | 131 | 06:00 | 119 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 140 | 03:00 | 135 | 10:00 | New | 135 | 00:00 | 126 | 15:00
Charsaidpur | 139 | 19:30 | 133 | 12:00 | Niamatpur | 140 | 00:00 | 136 | 09:00
Chauddagram | 137 | 04:00 | 132 | 12:00 | Noapara | 138 | 04:00 | 130 | 12:00
Chhatak | 134 | 05:00 | 126 | 12:00 | Pabna | 141 | 22:00 | 136 | 11:00
Chowmuhani | 136 | 02:00 | 131 | 15:00 | Palashbari | 137 | 17:00 | 132 | 10:00
Chuadanga | 140 | 03:00 | 130 | 12:00 | Panchagarh | 139 | 20:00 | 128 | 10:00
Coxsbazar | 129 | 02:00 | 121 | 13:00 | Patiya | 137 | 19:00 | 131 | 12:00
Cumilla(N) | 140 | 21:00 | 134 | 15:00 | Patuakhali | 139 | 09:00 | 135 | 01:00
Cumilla(S) | 139 | 00:00 | 125 | 09:00 | Payra | 139 | 03:00 | 137 | 13:00
Daganbhuiyan | 136 | 20:00 | 132 | 12:00 | PHP | 135 | 04:00 | 131 | 12:00
Daudkandi | 137 | 22:00 | 128 | 12:00 | Postogola | 138 | 22:00 | 130 | 12:00
DhakaUniversity | 134 | 00:00 | 126 | 13:00 | Purbachal | 135 | 03:00 | 126 | 12:00
Dhamrai | 139 | 22:00 | 131 | 15:00 | Purbasadipur | 137 | 20:00 | 128 | 09:00
Dhanmondi | 140.5 | 22:00 | 130 | 11:00 | Rahanpur | 141 | 22:00 | 137 | 10:00
Dohazari | 134 | 18:30 | 125 | 13:00 | Rahanpur-400 | 141 | 20:00 | 137 | 10:00
Faridpur | 138 | 04:00 | 134 | 16:00 | Rahim | 139 | 04:00 | 132 | 13:00
Fatullah | 141 | 22:00 | 128 | 12:00 | Rajbari | 138 | 04:00 | 133 | 12:00
Fenchuganj | 138 | 00:00 | 136 | 13:00 | Rajendrapur | 137 | 19:30 | 125 | 11:00
Feni | 135 | 05:00 | 130 | 14:00 | Rajshahi | 139 | 18:00 | 134 | 12:00
Feni-230 | 136 | 20:00 | 131 | 12:00 | Rajshahi-230 | 140 | 04:00 | 134 | 12:00
Ghatail | 131 | 23:00 | 122 | 08:00 | Ramganj | 137 | 18:30 | 132 | 12:00
Ghorashal | 134 | 00:00 | 130 | 12:00 | Rampur | 137 | 19:00 | 130 | 12:00
Goalpara | 139 | 05:00 | 131 | 08:00 | Rampura | 135 | 04:00 | 126 | 13:00
Gollamari | 138 | 05:00 | 131 | 08:00 | Rangamati | 137 | 18:30 | 132 | 12:00
Gopalganj | 140 | 03:00 | 135 | 08:00 | Rangpur | 140 | 20:00 | 134 | 10:00
Gopalganj-400 | 143 | 04:00 | 138 | 12:00 | Ruppur | 141 | 00:00 | 138 | 12:00
Gulshan | 133 | 04:00 | 127 | 12:00 | Saidpur | 139 | 19:30 | 131 | 10:00
Halishahar | 138 | 18:00 | 132 | 13:00 | Satkhira | 136 | 04:00 | 126 | 08:00
Haripur | 139 | 20:00 | 133 | 13:00 | Satmasjid | 138 | 00:00 | 131 | 13:00
HaripurSBU | 139 | 05:00 | 133 | 15:00 | Savar | 142 | 22:00 | 136 | 15:00
Hasnabad | 137 | 00:00 | 130 | 12:00 | SevenRings | 136 | 04:00 | 129 | 18:30
Hathazari | 137 | 07:00 | 134 | 12:00 | ShahCement | 139 | 19:30 | 133 | 12:00
Hatirjheel | 135 | 04:00 | 127 | 12:00 | Shahjadpur | 142 | 00:00 | 136 | 10:00
Ishurdi | 144 | 05:00 | 139 | 12:00 | Shahjibazar | 133 | 03:00 | 129 | 12:00
Jaldhaka | 136 | 20:00 | 127 | 10:00 | Shahmirpur | 138 | 18:30 | 132 | 12:00
Jamalpur | 130 | 00:00 | 122 | 03:00 | Shariatpur | 142 | 03:00 | 137 | 12:00
Jashore | 136 | 00:00 | 129 | 08:00 | Sherpur | 128 | 19:30 | 116 | 05:00
Jhenaidah | 140 | 00:00 | 126 | 08:00 | Shikalbaha | 127 | 18:30 | 121 | 12:00
Jhenaidah-230 | 141 | 05:00 | 127 | 09:00 | Shikalbaha-230 | 139 | 19:00 | 133 | 12:00
Joydebpur | 136 | 03:00 | 123 | 14:00 | Shitalakhya | 136.5 | 06:00 | 128 | 12:00
Joypurhat | 134 | 04:00 | 129 | 11:00 | Sholosohor | 137 | 18:30 | 133 | 12:00
Juldah | 138 | 17:00 | 132 | 12:00 | Shyampur | 138 | 22:00 | 129 | 13:00
Kabirpur | 140 | 20:00 | 122 | 15:00 | Shyampur-230 | 141 | 22:00 | 134 | 12:00
Kachua | 139 | 00:00 | 135 | 12:00 | Siddhirganj | 139 | 19:30 | 133 | 12:00
Kaliakoir | 142 | 22:00 | 135 | 06:00 | Sirajganj | 139 | 02:00 | 132 | 08:00
Kallyanpur | 141 | 00:00 | 135 | 12:00 | Sonargaon | 136 | 23:00 | 130 | 12:00
Kalurghat | 137 | 00:00 | 133 | 12:00 | Sreemongol | 135 | 05:00 | 130 | 12:00
Kamrangirchar | 136 | 00:00 | 127 | 12:00 | Sreepur | 139 | 21:00 | 132 | 14:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 137 | 05:00 | 129 | 12:00
Kasba | 138 | 03:00 | 130 | 12:00 | SSM | 140 | 00:00 | 138 | 13:00
Kazla | 139 | 06:00 | 126 | 13:00 | Sunamganj | 131 | 03:00 | 125 | 18:00
Keranigonj | 136 | 04:00 | 128 | 13:00 | Sylhet | 134 | 04:00 | 129 | 13:00
Khagrachori | 137 | 22:00 | 131 | 12:00 | Sylhet-132 | 133 | 00:00 | 129 | 12:00
Khulna | 137 | 03:00 | 128 | 08:00 | Tangail | 131 | 19:30 | 124 | 08:00
Khulna(S) | 139 | 04:00 | 131 | 12:00 | Taraganj | 138 | 20:00 | 131 | 10:00
Khulshi | 136 | 18:30 | 130 | 12:00 | Tasnim | 137 | 04:00 | 130 | 12:00
Kishoreganj | 135 | 01:00 | 130 | 14:00 | Thakurgaon | 141 | 20:00 | 128 | 10:00
Kodda | 139 | 19:30 | 129 | 12:00 | TK | 138 | 18:30 | 132 | 12:00
KSRM | 136 | 00:00 | 132 | 12:00 | Tongi | 136 | 00:00 | 128 | 12:00
Kulaura | 139 | 03:00 | 134 | 12:00 | Ullahpara | 139 | 03:00 | 132 | 08:00
Kurigram | 136 | 00:00 | 130 | 08:00 | Ullon | 135 | 06:00 | 127 | 12:00
Kushtia | 141 | 05:00 | 135 | 08:00 | Uttara | 134 | 00:00 | 123 | 16:00
[5 empty] | UttaraNew | 141 | 22:00 | 134 | 12:00
[5 empty] | Zigatola | 137 | 05:00 | 128 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 19-01-2026 | [28 empty] | Date: | 19-01-2026 | [28 empty] | Date: | 19-01-2026 | [28 empty] | Date: | 19-01-2026 | [28 empty] | Date: | 19-01-2026 | [17 empty] | Date: | 19-01-2026
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [17 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 47.6 | 0 | 119 | 0 | 145 | 0 | 35 | 154 | 0 | 0 | 0 | 375 | 0 | 35 | 270 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 25 | 0 | 46 | 0 | 31 | 355 | 0 | 0 | 0 | 0 | 98 | 185 | 0 | 0 | 0 | 1224 | 0 | 70 | 0 | 220 | 280 | 0 | 51 | 0 | 180 | 0 | 0 | 80 | 120 | 0 | 11 | 0 | 88 | 0 | 0 | 0 | 310 | 0 | 0 | 42 | 52 | 160 | 0 | 21 | 0 | 78 | 30 | 0 | 0 | 100 | 0 | 59 | 19 | 36 | 0 | 0 | 0 | 5519.6 | 451 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 0 | 0 | 759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 525 | 0 | 4113 | 9632.6 | 96.28
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 355 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 13.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 25 | 0 | 46 | 0 | 35 | 355 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 220 | 280 | 0 | 51 | 0 | 180 | 0 | 0 | 80 | 68 | 0 | 11 | 0 | 84 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 52 | 162 | 0 | 17 | 0 | 78 | 30 | 0 | 0 | 100 | 0 | 45 | 0 | 36 | 0 | 0 | 0 | 4862.5 | 452 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1122 | 0 | 0 | 0 | 758.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 528 | 0 | 4029.95 | 8892.45 | 96.28
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 13.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 36 | 355 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1110 | 0 | 0 | 0 | 220 | 280 | 0 | 51 | 0 | 180 | 0 | 0 | 80 | 0 | 0 | 11 | 0 | 82 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 52 | 159 | 0 | 17 | 0 | 78 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 4461.5 | 452 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1114 | 0 | 0 | 0 | 762.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 510 | 0 | 4003.37 | 8464.87 | 96.28
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 13.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 36 | 355 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1110 | 0 | 0 | 0 | 220 | 280 | 0 | 51 | 0 | 201 | 0 | 0 | 80 | 0 | 0 | 11 | 0 | 78 | 0 | 0 | 0 | 320 | 0 | 0 | 42 | 52 | 163 | 0 | 17 | 0 | 78 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 4499.5 | 452 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1020 | 0 | 0 | 0 | 633.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 130 | 220 | 0 | 0 | 510 | 0 | 3755.35 | 8254.85 | 96.27
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 13.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 36 | 355 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1060 | 0 | 0 | 0 | 220 | 280 | 0 | 51 | 0 | 193 | 0 | 0 | 80 | 0 | 0 | 11 | 0 | 78 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 52 | 161 | 0 | 17 | 0 | 78 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 4429.5 | 452 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 885 | 0 | 0 | 0 | 629.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 130 | 220 | 0 | 0 | 520 | 0 | 3626.08 | 8055.58 | 96.27
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 36 | 355 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1061 | 0 | 0 | 0 | 220 | 280 | 0 | 51 | 0 | 196 | 0 | 0 | 80 | 0 | 0 | 11 | 0 | 76 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 52 | 152 | 0 | 17 | 0 | 78 | 30 | 0 | 0 | 101 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 4408 | 452 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 0 | 0 | 0 | 622.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 115 | 180 | 0 | 0 | 544 | 0 | 3503.76 | 7911.76 | 96.27
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 39 | 355 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1161 | 0 | 0 | 0 | 220 | 315 | 0 | 51 | 0 | 202 | 0 | 0 | 80 | 0 | 0 | 11 | 0 | 84 | 0 | 0 | 0 | 320 | 0 | 0 | 42 | 52 | 152 | 0 | 17 | 0 | 78 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 4586 | 453 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 852 | 0 | 0 | 0 | 631.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 130 | 220 | 0 | 0 | 595 | 0 | 3657.75 | 8243.75 | 96.27
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 17 | 0 | 13 | 0 | 0 | 0 | 10 | 33 | 0 | 0 | 0 | 365 | 0 | 0 | 270 | 0 | 0 | 0 | 35 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 0.05 | 46 | 0 | 35 | 355 | 0 | 0 | 0 | 0 | 12 | 185 | 0 | 0 | 0 | 1208 | 1 | 0 | 0 | 230 | 375 | 0 | 51 | 0 | 214 | 0 | 0 | 80 | 6 | 0 | 11 | 0 | 86 | 0 | 2 | 0 | 315 | 0 | 0 | 41 | 52 | 163 | 0 | 17 | 0 | 78 | 30 | 0 | 0 | 100 | 0 | 27 | 19 | 50 | 0 | 0.57 | 0 | 4943.62 | 452 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.37 | 1058 | 0 | 0 | 0 | 757.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54 | 0 | 0 | 0 | 0.51 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06 | 0 | 0 | 50 | 0 | 40 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 286 | 130 | 220 | 0 | 0 | 612 | 0 | 4131.46 | 9075.08 | 96.26
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 45 | 25 | 98 | 0 | 95 | 0 | 35 | 147 | 0 | 0 | 0 | 405 | 0 | 40 | 300 | 0 | 0 | 5 | 70 | 20 | 15 | 0 | 0 | 1 | 45 | 0 | 0 | 1 | 0 | 0 | 0 | 12 | 25 | 0.55 | 46 | 8 | 8 | 355 | 0 | 0 | 6 | 0 | 78 | 185 | 0 | 0 | 0 | 1165 | 7 | 60 | 0 | 230 | 320 | 0 | 51 | 0 | 189 | 0 | 0 | 80 | 60 | 0 | 11 | 0 | 94 | 0 | 17 | 0 | 320 | 0 | 0 | 42 | 52 | 161 | 2 | 17 | 0 | 78 | 30 | 0 | 0 | 101 | 0 | 47 | 18 | 50 | 0 | 8.42 | 9 | 5636.97 | 453 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1134 | 0 | 0 | 0 | 764 | 0 | 0 | 0 | 90 | 58 | 0 | 0 | 0 | 0 | 7.83 | 15 | 0 | 0 | 8.67 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88 | 0 | 0 | 95 | 5 | 95 | 0 | 0 | 0 | 0.8 | 24 | 0.09 | 0 | 277 | 130 | 220 | 0 | 0 | 610 | 17 | 4540.27 | 10177.24 | 96.26
09:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 52.6 | 54 | 131 | 0 | 225 | 0 | 35 | 148 | 0 | 0 | 0 | 370 | 0 | 55 | 300 | 0 | 0 | 13 | 70 | 24 | 14 | 0 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 1.87 | 46 | 34 | 2 | 355 | 0 | 0 | 19 | 0 | 51 | 185 | 0 | 0 | 0 | 1157 | 13 | 117 | 0 | 215 | 295 | 0 | 51 | 0 | 172 | 0 | 0 | 80 | 85 | 0 | 11 | 0 | 98 | 0 | 35 | 0 | 315 | 0 | 0 | 42 | 52 | 163 | 5 | 17 | 0 | 78 | 30 | 0 | 0 | 100 | 0 | 57 | 18 | 43 | 1 | 20.76 | 12 | 5903.23 | 452 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 1140 | 0 | 0 | 0 | 756 | 0 | 0 | 0 | 90 | 105 | 0 | 0 | 0 | 0 | 21.63 | 40 | 0 | 0 | 23.44 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.12 | 0 | 0 | 115 | 13 | 107 | 0 | 0 | 0 | 2.6 | 72 | 0.22 | 0 | 273 | 130 | 220 | 0 | 0 | 597 | 35 | 4764.01 | 10667.24 | 96.26
10:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 47 | 54 | 132 | 0 | 278 | 0 | 35 | 144 | 0 | 0 | 0 | 345 | 0 | 55 | 300 | 0 | 0 | 20 | 125 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 2.67 | 46 | 0 | 1 | 355 | 0 | 0 | 0 | 0 | 17 | 185 | 0 | 0 | 0 | 1140 | 16 | 137 | 0 | 215 | 295 | 0 | 51 | 0 | 180 | 0 | 0 | 80 | 79 | 0 | 11 | 0 | 98 | 0 | 51 | 0 | 305 | 0 | 0 | 42 | 52 | 143 | 8 | 17 | 0 | 78 | 30 | 0 | 0 | 100 | 0 | 60 | 19 | 33 | 1 | 31.44 | 12 | 5833.11 | 452 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.5 | 1109 | 2 | 0 | 0 | 752 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 33.15 | 64 | 0 | 0 | 35.71 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.16 | 0 | 0 | 50 | 22 | 49 | 0 | 0 | 0 | 4 | 105 | 0.35 | 0 | 274 | 130 | 180 | 0 | 0 | 595 | 35 | 4528.87 | 10361.98 | 96.25
11:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 45.8 | 54 | 132 | 0 | 278 | 0 | 35 | 143 | 0 | 0 | 0 | 305 | 0 | 55 | 260 | 0 | 0 | 25 | 125 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 25 | 3.15 | 46 | 0 | 1 | 355 | 0 | 0 | 0 | 0 | 15 | 186 | 0 | 0 | 0 | 1158 | 19 | 142 | 0 | 215 | 280 | 0 | 51 | 0 | 184 | 0 | 0 | 80 | 77 | 0 | 11 | 0 | 100 | 0 | 60 | 0 | 300 | 0 | 0 | 42 | 52 | 132 | 9 | 20 | 0 | 78 | 30 | 0 | 0 | 100 | 0 | 60 | 19 | 33 | 2 | 37.49 | 12 | 5781.44 | 452 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 1098 | 17 | 0 | 0 | 759 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 42.32 | 78 | 0 | 0 | 44.86 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.99 | 0 | 0 | 50 | 28 | 49 | 0 | 0 | 0 | 5 | 129 | 0.44 | 0 | 274 | 115 | 180 | 0 | 0 | 595 | 38 | 4588.61 | 10370.05 | 96.25
12:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 51.2 | 54 | 147 | 0 | 278 | 0 | 35 | 142 | 0 | 0 | 0 | 350 | 0 | 35 | 260 | 0 | 0 | 28 | 142 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 25 | 3.28 | 46 | 0 | 3 | 355 | 0 | 0 | 0 | 0 | 16 | 186 | 0 | 0 | 0 | 1205 | 19 | 143 | 0 | 220 | 280 | 0 | 51 | 0 | 191 | 0 | 0 | 80 | 84 | 0 | 11 | 0 | 104 | 0 | 63 | 0 | 320 | 0 | 0 | 42 | 52 | 156 | 10 | 20 | 0 | 78 | 30 | 0 | 0 | 100 | 0 | 59 | 19 | 34 | 2 | 40.79 | 12 | 6005.27 | 452 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.39 | 1130 | 17 | 0 | 0 | 768 | 0 | 0 | 0 | 90 | 60 | 0 | 0 | 0 | 0 | 45.15 | 84 | 0 | 0 | 48.02 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.14 | 0 | 0 | 115 | 30 | 107 | 0 | 0 | 0 | 5.3 | 140 | 0.5 | 0 | 286 | 130 | 220 | 0 | 0 | 597 | 35 | 4952.5 | 10957.77 | 96.25
13:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 52 | 54 | 149 | 0 | 295 | 0 | 35 | 144 | 0 | 0 | 0 | 370 | 0 | 35 | 260 | 0 | 0 | 28 | 125 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 25 | 3.17 | 68 | 0 | 12 | 355 | 0 | 0 | 0 | 0 | 17 | 186 | 0 | 0 | 0 | 1187 | 18 | 140 | 0 | 220 | 280 | 0 | 51 | 0 | 190 | 0 | 0 | 80 | 85 | 0 | 11 | 0 | 110 | 0 | 63 | 0 | 335 | 0 | 0 | 42 | 52 | 161 | 9 | 20 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 59 | 19 | 33 | 2 | 38.41 | 12 | 6087.58 | 452 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 1143 | 17 | 0 | 0 | 765 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 41.74 | 81 | 0 | 0 | 46.59 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.15 | 0 | 0 | 115 | 29 | 107 | 0 | 0 | 0 | 5.2 | 137 | 0.44 | 0 | 278 | 130 | 220 | 0 | 0 | 597 | 35 | 5017.12 | 11104.7 | 96.25
14:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 51.2 | 17 | 149 | 0 | 195 | 0 | 35 | 146 | 0 | 0 | 0 | 410 | 0 | 35 | 260 | 0 | 0 | 24 | 125 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 25 | 2.62 | 68 | 0 | 6 | 355 | 0 | 0 | 0 | 0 | 15 | 186 | 0 | 0 | 0 | 1194 | 16 | 70 | 0 | 220 | 280 | 0 | 51 | 0 | 194 | 0 | 0 | 80 | 85 | 0 | 11 | 0 | 112 | 0 | 52 | 0 | 325 | 0 | 0 | 42 | 52 | 159 | 9 | 20 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 59 | 19 | 31 | 1.5 | 29.54 | 14 | 5877.86 | 453 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.52 | 1136 | 17 | 0 | 0 | 766 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 39.48 | 70 | 0 | 0 | 38.29 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.47 | 0 | 0 | 115 | 23 | 107 | 0 | 0 | 0 | 4.5 | 107 | 0.37 | 0 | 280 | 130 | 220 | 0 | 0 | 610 | 35 | 4822.63 | 10700.49 | 96.24
15:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 50.5 | 17 | 149 | 0 | 0 | 0 | 35 | 143 | 0 | 0 | 0 | 410 | 0 | 35 | 260 | 0 | 0 | 17 | 125 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 25 | 1.9 | 40 | 0 | 3 | 355 | 0 | 0 | 0 | 0 | 25 | 186 | 0 | 0 | 0 | 1163 | 13 | 90 | 0 | 220 | 280 | 0 | 51 | 0 | 194 | 0 | 0 | 80 | 84 | 0 | 11 | 0 | 110 | 0 | 37 | 0 | 320 | 0 | 0 | 42 | 52 | 157 | 5 | 20 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 59 | 19 | 32 | 1 | 21.96 | 18 | 5594.36 | 452 | 311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.85 | 1130 | 25 | 0 | 0 | 762 | 0 | 0 | 0 | 50 | 60 | 0 | 0 | 0 | 0 | 28.79 | 52 | 0 | 0 | 25.77 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.38 | 0 | 0 | 115 | 13 | 107 | 0 | 0 | 0 | 3.2 | 80 | 0.29 | 0 | 307 | 125 | 220 | 0 | 0 | 598 | 35 | 4739.28 | 10333.64 | 96.24
16:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 49.4 | 17 | 138 | 0 | 0 | 0 | 40 | 142 | 0 | 0 | 0 | 405 | 0 | 55 | 260 | 0 | 0 | 9 | 125 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 0 | 12 | 25 | 0.98 | 40 | 0 | 2 | 355 | 0 | 0 | 0 | 0 | 49 | 186 | 0 | 0 | 0 | 1168 | 8 | 100 | 0 | 220 | 280 | 0 | 51 | 0 | 195 | 0 | 2 | 80 | 91 | 0 | 12 | 0 | 102 | 0 | 17 | 0 | 315 | 0 | 0 | 42 | 52 | 157 | 2 | 20 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 59 | 18 | 32 | 1 | 9.45 | 18 | 5584.83 | 453 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.69 | 1117 | 33 | 0 | 0 | 767 | 0 | 0 | 0 | 50 | 70 | 0 | 0 | 0 | 0 | 11.71 | 25 | 0 | 0 | 10.42 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83 | 0 | 0 | 115 | 8 | 107 | 0 | 0 | 0 | 1.6 | 33 | 0.14 | 0 | 307 | 125 | 220 | 0 | 0 | 595 | 35 | 4606.39 | 10191.22 | 96.23
17:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 50.1 | 17 | 145 | 16 | 165 | 4 | 55 | 143 | 0 | 0 | 0 | 405 | 0 | 55 | 260 | 0 | 0 | 2 | 125 | 23 | 14 | 0 | 0 | 3 | 30 | 0 | 0 | 1 | 0 | 8 | 0 | 36 | 25 | 0.12 | 40 | 5 | 7 | 355 | 30 | 0 | 4 | 0 | 59 | 186 | 0 | 0 | 0 | 1133 | 1 | 100 | 0 | 220 | 280 | 0 | 51 | 0 | 193 | 0 | 16 | 80 | 100 | 5 | 11 | 17 | 104 | 0 | 3 | 0 | 315 | 0 | 0 | 42 | 52 | 157 | 0 | 20 | 0 | 83 | 30 | 0 | 0 | 100 | 7 | 59 | 18 | 33 | 0 | 1.76 | 17 | 5900.98 | 452 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1 | 1117 | 33 | 0 | 0 | 761 | 0 | 0 | 0 | 50 | 70 | 0 | 0 | 0 | 0 | 2.24 | 7 | 0 | 0 | 2.27 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 115 | 2 | 107 | 0 | 0 | 0 | 0.3 | 7 | 0.04 | 16 | 307 | 125 | 220 | 0 | 0 | 595 | 35 | 4522.15 | 10423.13 | 96.23
18:00 | 0 | 70 | 22 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 47.6 | 40 | 149 | 34 | 225 | 18 | 35 | 144 | 0 | 0 | 0 | 410 | 0 | 55 | 260 | 0 | 0 | 0 | 125 | 23 | 14 | 0 | 0 | 15 | 65 | 0 | 0 | 2 | 34 | 16 | 0 | 60 | 25 | 0 | 40 | 24 | 3 | 355 | 85 | 0 | 23 | 0 | 86 | 186 | 0 | 0 | 0 | 1200 | 0 | 122 | 0 | 220 | 280 | 0 | 51 | 0 | 193 | 0 | 16 | 80 | 104 | 9 | 11 | 34 | 114 | 8 | 0 | 24 | 320 | 0 | 0 | 42 | 52 | 146 | 0 | 20 | 0 | 83 | 30 | 0 | 0 | 100 | 35 | 59 | 18 | 35 | 0 | 0 | 12 | 6465.6 | 452 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1116 | 33 | 0 | 0 | 765 | 0 | 0 | 0 | 100 | 70 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 307 | 125 | 220 | 0 | 0 | 596 | 72 | 4613 | 11078.6 | 96.23
19:00 | 0 | 72 | 34 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 51.3 | 54 | 149 | 48 | 260 | 45 | 35 | 143 | 0 | 0 | 0 | 465 | 0 | 55 | 260 | 0 | 0 | 0 | 125 | 23 | 0 | 0 | 0 | 17 | 45 | 0 | 0 | 0 | 34 | 16 | 0 | 60 | 25 | 0 | 40 | 48 | 13 | 355 | 84 | 0 | 32 | 0 | 103 | 186 | 0 | 0 | 0 | 1175 | 0 | 150 | 0 | 220 | 280 | 0 | 51 | 0 | 197 | 0 | 15 | 80 | 136 | 9 | 13 | 34 | 108 | 8 | 0 | 17 | 325 | 0 | 0 | 42 | 52 | 163 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 100 | 35 | 59 | 18 | 34 | 0 | 0 | 12 | 6691.3 | 452 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1134 | 33 | 0 | 0 | 765 | 0 | 0 | 0 | 113 | 90 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 307 | 130 | 220 | 0 | 0 | 596 | 70 | 4727 | 11418.3 | 96.22
19:30 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 51.3 | 54 | 149 | 44 | 278 | 55 | 35 | 146 | 0 | 0 | 0 | 465 | 0 | 55 | 260 | 0 | 0 | 0 | 125 | 23 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 34 | 16 | 0 | 60 | 25 | 0 | 40 | 34 | 20 | 355 | 84 | 0 | 20 | 0 | 81 | 186 | 0 | 0 | 0 | 1168 | 0 | 150 | 0 | 220 | 280 | 0 | 51 | 0 | 193 | 0 | 16 | 80 | 136 | 9 | 11 | 17 | 110 | 8 | 0 | 17 | 325 | 0 | 0 | 42 | 52 | 163 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 100 | 35 | 59 | 18 | 34 | 0 | 0 | 12 | 6633.3 | 452 | 301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1126 | 40 | 0 | 0 | 771 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 307 | 130 | 220 | 0 | 0 | 600 | 70 | 4766 | 11399.3 | 96.22
20:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 51.6 | 54 | 149 | 32 | 278 | 55 | 35 | 142 | 0 | 0 | 0 | 460 | 0 | 55 | 260 | 0 | 0 | 0 | 125 | 23 | 5 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 34 | 16 | 0 | 36 | 25 | 0 | 40 | 16 | 20 | 355 | 86 | 0 | 19 | 0 | 68 | 186 | 0 | 0 | 0 | 1181 | 0 | 150 | 0 | 220 | 280 | 0 | 51 | 0 | 193 | 0 | 16 | 80 | 136 | 9 | 11 | 17 | 110 | 8 | 0 | 17 | 320 | 0 | 0 | 42 | 52 | 163 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 100 | 35 | 59 | 18 | 35 | 0 | 0 | 12 | 6554.6 | 452 | 301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1130 | 47 | 0 | 0 | 767 | 0 | 5 | 0 | 113 | 113 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 307 | 130 | 220 | 0 | 0 | 608 | 53 | 4770 | 11324.6 | 96.22
21:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 51.2 | 54 | 149 | 16 | 278 | 55 | 17 | 144 | 0 | 0 | 0 | 470 | 0 | 55 | 260 | 0 | 0 | 0 | 125 | 18 | 14 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 34 | 16 | 0 | 36 | 25 | 0 | 40 | 16 | 22 | 355 | 84 | 0 | 19 | 0 | 66 | 185 | 0 | 0 | 0 | 1177 | 0 | 150 | 0 | 220 | 280 | 0 | 51 | 0 | 190 | 0 | 15 | 80 | 133 | 0 | 11 | 17 | 112 | 25 | 0 | 17 | 325 | 0 | 0 | 42 | 52 | 163 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 100 | 35 | 59 | 18 | 35 | 0 | 0 | 12 | 6542.2 | 453 | 299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1135 | 51 | 0 | 0 | 770 | 0 | 21 | 0 | 113 | 113 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 307 | 130 | 220 | 0 | 0 | 615 | 53 | 4803 | 11345.2 | 96.22
22:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 51 | 54 | 149 | 0 | 278 | 30 | 17 | 143 | 0 | 0 | 0 | 460 | 0 | 55 | 260 | 0 | 0 | 0 | 90 | 18 | 15 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 16 | 0 | 36 | 25 | 0 | 40 | 16 | 33 | 355 | 44 | 0 | 19 | 0 | 66 | 185 | 0 | 0 | 0 | 1155 | 0 | 150 | 0 | 220 | 280 | 0 | 51 | 0 | 190 | 0 | 16 | 80 | 124 | 0 | 11 | 17 | 104 | 25 | 0 | 17 | 325 | 0 | 0 | 42 | 52 | 163 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 100 | 35 | 59 | 18 | 34 | 0 | 0 | 12 | 6287 | 452 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1127 | 53 | 0 | 0 | 766 | 0 | 22 | 0 | 70 | 113 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 130 | 220 | 0 | 0 | 620 | 48 | 4670 | 10957 | 96.21
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 47.1 | 0 | 149 | 0 | 278 | 0 | 17 | 144 | 0 | 0 | 0 | 450 | 0 | 55 | 260 | 0 | 0 | 0 | 17 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 25 | 0 | 40 | 0 | 36 | 355 | 20 | 0 | 0 | 0 | 65 | 185 | 0 | 0 | 0 | 1179 | 0 | 147 | 0 | 215 | 280 | 0 | 51 | 0 | 185 | 0 | 0 | 80 | 122 | 0 | 11 | 0 | 94 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 52 | 158 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 59 | 18 | 34 | 0 | 0 | 12 | 5796.1 | 452 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1116 | 17 | 0 | 0 | 766 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 180 | 0 | 0 | 622 | 53 | 4368 | 10164.1 | 96.21
Total KWH | 0 | 493440 | 289920 | 0 | 0 | 0 | 0 | 0 | 8258400 | 0 | 0 | 907560 | 649080 | 2572992 | 139680 | 3467815 | 248157 | 580545 | 2600640 | 0 | 0 | 0 | 9519091 | 0 | 838003 | 6516948 | 0 | 0 | 170894 | 1768800 | 461400 | 316440 | 0 | 0 | 65236 | 323673 | 0 | 0 | 17280 | 148506 | 183268 | 0 | 309120 | 476160 | 20520 | 1076220 | 234180 | 450720 | 8581818.18 | 426545 | 0 | 186720 | 8247.6 | 1067199 | 4281118 | 0 | 0 | 0 | 27850906 | 130950 | 2164509 | 0 | 5344500 | 7251600 | 0 | 1291685 | 0 | 4745000 | 0 | 120960 | 1905.02 | 1902720 | 33600 | 277630 | 158460 | 2326080 | 72946 | 401664 | 96416 | 7727500 | 0 | 0 | 993000 | 1274160 | 3799391 | 60888 | 474240 | 0 | 1892160 | 715200 | 0 | 0 | 2407950 | 204840 | 1100400 | 326400 | 871680 | 10650 | 243410 | 223920 | 134153655.8 | 10946181 | 7695360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 454320 | 26014600 | 405120 | 0 | 0 | 17875328 | 0 | 45000 | 0 | 1229376 | 1412832 | 0 | 0 | 115404 | 0 | 276924 | 529910 | 0 | 0 | 285744 | 4570727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24720 | 0 | 0 | 1737422 | 173500 | 1719398 | 0 | 0 | 0 | 32213.28 | 820080 | 2886 | 403296 | 7113000 | 3053000 | 5416220 | 0 | 0 | 14392727.27 | 733200 | 107478488.55 | 241632144.35