## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 21-01-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-01-2026 | during | 21-01-2026 | during | 21-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 343 | 366 | 412 | 412 | 392 | 392 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 280 | 335 | 335 | 335 | 335
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 49.2 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 48 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 21 | 24.75 | 24.75 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 15 | 15.1 | 15.1 | 15.1 | 15.1 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 34 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 277 | 294 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 120 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 108 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 13 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 400 | 445 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 125 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1742.2 | 2079 | 5327 | 5299 | 2618.13 | 2590.13
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 13 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 25 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 46 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 185 | 187 | 150 | 150 | 150 | 150 | Plant availability less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 66 | 105 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 16 | 16 | 16 | 16 | 16 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 51 | 51 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 36 | 60 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 7 | 18 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.89 | 0 | 3.28 | 0 | 3.28 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 30 | 65 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 34 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 65 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 30 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 72 | 126 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1140 | 613 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 3 | 18 | 14 | 18 | 14 | 18 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 355 | 415 | 415 | 415 | 355 | 355 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1973.89 | 1848 | 3169.14 | 3157.86 | 2711.78 | 2700.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 192 | 181 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 300 | 280 | 353.35 | 353.35 | 353.35 | 353.35 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 0 | 0 | Under maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 225 | 225 | 393 | 393 | 250 | 250 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 10 | 10 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | Gas shortage
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 137 | 147 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 30 | 42 | 42 | 42 | 42 | Machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 80 | 163 | 163 | 115 | 115 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 100 | 136 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 124 | 126 | 84 | 82 | 144 | 144 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 25 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 6 | 13 | 24.5 | 24.5 | 24.5 | 24.5 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 52 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 31 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1271 | 1346 | 2437.75 | 2370.75 | 1880.05 | 1815.05
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-01-2026 | during | 21-01-2026 | during | 21-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 32 | 30 | 157.5 | 157.5 | 50 | 50 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 19 | 20 | 20 | 20 | 20 | Fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 56 | 59 | 60 | 60 | 60 | 60 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 17.83 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 24 | 22 | 22 | 12 | 12 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 154.83 | 149 | 358.1 | 314 | 240.6 | 196.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 0 | 0 | 42 | 42 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 52 | 52 | 52 | 52 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 160 | 163 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 83 | 83 | 83 | 83 | 83
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 99 | 100 | 100 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 23 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 330 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 800 | 822 | 794 | 794 | 734 | 734
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 458 | 450 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 21 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 22 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 379 | 275 | 410 | 410 | 369 | 369 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 52 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 37 | 0 | 72 | 0 | 72 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1125 | 1155 | 1148.28 | 1148.28 | 1148 | 1148 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1999 | 1975 | 3492.28 | 3420.28 | 2696.1 | 2624.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 80 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 130 | 130 | 130 | 130 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 599 | 596 | 622 | 622 | 575 | 575 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 80 | 150 | 150 | 150 | 150 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 282 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.22 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1289.22 | 1388 | 1540 | 1539 | 1479 | 1478
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 20.57 | 0 | 44.5 | 0 | 44.5 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 130 | 169 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 6 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 108 | 50 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 75 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0 | 0 | 4.6 | 0 | 4.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 753.6 | 754 | 748 | 748 | 748 | 748 | U#1 Under AOH
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 18.7 | 0 | 60 | 0 | 60 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 39 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1190.87 | 1103 | 2028.3 | 1819.2 | 1534.9 | 1325.8
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 58 | 58 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 107 | 107 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.2 | 0 | 3.2 | 0 | 3.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 10 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 56 | 0 | 143.29 | 0 | 143.29 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 290.2 | 222 | 438.49 | 262 | 462.49 | 286
System Total |  |  |  |  | 28823.2 | 28382.248 | 10711.21 | 10932 | 19585.06 | 18976.09 | 14357.05 | 13750.08
Forecast Scenario (21-01-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9350 |  | 0 |  | 9350
|  |  |  | 1:00 | 8760 |  | 0 |  | 8760
|  |  |  | 2:00 | 8240 |  | 0 |  | 8240
|  |  |  | 3:00 | 8000 |  | 0 |  | 8000
|  |  |  | 4:00 | 7760 |  | 0 |  | 7760
|  |  |  | 5:00 | 7780 |  | 0 |  | 7780
|  |  |  | 6:00 | 8170 |  | 0 |  | 8170
|  |  |  | 7:00 | 9060 |  | 0 |  | 9060
|  |  |  | 8:00 | 10260 |  | 0 |  | 10260
|  |  |  | 9:00 | 10520 |  | 0 |  | 10520
|  |  |  | 10:00 | 10350 |  | 0 |  | 10350
|  |  |  | 11:00 | 10240 |  | 0 |  | 10240
|  |  |  | 12:00 | 10730 |  | 0 |  | 10730
|  |  |  | 13:00 | 11230 |  | 0 |  | 11230
|  |  |  | 14:00 | 10650 |  | 0 |  | 10650
|  |  |  | 15:00 | 10250 |  | 0 |  | 10250
|  |  |  | 16:00 | 9950 |  | 0 |  | 9950
|  |  |  | 17:00 | 10060 |  | 0 |  | 10060
|  |  |  | 18:00 | 11190 |  | 0 |  | 11190
|  |  |  | 18:30 | 11350 |  | 0 |  | 11350
|  |  |  | 19:00 | 11620 |  | 0 |  | 11620
|  |  |  | 19:30 | 11380 |  | 0 |  | 11380
|  |  |  | 20:00 | 11280 |  | 0 |  | 11280
|  |  |  | 21:00 | 11100 |  | 0 |  | 11100
|  |  |  | 22:00 | 10570 |  | 0 |  | 10570
|  |  |  | 23:00 | 9960 |  | 0 |  | 9960
Probable Maximum Temperature: |  |  | 26.60°C
Probable Maximum Demand at Day Peak: |  |  | 10730.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11620.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11620.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 237.08 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:53 hrs on 21-01-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 20-01-2026 | [28 empty] | Date: | 20-01-2026 | [28 empty] | Date: | 20-01-2026 | [28 empty] | Date: | 20-01-2026 | [28 empty] | Date: | 20-01-2026 | [17 empty] | Date: | 20-01-2026
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [17 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 51 | 0 | 149 | 0 | 95 | 0 | 17 | 17 | 0 | 0 | 0 | 455 | 0 | 55 | 260 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 0 | 37 | 355 | 0 | 0 | 0 | 0 | 66 | 185 | 0 | 0 | 0 | 1170 | 0 | 100 | 0 | 215 | 280 | 0 | 51 | 0 | 189 | 0 | 0 | 80 | 68 | 0 | 11 | 0 | 88 | 0 | 0 | 0 | 320 | 0 | 0 | 42 | 52 | 163 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 60 | 18 | 36 | 0 | 0 | 12 | 5362 | 452 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1128 | 0 | 0 | 0 | 759 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 180 | 0 | 0 | 560 | 50 | 4239 | 9601 | 96.21
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 49.5 | 0 | 86 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 455 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 0 | 37 | 355 | 0 | 0 | 0 | 0 | 65 | 186 | 0 | 0 | 0 | 1180 | 0 | 0 | 0 | 215 | 280 | 0 | 51 | 0 | 196 | 0 | 0 | 80 | 68 | 0 | 11 | 0 | 82 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 52 | 163 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 16 | 0 | 36 | 0 | 0 | 0 | 4959.5 | 453 | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1119 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 180 | 0 | 0 | 555 | 0 | 4031 | 8990.5 | 96.2
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 355 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 215 | 280 | 0 | 51 | 0 | 201 | 0 | 0 | 80 | 17 | 0 | 11 | 0 | 82 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 52 | 160 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 4620 | 452 | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1096 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 130 | 180 | 0 | 0 | 550 | 0 | 3913 | 8533 | 96.2
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 355 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 215 | 280 | 0 | 51 | 0 | 209 | 0 | 0 | 80 | 0 | 0 | 11 | 0 | 84 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 52 | 157 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 4625 | 452 | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 932 | 0 | 0 | 0 | 673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 130 | 180 | 0 | 0 | 500 | 0 | 3604 | 8229 | 96.2
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 355 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1128 | 0 | 0 | 0 | 220 | 280 | 0 | 51 | 0 | 207 | 0 | 0 | 80 | 0 | 0 | 11 | 0 | 76 | 0 | 0 | 0 | 325 | 0 | 0 | 42 | 52 | 144 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 4582 | 452 | 298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 828 | 0 | 0 | 0 | 571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 130 | 180 | 0 | 0 | 500 | 0 | 3401 | 7983 | 96.19
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 355 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1090 | 0 | 0 | 0 | 220 | 280 | 0 | 51 | 0 | 211 | 0 | 0 | 80 | 0 | 0 | 11 | 0 | 76 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 52 | 147 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 4522 | 452 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 839 | 0 | 0 | 0 | 578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283 | 130 | 220 | 0 | 0 | 450 | 0 | 3389 | 7911 | 96.19
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 355 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1130 | 0 | 0 | 0 | 225 | 280 | 0 | 51 | 0 | 211 | 0 | 0 | 80 | 0 | 0 | 11 | 0 | 84 | 0 | 0 | 0 | 320 | 0 | 0 | 42 | 52 | 148 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 4595 | 452 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 948 | 0 | 0 | 0 | 675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 450 | 0 | 3619 | 8214 | 96.19
07:00 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 35 | 0 | 3 | 0 | 110 | 0 | 0 | 17 | 0 | 0 | 0 | 435 | 0 | 17 | 250 | 0 | 0 | 1 | 35 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 12 | 0.1 | 40 | 0 | 36 | 355 | 45 | 0 | 0 | 0 | 19 | 185 | 0 | 0 | 0 | 1173 | 1 | 5 | 0 | 225 | 280 | 0 | 51 | 0 | 202 | 0 | 0 | 80 | 24 | 0 | 11 | 0 | 86 | 0 | 2 | 0 | 325 | 0 | 0 | 41 | 52 | 156 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 24 | 19 | 49 | 0 | 0.5 | 1 | 5031.6 | 452 | 311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1115 | 0 | 0 | 0 | 761 | 0 | 0 | 0 | 25 | 5 | 0 | 0 | 0 | 0 | 0.62 | 0 | 0 | 0 | 0.48 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0 | 0 | 105 | 0 | 70 | 0 | 0 | 0 | 0 | 1 | 0.01 | 0 | 307 | 130 | 220 | 0 | 0 | 522 | 2 | 4158.15 | 9189.75 | 96.18
08:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 52.3 | 0 | 84 | 0 | 277 | 42 | 0 | 17 | 0 | 0 | 0 | 415 | 0 | 30 | 250 | 0 | 0 | 6 | 70 | 21 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 12 | 25 | 0.59 | 40 | 0 | 15 | 355 | 72 | 0 | 0 | 0 | 68 | 185 | 0 | 0 | 0 | 1162 | 7 | 115 | 0 | 225 | 280 | 0 | 51 | 0 | 198 | 0 | 0 | 80 | 91 | 0 | 11 | 0 | 98 | 25 | 14 | 0 | 320 | 0 | 0 | 42 | 52 | 163 | 1 | 17 | 0 | 77 | 30 | 0 | 0 | 100 | 0.72 | 57 | 19 | 44 | 0 | 7.25 | 10 | 5761.86 | 452 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 1134 | 0 | 0 | 0 | 755.79 | 0 | 0 | 0 | 100 | 55 | 0 | 0 | 0 | 2 | 8.05 | 15 | 0 | 0 | 4.02 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 4 | 106 | 0 | 0 | 0 | 0.8 | 23 | 0.1 | 13 | 307 | 130 | 220 | 0 | 0 | 590 | 17 | 4579.76 | 10341.62 | 96.18
09:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 49.2 | 0 | 120 | 0 | 277 | 55 | 0 | 17 | 0 | 0 | 0 | 400 | 0 | 55 | 250 | 0 | 0 | 13 | 70 | 20 | 14 | 0 | 0 | 0 | 30 | 0 | 0 | 3 | 0 | 0 | 0 | 36 | 25 | 1.89 | 40 | 0 | 7 | 355 | 72 | 0 | 0 | 0 | 66 | 185 | 0 | 0 | 0 | 1140 | 13 | 137 | 0 | 225 | 300 | 0 | 51 | 0 | 192 | 0 | 0 | 80 | 100 | 0 | 6 | 0 | 124 | 25 | 31 | 0 | 320 | 0 | 0 | 42 | 52 | 160 | 2 | 17 | 0 | 77 | 30 | 0 | 0 | 100 | 17 | 56 | 19 | 32 | 1 | 17.83 | 12 | 5941.92 | 458 | 379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 1125 | 0 | 0 | 0 | 753.6 | 0 | 0 | 0 | 113 | 108 | 0 | 0 | 0 | 8 | 20.57 | 39 | 0 | 0 | 18.7 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 10 | 107 | 0 | 0 | 0 | 2.2 | 56 | 0.22 | 16 | 307 | 130 | 220 | 0 | 0 | 599 | 17 | 4769.29 | 10711.21 | 96.18
10:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 43.4 | 15 | 104 | 0 | 245 | 30 | 0 | 17 | 0 | 0 | 0 | 335 | 0 | 35 | 250 | 0 | 0 | 19 | 52 | 19.8 | 14 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 2 | 0 | 36 | 25 | 2.61 | 40 | 0 | 7 | 355 | 30 | 0 | 0 | 0 | 34 | 185 | 0 | 0 | 0 | 1145 | 17 | 70 | 0 | 225 | 290 | 0 | 51 | 0 | 187 | 0 | 0 | 80 | 68 | 0 | 11 | 0 | 120 | 8 | 46 | 0 | 305 | 0 | 0 | 42 | 52 | 153 | 6 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 17 | 59 | 19 | 32 | 1 | 28.57 | 12 | 5582.38 | 459 | 433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 1093 | 17 | 0 | 0 | 751.49 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 16 | 31.51 | 63 | 0 | 0 | 36.2 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.15 | 0 | 0 | 35 | 17 | 50 | 0 | 0 | 0 | 3.7 | 89 | 0.34 | 30 | 307 | 130 | 220 | 0 | 0 | 598 | 17 | 4656.39 | 10238.77 | 96.17
11:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 31.5 | 17 | 104 | 0 | 245 | 30 | 25 | 17 | 0 | 0 | 0 | 315 | 0 | 35 | 250 | 0 | 0 | 23 | 52 | 20.5 | 14 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 16 | 0 | 12 | 25 | 3.13 | 40 | 0 | 7 | 355 | 17 | 0 | 0 | 0 | 34 | 185 | 0 | 0 | 0 | 1170 | 19 | 70 | 0 | 215 | 300 | 0 | 51 | 0 | 177 | 0 | 0 | 80 | 65 | 0 | 11 | 0 | 130 | 8 | 56 | 9 | 310 | 0 | 0 | 42 | 52 | 158 | 7 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 17 | 59 | 19 | 30 | 2 | 34.76 | 12 | 5584.89 | 458 | 428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 1123 | 42 | 0 | 0 | 753.02 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 16 | 40.06 | 78 | 0 | 0 | 44.59 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.78 | 0 | 0 | 35 | 23 | 34 | 0 | 0 | 0 | 4.4 | 113 | 0.43 | 32 | 307 | 130 | 220 | 0 | 0 | 595 | 17 | 4765.28 | 10350.17 | 96.17
12:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 43 | 17 | 120 | 0 | 278 | 30 | 51 | 17 | 0 | 0 | 0 | 370 | 0 | 35 | 250 | 0 | 0 | 0 | 80 | 20.5 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 16 | 0 | 24 | 25 | 3.3 | 40 | 0 | 9 | 355 | 17 | 0 | 0 | 0 | 51 | 186 | 0 | 0 | 0 | 563 | 20 | 108 | 0 | 215 | 310 | 0 | 51 | 0 | 165 | 0 | 0 | 80 | 92 | 0 | 11 | 0 | 130 | 8 | 57 | 24 | 320 | 0 | 0 | 42 | 52 | 162 | 8 | 20 | 0 | 83 | 30 | 0 | 0 | 100 | 17 | 59 | 19 | 29 | 2 | 37.36 | 12 | 5280.16 | 458 | 423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 1131 | 51 | 0 | 0 | 755.25 | 0 | 0 | 0 | 76 | 40 | 0 | 0 | 0 | 16 | 42.23 | 90 | 0 | 0 | 48.23 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.08 | 0 | 0 | 110 | 23 | 100 | 0 | 0 | 0 | 4.7 | 123 | 0.46 | 31 | 307 | 130 | 220 | 0 | 0 | 594 | 17 | 4997.95 | 10278.11 | 96.17
13:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 49.9 | 17 | 142 | 48 | 278 | 48 | 55 | 35 | 0 | 0 | 0 | 450 | 0 | 35 | 250 | 0 | 0 | 26 | 125 | 15 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 7 | 0 | 16 | 0 | 24 | 25 | 3.18 | 40 | 0 | 6 | 355 | 54 | 0 | 0 | 0 | 65 | 185 | 0 | 0 | 0 | 536 | 19 | 150 | 0 | 215 | 280 | 0 | 51 | 0 | 177 | 0 | 0 | 80 | 117 | 0 | 11 | 34 | 138 | 34 | 56 | 17 | 315 | 0 | 0 | 42 | 52 | 158 | 8 | 20 | 0 | 83 | 30 | 0 | 0 | 100 | 17 | 59 | 19 | 29 | 2 | 34.57 | 12 | 5717.65 | 459 | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 1121 | 53 | 0 | 0 | 757.61 | 0 | 0 | 0 | 76 | 50 | 0 | 0 | 0 | 52.2 | 39.57 | 85 | 0 | 0 | 43.76 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.86 | 0 | 0 | 115 | 22 | 100 | 0 | 0 | 0 | 4.8 | 112 | 0.1 | 53 | 307 | 130 | 220 | 0 | 0 | 610 | 17 | 5049.9 | 10767.55 | 96.16
14:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 47.7 | 17 | 149 | 48 | 295 | 55 | 55 | 35 | 0 | 0 | 0 | 300 | 0 | 55 | 280 | 0 | 0 | 22 | 125 | 15 | 5 | 0 | 0 | 0 | 30 | 0 | 0 | 2 | 0 | 16 | 0 | 48 | 25 | 3 | 40 | 0 | 0 | 355 | 54 | 0 | 0 | 0 | 70 | 185 | 0 | 0 | 0 | 570 | 16 | 145 | 0 | 225 | 280 | 0 | 51 | 0 | 160 | 0 | 0 | 80 | 115 | 0 | 11 | 34 | 144 | 34 | 48 | 24 | 315 | 0 | 0 | 42 | 52 | 154 | 6 | 20.5 | 0 | 83 | 30 | 0 | 0 | 100 | 17 | 59 | 19 | 27 | 2 | 30.06 | 16 | 5686.26 | 458 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 1110 | 53 | 0 | 0 | 759 | 0 | 0 | 0 | 70 | 50 | 0 | 0 | 0 | 52.2 | 34.53 | 71 | 0 | 0 | 37.12 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.27 | 0 | 0 | 115 | 20 | 90 | 0 | 0 | 0 | 3.8 | 89 | 0.15 | 75 | 277 | 130 | 220 | 0 | 0 | 615 | 17 | 4957.07 | 10643.33 | 96.16
15:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 47 | 17 | 149 | 16 | 283 | 55 | 55 | 35 | 0 | 0 | 0 | 300 | 0 | 55 | 280 | 0 | 0 | 14 | 70 | 20.8 | 7 | 0 | 0 | 0 | 30 | 0 | 0 | 9 | 0 | 16 | 0 | 48 | 25 | 2.01 | 40 | 0 | 0 | 365 | 54 | 0 | 0 | 0 | 81 | 172 | 0 | 0 | 0 | 562 | 13 | 150 | 0 | 225 | 280 | 0 | 51 | 0 | 160 | 0 | 0 | 80 | 114 | 0 | 11 | 17 | 134 | 8 | 30 | 17 | 315 | 0 | 0 | 42 | 52 | 157 | 4 | 20.5 | 0 | 83 | 30 | 0 | 0 | 97 | 17 | 59 | 19 | 28 | 1 | 21.27 | 18 | 5503.58 | 459 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 1124 | 53 | 0 | 0 | 755 | 0 | 0 | 0 | 70 | 50 | 0 | 0 | 0 | 8 | 24.85 | 55 | 0 | 0 | 23.34 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.25 | 0 | 0 | 115 | 14 | 100 | 0 | 0 | 0 | 2.9 | 66 | 0.2 | 48 | 280 | 130 | 180 | 0 | 0 | 595 | 17 | 4767.54 | 10271.12 | 96.16
16:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 49.9 | 17 | 149 | 16 | 283 | 30 | 55 | 54 | 0 | 0 | 0 | 310 | 0 | 55 | 280 | 0 | 0 | 7 | 70 | 20.8 | 7 | 0 | 0 | 0 | 15 | 0 | 0 | 10 | 0 | 16 | 0 | 12 | 25 | 1.06 | 40 | 0 | 5 | 415 | 17 | 0 | 0 | 0 | 84 | 186 | 0 | 0 | 0 | 570 | 7 | 147 | 0 | 240 | 280 | 0 | 51 | 0 | 200 | 0 | 0 | 80 | 68 | 0 | 6 | 17 | 128 | 8 | 16 | 17 | 320 | 0 | 0 | 42 | 52 | 159 | 2 | 20.5 | 0 | 83 | 30 | 0 | 0 | 97 | 17 | 59 | 19 | 28 | 1 | 9.86 | 18 | 5476.12 | 458 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 1128 | 52 | 0 | 0 | 760 | 0 | 0 | 0 | 70 | 50 | 0 | 0 | 0 | 8 | 10.59 | 28 | 0 | 0 | 11.25 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 7 | 107 | 0 | 0 | 0 | 1.4 | 35 | 0.11 | 47 | 277 | 130 | 220 | 0 | 0 | 597 | 17 | 4702.35 | 10178.47 | 96.15
17:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 50.9 | 17 | 149 | 25 | 283 | 30 | 55 | 54 | 0 | 0 | 0 | 315 | 0 | 55 | 280 | 0 | 0 | 2 | 82 | 20.8 | 7 | 0 | 0 | 0 | 15 | 0 | 0 | 14 | 0 | 16 | 0 | 12 | 25 | 0.14 | 80 | 0 | 9 | 415 | 30 | 0 | 0 | 0 | 85 | 174 | 0 | 0 | 0 | 580 | 1 | 147 | 0 | 230 | 280 | 0 | 51 | 0 | 202 | 0 | 0 | 80 | 68 | 0 | 13 | 27 | 126 | 8 | 3 | 17 | 320 | 0 | 0 | 42 | 52 | 160 | 0 | 20.5 | 0 | 83 | 30 | 0 | 0 | 97 | 17 | 59 | 19 | 28 | 0 | 2.03 | 22 | 5552.37 | 458 | 360 | 0 | 7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 1126 | 52 | 0 | 0 | 758 | 0 | 0 | 0 | 75 | 50 | 0 | 0 | 12 | 8 | 2.22 | 7 | 6 | 0 | 2.59 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | 0 | 115 | 1 | 107 | 0 | 0 | 0 | 0.3 | 7 | 0.03 | 48 | 283 | 130 | 220 | 0 | 0 | 597 | 20 | 4589.36 | 10141.73 | 96.15
18:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 51 | 17 | 149 | 48 | 283 | 50 | 55 | 108 | 0 | 0 | 0 | 345 | 0 | 17 | 280 | 0 | 0 | 0 | 125 | 20.8 | 11 | 0 | 0 | 0 | 65 | 0 | 0 | 27 | 0 | 16 | 4 | 60 | 25 | 0 | 46 | 5 | 12 | 415 | 72 | 0 | 1 | 0 | 96 | 188 | 0 | 0 | 0 | 612 | 0 | 150 | 0 | 225 | 280 | 0 | 51 | 0 | 190 | 0 | 0 | 80 | 79 | 0 | 13 | 52 | 132 | 25 | 0 | 30 | 325 | 0 | 0 | 42 | 52 | 161 | 0 | 20.5 | 0 | 83 | 30 | 0 | 0 | 99 | 17 | 59 | 19 | 31 | 0 | 0 | 24 | 5975.3 | 458 | 333 | 0 | 30 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1137 | 52 | 0 | 0 | 769 | 0 | 0 | 0 | 75 | 50 | 0 | 0 | 0 | 25 | 0 | 0 | 6 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 280 | 130 | 220 | 0 | 0 | 598 | 80 | 4693 | 10668.3 | 96.15
19:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 17 | 149 | 48 | 288 | 55 | 17 | 108 | 0 | 0 | 0 | 400 | 0 | 0 | 280 | 0 | 0 | 0 | 125 | 21 | 15 | 0 | 0 | 18 | 70 | 0 | 0 | 23 | 0 | 16 | 34 | 60 | 25 | 0 | 46 | 46 | 16 | 415 | 126 | 0 | 23 | 0 | 104 | 173 | 0 | 0 | 0 | 612 | 0 | 147 | 0 | 225 | 280 | 0 | 51 | 0 | 186 | 0 | 0 | 80 | 124 | 0 | 13 | 52 | 128 | 25 | 0 | 30 | 320 | 0 | 0 | 42 | 52 | 163 | 0 | 23 | 0 | 83 | 30 | 0 | 0 | 99 | 17 | 59 | 19 | 30 | 0 | 0 | 24 | 6114 | 458 | 278 | 0 | 21 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1153 | 52 | 0 | 0 | 759 | 0 | 0 | 0 | 75 | 50 | 0 | 0 | 20 | 25 | 0 | 0 | 6 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 281 | 130 | 220 | 0 | 0 | 603 | 76 | 4695 | 10809 | 96.14
19:30 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 17 | 149 | 48 | 294 | 55 | 17 | 108 | 0 | 0 | 0 | 445 | 0 | 0 | 280 | 0 | 0 | 0 | 125 | 21 | 15 | 0 | 0 | 30 | 65 | 0 | 0 | 18 | 0 | 16 | 34 | 60 | 25 | 0 | 46 | 65 | 18 | 415 | 126 | 0 | 25 | 0 | 105 | 187 | 0 | 0 | 0 | 613 | 0 | 147 | 0 | 225 | 280 | 0 | 51 | 0 | 181 | 0 | 0 | 80 | 136 | 0 | 13 | 52 | 126 | 25 | 0 | 30 | 330 | 0 | 0 | 42 | 52 | 163 | 0 | 23 | 0 | 83 | 30 | 0 | 0 | 99 | 17 | 59 | 19 | 30 | 0 | 0 | 24 | 6244 | 450 | 275 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1155 | 52 | 0 | 0 | 754 | 0 | 0 | 0 | 75 | 50 | 0 | 0 | 24 | 25 | 0 | 0 | 6 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 282 | 130 | 220 | 0 | 0 | 596 | 80 | 4688 | 10932
20:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 17 | 149 | 48 | 294 | 55 | 17 | 108 | 0 | 0 | 0 | 425 | 0 | 0 | 280 | 0 | 0 | 0 | 125 | 21.5 | 15 | 0 | 0 | 32 | 45 | 0 | 0 | 16 | 0 | 16 | 34 | 60 | 25 | 0 | 46 | 67 | 25 | 415 | 126 | 0 | 25 | 0 | 102 | 186 | 0 | 0 | 0 | 612 | 0 | 147 | 0 | 215 | 280 | 0 | 51 | 0 | 180 | 0 | 0 | 80 | 136 | 0 | 13 | 52 | 120 | 25 | 0 | 30 | 325 | 0 | 0 | 42 | 52 | 163 | 0 | 23 | 0 | 83 | 30 | 0 | 0 | 99 | 17 | 59 | 19 | 30 | 0 | 0 | 24 | 6179.5 | 458 | 278 | 0 | 21 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1151 | 52 | 0 | 0 | 758 | 0 | 28 | 0 | 75 | 50 | 0 | 0 | 24 | 25 | 0 | 0 | 6 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 276 | 130 | 220 | 0 | 0 | 603 | 78 | 4734 | 10913.5 | 96.14
21:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 17 | 149 | 48 | 294 | 55 | 17 | 72 | 0 | 0 | 0 | 445 | 0 | 0 | 280 | 0 | 0 | 0 | 125 | 22.5 | 15 | 0 | 0 | 33 | 45 | 0 | 0 | 3 | 0 | 16 | 34 | 60 | 25 | 0 | 30 | 68 | 26 | 415 | 72 | 0 | 25 | 0 | 104 | 173 | 0 | 0 | 0 | 612 | 0 | 150 | 0 | 215 | 280 | 0 | 51 | 0 | 188 | 0 | 0 | 80 | 136 | 0 | 13 | 52 | 130 | 25 | 0 | 30 | 320 | 0 | 0 | 42 | 52 | 163 | 0 | 23 | 0 | 83 | 30 | 0 | 0 | 99 | 17 | 59 | 19 | 30 | 0 | 0 | 16 | 6089.5 | 458 | 274 | 0 | 21 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1152 | 52 | 0 | 0 | 757.86 | 0 | 22 | 0 | 75 | 50 | 0 | 0 | 24 | 25 | 0 | 0 | 6 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 288 | 130 | 220 | 0 | 0 | 615 | 81 | 4748.86 | 10838.36 | 96.14
22:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 17 | 149 | 48 | 277 | 55 | 0 | 54 | 0 | 0 | 0 | 430 | 0 | 0 | 280 | 0 | 0 | 0 | 125 | 21 | 15 | 0 | 0 | 34 | 30 | 0 | 0 | 17 | 0 | 16 | 34 | 60 | 25 | 0 | 30 | 67 | 28 | 415 | 55 | 0 | 25 | 0 | 104 | 194 | 0 | 0 | 0 | 612 | 0 | 150 | 0 | 215 | 280 | 0 | 51 | 0 | 191 | 0 | 0 | 80 | 136 | 0 | 13 | 52 | 116 | 25 | 0 | 32 | 320 | 0 | 0 | 42 | 52 | 163 | 0 | 22 | 0 | 83 | 30 | 0 | 0 | 99 | 17 | 59 | 19 | 30 | 0 | 0 | 16 | 6011 | 459 | 274 | 0 | 21 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1151 | 52 | 0 | 0 | 763.75 | 0 | 22 | 0 | 75 | 50 | 0 | 0 | 24 | 25 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 281 | 130 | 220 | 0 | 0 | 622 | 34 | 4705.75 | 10716.75 | 96.13
23:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 17 | 149 | 16 | 294 | 55 | 0 | 17 | 0 | 0 | 0 | 385 | 0 | 0 | 280 | 0 | 0 | 0 | 125 | 15 | 15 | 0 | 0 | 33 | 30 | 0 | 0 | 13 | 0 | 0 | 34 | 60 | 25 | 0 | 35 | 66 | 32 | 415 | 17 | 0 | 25 | 0 | 101 | 170 | 0 | 0 | 0 | 612 | 0 | 150 | 0 | 215 | 280 | 0 | 51 | 0 | 195 | 0 | 0 | 80 | 100 | 0 | 13 | 17 | 116 | 25 | 0 | 32 | 315 | 0 | 0 | 42 | 52 | 162 | 0 | 22 | 0 | 83 | 30 | 0 | 0 | 100 | 17 | 59 | 19 | 35 | 0 | 0 | 18 | 5697 | 462 | 278 | 0 | 21 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1139 | 52 | 0 | 0 | 766.09 | 0 | 14 | 0 | 35 | 50 | 0 | 0 | 24 | 25 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 279 | 130 | 220 | 0 | 0 | 622 | 35 | 4571.09 | 10268.09 | 96.13
Total KWH | 0 | 1148160 | 452160 | 0 | 0 | 0 | 0 | 0 | 8416800 | 0 | 0 | 623160 | 255600 | 2454624 | 419520 | 4745444 | 802355 | 492641 | 796320 | 0 | 0 | 0 | 9482727 | 0 | 533452 | 6496248 | 0 | 0 | 144705 | 1635600 | 438600 | 288000 | 0 | 0 | 184418 | 552000 | 0 | 0 | 197280 | 0 | 190741 | 229335 | 669120 | 458880 | 20398 | 1039700 | 405634 | 508800 | 9105454.55 | 861454 | 0 | 1564800 | 0 | 1523017 | 4263582 | 0 | 0 | 0 | 20825452 | 133785 | 2363563 | 0 | 5366500 | 7145500 | 0 | 1262689 | 0 | 4733000 | 0 | 0 | 1900219 | 1956480 | 0 | 267360 | 477660 | 2719680 | 331865 | 360473 | 325216 | 7754500 | 0 | 0 | 992000 | 1291200 | 3810682 | 46213 | 447840 | 0 | 1933440 | 719616 | 0 | 0 | 2391800 | 284760 | 1063200 | 336000 | 755520 | 9950 | 217560 | 294960 | 133919412.55 | 11048727 | 8305056 | 0 | 125280 | 122752 | 0 | 0 | 0 | 0 | 0 | 0 | 452160 | 26131000 | 711840 | 0 | 0 | 17673019 | 0 | 84600 | 0 | 1172640 | 1021056 | 0 | 0 | 110534 | 360504 | 256688 | 546860 | 30646 | 0 | 273000 | 3617273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19620 | 0 | 0 | 1835563 | 142183 | 1705939 | 0 | 0 | 0 | 28725.36 | 704880 | 2229 | 950496 | 7069000 | 3109000 | 5415090 | 0 | 0 | 14129454.55 | 622800 | 107778614.91 | 241698027.46

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 20-01-2026
Power Supply Scenario
| Day Peak Generation |  |  | 10711.21 | MW | 09:00 Hr. | Energy Generated |  |  | 241.698 |  | MKWHr.
| Day Peak Demand |  |  | 10711.21 | MW | 09:00 Hr. | Energy Unserverd |  |  | 3.236 |  | MKWHr.
| Evening Peak Generation |  |  | 10932 | MW | 19:30 Hr. | Energy Demand |  |  | 244.934 |  | MKWHr.
| Evening Peak Demand |  |  | 11498 | MW | 19:30 Hr. | Maximum Temperature |  |  | 26.8 |  | °C
| Minimum Generation of the Day |  |  | 7911 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 678.52 |  | MMCFD
| Maximum Generation of the Day |  |  | 10932 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 7.1716 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 25.1224 | 0 | 14.359 | 0 | 0 | 0.14471 | 0 | 0 | 39.6261 | Gas | 91.113 | Gas | 322744271.36
| Chattogram Zone |  |  | 4.7724 | 29.9309 | 6.6394 | 0 | 1.0397 | 0.15418 | 0 | 0.19728 | 42.7339 | Coal | 77.2604 | Coal | 507551071.8305
| Cumilla Zone |  |  | 20.6753 | 0 | 5.4548 | 0 | 0 | 0.36047 | 2.7197 | 0 | 29.2102 | HFO | 37.2868 | HFO | 654081616.32
| Mymensingh Zone |  |  | 0.75552 | 0 | 1.9789 | 0 | 0 | 0.22751 | 0 | 0 | 2.9619 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 19.3411 | 0 | 0 | 0 | 0 | 0.046213 | 0 | 0 | 19.3873 | Hydro | 1.0397 | Hydro | 103970
| Khulna Zone |  |  | 8.3051 | 26.131 | 0.95987 | 0 | 0 | 0.45216 | 11.0487 | 0 | 46.8968 | Solar | 3.3594 | Solar | 52668817.322
| Barishal Zone |  |  | 8.5241 | 21.1985 | 1.5733 | 0 | 0 | 0.002229 | 0 | 0 | 31.2981 | Import | 31.4414 | Import | 193301844.72
| Rajshahi Zone |  |  | 3.6173 | 0 | 2.78 | 0 | 0 | 1.0962 | 17.673 | 0 | 25.1664 | Wind | 0.19728 | Wind | 2901988.8
| Rangpur Zone |  |  | 0 | 0 | 3.5415 | 0 | 0 | 0.87579 | 0 | 0 | 4.4173
| Total |  |  | 91.113 | 77.2604 | 37.2868 | 0 | 1.0397 | 3.3594 | 31.4414 | 0.19728 | 241.698
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 322744271.36 |  | Hydro | 103970
|  |  |  | Coal | 507551071.8305 |  | Solar | 52668817.322
|  |  |  | HFO | 654081616.32 |  | Import | 193301844.72
|  |  |  | HSD | 0 |  | Wind | 2901988.8
[5 empty] | Total: | 173,33,53,580 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 11.0487 | Peak Hr Flow | 450.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 33272400.03 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 17.673 | Peak Hr Flow | 754.00 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1491 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.7197 | Peak Hr Flow | 126.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1928 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 31.4414 | Peak Hr Flow | 1330.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 180 |  | 4229
|  |  |  | Chattogram |  | 0 |  | 1215
|  |  |  | Cumilla |  | 0 |  | 984
|  |  |  | Mymensingh |  | 100 |  | 960
|  |  |  | Sylhet |  | 0 |  | 417
|  |  |  | Khulna |  | 110 |  | 1260
|  |  |  | Barishal |  | 10 |  | 268
|  |  |  | Rajshahi |  | 120 |  | 1095
|  |  |  | Rangpur |  | 22 |  | 697
|  |  |  | Total |  | 542 |  | 11125
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:02 | 17:39 | Fenchuganj 230/132/33kV S/S TR-01 LT Scheduled S/D Due to 132 KV BUS -1 Annual
Maintenance
| 08:07 | 17:39 | Fenchuganj 230/132/33kV S/S TR-01 HT Scheduled S/D Due to 132 KV BUS -1 Annual
Maintenance
| 08:09 | 17:26 | Fenchuganj 230/132/33kV S/S 132 KV Bus-1 Scheduled S/D Due to Annual maintenance
| 08:10 | 17:46 | Payra 400/132/33kV S/S 132/33 kV Transformer-04 LT Scheduled S/D Due to Maintenance
| 08:11 | 17:45 | Payra 400/132/33kV S/S 132/33 kV Transformer-04 HT Scheduled S/D Due to Maintenance
| 08:20 | 16:45 | Candpur (Desh)- Chandpur 132kV Ckt-1 Scheduled S/D from Chandpur 132/33kV end Due to
Annual maintenance work.
| 08:24 | 16:52 | Aminbazar 400/230/132kV S/S ATR-02 HT Scheduled S/D Due to Annual maintenance
| 08:24 | 17:54 | Aminbazar 400/230/132kV S/S ATR-02 LT Scheduled S/D Due to Annual maintenance
| 08:34 | 15:16 | Ramganj 132/33kV S/S Ramgonj-Desh Energy Ckt-02 Scheduled S/D Due to IVT Replacement Work
(B phase) .
| 08:36 | 15:49 | Taraganj 132/33kV S/S Taraganj-Saidpur CKT-01 Scheduled S/D Due to For annual maintenance
| 08:36 | 15:49 | Rangpur-Saidpur 132kV Ckt-1 Scheduled S/D from Saidpur 132/33kV end Due to Annual
maintenance
| 08:36 | 16:38 | Rangpur-Saidpur 132kV Ckt-2 Scheduled S/D from Rangpur 132/33kV end Due to Instruction
of ALDC Bogura
| 08:38 | 16:39 | Taraganj 132/33kV S/S Taraganj-Rangpur CKT-02 Scheduled S/D Due to For annual maintenance
| 08:39 | 18:09 | Aggreko-keraniganj 132kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to Dead
line checking by Keraniganj grid.
| 08:44 | 16:34 | Keraniganj-Sreenagar 132kV Ckt-1 Scheduled S/D from Srinagar 132/33kV end Due to Dead
Line Checking. and from Keranigonj 230/132/33kV end Due to Dead line checking by
Keraniganj grid.
| 08:46 | 16:35 | Gopalganj 400/132kV S/S 400kV Rampal Ckt-1 Scheduled S/D
| 08:47 | 16:45 | Rampal 400/230kV S/S Gopalganj Line-1 Reactor Forced S/D Due to Khulna ALDC Demand(Annual
Maintenance)
| 08:47 | 16:34 | Gopalganj(N)-Rampal Ckt-1 Forced S/D from Rampal 400/230kV end Due to Khulna ALDC
Demand(Annual Maintenance)
| 08:52 | 16:55 | Bogura-Rahanpur 400kV Ckt-2 Scheduled S/D from Rahanpur 400/132kV end Due to Annual
maintenance work and from Bogura 400/230kV end Due to Annual maintenance.
| 09:00 |  | Day Peak Generation: 10707 MW.
| 09:03 | 16:35 | Mymensingh RPCL-Tangail 132kV Ckt-1 Scheduled S/D from Muktagacha 132/33kV end.
| 09:05 | 16:46 | Daudkandi-Sonargaon 132 kV Ckt-2 Scheduled S/D from Sonargaon 132/33kV end Due to Annual
Maintenance
| 09:17 | 16:42 | Gopalganj(N)-Madaripur 132kV Ckt-3 Scheduled S/D from Madaripur 132/33kV end Due to
Annual maintenance and from Gopalganj 400/132kVend.
| 09:17 | 16:44 | Madaripur 132/33kV S/S Gopaganj North CKT-04 Scheduled S/D Due to Annual maintenance
| 09:26 | 14:41 | Goalpara-Labanchura 132kV Ckt-2 Scheduled S/D from Goalpara 132/33kV end Due to Annual
Maintenence works.
| 09:27 | 16:44 | Gopalganj 400/132kV S/S 132kV Madaripur Ckt-4 Scheduled S/D
| 09:28 | 19:40 | Sylhet 132/33kV S/S Sylhet-90MW P/S Scheduled S/D Due to OPGW change Purpose.
| 09:40 | 15:23 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Cumilla(N) Ckt-01 Scheduled S/D Due to
Maintenance Work
| 09:44 | 12:13 | Fenchuganj-Sreemangal 132kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Annual Maintenance
| 09:45 | 17:10 | Kodda(300MW)-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end.
| 09:51 | 16:29 | BIPTC S/S Baharampur-2 Scheduled S/D Due to Annual Maintenance
| 09:53 | 16:35 | Kabirpur -Kodda 132kV Ckt-2 Scheduled S/D from Kabirpur 132/33kV end Due to Annual Main
| 09:55 | 12:12 | Fenchuganj-Sreemangal 132kV Ckt-1 Forced S/D from Sreemongol 132/33kV end Due to NLDC
| 10:08 |  | Chowmuhani-Ramganj 132 kV Ckt-1 Scheduled S/D from Chowmuhani 132/33kV end Due to 132/33
kV Chowmuhani AIS Substation with new panels and integrating them into the SAS.
| 10:08 | 11:39 | Khulna(C )-Noapara 132kV Ckt-1 Scheduled S/D from Noapara 132/33kV end. and from Khulna
(C) end Due to For Kite removal
| 10:14 | 18:08 | Aminbazar-Kaliakoir 230kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to
Deadline Check.
| 10:52 | 12:49 | Fenchuganj-Fenchuganj 132 kV Ckt-4 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Annual Maintenance
| 10:55 | 12:25 | Ishurdi 132/33kV S/S 132/33 kV T-1 LT Scheduled S/D Due to 33 kv bus-2 A/M work | [7 empty] | 10.0MW load
interrup.
| 10:56 | 12:25 | Ishurdi 132/33kV S/S 132/33 kV T-1 HT Scheduled S/D Due to 33 kv bus-2 A/M work at NESCO | [7 empty] | 10.0MW load
interrup.
| 10:57 | 11:36 | Jhenaidah-Khulna 230kV Ckt-1 Tripped from Jhenaidah 230/132kV end showing 7sJ85 relays
Due to False Operation
| 11:10 | 19:55 | Chauddagram-Feni 132 kV Ckt-1 Project Work S/D from Feni 230/132kV end Due to circuit
breaker work
| 11:27 | 12:44 | Ullahpara 132/33kV S/S Power Transformer -1 LT Scheduled S/D Due to Oil Change/filling of
Incomer -1 PT.
| 11:28 | 12:44 | Ullahpara 132/33kV S/S Power Transformer -1 HT Scheduled S/D Due to Oil Change/filling of
Incomer -1 PT.
| 11:38 |  | SS Power Tripped
| 11:40 |  | SS Power Tripped with remarks:- unit-2
| 11:40 |  | SS Power Tripped
| 11:41 |  | SS Power Synchronized with remarks:- unit-1
| 11:41 |  | SS Power Synchronized with remarks:- unit-1(False)
| 12:53 | 15:29 | Fenchuganj-Fenchuganj 132 kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Annual Maintenance
| 12:59 | 13:48 | Ullahpara 132/33kV S/S Power Transformer-2 LT Scheduled S/D Due to Oil Change/filling of
Incomer -2 PT.
| 12:59 | 13:48 | Ullahpara 132/33kV S/S Power Transformer-2 HT Scheduled S/D Due to Oil Change/filling of
Incomer -2 PT.
| 15:02 | 16:25 | Fenchuganj 230/132/33kV S/S AT-02 LT Scheduled S/D Due to 132kV Bus-01 Annual Maintenance
| 15:03 | 16:24 | Fenchuganj 230/132/33kV S/S AT-02 HT Scheduled S/D Due to 132kV bus-02 Annual Maintenance
| 15:33 | 20:05 | Korerhat 400/230/132kV S/S ATR-3(7103T) HT Project Work S/D Due to Due to project work.
| 15:37 | 17:13 | Fenchuganj-Fenchuganj 132 kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
132kV BUS-01 Annual Maintenance
|  | 16:35 | Mymensingh RPCL-Tangail 132kV Ckt-1 is restored.
| 17:00 | 17:57 | Chandpur 132/33kV S/S 422T(T-5) HT Forced S/D Due to To remove the kite and kite string
| 17:00 | 17:57 | Chandpur 132/33kV S/S 422T(T-5) LT Forced S/D Due to To remove the kite and kite string
| 17:08 | 17:55 | Chandpur 132/33kV S/S Bus-B Forced S/D Due to To remove the kite and kite string
| 17:13 | 17:25 | Ghorasal-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Shutdown
taken by NLDC
|  | 17:28 | Ashuganj-Bhulta 400 kV Ckt-1 is restored.
| 19:30 |  | Evening Peak Generation: 10932 MW
| 05:00 |  | Minimum Generation is 7915 MW
| 07:29 |  | Sylhet 132/33kV S/S Sylhet-90MW P/S Project Work S/D Due to OPGW Replace
| 07:29 |  | Sylhet 132/33kV S/S Sylhet-90MW P/S Project Work S/D Due to OPGW Replace
| 07:42 |  | Candpur (Desh)- Chandpur 132kV Ckt-1 Scheduled S/D from Chandpur 132/33kV end Due to
Annual Maintenance
| 07:55 |  | Hasnabad 230/132kV S/S Bus-2 Scheduled S/D Due to annual maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 20-01-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 366 | 8416800 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 802355 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 6496248 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 623160 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 48 | 419520 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 492641 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 533452 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21 | 438600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 288000 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 34 | 452160 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 294 | 4745444 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2454624 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1148160 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 796320 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 144705 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 255600 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 445 | 9482727 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 125 | 1635600 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 2079 | 39626116
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 133785 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 25 | 1564800 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1039700 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 187 | 4263582 | Plant availability less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1523017 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 16 | 190741 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 60 | 669120 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 18 | 508800 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20398 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 65 | 552000 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 34 | 229335 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 65 | 405634 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 458880 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 30 | 184418 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 126 | 861454 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 613 | 20825452 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 18 | 197280 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 415 | 9105454.55 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4898.863 | 1848 | 42733850.55
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 181 | 4733000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 280 | 7145500 | STG Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Under maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 225 | 5366500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1262689 | Gas shortage
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 147 | 2363563 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 30 | 325216 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1900219 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 136 | 1956480 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 126 | 2719680 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 331865 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 267360 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 52 | 477660 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 360473 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1346 | 29210205
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 30 | 755520 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 336000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 1063200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 217560 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 294960 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 284760 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 149 | 2961950
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 46213 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 992000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 52 | 1291200 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3810682 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 719616 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1933440 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 99 | 2391800 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 23 | 447840 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 330 | 7754500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 822 | 19387291
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 450 | 11048727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 21 | 125280 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 22 | 122752 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 275 | 8305056 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 52 | 711840 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 452160 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1155 | 26131000 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1975 | 46896815
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 80 | 950496 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 3109000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 596 | 14129454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5415090 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 80 | 622800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 282 | 7069000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2229 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1388 | 31298069.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 256688 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 84600 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 110534 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 169 | 3617273 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 0 | 0 | Under Maintenance
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 6 | 30646 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 25 | 360504 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 1021056 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 75 | 1172640 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 19620 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 754 | 17673019 | U#1 Under AOH
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 273000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 546860 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1103 | 25166440
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 1705939 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 28725.36 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1835563 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 142183 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 704880 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 222 | 4417290.36
Eastern Grid Total |  |  |  |  | 17398.245 | 6244 | 133919412.55
Western Grid Total |  |  |  |  | 10984.003 | 4688 | 107778614.91
National Grid Total |  |  |  |  | 28382.248 | 10932 | 241698027.46
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 20-01-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7525.69 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3057.9 | MW
i) Dhaka area |  |  | 4049.29 |  | MW | i) Khulna area |  |  |  | 1149.5 | MW
ii) Chattogram area |  |  | 1215.4 |  | MW | ii) Barishal area |  |  |  | 258 | MW
iii) Cumilla area |  |  | 984 |  | MW | iii) Rajshahi area |  |  |  | 975.4 | MW
iv) Mymensingh area |  |  | 860 |  | MW | iv) Rangpur area |  |  |  | 675 | MW
v) Sylhet area |  |  | 417 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10583.59 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 14 | 19:00 | 67 | Hasnabad | 77 | 12:00 | 133 | Netrakona | 127 | 17:00
2 | AKSML | 77.4 | 04:00 | 68 | Hathazari | 62 | 13:00 | 134 | New | 68.6 | 12:00
3 | Aftabnagar | 26 | 13:00 | 69 | Hatirjheel | 24 | 15:00 | 135 | Niamatpur | 73 | 07:00
4 | Agargaon | 93 | 13:00 | 70 | Ishurdi | 48 | 13:00 | 136 | Noapara | 37 | 08:00
5 | Agrabad | 50 | 18:00 | 71 | Jaldhaka | 52 | 08:00 | 137 | PHP | 9 | 10:00
6 | Amnura | 33 | 08:00 | 72 | Jamalpur | 84 | 09:00 | 138 | Pabna | 73 | 12:00
7 | Ashuganj | 67 | 14:00 | 73 | Jashore | 100 | 09:00 | 139 | Palashbari | 86 | 08:00
8 | BSRM | 196 | 03:00 | 74 | Jhenaidah | 91 | 09:00 | 140 | Panchagarh | 42 | 18:30
9 | Bagerhat | 61 | 22:00 | 75 | Joydebpur | 106 | 09:00 | 141 | Patiya | 6 | 18:00
10 | Bajitpur | 59 | 14:00 | 76 | Joypurhat | 40 | 08:00 | 142 | Patuakhali | 37.5 | 21:00
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 17.5 | 14:00 | 143 | Payra | 44 | 15:00
12 | Bakulia | 68 | 18:00 | 78 | KSRM | 13 | 06:00 | 144 | Postogola | 42 | 13:00
13 | Banani | 39.6 | 13:00 | 79 | Kabirpur | 190 | 18:00 | 145 | Purbachal | 22 | 13:00
14 | Bangabhaban | 8 | 10:00 | 80 | Kachua | 61 | 18:00 | 146 | Purbasadipur | 107 | 12:00
15 | Barapukuria | 51 | 08:00 | 81 | Kallyanpur | 81 | 13:00 | 147 | Rahanpur | 23 | 08:00
16 | Barguna | 14 | 18:00 | 82 | Kalurghat | 34 | 12:00 | 148 | Rahim | 50 | 11:00
17 | Barishal | 93 | 13:00 | 83 | Kamrangirchar | 68 | 13:00 | 149 | Rajbari | 54 | 19:00
18 | Barishal-230 | 66 | 18:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 115 | 18:00
19 | Baroaulia | 57 | 11:00 | 85 | Kasba | 28 | 18:00 | 151 | Rajshahi | 75 | 19:30
20 | Baroirhat | 51 | 18:00 | 86 | Kazla | 94 | 13:00 | 152 | Rajshahi-230 | 71 | 13:00
21 | Bashundhara | 159 | 13:00 | 87 | Keranigonj | 70 | 11:00 | 153 | Ramganj | 68 | 18:00
22 | BashundharaCement | 7 | 01:00 | 88 | Khagrachori | 26 | 18:00 | 154 | Rampur | 29 | 19:30
23 | Beanibazar | 48 | 18:00 | 89 | Khulna | 49 | 13:00 | 155 | Rangamati | 14 | 18:30
24 | Benapole | 68 | 09:00 | 90 | Khulshi | 152 | 14:00 | 156 | Rangpur | 108 | 08:00
25 | Bhaluka | 138 | 17:00 | 91 | Kishoreganj | 94 | 22:00 | 157 | Ruppur | 2.6 | 11:00
26 | Bhandaria | 38 | 22:00 | 92 | Kodda | 268 | 18:30 | 158 | SSM | 0 | 00:00
27 | Bhangura | 44 | 21:00 | 93 | Kulaura | 29 | 18:00 | 159 | Saidpur | 90 | 08:00
28 | Bheramara(GK) | 40 | 19:30 | 94 | Kurigram | 56 | 08:00 | 160 | Satkhira | 100 | 19:30
29 | Bhulta | 179 | 08:00 | 95 | Kushtia | 113 | 13:00 | 161 | Satmasjid | 80 | 14:00
30 | Bog-Sherpur | 60 | 08:00 | 96 | Laksam | 14 | 21:00 | 162 | Savar | 173 | 11:00
31 | Bogura | 122 | 18:30 | 97 | Lakshmipur | 24 | 18:00 | 163 | SevenRings | 23.03 | 15:00
32 | Borhanuddin | 65 | 22:00 | 98 | Lalbag | 54 | 11:00 | 164 | ShahCement | 36 | 02:00
33 | Brahmanbaria | 90 | 21:00 | 99 | Lalmonirhat | 47 | 18:30 | 165 | Shahjadpur | 56 | 12:00
34 | Cantonment | 74 | 13:00 | 100 | MI_Cement | 16.8 | 02:00 | 166 | Shahjibazar | 102 | 21:00
35 | Chandina | 20 | 13:00 | 101 | Madanganj | 26 | 18:30 | 167 | Shahmirpur | 41 | 18:30
36 | Chandpur | 54 | 13:00 | 102 | Madaripur | 71 | 19:30 | 168 | Shariatpur | 56 | 22:00
37 | Chandraghona | 28 | 18:30 | 103 | Madartek | 60 | 14:00 | 169 | Sherpur | 124 | 07:00
38 | Chapai | 53 | 08:00 | 104 | Madunaghat | 38 | 18:00 | 170 | Shikalbaha | 28.5 | 18:30
39 | Charsaidpur | 41 | 02:00 | 105 | Magura | 48 | 08:00 | 171 | Shitalakhya | 69 | 12:00
40 | Chauddagram | 53 | 13:00 | 106 | Mahasthangarh | 48 | 08:00 | 172 | Sholosohor | 37 | 15:00
41 | Chhatak | 29 | 18:00 | 107 | Maijdee | 38 | 22:00 | 173 | Shyampur | 140 | 11:00
42 | Chowmuhani | 117 | 18:00 | 108 | Manikganj | 91 | 19:00 | 174 | Siddhirganj | 113 | 12:00
43 | Chuadanga | 82 | 08:00 | 109 | Maniknagar | 46 | 13:00 | 175 | Sirajganj | 80 | 19:00
44 | Coxsbazar | 109 | 19:30 | 110 | Matarbari | 46 | 18:00 | 176 | Sonargaon | 138 | 07:00
45 | Cumilla(N) | 109 | 19:30 | 111 | Matuail | 56 | 10:00 | 177 | Sreemongol | 57 | 18:00
46 | Cumilla(S) | 144 | 14:00 | 112 | Metrorail_Motijheel | 25 | 09:00 | 178 | Sreepur | 99 | 11:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 6 | 10:00 | 179 | Srinagar | 33.16 | 14:00
48 | Daudkandi | 103 | 23:00 | 114 | Millgate | 82 | 15:00 | 180 | Sunamganj | 41 | 20:00
49 | DhakaUniversity | 54 | 13:00 | 115 | Mirpur | 114 | 14:00 | 181 | Sylhet | 42 | 18:00
50 | Dhamrai | 106 | 09:00 | 116 | Mirsorai | 10 | 15:00 | 182 | Sylhet-132 | 70 | 19:00
51 | Dhanmondi | 71 | 13:00 | 117 | Mirzapur | 39 | 12:00 | 183 | TK | 15 | 16:00
52 | Dohazari | 77 | 19:30 | 118 | Mithapukur | 44 | 08:00 | 184 | Tangail | 134 | 08:00
53 | Faridpur | 124 | 20:00 | 119 | Modern | N/A | N/A | 185 | Taraganj | 24 | 13:00
54 | Fatullah | 95 | 12:00 | 120 | Mogbazar | 54.2 | 14:00 | 186 | Tasnim | 30 | 12:00
55 | Fenchuganj | 23 | 18:00 | 121 | Mongla | 28 | 16:00 | 187 | Thakurgaon | 75 | 18:00
56 | Feni | 70 | 13:00 | 122 | Motijheel | 35 | 12:00 | 188 | Tongi | 116 | 20:00
57 | GPH | 96 | 09:00 | 123 | Muktagacha | 29 | 09:00 | 189 | Ullahpara | 27 | 18:30
58 | Ghatail | 62 | 17:00 | 124 | Munshiganj | 66 | 08:00 | 190 | Ullon | 40 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 0 | 00:00 | 191 | Uttara | 54 | 18:00
60 | Ghorashal-230 | 82 | 09:00 | 126 | Mymensingh | 154 | 08:00 | 192 | UttaraNew | 30 | 13:00
61 | Goalpara | 30 | 13:00 | 127 | Naogaon | 98 | 08:00 | 193 | Zigatola | 78 | 13:00
62 | Gollamari | 80 | 14:00 | 128 | Narail | 39 | 22:00
63 | Gopalganj | 78 | 08:00 | 129 | Narinda | 56 | 13:00
64 | Gulshan | 76 | 13:00 | 130 | Narshingdi | 133 | 23:00
65 | Halishahar | 70 | 14:00 | 131 | Natore | 105 | 08:00
66 | HaripurSBU | 134 | 12:00 | 132 | Nawabganj | 31.6 | 14:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 20-01-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 9601 | 0 |  | 9601
1:00 | 8990.5 | 0 |  | 8990.5
2:00 | 8533 | 0 |  | 8533
3:00 | 8229 | 0 |  | 8229
4:00 | 7983 | 0 |  | 7983
5:00 | 7911 | 0 |  | 7911
6:00 | 8214 | 0 |  | 8214
7:00 | 9189.75 | 0 |  | 9189.75
8:00 | 10341.62 | 0 |  | 10341.62
9:00 | 10711.21 | 0 |  | 10711.21
10:00 | 10238.77 | 0 |  | 10238.77
11:00 | 10350.17 | 0 |  | 10350.17
12:00 | 10278.11 | 0 |  | 10278.11
13:00 | 10767.55 | 418 |  | 11204.55
14:00 | 10643.33 | 392 |  | 11053.33
15:00 | 10271.12 | 347 |  | 10634.12
16:00 | 10178.47 | 0 |  | 10178.47
17:00 | 10141.73 | 0 |  | 10141.73
18:00 | 10668.3 | 480 |  | 11170.3
19:00 | 10809 | 612 |  | 11449
19:30 | 10932 | 542 |  | 11498
20:00 | 10913.5 | 465 |  | 11399.5
21:00 | 10838.36 | 394 |  | 11250.36
22:00 | 10716.75 | 128 |  | 10850.75
23:00 | 10268.09 | 0 |  | 10268.09
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 20-01-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5362 | 4239 | 9601 | DAILY GENERATION CURVE
00:30 | 5160.75 | 4135 | 9295.75
01:00 | 4959.5 | 4031 | 8990.5 | 20-01-2026
01:30 | 4789.75 | 3972 | 8761.75
02:00 | 4620 | 3913 | 8533
02:30 | 4622.5 | 3758.5 | 8381
03:00 | 4625 | 3604 | 8229
03:30 | 4603.5 | 3502.5 | 8106
04:00 | 4582 | 3401 | 7983
04:30 | 4552 | 3395 | 7947
05:00 | 4522 | 3389 | 7911
05:30 | 4558.5 | 3504 | 8062.5
06:00 | 4595 | 3619 | 8214
06:30 | 4813.3 | 3888.575 | 8701.875
07:00 | 5031.6 | 4158.15 | 9189.75
07:30 | 5396.73 | 4368.955 | 9765.685
08:00 | 5761.86 | 4579.76 | 10341.62
08:30 | 5851.89 | 4674.525 | 10526.415
09:00 | 5941.92 | 4769.29 | 10711.21
09:30 | 5762.15 | 4712.84 | 10474.99
10:00 | 5582.38 | 4656.39 | 10238.77
10:30 | 5583.635 | 4710.835 | 10294.47
11:00 | 5584.89 | 4765.28 | 10350.17
11:30 | 5432.525 | 4881.615 | 10314.14
12:00 | 5280.16 | 4997.95 | 10278.11
12:30 | 5498.905 | 5023.925 | 10522.83
13:00 | 5717.65 | 5049.9 | 10767.55
13:30 | 5701.955 | 5003.485 | 10705.44
14:00 | 5686.26 | 4957.07 | 10643.33
14:30 | 5594.92 | 4862.305 | 10457.225
15:00 | 5503.58 | 4767.54 | 10271.12
15:30 | 5489.85 | 4734.945 | 10224.795
16:00 | 5476.12 | 4702.35 | 10178.47
16:30 | 5514.245 | 4645.855 | 10160.1
17:00 | 5552.37 | 4589.36 | 10141.73
17:30 | 5763.835 | 4641.18 | 10405.015
18:00 | 5975.3 | 4693 | 10668.3
18:30 | 6044.65 | 4694 | 10738.65
19:00 | 6114 | 4695 | 10809
19:30 | 6244 | 4688 | 10932
20:00 | 6179.5 | 4734 | 10913.5
20:30 | 6134.5 | 4741.43 | 10875.93 |  | Executive Engineer
21:00 | 6089.5 | 4748.86 | 10838.36 |  | Network Operation Division
21:30 | 6050.25 | 4727.305 | 10777.555
22:00 | 6011 | 4705.75 | 10716.75
22:30 | 5854 | 4638.42 | 10492.42
23:00 | 5697 | 4571.09 | 10268.09

## En-Curve
QF-LDC-12
Date | 20-01-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2397 | 1350 | 452 | 0 | 88 | 759 | 40 | 3520 | 0 | 0 | 995 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2399.5 | 1345.5 | 452.5 | 0 | 85 | 758.5 | 40 | 3518 | 0 | 0 | 696.75 | 0 | 0 | 0 | 0 | 20-01-2026
01:00 | 2402 | 1341 | 453 | 0 | 82 | 758 | 40 | 3516 | 0 | 0 | 398.5 | 0 | 0 | 0 | 0
01:30 | 2398.5 | 1337 | 452.5 | 0 | 82 | 756.5 | 40 | 3485.5 | 0 | 0 | 207.75 | 0 | 0 | 2 | 0 | Energy Generated | 241.698 |  | MKWHr
02:00 | 2395 | 1333 | 452 | 0 | 82 | 755 | 40 | 3455 | 0 | 0 | 17 | 0 | 0 | 4 | 0 | Energy not Served | 3.236 |  | MKWHr
02:30 | 2402.5 | 1334 | 452 | 0 | 83 | 714 | 40 | 3340.5 | 0 | 0 | 8.5 | 0 | 0 | 6.5 | 0 | Total Energy Requirement | 244.934 |  | MKWHr
03:00 | 2410 | 1335 | 452 | 0 | 84 | 673 | 40 | 3226 | 0 | 0 | 0 | 0 | 0 | 9 | 0
03:30 | 2413.5 | 1333.5 | 452 | 0 | 80 | 622 | 40 | 3157 | 0 | 0 | 0 | 0 | 0 | 8 | 0
04:00 | 2417 | 1332 | 452 | 0 | 76 | 571 | 40 | 3088 | 0 | 0 | 0 | 0 | 0 | 7 | 0
04:30 | 2417 | 1327 | 452 | 0 | 76 | 574.5 | 40 | 3052.5 | 0 | 0 | 0 | 0 | 0 | 8 | 0
05:00 | 2417 | 1322 | 452 | 0 | 76 | 578 | 40 | 3017 | 0 | 0 | 0 | 0 | 0 | 9 | 0
05:30 | 2421 | 1331.5 | 452 | 0 | 80 | 626.5 | 40 | 3103.5 | 0 | 0 | 0 | 0 | 0 | 8 | 0
06:00 | 2425 | 1341 | 452 | 0 | 84 | 675 | 40 | 3190 | 0 | 0 | 0 | 0 | 0 | 7 | 0
06:30 | 2423.5 | 1353.5 | 452 | 0 | 85 | 718 | 40 | 3331 | 3.875 | 18.5 | 269 | 0 | 0 | 7.5 | 0
07:00 | 2422 | 1366 | 452 | 0 | 86 | 761 | 40 | 3472 | 7.75 | 37 | 538 | 0 | 0 | 8 | 0
07:30 | 2452 | 1345.5 | 452 | 0 | 92 | 758.395 | 40 | 3510 | 57.28 | 78.5 | 971.51 | 0 | 0 | 8.5 | 0
08:00 | 2482 | 1325 | 452 | 0 | 98 | 755.79 | 40 | 3548 | 106.81 | 120 | 1405.02 | 0 | 0 | 9 | 0
08:30 | 2476 | 1308.5 | 455 | 0 | 111 | 754.695 | 40 | 3537 | 185.11 | 124.5 | 1528.61 | 0 | 0 | 6 | 0
09:00 | 2470 | 1292 | 458 | 0 | 124 | 753.6 | 40 | 3526 | 263.41 | 129 | 1652.2 | 0 | 0 | 3 | 0
09:30 | 2476.5 | 1252.4 | 458.5 | 0 | 122 | 752.545 | 40 | 3512 | 341.745 | 125.5 | 1392.3 | 0 | 0 | 1.5 | 0
10:00 | 2483 | 1212.8 | 459 | 0 | 120 | 751.49 | 40 | 3498 | 420.08 | 122 | 1132.4 | 0 | 0 | 0 | 0
10:30 | 2482.5 | 1208.15 | 458.5 | 0 | 125 | 752.255 | 40 | 3524 | 470.115 | 116 | 1117.95 | 0 | 0 | 0 | 0
11:00 | 2482 | 1203.5 | 458 | 0 | 130 | 753.02 | 40 | 3550 | 520.15 | 110 | 1103.5 | 0 | 0 | 0 | 0
11:30 | 2488.5 | 1235 | 458 | 0 | 130 | 754.135 | 40 | 3250 | 528.255 | 131.5 | 1298.75 | 0 | 0 | 0 | 0
12:00 | 2495 | 1266.5 | 458 | 0 | 130 | 755.25 | 40 | 2950 | 536.36 | 153 | 1494 | 0 | 0 | 0 | 0
12:30 | 2481 | 1297.75 | 458.5 | 0 | 134 | 756.43 | 40 | 2939.5 | 530.1 | 227 | 1655.05 | 0 | 0 | 3.5 | 209
13:00 | 2467 | 1329 | 459 | 0 | 138 | 757.61 | 40 | 2929 | 523.84 | 301 | 1816.1 | 0 | 0 | 7 | 418
13:30 | 2475.5 | 1251.75 | 458.5 | 0 | 141 | 758.305 | 40 | 2928 | 482.385 | 309 | 1856.5 | 0 | 0 | 4.5 | 405
14:00 | 2484 | 1174.5 | 458 | 0 | 144 | 759 | 40 | 2927 | 440.93 | 317 | 1896.9 | 0 | 0 | 2 | 392
14:30 | 2474 | 1159.9 | 458.5 | 0 | 139 | 757 | 40 | 2926.5 | 379.875 | 270 | 1846.95 | 0 | 0 | 5.5 | 369.5
15:00 | 2464 | 1145.3 | 459 | 0 | 134 | 755 | 40 | 2926 | 318.82 | 223 | 1797 | 0 | 0 | 9 | 347
15:30 | 2504.5 | 1173.8 | 458.5 | 0 | 131 | 757.5 | 40 | 2956.5 | 239.545 | 223 | 1730.95 | 0 | 0 | 9.5 | 173.5
16:00 | 2545 | 1202.3 | 458 | 0 | 128 | 760 | 40 | 2987 | 160.27 | 223 | 1664.9 | 0 | 0 | 10 | 0
16:30 | 2511.5 | 1210.8 | 458 | 0 | 127 | 759 | 60 | 2994 | 96.9 | 247 | 1683.9 | 0 | 0 | 12 | 0
17:00 | 2478 | 1219.3 | 458 | 0 | 126 | 758 | 80 | 3001 | 33.53 | 271 | 1702.9 | 0 | 0 | 14 | 0
17:30 | 2478 | 1240.8 | 458 | 0 | 129 | 763.5 | 63 | 3021.5 | 16.765 | 337.5 | 1876.45 | 0 | 0 | 20.5 | 240
18:00 | 2478 | 1262.3 | 458 | 0 | 132 | 769 | 46 | 3042 | 0 | 404 | 2050 | 0 | 0 | 27 | 480
18:30 | 2436 | 1293.65 | 458 | 0 | 130 | 764 | 46 | 3053 | 0 | 414.5 | 2118.5 | 0 | 0 | 25 | 546
19:00 | 2394 | 1325 | 458 | 0 | 128 | 759 | 46 | 3064 | 0 | 425 | 2187 | 0 | 0 | 23 | 612
19:30 | 2426 | 1382 | 450 | 0 | 126 | 754 | 46 | 3061 | 0 | 431 | 2238 | 0 | 0 | 18 | 542
20:00 | 2410 | 1364.5 | 458 | 0 | 120 | 758 | 46 | 3057 | 0 | 467 | 2217 | 0 | 0 | 16 | 465
20:30 | 2410 | 1373 | 458 | 0 | 125 | 757.93 | 38 | 3069.5 | 0 | 462 | 2173 | 0 | 0 | 9.5 | 429.5
21:00 | 2410 | 1381.5 | 458 | 0 | 130 | 757.86 | 30 | 3082 | 0 | 457 | 2129 | 0 | 0 | 3 | 394
21:30 | 2420 | 1373.75 | 458.5 | 0 | 123 | 760.805 | 30 | 3081.5 | 0 | 456.5 | 2063.5 | 0 | 0 | 10 | 261
22:00 | 2430 | 1366 | 459 | 0 | 116 | 763.75 | 30 | 3081 | 0 | 456 | 1998 | 0 | 0 | 17 | 128
22:30 | 2417.5 | 1339.5 | 460.5 | 0 | 116 | 764.92 | 32.5 | 3074 | 0 | 402 | 1870.5 | 0 | 0 | 15 | 64
23:00 | 2405 | 1313 | 462 | 0 | 116 | 766.09 | 35 | 3067 | 0 | 348 | 1743 | 0 | 0 | 13 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 20-01-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 422 | 00:00 | 414 | 16:00 | Madunaghat | 423 | 00:00 | 403 | 02:00
Amtali | N/A | N/A | N/A | N/A | Meghnaghat | 427 | 23:00 | 414 | 11:00
Ashuganj | 413 | 23:00 | 401 | 11:00 | Payra | 425 | 01:00 | 419 | 11:00
Bhulta | 405 | 23:00 | 387 | 11:00 | Rahanpur | 420 | 04:00 | 408 | 11:00
Bibiana | 424 | 20:00 | 418 | 02:00 | Rampal | 418 | 04:00 | 406 | 09:00
BIPTC | 407 | 02:00 | 393 | 12:00
Bogura | 418 | 22:00 | 401 | 11:00
Gopalganj | 422 | 04:00 | 411 | 11:00
Kaliakoir | 420 | 22:00 | 406 | 11:00
Korerhat | 427 | 21:00 | 419 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 244 | 00:00 | 235 | 11:00 | Kachua | 244 | 18:30 | 240 | 02:00
AKSML | 242 | 21:00 | 235 | 15:00 | Kaliakoir | 245 | 21:00 | 239 | 11:00
Aminbazar | 244 | 00:00 | 236 | 16:00 | Keranigonj | 242 | 04:00 | 233 | 11:00
Ashuganj | 243 | 23:00 | 232 | 11:00 | Khulna(S) | 246 | 04:00 | 239 | 08:00
Ashuganj-400 | 240 | 23:00 | 230 | 11:00 | Korerhat | 243 | 18:30 | 236 | 11:00
Baghabari | 244 | 22:00 | 235 | 11:00 | Madunaghat | 239 | 22:00 | 230 | 11:00
Barapukuria | 239 | 19:00 | 224 | 10:00 | Madunaghat-400 | 240 | 21:00 | 232 | 11:00
Barapukuria-230 | 239 | 19:00 | 222 | 11:00 | Maniknagar | 244 | 04:00 | 231 | 11:00
Barishal | 238 | 03:00 | 235 | 11:00 | Meghnaghat | 247 | 22:00 | 238 | 11:00
Bheramara | 242 | 13:00 | 237 | 07:00 | Meghnaghat-400 | 242 | 23:00 | 234 | 11:00
Bhulta | 243 | 05:00 | 233 | 11:00 | Mirsorai | 245 | 18:30 | 236 | 11:00
Bibiana | 246 | 05:00 | 240 | 10:00 | Rajshahi | 241 | 19:00 | 236 | 07:00
BIPTC | 244 | 13:00 | 236 | 07:00 | Rampal | 242 | 04:00 | 234 | 09:00
Bogura | 246 | 22:00 | 236 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 245 | 22:00 | 234 | 11:00 | Rampura | 242 | 04:00 | 232 | 11:00
Borhanuddin | 240 | 04:00 | 237 | 11:00 | Shikalbaha | 239 | 21:00 | 229 | 11:00
BSRM | 243 | 18:00 | 235 | 11:00 | Shyampur | 241 | 00:00 | 232 | 11:00
Cumilla(N) | 241 | 18:00 | 234 | 10:00 | Siddhirganj | 243 | 22:00 | 234 | 11:00
Faridpur | 238 | 03:00 | 233 | 11:00 | Sirajgonj | 248 | 04:00 | 240 | 11:00
Fenchuganj | 247 | 22:00 | 240 | 21:00 | Sreepur | 241 | 23:00 | 230 | 11:00
Feni | 244 | 20:00 | 236 | 11:00 | Tongi | 245 | 23:00 | 233 | 11:00
Ghorashal | 243 | 00:00 | 235 | 14:00
Ghorashal-230 | 243 | 23:00 | 234 | 11:00
Gopalganj | 237 | 04:00 | 231 | 11:00
GPH | 241 | 20:00 | 232 | 11:00
Haripur | 242 | 04:00 | 234 | 11:00
Hasnabad | 243 | 23:00 | 234 | 11:00
Hathazari | 239 | 22:00 | 229 | 10:00
Ishurdi | 246 | 13:00 | 240 | 07:00
Jhenaidah | 243 | 05:00 | 237 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 05:00 | 128 | 11:00 | Lalbag | 136 | 23:00 | 129 | 11:00
Agargaon | 139 | 04:00 | 133 | 11:00 | Lalmonirhat | 135 | 00:00 | 127 | 10:00
Agrabad | 139 | 22:00 | 133 | 11:00 | Madanganj | 138 | 18:30 | 134 | 12:00
AKS | 135 | 18:30 | 131 | 11:00 | Madaripur | 141 | 00:00 | 138 | 10:00
Aminbazar | 141 | 00:00 | 135 | 12:00 | Madartek | 137 | 02:00 | 128 | 11:00
Amnura | 140 | 23:00 | 135 | 11:00 | Madunaghat | 139 | 00:00 | 134 | 11:00
Ashuganj | 140 | 18:00 | 137 | 10:00 | Magura | 139 | 04:00 | 134 | 08:00
Bagerhat | 138 | 18:30 | 129 | 08:00 | Mahasthangarh | 138 | 00:00 | 132 | 11:00
Bajitpur | 137 | 22:00 | 132 | 07:00 | Manikganj | 130 | 00:00 | 125 | 11:00
Bakerganj | 141 | 18:00 | 138 | 05:00 | Maniknagar | 139 | 04:00 | 134 | 11:00
Bakulia | 139 | 22:00 | 134 | 11:00 | Matarbari | 133 | 12:00 | 124 | 13:00
Banani | 135 | 04:00 | 128 | 11:00 | Matuail | 139 | 04:00 | 134 | 11:00
Bangabhaban | 141 | 04:00 | 133 | 11:00 | Metrorail_Motijheel | 139 | 04:00 | 134 | 11:00
Barapukuria | 139 | 19:00 | 130 | 10:00 | Metrorail_Uttara | 139 | 00:00 | 134 | 11:00
Barguna | 141 | 19:00 | 138 | 11:00 | Millgate | 134 | 00:00 | 127 | 11:00
Barishal | 141 | 19:00 | 137 | 11:00 | Mirpur | 140 | 00:00 | 134 | 11:00
Barishal-230 | 140 | 03:00 | 137 | 11:00 | Mirzapur | 136 | 13:00 | 130 | 07:00
Baroaulia | 139 | 22:00 | 133 | 11:00 | Mithapukur | 139 | 00:00 | 131 | 10:00
Baroirhat | 136 | 18:00 | 132 | 11:00 | MI_Cement | 137 | 01:00 | 129 | 11:00
Bashundhara | 135 | 03:00 | 128 | 11:00 | Modern | N/A | N/A | N/A | N/A
BashundharaCement | 138 | 18:30 | 134 | 12:00 | Mogbazar | 136 | 04:00 | 130 | 11:00
Beanibazar | 134 | 02:00 | 129 | 16:00 | Mongla | 136 | 13:00 | 131 | 06:00
Benapole | 137 | 04:00 | 128 | 08:00 | Motijheel | 141 | 04:00 | 133 | 11:00
Bhaluka | 137 | 22:00 | 128 | 11:00 | Muktagacha | 133 | 13:00 | 124 | 17:00
Bhandaria | 140 | 19:00 | 136 | 12:00 | Munshiganj | 138 | 18:00 | 133 | 10:00
Bhangura | 141 | 03:00 | 135 | 10:00 | Muradnagar | 140 | 22:00 | 133 | 11:00
Bheramara | 141 | 03:00 | 137 | 10:00 | Mymensingh | 134 | 13:00 | 123 | 06:00
Bheramara(GK) | 141 | 04:00 | 137 | 08:00 | Naogaon | 136 | 04:00 | 129 | 11:00
Bhulta | 134 | 00:00 | 130 | 10:00 | Narail | 139 | 04:00 | 134 | 08:00
Bog-Sherpur | 140 | 23:00 | 133 | 10:00 | Narinda | 139 | 4:00 | 134 | 11:00
Bogura | 140 | 18:00 | 134 | 10:00 | Narshingdi | 137 | 00:00 | 124 | 11:00
Bogura-230 | 140 | 18:00 | 134 | 11:00 | Natore | 139 | 18:00 | 134 | 08:00
Brahmanbaria | 132 | 18:00 | 127 | 11:00 | Nawabganj | 137 | 05:00 | 129 | 11:00
Cantonment | 138 | 00:00 | 133 | 11:00 | Netrakona | 131 | 21:00 | 119 | 08:00
Chandina | 141 | 20:00 | 136 | 11:00 | New | 135 | 22:00 | 128 | 11:00
Chandpur | 141 | 08:00 | 138 | 10:00 | Niamatpur | 140 | 01:00 | 135 | 10:00
Chandraghona | 140 | 22:00 | 132 | 05:00 | Noapara | 137 | 03:00 | 131 | 08:00
Chapai | 140 | 19:00 | 136 | 09:00 | Pabna | 141 | 23:00 | 135 | 10:00
Charsaidpur | 139 | 22:00 | 134 | 11:00 | Palashbari | 137 | 00:00 | 130 | 10:00
Chauddagram | 138 | 20:00 | 133 | 11:00 | Panchagarh | 139 | 07:00 | 126 | 11:00
Chhatak | 132 | 00:00 | 127 | 10:00 | Patiya | 139 | 23:00 | 133 | 11:00
Chowmuhani | 135 | 19:30 | 131 | 11:00 | Patuakhali | 138 | 19:00 | 136 | 01:00
Chuadanga | 139 | 04:00 | 132 | 09:00 | Payra | 140 | 04:00 | 138 | 08:00
Coxsbazar | 130 | 23:00 | 126 | 06:00 | PHP | 137 | 22:00 | 132 | 11:00
Cumilla(N) | 140 | 18:00 | 135 | 11:00 | Postogola | 137 | 00:00 | 131 | 11:00
Cumilla(S) | 141 | 22:00 | 122 | 13:00 | Purbachal | 135 | 05:00 | 128 | 11:00
Daganbhuiyan | 137 | 18:30 | 132 | 13:00 | Purbasadipur | 137 | 22:00 | 127 | 11:00
Daudkandi | 137 | 05:00 | 132 | 10:00 | Rahanpur | 140 | 00:00 | 137 | 10:00
DhakaUniversity | 134 | 00:00 | 129 | 11:00 | Rahanpur-400 | 141 | 03:00 | 137 | 10:00
Dhamrai | 139 | 00:00 | 134 | 06:00 | Rahim | 138 | 19:30 | 133 | 11:00
Dhanmondi | 140 | 04:00 | 134.5 | 11:00 | Rajbari | 138 | 03:00 | 135 | 10:00
Dohazari | 136 | 23:00 | 131 | 11:00 | Rajendrapur | 136 | 05:00 | 129 | 10:00
Faridpur | 138 | 03:00 | 135 | 08:00 | Rajshahi | 140 | 05:00 | 136 | 08:00
Fatullah | 140 | 21:00 | 129 | 11:00 | Rajshahi-230 | 139 | 18:00 | 136 | 07:00
Fenchuganj | 139 | 22:00 | 136 | 15:00 | Ramganj | 137 | 07:00 | 135 | 05:00
Feni | 135 | 18:00 | 132 | 10:00 | Rampur | 138 | 21:00 | 133 | 15:00
Feni-230 | 137 | 20:00 | 132 | 11:00 | Rampura | 134 | 00:00 | 128 | 11:00
Ghatail | 132 | 13:00 | 125 | 07:00 | Rangamati | 139 | 22:00 | 134 | 11:00
Ghorashal | 134 | 22:00 | 129 | 11:00 | Rangpur | 139 | 01:00 | 129 | 11:00
Goalpara | 139 | 04:00 | 132 | 08:00 | Ruppur | 142 | 04:00 | 135 | 10:00
Gollamari | 138 | 04:00 | 132 | 08:00 | Saidpur | 138 | 07:00 | 127 | 10:00
Gopalganj | 140 | 03:00 | 136 | 07:00 | Satkhira | 136 | 04:00 | 128 | 08:00
Gopalganj-400 | 145 | 21:00 | 139 | 11:00 | Satmasjid | 138 | 00:00 | 133 | 11:00
Gulshan | 133 | 00:00 | 128 | 11:00 | Savar | 140 | 18:00 | 134 | 10:00
Halishahar | 140 | 22:00 | 134 | 11:00 | SevenRings | 135 | 22:00 | 128 | 11:00
Haripur | 139 | 22:00 | 134 | 11:00 | ShahCement | 139 | 22:00 | 134 | 11:00
HaripurSBU | 139 | 22:00 | 134 | 11:00 | Shahjadpur | 145 | 03:00 | 137 | 11:00
Hasnabad | 138 | 02:00 | 131 | 10:00 | Shahjibazar | 133 | 04:00 | 128 | 11:00
Hathazari | 140 | 19:00 | 134 | 11:00 | Shahmirpur | 140 | 23:00 | 134 | 11:00
Hatirjheel | 135 | 04:00 | 128 | 11:00 | Shariatpur | 141 | 03:00 | 138 | 11:00
Ishurdi | 143 | 03:00 | 136 | 17:00 | Sherpur | 131 | 13:00 | 118 | 05:00
Jaldhaka | 135 | 00:00 | 126 | 10:00 | Shikalbaha | 129 | 22:00 | 123 | 10:00
Jamalpur | 133 | 13:00 | 121 | 05:00 | Shikalbaha-230 | 141 | 22:00 | 135 | 16:00
Jashore | 136 | 03:00 | 130 | 08:00 | Shitalakhya | 137 | 01:00 | 129 | 11:00
Jhenaidah | 140 | 03:00 | 129 | 08:00 | Sholosohor | 139 | 19:30 | 134 | 11:00
Jhenaidah-230 | 141 | 04:00 | 132 | 08:00 | Shyampur | 138 | 00:00 | 130 | 15:00
Joydebpur | 133 | 21:00 | 126 | 10:00 | Shyampur-230 | 140 | 04:00 | 135 | 11:00
Joypurhat | 135 | 19:00 | 129 | 10:00 | Siddhirganj | 139 | 03:00 | 134 | 11:00
Juldah | 139 | 22:00 | 134 | 11:00 | Sirajganj | 139 | 04:00 | 132 | 10:00
Kabirpur | 141 | 13:00 | 126 | 10:00 | Sonargaon | 137 | 20:00 | 132 | 12:00
Kachua | 140 | 18:30 | 136 | 11:00 | Sreemongol | 134 | 08:00 | 130 | 11:00
Kaliakoir | 142 | 22:00 | 137 | 02:00 | Sreepur | 138 | 22:00 | 132 | 11:00
Kallyanpur | 140 | 00:00 | 135 | 10:00 | Srinagar | 136 | 00:00 | 129 | 11:00
Kalurghat | 139 | 18:30 | 134 | 11:00 | SSM | 140 | 00:00 | 140 | 00:00
Kamrangirchar | 136 | 00:00 | 128 | 11:00 | Sunamganj | 130 | 02:00 | 126 | 19:30
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 134 | 03:00 | 130 | 16:00
Kasba | 139 | 20:00 | 132 | 11:00 | Sylhet-132 | 133 | 00:00 | 129 | 12:00
Kazla | 140 | 05:00 | 133 | 12:00 | Tangail | 133 | 12:00 | 126 | 07:00
Keranigonj | 137 | 04:00 | 130 | 11:00 | Taraganj | 138 | 01:00 | 126 | 11:00
Khagrachori | 138 | 19:00 | 134 | 11:00 | Tasnim | 137 | 04:00 | 132 | 12:00
Khulna | 137 | 18:00 | 132 | 09:00 | Thakurgaon | 141 | 07:00 | 127 | 10:00
Khulna(S) | 138 | 04:00 | 133 | 08:00 | TK | 140 | 03:00 | 135 | 11:00
Khulshi | 138 | 23:00 | 128 | 04:00 | Tongi | 136 | 00:00 | 130 | 11:00
Kishoreganj | 136 | 18:00 | 131 | 11:00 | Ullahpara | 140 | 00:00 | 133 | 11:00
Kodda | 139 | 13:00 | 129 | 06:00 | Ullon | 135 | 04:00 | 128 | 11:00
KSRM | 139 | 23:00 | 133 | 11:00 | Uttara | 134 | 00:00 | 127 | 11:00
Kulaura | 138 | 04:00 | 135 | 16:00 | UttaraNew | 139 | 00:00 | 134 | 11:00
Kurigram | 135 | 00:00 | 126 | 11:00 | Zigatola | 137 | 05:00 | 129 | 11:00
Kushtia | 139 | 02:00 | 135 | 08:00
Laksam | 140 | 19:30 | 136 | 11:00
Lakshmipur | 136 | 18:00 | 132 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division