## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 23-01-2026 | [28 empty] | Date: | 23-01-2026 | [28 empty] | Date: | 23-01-2026 | [28 empty] | Date: | 23-01-2026 | [28 empty] | Date: | 23-01-2026 | [17 empty] | Date: | 23-01-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [17 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 85 | 0 | 95 | 0 | 17 | 35 | 0 | 0 | 0 | 385 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 14 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 86 | 28 | 29 | 415 | 0 | 0 | 0 | 0 | 65 | 186 | 0 | 0 | 0 | 1170 | 0 | 85 | 0 | 215 | 280 | 0 | 51 | 0 | 194 | 0 | 16 | 104 | 51 | 0 | 13 | 0 | 110 | 0 | 0 | 0 | 325 | 0 | 0 | 42 | 52 | 146 | 0 | 21 | 0 | 80 | 30 | 0 | 0 | 100 | 17 | 57 | 19 | 32 | 0 | 0 | 12 | 5419 | 473 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1071 | 0 | 0 | 0 | 763.69 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 55 | 50 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286 | 130 | 220 | 0 | 0 | 575 | 0 | 4194.69 | 9613.69 | 95.97
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 13 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 29 | 415 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 1161 | 0 | 0 | 0 | 230 | 280 | 0 | 51 | 0 | 197 | 0 | 0 | 105 | 0 | 0 | 13 | 0 | 100 | 0 | 0 | 0 | 320 | 0 | 0 | 42 | 52 | 144 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 17 | 0 | 0 | 32 | 0 | 0 | 0 | 4810 | 474 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1082 | 0 | 0 | 0 | 768.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 130 | 220 | 0 | 0 | 622 | 0 | 4119.38 | 8929.38 | 95.96
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 29 | 415 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 1106 | 0 | 0 | 0 | 230 | 280 | 0 | 51 | 0 | 194 | 0 | 0 | 104 | 0 | 0 | 13 | 0 | 92 | 0 | 0 | 0 | 325 | 0 | 0 | 42 | 52 | 143 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 4707 | 474 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1062 | 0 | 0 | 0 | 725.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 130 | 220 | 0 | 0 | 570 | 0 | 3955.03 | 8662.03 | 95.96
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 31 | 415 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 1105 | 0 | 0 | 0 | 230 | 280 | 0 | 51 | 0 | 189 | 0 | 0 | 105 | 0 | 0 | 13 | 0 | 96 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 52 | 143 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 4689 | 474 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 887 | 0 | 0 | 0 | 669.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 130 | 220 | 0 | 0 | 520 | 0 | 3665.91 | 8354.91 | 95.96
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 31 | 415 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1050 | 0 | 0 | 0 | 225 | 280 | 0 | 51 | 0 | 188 | 0 | 0 | 107 | 0 | 0 | 13 | 0 | 92 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 52 | 142 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 4622 | 473 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 799 | 0 | 0 | 0 | 641.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 130 | 220 | 0 | 0 | 480 | 0 | 3473.27 | 8095.27 | 95.95
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 29 | 415 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 1021 | 0 | 0 | 0 | 225 | 280 | 0 | 51 | 0 | 193 | 0 | 0 | 108 | 0 | 0 | 13 | 0 | 92 | 0 | 0 | 0 | 320 | 0 | 0 | 42 | 52 | 146 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 4621 | 473 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 788 | 0 | 0 | 0 | 527.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 130 | 220 | 0 | 0 | 450 | 0 | 3321.68 | 7942.68 | 95.95
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 39 | 415 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 1138 | 0 | 0 | 0 | 230 | 280 | 0 | 51 | 0 | 191 | 0 | 0 | 108 | 0 | 0 | 13 | 0 | 100 | 0 | 0 | 0 | 320 | 0 | 0 | 42 | 52 | 147 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 4753 | 474 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 883 | 0 | 0 | 0 | 527.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264 | 130 | 220 | 0 | 0 | 415 | 0 | 3465.15 | 8218.15 | 95.95
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0.08 | 86 | 0 | 41 | 415 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 1200 | 1 | 0 | 0 | 230 | 280 | 0 | 51 | 0 | 188 | 0 | 0 | 108 | 0 | 0 | 13 | 0 | 94 | 0 | 2 | 0 | 325 | 0 | 0 | 42 | 52 | 144 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 34 | 0 | 0.69 | 0 | 4787.77 | 473 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1002 | 0 | 0 | 0 | 685.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 | 0.6 | 135 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0.07 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.01 | 0 | 286 | 130 | 220 | 0 | 0 | 410 | 0 | 3767.34 | 8555.11 | 95.94
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 14.9 | 0 | 12 | 0 | 80 | 0 | 3 | 48 | 0 | 0 | 0 | 375 | 0 | 0 | 335 | 0 | 0 | 6 | 0 | 13 | 21 | 0 | 0 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 0 | 12 | 25 | 0.59 | 86 | 0 | 42 | 415 | 0 | 0 | 0 | 0 | 16 | 185 | 0 | 0 | 0 | 1168 | 6 | 24 | 0 | 220 | 280 | 0 | 51 | 0 | 185 | 0 | 0 | 109 | 14 | 0 | 13 | 0 | 96 | 0 | 17 | 0 | 320 | 0 | 0 | 42 | 52 | 156 | 1 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 35 | 19 | 34 | 0 | 8.02 | 0 | 5134.51 | 473 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 1106 | 0 | 0 | 0 | 764.17 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8.6 | 0 | 0 | 0 | 9.05 | 135 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0.9 | 0 | 55 | 35 | 4 | 34 | 0 | 0 | 0 | 0.8 | 18 | 0.1 | 0 | 280 | 130 | 220 | 0 | 0 | 428 | 2 | 4087.62 | 9222.13 | 95.94
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 15.7 | 0 | 33 | 0 | 30 | 0 | 17 | 17 | 0 | 0 | 0 | 373 | 0 | 0 | 335 | 0 | 0 | 14 | 0 | 13.5 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 1.9 | 86 | 0 | 42 | 415 | 0 | 0 | 0 | 0 | 17 | 168 | 0 | 0 | 0 | 1161 | 13 | 20 | 0 | 220 | 280 | 0 | 51 | 0 | 180 | 0 | 16 | 106 | 17 | 0 | 13 | 0 | 96 | 0 | 37 | 0 | 315 | 0 | 0 | 42 | 52 | 159 | 5 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 35 | 19 | 32 | 1 | 20.38 | 0 | 5059.48 | 474 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 1106 | 0 | 0 | 0 | 767.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.87 | 0 | 0 | 0 | 25.31 | 136 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 2.27 | 0 | 55 | 35 | 11 | 34 | 0 | 0 | 0 | 2.2 | 58 | 0.25 | 0 | 279 | 130 | 220 | 0 | 0 | 479 | 0 | 4243.68 | 9303.16 | 95.94
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 34 | 0 | 30 | 0 | 17 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 335 | 0 | 0 | 21 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.72 | 86 | 0 | 36 | 355 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 1140 | 17 | 10 | 0 | 220 | 280 | 0 | 51 | 0 | 182 | 0 | 0 | 104 | 0 | 0 | 13 | 0 | 96 | 0 | 52 | 0 | 305 | 0 | 0 | 42 | 52 | 155 | 9 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 35 | 19 | 33 | 1 | 31.26 | 0 | 4883.98 | 473 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 1095 | 0 | 0 | 0 | 753.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.81 | 0 | 0 | 0 | 40.38 | 136 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 3.55 | 0 | 55 | 35 | 19 | 34 | 0 | 0 | 0 | 3.7 | 99 | 0.38 | 0 | 273 | 130 | 220 | 0 | 0 | 534 | 0 | 4363.85 | 9247.83 | 95.93
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 34 | 0 | 30 | 0 | 17 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 335 | 0 | 0 | 26 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 35 | 300 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1192 | 18 | 13 | 0 | 220 | 280 | 0 | 51 | 0 | 189 | 0 | 0 | 102 | 0 | 6 | 13 | 0 | 110 | 0 | 61 | 0 | 315 | 0 | 0 | 0 | 0 | 161 | 11 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 35 | 19 | 33 | 2 | 38.16 | 0 | 4879.16 | 473 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 1116 | 0 | 0 | 0 | 769.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.12 | 0 | 0 | 0 | 51.49 | 136 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 4.36 | 0 | 55 | 35 | 24 | 34 | 0 | 0 | 0 | 4.7 | 124 | 0.46 | 0 | 294 | 130 | 220 | 0 | 0 | 580 | 0 | 4530.54 | 9409.7 | 95.93
12:00 | 0 | 17 | 2 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 11 | 0 | 43 | 32 | 105 | 13 | 17 | 65 | 0 | 0 | 0 | 380 | 0 | 30 | 335 | 0 | 0 | 27 | 34 | 19 | 22 | 0 | 0 | 18 | 30 | 0 | 0 | 0 | 0 | 4 | 9 | 36 | 25 | 3.46 | 86 | 13 | 35 | 210 | 68 | 0 | 14 | 0 | 22 | 175 | 0 | 0 | 0 | 1160 | 19 | 70 | 0 | 220 | 280 | 0 | 51 | 0 | 186 | 0 | 12 | 100 | 22 | 9 | 13 | 33 | 124 | 7 | 63 | 2 | 315 | 0 | 0 | 0 | 0 | 161 | 11 | 21 | 0 | 80 | 30 | 0 | 0 | 100 | 5 | 35 | 19 | 31 | 2 | 39.72 | 1 | 5467.18 | 473 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 1112 | 0 | 0 | 0 | 760.61 | 0 | 0 | 0 | 35 | 15 | 0 | 0 | 0 | 0 | 46.03 | 86 | 0 | 0 | 52.56 | 136 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 4.88 | 0 | 55 | 35 | 26 | 34 | 0 | 0 | 0 | 5.2 | 139 | 0.49 | 10 | 279 | 130 | 220 | 0 | 0 | 598 | 7 | 4700.77 | 10167.95 | 95.93
13:00 | 0 | 34 | 14 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 29 | 0 | 50 | 32 | 145 | 30 | 22 | 71 | 0 | 0 | 0 | 465 | 0 | 35 | 335 | 0 | 0 | 28 | 52 | 15 | 14 | 0 | 0 | 50 | 80 | 0 | 0 | 0 | 0 | 8 | 25 | 36 | 25 | 3.25 | 86 | 48 | 41 | 175 | 62 | 0 | 25 | 0 | 50 | 175 | 0 | 0 | 0 | 1162 | 17 | 70 | 0 | 220 | 280 | 0 | 51 | 0 | 185 | 0 | 16 | 100 | 34 | 15 | 13 | 33 | 136 | 16 | 64 | 14 | 325 | 0 | 0 | 0 | 0 | 161 | 11 | 21 | 0 | 80 | 30 | 0 | 0 | 100 | 17 | 35 | 19 | 31 | 2 | 36.86 | 11 | 5909.11 | 474 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 1128 | 0 | 0 | 0 | 758.52 | 0 | 0 | 0 | 50 | 45 | 0 | 0 | 0 | 0 | 45.92 | 81 | 0 | 0 | 51.94 | 136 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 4.36 | 0 | 55 | 35 | 25 | 34 | 0 | 0 | 0 | 5 | 132 | 0.49 | 43 | 307 | 130 | 220 | 0 | 0 | 600 | 24 | 4823.23 | 10732.34 | 95.92
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 19.3 | 0 | 45 | 0 | 30 | 0 | 17 | 17 | 0 | 0 | 0 | 435 | 0 | 17 | 335 | 0 | 0 | 26 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 2.7 | 86 | 0 | 38 | 155 | 0 | 0 | 0 | 0 | 17 | 165 | 0 | 0 | 0 | 1150 | 15 | 12 | 0 | 220 | 280 | 0 | 51 | 0 | 185 | 0 | 0 | 100 | 17 | 0 | 13 | 0 | 114 | 0 | 50 | 0 | 315 | 0 | 0 | 0 | 0 | 159 | 9 | 21 | 0 | 80 | 30 | 0 | 0 | 97 | 0 | 35 | 19 | 31 | 2 | 30.63 | 0 | 4820.63 | 474 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 1108 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.99 | 72 | 0 | 0 | 45.02 | 142 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 3.87 | 0 | 55 | 35 | 21 | 0 | 0 | 0 | 0 | 4.3 | 108 | 0.41 | 0 | 276 | 130 | 220 | 0 | 0 | 622 | 0 | 4548.59 | 9369.22 | 95.92
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 331 | 0 | 0 | 18 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.04 | 86 | 0 | 36 | 155 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 1017 | 11 | 0 | 0 | 220 | 280 | 0 | 51 | 0 | 188 | 0 | 0 | 100 | 0 | 0 | 13 | 0 | 102 | 0 | 36 | 0 | 310 | 0 | 0 | 0 | 0 | 152 | 7 | 20 | 0 | 80 | 30 | 0 | 0 | 97 | 0 | 25 | 19 | 31 | 1 | 21.42 | 0 | 4376.46 | 474 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 1038 | 0 | 0 | 0 | 757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.04 | 49 | 0 | 0 | 31.69 | 150 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 2.9 | 0 | 55 | 0 | 15 | 0 | 0 | 0 | 0 | 3 | 76 | 0.32 | 0 | 232 | 130 | 220 | 0 | 0 | 560 | 0 | 4236.95 | 8613.41 | 95.92
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 6 | 0 | 17 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 405 | 0 | 0 | 270 | 0 | 0 | 10 | 0 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 22 | 1.06 | 86 | 0 | 36 | 155 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 1030 | 7 | 0 | 0 | 220 | 280 | 0 | 51 | 0 | 192 | 0 | 0 | 100 | 3 | 0 | 13 | 0 | 96 | 0 | 17 | 0 | 320 | 0 | 0 | 0 | 0 | 144 | 3 | 20 | 0 | 80 | 30 | 0 | 0 | 97 | 0 | 25 | 19 | 33 | 1 | 11.15 | 0 | 4376.21 | 473 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 928 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.49 | 26 | 0 | 0 | 13.35 | 156 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 1.23 | 0 | 55 | 0 | 9 | 0 | 0 | 0 | 0 | 1.6 | 39 | 0 | 0 | 180 | 130 | 180 | 0 | 0 | 500 | 0 | 3874.67 | 8250.88 | 95.91
17:00 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 15.8 | 1 | 24 | 0 | 60 | 4 | 11 | 31 | 0 | 0 | 0 | 395 | 0 | 25 | 250 | 0 | 0 | 2 | 52 | 12 | 14 | 0 | 0 | 12 | 15 | 0 | 0 | 6 | 10 | 8 | 0 | 12 | 25 | 0.16 | 86 | 7 | 36 | 155 | 16 | 0 | 1 | 0 | 20 | 186 | 0 | 0 | 0 | 1028 | 1 | 13 | 0 | 220 | 280 | 0 | 51 | 0 | 192 | 0 | 4 | 102 | 25 | 0 | 13 | 0 | 88 | 0 | 3 | 0 | 315 | 0 | 0 | 0 | 0 | 141 | 1 | 20 | 0 | 80 | 30 | 0 | 0 | 97 | 0 | 38 | 19 | 48 | 0 | 2.37 | 2 | 4639.33 | 473 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 905 | 0 | 0 | 0 | 754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.57 | 6 | 0 | 0 | 2.96 | 164 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0.27 | 0 | 55 | 0 | 3 | 34 | 0 | 0 | 0 | 0.5 | 7 | 0 | 1 | 181 | 100 | 180 | 0 | 0 | 500 | 15 | 3789.3 | 8428.63 | 95.91
18:00 | 0 | 34 | 2 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 27.6 | 17 | 50 | 48 | 145 | 19 | 35 | 82 | 0 | 0 | 0 | 310 | 0 | 35 | 250 | 0 | 0 | 0 | 52 | 0 | 7 | 0 | 0 | 31 | 30 | 18 | 0 | 7 | 32 | 8 | 14 | 50 | 25 | 0 | 86 | 34 | 38 | 155 | 53 | 0 | 20 | 4 | 32 | 186 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 220 | 280 | 0 | 0 | 0 | 197 | 0 | 15 | 103 | 50 | 0 | 19 | 29 | 100 | 11 | 0 | 16 | 325 | 0 | 0 | 0 | 0 | 143 | 0 | 20 | 0 | 80 | 30 | 0 | 0 | 97 | 5 | 57 | 19 | 49 | 0 | 0 | 12 | 5333.6 | 474 | 120 | 0 | 30 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 907 | 0 | 0 | 0 | 759 | 0 | 0 | 0 | 35 | 20 | 0 | 0 | 12 | 8 | 0 | 0 | 7 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 55 | 45 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 209 | 130 | 220 | 0 | 0 | 515 | 54 | 4171 | 9504.6 | 95.91
19:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 33.3 | 17 | 78 | 16 | 145 | 30 | 35 | 86 | 0 | 0 | 0 | 405 | 0 | 35 | 280 | 0 | 0 | 0 | 52 | 12 | 22 | 0 | 0 | 30 | 30 | 30 | 0 | 5 | 32 | 8 | 17 | 50 | 25 | 0 | 86 | 33 | 40 | 155 | 78 | 0 | 26 | 8 | 51 | 186 | 0 | 0 | 0 | 1163 | 0 | 0 | 0 | 220 | 280 | 0 | 0 | 0 | 188 | 0 | 16 | 104 | 51 | 0 | 13 | 15 | 100 | 25 | 0 | 16 | 315 | 0 | 0 | 0 | 0 | 157 | 0 | 21 | 0 | 80 | 30 | 0 | 0 | 97 | 17 | 57 | 19 | 49 | 0 | 0 | 12 | 5566.3 | 473 | 145 | 0 | 30 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1101 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 50 | 32 | 0 | 0 | 23 | 25 | 0 | 0 | 8 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 55 | 50 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 278 | 130 | 220 | 0 | 0 | 555 | 48 | 4598 | 10164.3 | 95.9
19:30 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 33.3 | 17 | 78 | 16 | 95 | 30 | 35 | 53 | 0 | 0 | 0 | 430 | 0 | 35 | 300 | 0 | 0 | 0 | 35 | 12 | 22 | 0 | 0 | 32 | 30 | 0 | 0 | 2 | 32 | 8 | 17 | 50 | 25 | 0 | 86 | 34 | 38 | 155 | 17 | 0 | 26 | 8 | 65 | 185 | 0 | 0 | 0 | 1170 | 0 | 0 | 0 | 220 | 280 | 0 | 0 | 0 | 188 | 0 | 16 | 104 | 51 | 0 | 13 | 17 | 102 | 8 | 0 | 16 | 320 | 0 | 0 | 0 | 0 | 161 | 0 | 21 | 0 | 80 | 30 | 0 | 0 | 97 | 17 | 57 | 18 | 49 | 0 | 0 | 12 | 5446.3 | 473 | 147 | 0 | 15 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1130 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 23 | 8 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 56 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 297 | 130 | 220 | 0 | 0 | 560 | 54 | 4628 | 10074.3
20:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 33.3 | 17 | 78 | 16 | 95 | 30 | 35 | 52 | 0 | 0 | 0 | 425 | 0 | 35 | 300 | 0 | 0 | 0 | 35 | 12 | 22 | 0 | 0 | 32 | 30 | 0 | 0 | 3 | 32 | 8 | 17 | 50 | 25 | 0 | 86 | 34 | 42 | 155 | 16 | 0 | 26 | 8 | 66 | 185 | 0 | 0 | 0 | 1170 | 0 | 0 | 0 | 220 | 280 | 0 | 0 | 0 | 195 | 0 | 15 | 105 | 51 | 0 | 13 | 16 | 100 | 8 | 0 | 16 | 325 | 0 | 0 | 0 | 0 | 162 | 0 | 21 | 0 | 80 | 30 | 0 | 0 | 97 | 17 | 57 | 18 | 50 | 0 | 0 | 12 | 5446.3 | 473 | 152 | 0 | 15 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1141 | 0 | 0 | 0 | 759 | 0 | 0 | 0 | 35 | 48 | 0 | 0 | 24 | 8 | 0 | 0 | 8 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 56 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 307 | 130 | 220 | 0 | 0 | 560 | 53 | 4653 | 10099.3 | 95.9
21:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 17 | 78 | 16 | 95 | 30 | 0 | 51 | 0 | 0 | 0 | 425 | 0 | 35 | 300 | 0 | 0 | 0 | 35 | 12 | 22 | 0 | 0 | 33 | 30 | 0 | 0 | 0 | 32 | 8 | 17 | 50 | 25 | 0 | 86 | 34 | 42 | 155 | 17 | 0 | 26 | 8 | 67 | 185 | 0 | 0 | 0 | 1170 | 0 | 0 | 0 | 220 | 280 | 0 | 0 | 0 | 216 | 0 | 16 | 105 | 51 | 0 | 13 | 15 | 104 | 8 | 0 | 16 | 320 | 0 | 0 | 0 | 0 | 163 | 0 | 21 | 0 | 80 | 30 | 0 | 0 | 97 | 17 | 57 | 18 | 50 | 0 | 0 | 12 | 5400 | 474 | 178 | 0 | 15 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1133 | 0 | 0 | 0 | 763.55 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 56 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 130 | 220 | 0 | 0 | 560 | 51 | 4669.55 | 10069.55 | 95.9
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 17 | 78 | 0 | 95 | 0 | 0 | 52 | 0 | 0 | 0 | 410 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 12 | 22 | 0 | 0 | 32 | 30 | 0 | 0 | 0 | 32 | 8 | 0 | 50 | 25 | 0 | 86 | 34 | 42 | 155 | 0 | 0 | 26 | 0 | 66 | 185 | 0 | 0 | 0 | 1170 | 0 | 0 | 0 | 230 | 280 | 0 | 0 | 0 | 222 | 0 | 15 | 105 | 50 | 0 | 13 | 0 | 104 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 160 | 0 | 21 | 0 | 80 | 30 | 0 | 0 | 97 | 0 | 57 | 18 | 50 | 0 | 0 | 12 | 5154 | 474 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1130 | 0 | 0 | 0 | 766.39 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 56 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 560 | 53 | 4561.39 | 9715.39 | 95.89
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 78 | 0 | 45 | 0 | 0 | 50 | 0 | 0 | 0 | 400 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 86 | 30 | 42 | 155 | 0 | 0 | 0 | 0 | 65 | 185 | 0 | 0 | 0 | 1171 | 0 | 0 | 0 | 240 | 280 | 0 | 0 | 0 | 222 | 0 | 0 | 106 | 49 | 0 | 13 | 0 | 102 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 157 | 0 | 21 | 0 | 80 | 30 | 0 | 0 | 98 | 0 | 57 | 18 | 50 | 0 | 0 | 12 | 4860 | 473 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1124 | 0 | 0 | 0 | 758.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 56 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 560 | 17 | 4478.11 | 9338.11 | 95.89
Total KWH | 0 | 171840 | 84960 | 0 | 0 | 0 | 0 | 0 | 8290800 | 0 | 0 | 259200 | 100440 | 825408 | 156960 | 1165222 | 194416 | 266437 | 692640 | 0 | 0 | 0 | 9339334 | 0 | 270842 | 7647922 | 0 | 0 | 176506 | 364800 | 332400 | 426240 | 0 | 0 | 277255 | 336218 | 48960 | 0 | 204960 | 160125 | 56976 | 144331 | 384960 | 294720 | 19922 | 2069600 | 339600 | 927840 | 6603636.36 | 259273 | 0 | 194880 | 33784.2 | 618909 | 4269302 | 0 | 0 | 0 | 27267270 | 126360 | 362981 | 0 | 5434500 | 7088400 | 0 | 917331 | 0 | 4783000 | 0 | 182400 | 2479492 | 592800 | 41160 | 343260 | 148200 | 2395200 | 90418 | 408982 | 79552 | 7737000 | 0 | 0 | 413000 | 523000 | 3669545 | 68570 | 452976 | 0 | 1885440 | 718944 | 0 | 0 | 2359220 | 132120 | 775200 | 316800 | 862080 | 11050 | 240910 | 109440 | 121028219.56 | 11456000 | 2336832 | 0 | 77280 | 139520 | 0 | 0 | 0 | 0 | 0 | 0 | 506160 | 24850900 | 0 | 0 | 0 | 17098546 | 0 | 0 | 0 | 324384 | 391488 | 0 | 0 | 72542 | 47309 | 287172 | 357200 | 20295 | 0 | 326256 | 3692545 | 0 | 0 | 0 | 0 | 0 | 7684509 | 0 | 28680 | 0 | 1284655 | 576182 | 156708 | 615945 | 0 | 0 | 0 | 31199.52 | 802080 | 3109 | 259392 | 6262000 | 3094000 | 5514330 | 0 | 0 | 13249454.55 | 328800 | 101875473.07 | 222903692.63

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 24-01-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-01-2026 | during | 24-01-2026 | during | 24-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 345 | 335 | 412 | 412 | 392 | 392 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 13 | 30 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 280 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 11 | 33.3 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 32 | 16 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 30 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19 | 12 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 15.1 | 15.1 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 2 | 16 | 52.19 | 52.19 | 52.19 | 52.19 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 105 | 145 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 43 | 78 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 34 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 65 | 86 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 27 | 0 | 27 | 0 | 27 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 380 | 405 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 34 | 52 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1497 | 1631.3 | 5356.35 | 5329.35 | 2644.32 | 2617.32
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 14 | 26 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 86 | 46 | 46 | 46 | 46 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 175 | 186 | 150 | 150 | 150 | 150 | Plant availability less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 22 | 51 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 4 | 8 | 8 | 8 | 16 | 16 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 32 | 34 | 34 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 36 | 50 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 35 | 40 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 30 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.46 | 0 | 3.27 | 0 | 3.27 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 30 | 30 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 9 | 17 | 54.36 | 54.36 | 17 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 13 | 33 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 51 | 51 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 18 | 30 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 68 | 78 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1163 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 5 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 210 | 155 | 415 | 415 | 355 | 355 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1927.46 | 2053 | 3136.13 | 3128.86 | 2729.77 | 2759.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 186 | 188 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 280 | 280 | 353.35 | 353.35 | 353.35 | 353.35 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 220 | 220 | 393 | 393 | 250 | 250 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 10 | 10 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 0 | 51 | 51 | 51 | 51 | Gas shortage
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 70 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 2 | 16 | 42 | 42 | 42 | 42 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 104 | 163 | 163 | 115 | 115 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 22 | 51 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 124 | 100 | 84 | 80 | 144 | 144 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 7 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 13 | 24.5 | 24.5 | 24.5 | 24.5 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 33 | 15 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 12 | 16 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 63 | 0 | 62 | 0 | 62 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1192 | 1028 | 2434.75 | 2368.75 | 1877.05 | 1815.05
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-01-2026 | during | 24-01-2026 | during | 24-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 31 | 49 | 157.5 | 157.5 | 50 | 50 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 19 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 35 | 57 | 60 | 60 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 39.72 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 1 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 5 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 132.72 | 154 | 358.1 | 314 | 240.6 | 196.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 42 | 42 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 60 | 60 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 161 | 157 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 80 | 80 | 80 | 83 | 83 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 97 | 100 | 100 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 21 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 718 | 700 | 799 | 799 | 734 | 734
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 473 | 473 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 30 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 32 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 62 | 145 | 410 | 410 | 369 | 369 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 79 | 0 | 0 | 0 | 0 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1112 | 1101 | 0 | 0 | 1148 | 1148 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1726 | 1781 | 2272 | 2272 | 2624.1 | 2624.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 10 | 45 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 130 | 130 | 130 | 130 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 598 | 555 | 622 | 622 | 622 | 622 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 7 | 48 | 150 | 150 | 150 | 150 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 279 | 278 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.49 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1244.49 | 1276 | 1540 | 1539 | 1526 | 1525
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 46.03 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 23 | 0 | 0 | 32 | 32 | Shutdown for Pond Cleaning.
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 136 | 177 | 214 | 214 | 192.6 | 192.6 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 300 | 300 | 413.79 | 413.79 | 0 | 0 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 8 | 22 | 22 | 28 | 28 | machine problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 15 | 32 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 50 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.88 | 0 | 4.6 | 0 | 4.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 760.61 | 758 | 748 | 748 | 748 | 748 | U#1 Under AOH
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 52.56 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 86 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1436.08 | 1373 | 2342.59 | 2187.99 | 1480.4 | 1325.8
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 55 | 55 | 56 | 56 | 58 | 58 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 63 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.2 | 0 | 4.8 | 0 | 4.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 26 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 139 | 0 | 136.03 | 0 | 136.03 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 294.2 | 168 | 486.83 | 318 | 454.83 | 286
System Total |  |  |  |  | 28823.2 | 28382.248 | 10167.95 | 10164.3 | 18725.75 | 18256.95 | 14311.07 | 13883.27
Forecast Scenario (24-01-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8930 |  | 0 |  | 8930
|  |  |  | 1:00 | 8470 |  | 0 |  | 8470
|  |  |  | 2:00 | 7870 |  | 0 |  | 7870
|  |  |  | 3:00 | 7660 |  | 0 |  | 7660
|  |  |  | 4:00 | 7380 |  | 0 |  | 7380
|  |  |  | 5:00 | 7410 |  | 0 |  | 7410
|  |  |  | 6:00 | 7750 |  | 0 |  | 7750
|  |  |  | 7:00 | 8480 |  | 0 |  | 8480
|  |  |  | 8:00 | 9440 |  | 0 |  | 9440
|  |  |  | 9:00 | 9550 |  | 0 |  | 9550
|  |  |  | 10:00 | 8830 |  | 0 |  | 8830
|  |  |  | 11:00 | 9090 |  | 0 |  | 9090
|  |  |  | 12:00 | 9760 |  | 0 |  | 9760
|  |  |  | 13:00 | 10330 |  | 0 |  | 10330
|  |  |  | 14:00 | 9950 |  | 0 |  | 9950
|  |  |  | 15:00 | 9620 |  | 0 |  | 9620
|  |  |  | 16:00 | 9160 |  | 0 |  | 9160
|  |  |  | 17:00 | 9470 |  | 0 |  | 9470
|  |  |  | 18:00 | 10830 |  | 0 |  | 10830
|  |  |  | 18:30 | 11000 |  | 0 |  | 11000
|  |  |  | 19:00 | 11370 |  | 0 |  | 11370
|  |  |  | 19:30 | 11460 |  | 0 |  | 11460
|  |  |  | 20:00 | 11270 |  | 0 |  | 11270
|  |  |  | 21:00 | 11320 |  | 0 |  | 11320
|  |  |  | 22:00 | 10690 |  | 0 |  | 10690
|  |  |  | 23:00 | 10150 |  | 0 |  | 10150
Probable Maximum Temperature: |  |  | 27.00°C
Probable Maximum Demand at Day Peak: |  |  | 9760.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11460.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11460.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 224.78 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:42 hrs on 24-01-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 23-01-2026
Power Supply Scenario
| Day Peak Generation |  |  | 10167.95 | MW | 12:00 Hr. | Energy Generated |  |  | 222.9037 |  | MKWHr.
| Day Peak Demand |  |  | 10167.95 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.117 |  | MKWHr.
| Evening Peak Generation |  |  | 10164.3 | MW | 19:00 Hr. | Energy Demand |  |  | 223.0207 |  | MKWHr.
| Evening Peak Demand |  |  | 10164.3 | MW | 19:00 Hr. | Maximum Temperature |  |  | 27.4 |  | °C
| Minimum Generation of the Day |  |  | 7942.68 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 696.45 |  | MMCFD
| Maximum Generation of the Day |  |  | 10732.34 | MW | 13:00 Hr. | Production Cost per KWHr |  |  | 5.9634 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 26.0367 | 0 | 4.5532 | 0 | 0 | 0.17651 | 0 | 0 | 30.7664 | Gas | 93.2232 | Gas | 328796508.29
| Chattogram Zone |  |  | 5.1971 | 33.8709 | 3.15 | 0 | 2.0696 | 0.14628 | 0 | 0.20496 | 44.6389 | Coal | 79.5179 | Coal | 520624084.7198
| Cumilla Zone |  |  | 21.046 | 0 | 1.4975 | 0 | 0 | 0.40898 | 2.3952 | 0 | 25.3477 | HFO | 13.3874 | HFO | 232929982.184
| Mymensingh Zone |  |  | 0.86208 | 0 | 1.3336 | 0 | 0 | 0.25196 | 0 | 0 | 2.4476 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 17.7591 | 0 | 0 | 0 | 0 | 0.06857 | 0 | 0 | 17.8277 | Hydro | 2.0696 | Hydro | 206960
| Khulna Zone |  |  | 2.3368 | 24.8509 | 0.2168 | 0 | 0 | 0.50616 | 11.456 | 0 | 39.3667 | Solar | 3.5509 | Solar | 55572071.914
| Barishal Zone |  |  | 8.6083 | 19.5115 | 0.58819 | 0 | 0 | 0.003109 | 0 | 0 | 28.7111 | Import | 30.9497 | Import | 188117382.64
| Rajshahi Zone |  |  | 11.3771 | 0 | 0.85602 | 0 | 0 | 0.99931 | 17.0985 | 0 | 30.3309 | Wind | 0.20496 | Wind | 3014961.6
| Rangpur Zone |  |  | 0 | 1.2847 | 1.1921 | 0 | 0 | 0.98999 | 0 | 0 | 3.4668
| Total |  |  | 93.2232 | 79.5179 | 13.3874 | 0 | 2.0696 | 3.5509 | 30.9497 | 0.20496 | 222.9037
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 328796508.29 |  | Hydro | 206960
|  |  |  | Coal | 520624084.7198 |  | Solar | 55572071.914
|  |  |  | HFO | 232929982.184 |  | Import | 188117382.64
|  |  |  | HSD | 0 |  | Wind | 3014961.6
[5 empty] | Total: | 132,92,61,951 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 8363.64 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 11.456 | Peak Hr Flow | 473.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 29442164.09 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 17.0985 | Peak Hr Flow | 758.00 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1311 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.3952 | Peak Hr Flow | 100.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1754 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 30.9497 | Peak Hr Flow | 1331.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3372
|  |  |  | Chattogram |  | 0 |  | 1076
|  |  |  | Cumilla |  | 0 |  | 906
|  |  |  | Mymensingh |  | 0 |  | 923
|  |  |  | Sylhet |  | 0 |  | 386
|  |  |  | Khulna |  | 0 |  | 1171
|  |  |  | Barishal |  | 0 |  | 305
|  |  |  | Rajshahi |  | 0 |  | 988
|  |  |  | Rangpur |  | 0 |  | 676
|  |  |  | Total |  | 0 |  | 9803
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Pabna Solar 100 MW |  |  | 100 | 1 | Ashuganj 51 MW PP (Midland) |  |  | 51
|  | 2 | Baghabari 100 MW GTPP |  |  | 100
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 400 |  |  |  | Total | 51
|  |  |  | Total Unavailable Capacity |  |  |  | 451
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:17 | 10:21 | Ishurdi 132/33kV S/S 132/33 kV T-3 HT Scheduled S/D Due to Work by Dasuria PBS at 33 kv | [7 empty] | 20.0MW load
|  |  | bus-1 | [7 empty] | interrup.
| 08:17 | 10:23 | Ishurdi 132/33kV S/S 132/33 kV T-3 LT Scheduled S/D Due to Work by Dasuria PBS at 33 kv | [7 empty] | 20.0MW load
|  |  | bus-1 | [7 empty] | interrup.
| 08:20 | 10:21 | Bogura 132/33kV S/S Transformer-3 LT Scheduled S/D Due to maintenance work | [7 empty] | 5.0MW load
interrup.
| 08:20 | 10:20 | Bogura 132/33kV S/S Transformer-3 HT Scheduled S/D Due to maintenance work | [7 empty] | 5.0MW load
interrup.
| 08:21 | 16:25 | Fenchuganj-Sreemangal 132kV Ckt-1 Scheduled S/D from Sreemongol 132/33kV end Due to For
maintenance work at Fenchuganj SS. and from Fenchuganj 230/132/33kV end Due to For
deadline checking.
| 08:27 | 16:29 | Gopalganj 400/132kV S/S 400kV Rampal Ckt-2 Scheduled S/D Due to Annual Maintenance
| 08:43 |  | Natore-Rajshahi 132kV Ckt-2 Scheduled S/D from Natore 132/33kV end Due to Shutdown
taken from rajshahi 132/33 kV Grid. and from Rajshahi 132/33kV end Due to Project work
| 08:48 |  | Sirajgonj 225MW CCPP Unit-1, FGMO is OFF with remarks:-
| 08:50 | 10:56 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing MicohomP441 relays.
| 09:09 |  | Rajshahi 132/33kV S/S Transformer T-2(415T) LT Scheduled S/D Due to Project work
| 09:10 |  | Rajshahi 132/33kV S/S Transformer T-2(415T) HT Scheduled S/D Due to Project work
| 09:28 | 16:28 | Gopalganj(N)-Rampal Ckt-2 Scheduled S/D from Rampal 400/230kV end Due to Yearly
Maintenance By Khulna ALDC
|  | 09:28 | Feni 132/33kV S/S T-1(405T) HT is restored.
|  | 09:28 | Feni 132/33kV S/S T-1(405T) LT is restored.
| 09:58 | 15:43 | Madunaghat 400/230kV S/S Madunaghat-Shikalbaha 230kV Ckt.-1 Scheduled S/D Due to Annual
Maintenance.
| 10:27 | 15:24 | Gopalganj(N)-Madaripur 132kV Ckt-3 Scheduled S/D from Gopalganj 400/132kV end Due to
Annual Maintenance
| 10:30 | 15:24 | Gopalganj 400/132kV S/S 132kV Madaripur Ckt-4 Scheduled S/D Due to Annual Maintenance
| 10:31 | 15:48 | Taraganj 132/33kV S/S Taraganj-Rangpur CKT-01 Project Work S/D Due to Due to ALDC
information.
| 10:57 |  | DSEPL(Pabna 100 MW Solar)-Joynagar 132 KV Ckt 1 Sync
| 10:59 |  | DSEPL(Pabna 100 MW Solar)-Joynagar 132 KV Ckt -2 Sync
|  | 12:37 | Rampura 230/132kV S/S 230kV Busbar-1 is restored.
|  | 12:48 | Baghabari-Roppur 230kV Ckt-2 is restored.
|  | 14:38 | Kamrangirchar-Keraniganj 132kV Ckt is restored.
| 14:51 | 17:11 | Rampura 230/132kV S/S 230kV Busbar-2 Scheduled S/D Due to Annual maintenance.
| 15:20 | 19:49 | Fenchuganj-Fenchuganj 132 kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Fenchuganj 90MW power station end work.
| 15:20 | 20:39 | Fenchuganj-Fenchuganj 132 kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Fenchuganj 90MW power station end work.
|  | 15:28 | Baghabari-Roppur 230kV Ckt-1 is restored.
|  | 16:49 | Lalmonirhat-Rangpur 132 kV Ckt-2 is restored.
|  | 17:44 | Khulna (C) S/S Tr-3 405T HT is restored.
|  | 17:45 | Khulna (C) S/S Tr-3 405T LT is restored.
|  | 17:55 | Madunaghat-Meghnaghat 400kV Ckt-1 is restored.
|  | 21:31 | Fenchuganj-Fenchuganj 132 kV Ckt-4 is restored.
|  | 21:32 | Sylhet 132/33kV S/S Sylhet-90MW P/S is restored.
| 23:27 |  | Maniknagar 132/33kV S/S Transformer GT-2 HT Scheduled S/D Due to DPDC 33 KV GIS SS
Testing and commissioning work by DPDC PDSD Project.
| 05:00 |  | Minimum Generation: 7419 MW.
| 05:45 | 06:20 | Bakerganj 132/33kV S/S T1 LT Tripped showing Over voltage relay relays Due to Over
Voltage
| 05:45 | 06:20 | Bakerganj 132/33kV S/S T1 HT Tripped showing Over Voltage Relay relays Due to Over
Voltage
| 06:21 |  | Baghabari-Roppur 230kV Ckt-1 Project Work S/D from Baghabari 230/132kV end Due to
Temporary cradle
| 06:22 |  | Baghabari-Roppur 230kV Ckt-2 Project Work S/D from Baghabari 230/132kV end Due to
Temporary cradle
| 06:32 |  | Kalurghat 132/33kV S/S TRFO-01(506T) LT Tripped showing REF 615 relays. | [7 empty] | 14.0MW load
interrup.
| 06:35 |  | Kalurghat 132/33kV S/S TRFO-01(506T) HT Tripped showing RET 650 RET 670 relays. | [7 empty] | 14.0MW load
interrup.
| 07:18 |  | Keranigonj 230/132/33kV S/S 132 kV Lalbagh Ckt. 3 Scheduled S/D Due to Annual maintenance
and deadline checking.
| 07:36 |  | Bakulia 132/33kV S/S T-3 (422T) LT Scheduled S/D Due to Annual Maintenance | [7 empty] | 10.0MW load
interrup.
| 07:36 |  | Bakulia 132/33kV S/S T-3 (422T) HT Scheduled S/D Due to Annual Maintenance | [7 empty] | 10.0MW load
interrup.
| 07:41 |  | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-2 Project Work S/D Due to opgw change
work
| 07:41 |  | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-1 Project Work S/D Due to opgw change
work.
| 07:41 |  | Fenchuganj -Sylhet 132kV Ckt-1 Scheduled S/D from Beanibazar 132/33kV end Due to OPGW | [7 empty] | 32.0MW load
|  |  | project work | [7 empty] | interrup.
Beanibazar 132/33kV
end
| 07:42 |  | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Scheduled S/D from Beanibazar 132/33kV
end Due to OPGW project work and from Fenchuganj 230/132/33kV end Due to For OPGW
upgradation work.
| 07:46 |  | Cumilla(N)-Cumilla(S) 132 kV Ckt-1 Scheduled S/D from Cumilla(S) 132/33kV end Due to
Annual Maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 23-01-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 335 | 8290800 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 194416 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 7647922 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 33.3 | 259200 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 16 | 156960 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 266437 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 270842 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 12 | 332400 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 426240 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 84960 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 1165222 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 78 | 825408 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 171840 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 86 | 692640 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 176506 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 100440 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 405 | 9339334 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 52 | 364800 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1631.3 | 30766367
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 33784.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 126360 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 26 | 194880 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 2069600 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 186 | 4269302 | Plant availability less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 618909 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 8 | 56976 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 32 | 160125 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 384960 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 40 | 927840 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 30 | 48960 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 19922 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 30 | 336218 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 17 | 144331 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 33 | 339600 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 294720 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 30 | 277255 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 78 | 259273 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1163 | 27267270 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 5 | 204960 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 155 | 6603636.36 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4898.863 | 2053 | 44638881.56
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 188 | 4783000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 280 | 7088400 | STG Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 220 | 5434500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 0 | 917331 | Gas shortage
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 362981 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 16 | 79552 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 104 | 2479492 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 592800 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 100 | 2395200 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 90418 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 343260 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 15 | 148200 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 41160 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 16 | 182400 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 408982 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1028 | 25347676
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 49 | 862080 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 316800 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 57 | 775200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 240910 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 109440 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 132120 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 154 | 2447600
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 68570 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 413000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 523000 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 157 | 3669545 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 718944 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1885440 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 97 | 2359220 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 452976 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7737000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 700 | 17827695
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 473 | 11456000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 30 | 77280 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 32 | 139520 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 145 | 2336832 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 506160 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1101 | 24850900 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1781 | 39366692
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 45 | 259392 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 3094000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 555 | 13249454.55 | -
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5514330 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 48 | 328800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 278 | 6262000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3109 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1276 | 28711085.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 287172 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 23 | 72542 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 177 | 3692545 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 300 | 7684509 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 8 | 20295 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 25 | 47309 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 32 | 391488 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 50 | 324384 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 28680 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 758 | 17098546 | U#1 Under AOH
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 326256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 357200 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1373 | 30330926
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 55 | 1284655 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 63 | 615945 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 31199.52 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 576182 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 156708 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 802080 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 168 | 3466769.52
Eastern Grid Total |  |  |  |  | 17398.245 | 5566.3 | 121028219.56
Western Grid Total |  |  |  |  | 10984.003 | 4598 | 101875473.07
National Grid Total |  |  |  |  | 28382.248 | 10164.3 | 222903692.63
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 23-01-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6662.85 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3140.4 | MW
i) Dhaka area |  |  | 3372.25 |  | MW | i) Khulna area |  |  |  | 1170.8 | MW
ii) Chattogram area |  |  | 1075.6 |  | MW | ii) Barishal area |  |  |  | 305.4 | MW
iii) Cumilla area |  |  | 906 |  | MW | iii) Rajshahi area |  |  |  | 988.2 | MW
iv) Mymensingh area |  |  | 923 |  | MW | iv) Rangpur area |  |  |  | 676 | MW
v) Sylhet area |  |  | 386 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 9803.25 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 9 | 00:00 | 67 | Hasnabad | 71 | 12:00 | 133 | Netrakona | 126 | 18:00
2 | AKSML | 136 | 02:00 | 68 | Hathazari | 54 | 12:00 | 134 | New | 43.2 | 12:00
3 | Aftabnagar | 28 | 13:00 | 69 | Hatirjheel | 25 | 12:00 | 135 | Niamatpur | 84 | 08:00
4 | Agargaon | 89 | 13:00 | 70 | Ishurdi | 43 | 18:30 | 136 | Noapara | 29 | 18:30
5 | Agrabad | 32 | 00:00 | 71 | Jaldhaka | 54 | 18:30 | 137 | PHP | 9 | 06:00
6 | Amnura | 32 | 09:00 | 72 | Jamalpur | 94 | 09:00 | 138 | Pabna | 64 | 13:00
7 | Ashuganj | 77 | 13:00 | 73 | Jashore | 97 | 13:00 | 139 | Palashbari | 80 | 08:00
8 | BSRM | 187 | 06:00 | 74 | Jhenaidah | 97 | 07:00 | 140 | Panchagarh | 42 | 18:30
9 | Bagerhat | 64 | 18:30 | 75 | Joydebpur | 87 | 13:00 | 141 | Patiya | 7.2 | 18:00
10 | Bajitpur | 58 | 18:00 | 76 | Joypurhat | 40 | 09:00 | 142 | Patuakhali | 38.5 | 21:00
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 14 | 00:00 | 143 | Payra | 26 | 12:00
12 | Bakulia | 54 | 12:00 | 78 | KSRM | 18 | 11:00 | 144 | Postogola | 37 | 13:00
13 | Banani | 30.8 | 13:00 | 79 | Kabirpur | 145 | 13:00 | 145 | Purbachal | 22 | 12:00
14 | Bangabhaban | 3 | 00:00 | 80 | Kachua | 65 | 13:00 | 146 | Purbasadipur | 113 | 12:00
15 | Barapukuria | 50 | 09:00 | 81 | Kallyanpur | 78 | 13:00 | 147 | Rahanpur | 24 | 08:00
16 | Barguna | 14 | 18:30 | 82 | Kalurghat | 21 | 00:00 | 148 | Rahim | 45 | 01:00
17 | Barishal | 84 | 13:00 | 83 | Kamrangirchar | 50 | 00:00 | 149 | Rajbari | 53 | 18:30
18 | Barishal-230 | 70 | 13:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 97 | 12:00
19 | Baroaulia | 55 | 18:00 | 85 | Kasba | 30 | 13:00 | 151 | Rajshahi | 66 | 12:00
20 | Baroirhat | 53 | 13:00 | 86 | Kazla | 88 | 13:00 | 152 | Rajshahi-230 | 76 | 13:00
21 | Bashundhara | 162 | 13:00 | 87 | Keranigonj | 59 | 13:00 | 153 | Ramganj | 86 | 13:00
22 | BashundharaCement | 7 | 00:00 | 88 | Khagrachori | 24 | 18:00 | 154 | Rampur | 27 | 12:00
23 | Beanibazar | 48 | 13:00 | 89 | Khulna | 41 | 13:00 | 155 | Rangamati | 13 | 18:00
24 | Benapole | 70 | 08:00 | 90 | Khulshi | 153 | 12:00 | 156 | Rangpur | 100 | 12:00
25 | Bhaluka | 120 | 08:00 | 91 | Kishoreganj | 100 | 18:30 | 157 | Ruppur | 2 | 08:00
26 | Bhandaria | 36 | 21:00 | 92 | Kodda | 178 | 00:00 | 158 | SSM | 2 | 00:00
27 | Bhangura | 24 | 18:30 | 93 | Kulaura | 28 | 13:00 | 159 | Saidpur | 77 | 09:00
28 | Bheramara(GK) | 37 | 18:30 | 94 | Kurigram | 52 | 18:00 | 160 | Satkhira | 102 | 08:00
29 | Bhulta | 172 | 00:00 | 95 | Kushtia | 105 | 13:00 | 161 | Satmasjid | 83 | 13:00
30 | Bog-Sherpur | 48 | 08:00 | 96 | Laksam | 16 | 13:00 | 162 | Savar | 134 | 12:00
31 | Bogura | 106 | 18:30 | 97 | Lakshmipur | 23 | 14:00 | 163 | SevenRings | 15.66 | 08:00
32 | Borhanuddin | 64 | 19:00 | 98 | Lalbag | 48 | 00:00 | 164 | ShahCement | 25 | 09:00
33 | Brahmanbaria | 94 | 12:00 | 99 | Lalmonirhat | 43 | 18:00 | 165 | Shahjadpur | 43 | 18:00
34 | Cantonment | 88 | 13:00 | 100 | MI_Cement | 17 | 10:00 | 166 | Shahjibazar | 89 | 18:30
35 | Chandina | 14 | 13:00 | 101 | Madanganj | 27 | 11:00 | 167 | Shahmirpur | 30 | 12:00
36 | Chandpur | 58 | 13:00 | 102 | Madaripur | 70 | 19:00 | 168 | Shariatpur | 52 | 19:00
37 | Chandraghona | 28 | 18:00 | 103 | Madartek | 59 | 13:00 | 169 | Sherpur | 120 | 20:00
38 | Chapai | 54 | 08:00 | 104 | Madunaghat | 35 | 18:00 | 170 | Shikalbaha | 20 | 18:30
39 | Charsaidpur | 41 | 00:00 | 105 | Magura | 47 | 18:30 | 171 | Shitalakhya | 45.4 | 13:00
40 | Chauddagram | 61 | 13:00 | 106 | Mahasthangarh | 58 | 09:00 | 172 | Sholosohor | 28 | 12:00
41 | Chhatak | 28 | 18:00 | 107 | Maijdee | 33 | 21:00 | 173 | Shyampur | 148 | 11:00
42 | Chowmuhani | 116 | 13:00 | 108 | Manikganj | 82 | 00:00 | 174 | Siddhirganj | 94 | 12:00
43 | Chuadanga | 76 | 18:30 | 109 | Maniknagar | 50 | 13:00 | 175 | Sirajganj | 70 | 18:30
44 | Coxsbazar | 107 | 13:00 | 110 | Matarbari | 40 | 18:30 | 176 | Sonargaon | 130 | 00:00
45 | Cumilla(N) | 113 | 12:00 | 111 | Matuail | 44 | 00:00 | 177 | Sreemongol | 51 | 18:30
46 | Cumilla(S) | 132 | 13:00 | 112 | Metrorail_Motijheel | 23 | 17:00 | 178 | Sreepur | 81 | 12:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 0 | 00:00 | 179 | Srinagar | 38.4 | 13:00
48 | Daudkandi | 109 | 20:00 | 114 | Millgate | 58 | 12:00 | 180 | Sunamganj | 39 | 19:30
49 | DhakaUniversity | 34 | 13:00 | 115 | Mirpur | 112 | 12:00 | 181 | Sylhet | 44 | 13:00
50 | Dhamrai | 80 | 00:00 | 116 | Mirsorai | 42 | 06:00 | 182 | Sylhet-132 | 61 | 13:00
51 | Dhanmondi | 71 | 13:00 | 117 | Mirzapur | 39 | 18:00 | 183 | TK | 18 | 18:30
52 | Dohazari | 78 | 18:00 | 118 | Mithapukur | 40 | 08:00 | 184 | Tangail | 124 | 07:00
53 | Faridpur | 101 | 21:00 | 119 | Modern | N/A | N/A | 185 | Taraganj | 16 | 09:00
54 | Fatullah | 76 | 00:00 | 120 | Mogbazar | 56 | 13:00 | 186 | Tasnim | 32 | 14:00
55 | Fenchuganj | 24 | 13:00 | 121 | Mongla | 30 | 00:00 | 187 | Thakurgaon | 74 | 13:00
56 | Feni | 75 | 13:00 | 122 | Motijheel | 28 | 12:00 | 188 | Tongi | 112 | 12:00
57 | GPH | 89 | 05:00 | 123 | Muktagacha | 39 | 13:00 | 189 | Ullahpara | 24 | 18:00
58 | Ghatail | 64 | 10:00 | 124 | Munshiganj | 68 | 21:00 | 190 | Ullon | 53 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 0 | 00:00 | 191 | Uttara | 58 | 12:00
60 | Ghorashal-230 | 83 | 09:00 | 126 | Mymensingh | 158 | 13:00 | 192 | UttaraNew | 13 | 13:00
61 | Goalpara | 27 | 13:00 | 127 | Naogaon | 94 | 18:30 | 193 | Zigatola | 66 | 11:00
62 | Gollamari | 72 | 12:00 | 128 | Narail | 42 | 08:00
63 | Gopalganj | 84 | 18:30 | 129 | Narinda | 42 | 13:00
64 | Gulshan | 60 | 13:00 | 130 | Narshingdi | 135 | 20:00
65 | Halishahar | 54 | 19:30 | 131 | Natore | 103 | 18:30
66 | HaripurSBU | 99 | 04:00 | 132 | Nawabganj | 35.8 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 23-01-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 9613.69 | 0 |  | 9613.69
1:00 | 8929.38 | 0 |  | 8929.38
2:00 | 8662.03 | 0 |  | 8662.03
3:00 | 8354.91 | 0 |  | 8354.91
4:00 | 8095.27 | 0 |  | 8095.27
5:00 | 7942.68 | 0 |  | 7942.68
6:00 | 8218.15 | 0 |  | 8218.15
7:00 | 8555.11 | 0 |  | 8555.11
8:00 | 9222.13 | 0 |  | 9222.13
9:00 | 9303.16 | 0 |  | 9303.16
10:00 | 9247.83 | 0 |  | 9247.83
11:00 | 9409.7 | 0 |  | 9409.7
12:00 | 10167.95 | 0 |  | 10167.95
13:00 | 10732.34 | 117 |  | 10854.34
14:00 | 9369.22 | 0 |  | 9369.22
15:00 | 8613.41 | 0 |  | 8613.41
16:00 | 8250.88 | 0 |  | 8250.88
17:00 | 8428.63 | 0 |  | 8428.63
18:00 | 9504.6 | 0 |  | 9504.6
19:00 | 10164.3 | 0 |  | 10164.3
19:30 | 10074.3 | 0 |  | 10074.3
20:00 | 10099.3 | 0 |  | 10099.3
21:00 | 10069.55 | 0 |  | 10069.55
22:00 | 9715.39 | 0 |  | 9715.39
23:00 | 9338.11 | 0 |  | 9338.11
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 23-01-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5419 | 4194.69 | 9613.69 | DAILY GENERATION CURVE
00:30 | 5114.5 | 4157.035 | 9271.535
01:00 | 4810 | 4119.38 | 8929.38 | 23-01-2026
01:30 | 4758.5 | 4037.205 | 8795.705
02:00 | 4707 | 3955.03 | 8662.03
02:30 | 4698 | 3810.47 | 8508.47
03:00 | 4689 | 3665.91 | 8354.91
03:30 | 4655.5 | 3569.59 | 8225.09
04:00 | 4622 | 3473.27 | 8095.27
04:30 | 4621.5 | 3397.475 | 8018.975
05:00 | 4621 | 3321.68 | 7942.68
05:30 | 4687 | 3393.415 | 8080.415
06:00 | 4753 | 3465.15 | 8218.15
06:30 | 4770.385 | 3616.245 | 8386.63
07:00 | 4787.77 | 3767.34 | 8555.11
07:30 | 4961.14 | 3927.48 | 8888.62
08:00 | 5134.51 | 4087.62 | 9222.13
08:30 | 5096.995 | 4165.65 | 9262.645
09:00 | 5059.48 | 4243.68 | 9303.16
09:30 | 4971.73 | 4303.765 | 9275.495
10:00 | 4883.98 | 4363.85 | 9247.83
10:30 | 4881.57 | 4447.195 | 9328.765
11:00 | 4879.16 | 4530.54 | 9409.7
11:30 | 5173.17 | 4615.655 | 9788.825
12:00 | 5467.18 | 4700.77 | 10167.95
12:30 | 5688.145 | 4762 | 10450.145
13:00 | 5909.11 | 4823.23 | 10732.34
13:30 | 5364.87 | 4685.91 | 10050.78
14:00 | 4820.63 | 4548.59 | 9369.22
14:30 | 4598.545 | 4392.77 | 8991.315
15:00 | 4376.46 | 4236.95 | 8613.41
15:30 | 4376.335 | 4055.81 | 8432.145
16:00 | 4376.21 | 3874.67 | 8250.88
16:30 | 4507.77 | 3831.985 | 8339.755
17:00 | 4639.33 | 3789.3 | 8428.63
17:30 | 4986.465 | 3980.15 | 8966.615
18:00 | 5333.6 | 4171 | 9504.6
18:30 | 5449.95 | 4384.5 | 9834.45
19:00 | 5566.3 | 4598 | 10164.3
19:30 | 5446.3 | 4628 | 10074.3
20:00 | 5446.3 | 4653 | 10099.3
20:30 | 5423.15 | 4661.275 | 10084.425 |  | Executive Engineer
21:00 | 5400 | 4669.55 | 10069.55 |  | Network Operation Division
21:30 | 5277 | 4615.47 | 9892.47
22:00 | 5154 | 4561.39 | 9715.39
22:30 | 5007 | 4519.75 | 9526.75
23:00 | 4860 | 4478.11 | 9338.11

## En-Curve
QF-LDC-12
Date | 23-01-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2550 | 1304 | 473 | 0 | 110 | 763.69 | 86 | 3572 | 0 | 0 | 730 | 0 | 0 | 25 | 0 | DAILY ENERGY CURVE
00:30 | 2554 | 1294.5 | 473.5 | 0 | 105 | 766.035 | 86 | 3592.5 | 0 | 0 | 373.5 | 0 | 0 | 26.5 | 0 | 23-01-2026
01:00 | 2558 | 1285 | 474 | 0 | 100 | 768.38 | 86 | 3613 | 0 | 0 | 17 | 0 | 0 | 28 | 0
01:30 | 2555 | 1281 | 474 | 0 | 96 | 746.705 | 86 | 3524.5 | 0 | 0 | 8.5 | 0 | 0 | 24 | 0 | Energy Generated | 222.9037 |  | MKWHr
02:00 | 2552 | 1277 | 474 | 0 | 92 | 725.03 | 86 | 3436 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | Energy not Served | 0.117 |  | MKWHr
02:30 | 2550.5 | 1268 | 474 | 0 | 94 | 697.47 | 86 | 3318.5 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | Total Energy Requirement | 223.0207 |  | MKWHr
03:00 | 2549 | 1259 | 474 | 0 | 96 | 669.91 | 86 | 3201 | 0 | 0 | 0 | 0 | 0 | 20 | 0
03:30 | 2544.5 | 1256 | 473.5 | 0 | 94 | 655.59 | 86 | 3091 | 0 | 0 | 0 | 0 | 0 | 24.5 | 0
04:00 | 2540 | 1253 | 473 | 0 | 92 | 641.27 | 86 | 2981 | 0 | 0 | 0 | 0 | 0 | 29 | 0
04:30 | 2547.5 | 1261.5 | 473 | 0 | 92 | 584.475 | 86 | 2947 | 0 | 0 | 0 | 0 | 0 | 27.5 | 0
05:00 | 2555 | 1270 | 473 | 0 | 92 | 527.68 | 86 | 2913 | 0 | 0 | 0 | 0 | 0 | 26 | 0
05:30 | 2557.5 | 1275.5 | 473.5 | 0 | 96 | 527.415 | 86 | 3042.5 | 0 | 0 | 0 | 0 | 0 | 22 | 0
06:00 | 2560 | 1281 | 474 | 0 | 100 | 527.15 | 86 | 3172 | 0 | 0 | 0 | 0 | 0 | 18 | 0
06:30 | 2552 | 1280.5 | 473.5 | 0 | 97 | 606.105 | 86 | 3271 | 4.525 | 0 | 0 | 0 | 0 | 16 | 0
07:00 | 2544 | 1280 | 473 | 0 | 94 | 685.06 | 86 | 3370 | 9.05 | 0 | 0 | 0 | 0 | 14 | 0
07:30 | 2549 | 1294 | 473 | 0 | 95 | 724.615 | 86 | 3411 | 54.055 | 0 | 189.95 | 0 | 0 | 12 | 0
08:00 | 2554 | 1308 | 473 | 0 | 96 | 764.17 | 86 | 3452 | 99.06 | 0 | 379.9 | 0 | 0 | 10 | 0
08:30 | 2527 | 1295.75 | 473.5 | 0 | 96 | 765.975 | 86 | 3473.5 | 177.62 | 0 | 362.3 | 0 | 0 | 5 | 0
09:00 | 2500 | 1283.5 | 474 | 0 | 96 | 767.78 | 86 | 3495 | 256.18 | 0 | 344.7 | 0 | 0 | 0 | 0
09:30 | 2503.5 | 1276.75 | 473.5 | 0 | 96 | 760.405 | 86 | 3473.5 | 326.49 | 0 | 279.35 | 0 | 0 | 0 | 0
10:00 | 2507 | 1270 | 473 | 0 | 96 | 753.03 | 86 | 3452 | 396.8 | 0 | 214 | 0 | 0 | 0 | 0
10:30 | 2471 | 1282 | 473 | 0 | 103 | 761.22 | 86 | 3494.5 | 439.545 | 0 | 218.5 | 0 | 0 | 0 | 0
11:00 | 2435 | 1294 | 473 | 0 | 110 | 769.41 | 86 | 3537 | 482.29 | 0 | 223 | 0 | 0 | 0 | 0
11:30 | 2432.5 | 1305.5 | 473 | 0 | 117 | 765.01 | 86 | 3475.5 | 543.315 | 45.5 | 545.5 | 0 | 0 | 0 | 0
12:00 | 2430 | 1317 | 473 | 0 | 124 | 760.61 | 86 | 3414 | 604.34 | 91 | 868 | 0 | 0 | 0 | 0
12:30 | 2428.5 | 1361.5 | 473.5 | 0 | 130 | 759.565 | 86 | 3420.5 | 594.08 | 122.5 | 1074 | 0 | 0 | 0 | 58.5
13:00 | 2427 | 1406 | 474 | 0 | 136 | 758.52 | 86 | 3427 | 583.82 | 154 | 1280 | 0 | 0 | 0 | 117
13:30 | 2424.5 | 1383.5 | 474 | 0 | 125 | 758.26 | 86 | 3396.5 | 539.87 | 77 | 786.15 | 0 | 0 | 0 | 58.5
14:00 | 2422 | 1361 | 474 | 0 | 114 | 758 | 86 | 3366 | 495.92 | 0 | 292.3 | 0 | 0 | 0 | 0
14:30 | 2429 | 1326 | 474 | 0 | 108 | 757.5 | 86 | 3211.5 | 422.665 | 0 | 176.65 | 0 | 0 | 0 | 0
15:00 | 2436 | 1291 | 474 | 0 | 102 | 757 | 86 | 3057 | 349.41 | 0 | 61 | 0 | 0 | 0 | 0
15:30 | 2425 | 1287 | 473.5 | 0 | 99 | 757.5 | 86 | 2952.5 | 264.645 | 0 | 86.5 | 0 | 0 | 0.5 | 0
16:00 | 2414 | 1283 | 473 | 0 | 96 | 758 | 86 | 2848 | 179.88 | 0 | 112 | 0 | 0 | 1 | 0
16:30 | 2405 | 1270 | 473 | 0 | 92 | 756 | 86 | 2836 | 109.355 | 37.5 | 271.4 | 0 | 0 | 3.5 | 0
17:00 | 2396 | 1257 | 473 | 0 | 88 | 754 | 86 | 2824 | 38.83 | 75 | 430.8 | 0 | 0 | 6 | 0
17:30 | 2444 | 1209.5 | 473.5 | 0 | 94 | 756.5 | 86 | 2912.5 | 19.415 | 168 | 796.7 | 0 | 0 | 6.5 | 0
18:00 | 2492 | 1162 | 474 | 0 | 100 | 759 | 86 | 3001 | 0 | 261 | 1162.6 | 0 | 0 | 7 | 0
18:30 | 2506.5 | 1223.5 | 473.5 | 0 | 100 | 758.5 | 86 | 3154 | 0 | 264 | 1262.45 | 0 | 0 | 6 | 0
19:00 | 2521 | 1285 | 473 | 0 | 100 | 758 | 86 | 3307 | 0 | 267 | 1362.3 | 0 | 0 | 5 | 0
19:30 | 2575 | 1317 | 473 | 0 | 102 | 758 | 86 | 3368 | 0 | 226 | 1167.3 | 0 | 0 | 2 | 0
20:00 | 2577 | 1322 | 473 | 0 | 100 | 759 | 86 | 3389 | 0 | 227 | 1163.3 | 0 | 0 | 3 | 0
20:30 | 2604 | 1320 | 473.5 | 0 | 102 | 761.275 | 86 | 3385 | 0 | 220.5 | 1130.65 | 0 | 0 | 1.5 | 0
21:00 | 2631 | 1318 | 474 | 0 | 104 | 763.55 | 86 | 3381 | 0 | 214 | 1098 | 0 | 0 | 0 | 0
21:30 | 2643.5 | 1309 | 474 | 0 | 104 | 764.97 | 86 | 3379.5 | 0 | 135.5 | 996 | 0 | 0 | 0 | 0
22:00 | 2656 | 1300 | 474 | 0 | 104 | 766.39 | 86 | 3378 | 0 | 57 | 894 | 0 | 0 | 0 | 0
22:30 | 2679 | 1291 | 473.5 | 0 | 103 | 762.25 | 86 | 3375.5 | 0 | 37 | 719.5 | 0 | 0 | 0 | 0
23:00 | 2702 | 1282 | 473 | 0 | 102 | 758.11 | 86 | 3373 | 0 | 17 | 545 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 23-01-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 422 | 04:00 | 412 | 12:00 | Madunaghat | 417 | 19:00 | 409 | 11:00
Amtali | 427 | 05:00 | 418 | 11:00 | Meghnaghat | 428 | 18:00 | 414 | 11:00
Ashuganj | 413 | 4:00 | 400 | 11:00 | Payra | 427 | 04:00 | 420 | 11:00
Bhulta | 405 | 04:00 | 394 | 11:00 | Rahanpur | 420 | 04:00 | 409 | 09:00
Bibiana | 425 | 18:00 | 415 | 11:00 | Rampal | 418 | 05:00 | 407 | 14:00
BIPTC | 407 | 03:00 | 396 | 10:00
Bogura | 417 | 04:00 | 403 | 09:00
Gopalganj | 423 | 05:00 | 411 | 11:00
Kaliakoir | 419 | 18:00 | 406 | 11:00
Korerhat | 427 | 18:00 | 413 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 245 | 05:00 | 236 | 11:00 | Jhenaidah | 242 | 03:00 | 221 | 08:00
AKSML | 240.4 | 04:00 | 228 | 12:00 | Kachua | 243 | 18:00 | 238 | 10:00
Aminbazar | 245 | 05:00 | 240 | 01:00 | Kaliakoir | 245 | 18:00 | 237 | 11:00
Ashuganj | 240 | 17:00 | 234 | 11:00 | Keranigonj | 243 | 18:00 | 235 | 11:00
Ashuganj-400 | 240 | 17:00 | 234 | 11:00 | Khulna(S) | 246 | 04:00 | 235 | 11:00
Baghabari | 242 | 04:00 | 234 | 09:00 | Korerhat | 242 | 18:00 | 236 | 10:00
Barapukuria | 232 | 00:00 | 223 | 09:00 | Madunaghat | 240 | 18:00 | 235 | 07:00
Barapukuria-230 | 232 | 00:00 | 223 | 09:00 | Madunaghat-400 | 240 | 19:00 | 234 | 11:00
Barishal | 240 | 04:00 | 233 | 11:00 | Maniknagar | 242 | 18:00 | 235 | 11:00
Bheramara | 241 | 04:00 | 230 | 11:00 | Meghnaghat | 247 | 18:00 | 240 | 11:00
Bhulta | 243 | 04:00 | 236 | 11:00 | Meghnaghat-400 | 243 | 18:00 | 235 | 11:00
Bibiana | 243 | 18:00 | 239 | 11:00 | Mirsorai | 244 | 18:30 | 236 | 11:00
BIPTC | 242 | 03:00 | 229 | 08:00 | Rajshahi | 241 | 04:00 | 228 | 11:00
Bogura | 244 | 04:00 | 235 | 09:00 | Rampal | 243 | 05:00 | 233 | 10:00
Bogura-400 | 243 | 03:00 | 234 | 09:00 | Rampur | N/A | N/A | N/A | N/A
Borhanuddin | 241 | 20:00 | 237 | 11:00 | Rampura | 243 | 18:00 | 234 | 11:00
BSRM | 242 | 18:00 | 235 | 11:00 | Shikalbaha | 239 | 18:00 | 232 | 11:00
Chowmuhani | 243 | 18:00 | 236 | 11:00 | Shyampur | 241 | 04:00 | 234 | 11:00
Cumilla(N) | 241 | 18:00 | 234 | 11:00 | Siddhirganj | 244 | 17:00 | 237 | 10:00
Faridpur | 239 | 04:00 | 233 | 11:00 | Sirajgonj | 246 | 04:00 | 240 | 11:00
Fenchuganj | 246 | 04:00 | 242 | 11:00 | Sreepur | 237 | 04:00 | 230 | 11:00
Feni | 242 | 04:00 | 236 | 11:00 | Tongi | 241 | 01:00 | 236 | 11:00
Ghorashal | 245 | 04:00 | 240 | 00:00
Ghorashal-230 | 242 | 04:00 | 233 | 11:00
Gopalganj | 237 | 04:00 | 231 | 11:00
GPH | 241 | 18:00 | 234 | 11:00
Haripur | 243 | 18:00 | 236 | 11:00
Hasnabad | 244 | 18:00 | 236 | 10:00
Hathazari | 239 | 18:00 | 233 | 10:00
Ishurdi | 243 | 04:00 | 232 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 04:00 | 130 | 11:00 | Maijdee | 136 | 18:00 | 133 | 09:00
Agargaon | 139 | 04:00 | 134 | 11:00 | Manikganj | 133 | 17:00 | 124 | 08:00
Agrabad | 139 | 18:00 | 135 | 11:00 | Maniknagar | 140 | 04:00 | 136 | 11:00
AKS | 136 | 17:00 | 130 | 00:00 | Matarbari | 130 | 02:00 | 126 | 13:00
Aminbazar | 141 | 17:00 | 130 | 01:00 | Matuail | 140 | 18:00 | 135 | 11:00
Amnura | 138 | 02:00 | 131 | 13:00 | Metrorail_Motijheel | 140 | 04:00 | 136 | 11:00
Ashuganj | 140 | 04:00 | 137 | 11:00 | Metrorail_Uttara | 140 | 05:00 | 134 | 11:00
Bagerhat | 136 | 05:00 | 128 | 08:00 | Millgate | 135 | 18:00 | 129 | 11:00
Bajitpur | 135 | 17:00 | 131 | 13:00 | Mirpur | 140 | 17:00 | 135 | 11:00
Bakerganj | 141 | 05:00 | 139 | 10:00 | Mirzapur | 135 | 17:00 | 130 | 01:00
Bakulia | 140 | 18:00 | 135 | 11:00 | Mithapukur | 136 | 00:00 | 129 | 09:00
Banani | 135 | 04:00 | 129 | 11:00 | MI_Cement | 137 | 17:00 | 132 | 11:00
Bangabhaban | 140 | 06:00 | 136 | 08:00 | Modern | N/A | N/A | N/A | N/A
Barapukuria | 135 | 00:00 | 129 | 08:00 | Mogbazar | 136 | 03:00 | 131 | 11:00
Barguna | 142 | 18:00 | 139 | 01:00 | Mongla | 135 | 05:00 | 128 | 11:00
Barishal | 141 | 17:00 | 137 | 13:00 | Motijheel | 140 | 06:00 | 136 | 08:00
Barishal-230 | 142 | 04:00 | 136 | 11:00 | Muktagacha | 131 | 10:00 | 121 | 07:00
Baroaulia | 139 | 03:00 | 135 | 11:00 | Munshiganj | 138 | 17:00 | 133 | 11:00
Baroirhat | 137 | 18:00 | 132 | 11:00 | Muradnagar | 139 | 04:00 | 135 | 10:00
Bashundhara | 135 | 04:00 | 130 | 11:00 | Mymensingh | 129 | 14:00 | 118 | 07:00
BashundharaCement | 139 | 18:30 | 135 | 00:00 | Naogaon | 136 | 04:00 | 128 | 09:00
Beanibazar | 133 | 04:00 | 130 | 11:00 | Narail | 140 | 04:00 | 130 | 08:00
Benapole | 136 | 03:00 | 125 | 08:00 | Narinda | 140 | 04:00 | 136 | 11:00
Bhaluka | 133 | 05:00 | 127 | 08:00 | Narshingdi | 138 | 17:00 | 126 | 03:00
Bhandaria | 140 | 05:00 | 135 | 11:00 | Natore | 138 | 03:00 | 132 | 08:00
Bhangura | 140 | 03:00 | 135 | 08:00 | Nawabganj | 137 | 04:00 | 132 | 11:00
Bheramara | 139 | 04:00 | 133 | 08:00 | Netrakona | 124 | 02:00 | 116 | 08:00
Bheramara(GK) | 139 | 05:00 | 133 | 09:00 | New | 135 | 02:00 | 130 | 11:00
Bhulta | 134 | 18:00 | 130 | 00:00 | Niamatpur | 140 | 01:00 | 136 | 07:00
Bog-Sherpur | 138 | 00:00 | 133 | 09:00 | Noapara | 137 | 05:00 | 129 | 08:00
Bogura | 138 | 02:00 | 132 | 13:00 | Pabna | 140 | 04:00 | 133 | 09:00
Bogura-230 | 139 | 04:00 | 133 | 09:00 | Palashbari | 134 | 05:00 | 127 | 09:00
Brahmanbaria | 132 | 04:00 | 128 | 12:00 | Panchagarh | 135 | 00:00 | 126 | 09:00
Cantonment | 139 | 04:00 | 134 | 11:00 | Patiya | 139 | 18:00 | 135 | 11:00
Chandina | 141 | 18:00 | 136 | 11:00 | Patuakhali | 141 | 16:00 | 136 | 00:00
Chandpur | 141 | 18:00 | 135 | 11:00 | Payra | 142 | 03:00 | 140 | 00:00
Chandraghona | 140 | 18:00 | 137 | 10:00 | PHP | 136 | 04:00 | 132 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 139 | 01:00 | 135 | 08:00 | Postogola | 139 | 19:30 | 134 | 01:00
Charsaidpur | 140 | 18:00 | 134 | 11:00 | Purbachal | 134 | 02:00 | 129 | 11:00
Chauddagram | 137 | 03:00 | 133 | 11:00 | Purbasadipur | 133 | 03:00 | 126 | 09:00
Chhatak | 132 | 03:00 | 126 | 12:00 | Rahanpur | 140 | 03:00 | 137 | 08:00
Chowmuhani | 135 | 00:00 | 132 | 15:00 | Rahanpur-400 | 141 | 03:00 | 137 | 09:00
Chuadanga | 139 | 04:00 | 129 | 08:00 | Rahim | 139 | 18:00 | 135 | 11:00
Coxsbazar | 131 | 03:00 | 127 | 07:00 | Rajbari | 138 | 03:00 | 135 | 11:00
Cumilla(N) | 141 | 18:00 | 136 | 11:00 | Rajendrapur | 134 | 03:00 | 128 | 11:00
Cumilla(S) | 140 | 04:00 | 124 | 11:00 | Rajshahi | 138 | 01:00 | 132 | 11:00
Daganbhuiyan | 137 | 18:00 | 132 | 11:00 | Rajshahi-230 | 139 | 03:00 | 131 | 11:00
Daudkandi | 137 | 18:00 | 132 | 11:00 | Ramganj | 137 | 17:00 | 133 | 12:00
DhakaUniversity | 135 | 04:00 | 130 | 11:00 | Rampur | 139 | 18:00 | 135 | 10:00
Dhamrai | 139 | 17:00 | 134 | 11:00 | Rampura | 134 | 03:00 | 129 | 11:00
Dhanmondi | 140 | 18:00 | 136 | 11:00 | Rangamati | 139 | 18:00 | 137 | 00:00
Dohazari | 136 | 17:00 | 133 | 10:00 | Rangpur | 135 | 00:00 | 129 | 07:00
Faridpur | 139 | 04:00 | 135 | 11:00 | Ruppur | 142 | 04:00 | 134 | 08:00
Fatullah | 141 | 19:00 | 133 | 00:00 | Saidpur | 134 | 04:00 | 127 | 09:00
Fenchuganj | 139 | 04:00 | 137 | 11:00 | Satkhira | 136 | 04:00 | 126 | 08:00
Feni | 135 | 05:00 | 131 | 10:00 | Satmasjid | 139 | 05:00 | 133 | 11:00
Feni-230 | 136 | 04:00 | 132 | 11:00 | Savar | 141 | 18:00 | 135 | 11:00
Ghatail | 130 | 10:00 | 122 | 02:00 | SevenRings | 134 | 03:00 | 130 | 11:00
Ghorashal | 134 | 04:00 | 131 | 10:00 | ShahCement | 140 | 18:00 | 134 | 11:00
Goalpara | 139 | 03:00 | 131 | 08:00 | Shahjadpur | 143 | 04:00 | 136 | 10:00
Gollamari | 138 | 05:00 | 131 | 11:00 | Shahjibazar | 134 | 02:00 | 130 | 11:00
Gopalganj | 141 | 04:00 | 135 | 09:00 | Shahmirpur | 140 | 17:00 | 136 | 10:00
Gopalganj-400 | 143 | 04:00 | 124 | 21:00 | Shariatpur | 142 | 03:00 | 137 | 11:00
Gulshan | 133 | 03:00 | 129 | 11:00 | Sherpur | 125 | 13:00 | 114 | 06:00
Halishahar | 140 | 18:00 | 135 | 11:00 | Shikalbaha | 129 | 18:00 | 124 | 18:30
Haripur | 139 | 17:00 | 135 | 11:00 | Shikalbaha-230 | 141 | 18:00 | 136 | 11:00
HaripurSBU | 139 | 17:00 | 135 | 01:00 | Shitalakhya | 137 | 17:00 | 132 | 11:00
Hasnabad | 138 | 17:00 | 134 | 10:00 | Sholosohor | 140 | 18:00 | 136 | 11:00
Hathazari | 140 | 17:00 | 136 | 05:00 | Shyampur | 139 | 18:00 | 135 | 11:00
Hatirjheel | 135 | 04:00 | 130 | 11:00 | Shyampur-230 | 140 | 04:00 | 136 | 11:00
Ishurdi | 141 | 03:00 | 135 | 08:00 | Siddhirganj | 139 | 04:00 | 135 | 11:00
Jaldhaka | 132 | 00:00 | 124 | 09:00 | Sirajganj | 139 | 04:00 | 132 | 09:00
Jamalpur | 130 | 10:00 | 115 | 03:00 | Sonargaon | 136 | 04:00 | 134 | 11:00
Jashore | 135 | 02:00 | 127 | 08:00 | Sreemongol | 135 | 17:00 | 131 | 11:00
Jhenaidah | 139 | 02:00 | 121 | 09:00 | Sreepur | 135 | 03:00 | 130 | 08:00
Jhenaidah-230 | 140 | 04:00 | 132 | 08:00 | Srinagar | 137 | 17:00 | 132 | 11:00
Joydebpur | 132 | 01:00 | 128 | 21:00 | SSM | 142 | 00:00 | 140 | 01:00
Joypurhat | 134 | 03:00 | 123 | 13:00 | Sunamganj | 130 | 23:00 | 125 | 12:00
Juldah | 140 | 18:00 | 136 | 11:00 | Sylhet | 133 | 03:00 | 130 | 11:00
Kabirpur | 140 | 13:00 | 128 | 11:00 | Sylhet-132 | 132 | 04:00 | 130 | 10:00
Kachua | 139 | 18:00 | 135 | 10:00 | Tangail | 130 | 13:00 | 124 | 01:00
Kaliakoir | 142 | 18:00 | 136 | 01:00 | Taraganj | 135 | 01:00 | 127 | 09:00
Kallyanpur | 141 | 18:00 | 138 | 10:00 | Tasnim | 138 | 05:00 | 134 | 11:00
Kalurghat | 140 | 18:00 | 136 | 11:00 | Thakurgaon | 136 | 19:00 | 125 | 01:00
Kamrangirchar | 136 | 04:00 | 131 | 11:00 | TK | 140 | 20:00 | 136 | 11:00
Kaptai | 141 | 19:00 | 138 | 14:00 | Tongi | 137 | 01:00 | 131 | 13:00
Kasba | 139 | 04:00 | 135 | 10:00 | Ullahpara | 139 | 03:00 | 133 | 09:00
Kazla | 140 | 04:00 | 136 | 11:00 | Ullon | 136 | 08:00 | 129 | 11:00
Keranigonj | 136 | 04:00 | 132 | 11:00 | Uttara | 134 | 04:00 | 129 | 11:00
Khagrachori | 138 | 03:00 | 135 | 11:00 | UttaraNew | 140 | 04:00 | 134 | 11:00
Khulna | 136 | 04:00 | 130 | 12:00 | Zigatola | 137 | 05:00 | 131 | 11:00
Khulna(S) | 138 | 04:00 | 131 | 08:00
Khulshi | 138 | 18:00 | 134 | 11:00
Kishoreganj | 135 | 03:00 | 130 | 11:00
Kodda | 138 | 18:00 | 133 | 11:00
KSRM | 140 | 18:30 | 135 | 11:00
Kulaura | 139 | 05:00 | 136 | 11:00
Kurigram | 131 | 22:00 | 122 | 09:00
Kushtia | 137 | 03:00 | 129 | 09:00
Laksam | 140 | 18:00 | 135 | 11:00
Lakshmipur | 136 | 04:00 | 132 | 11:00
Lalbag | 137 | 13:00 | 134 | 00:00
Lalmonirhat | 130 | 17:00 | 120 | 09:00
Madanganj | 139 | 18:30 | 135 | 00:00
Madaripur | 142 | 04:00 | 138 | 11:00
Madartek | 134 | 03:00 | 129 | 13:00
Madunaghat | 140 | 18:00 | 137 | 00:00
Magura | 139 | 03:00 | 130 | 08:00
Mahasthangarh | 137 | 03:00 | 131 | 09:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division