## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 25-01-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-01-2026 | during | 25-01-2026 | during | 25-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 328 | 326 | 412 | 412 | 392 | 392 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 30 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 335 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 16.5 | 33.7 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 38 | 64 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 28 | 24.75 | 24.75 | 33 | 33 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 15 | 22 | 22 | 15.1 | 15.1 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 75 | 195 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 51 | 80 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 20 | 51 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 45 | 86 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 0 | 0 | 29 | 0 | 29 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 0 | 55 | 55 | 55 | 55 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 360 | 395 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 90 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1359.5 | 1823.7 | 5350.1 | 5321.1 | 2646.32 | 2617.32
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 24 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 46 | 46 | 46 | 46 | 46 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 187 | 187 | 150 | 150 | 150 | 150 | Plant availability less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 20 | 49 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 8 | 8 | 8 | 8 | 16 | 16 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 16 | 34 | 34 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 36 | 50 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 10 | 19 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 30 | 62 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.29 | 0 | 3.22 | 0 | 3.22 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 16 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 35 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 67 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 51 | 51 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 7 | 65 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 16 | 87 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1224 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 1 | 14 | 1 | 14 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 415 | 415 | 415 | 415 | 355 | 355 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2081.29 | 2403 | 3137.08 | 3146.86 | 2768.08 | 2777.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 204 | 152 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 280 | 280 | 353.35 | 353.35 | 353.35 | 353.35
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 215 | 215 | 393 | 393 | 250 | 250 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 10 | 10 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 0 | 0 | 51 | 51 | 51 | 51 | Gas shortage
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 7 | 30 | 42 | 42 | 42 | 42 | Machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 102 | 105 | 163 | 163 | 115 | 115 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 19 | 100 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 126 | 126 | 84 | 76 | 144 | 144 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 13 | 24.5 | 24.5 | 24.5 | 24.5 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 2 | 48 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 1 | 50 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 65 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1032 | 1144 | 2432.75 | 2364.75 | 1875.05 | 1815.05
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-01-2026 | during | 25-01-2026 | during | 25-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 63 | 34 | 157.5 | 157.5 | 50 | 50 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 18 | 20 | 20 | 20 | 20 | Fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 35 | 59 | 60 | 60 | 60 | 60 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 35.5 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 12 | 22 | 22 | 12 | 12 | Fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 175.5 | 140 | 358.1 | 314 | 240.6 | 196.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 30 | 0 | 0 | 42 | 42 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 20 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 153 | 161 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 80 | 83 | 83 | 83 | 83
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 20 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 320 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 706 | 761 | 742 | 742 | 734 | 734
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 474 | 473 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 10 | 30 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 37 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 230 | 230 | 410 | 410 | 369 | 369 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 35 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 0 | 0 | 77 | 0 | 77 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1119 | 1130 | 1148.28 | 1148.28 | 1148 | 1148 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1833 | 1900 | 3497.28 | 3420.28 | 2701.1 | 2659
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 32 | 47 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 130 | 130 | 130 | 130 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 556 | 622 | 622 | 622 | 622 | 622 | -
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 54 | 150 | 150 | 150 | 150 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 276 | 307 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.52 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1231.52 | 1380 | 1540 | 1539 | 1526 | 1525
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 41.92 | 0 | 43 | 0 | 43 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 31 | 40 | 40 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 0 | 32 | 32
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 181 | 214 | 214 | 214 | 192.6 | 192.6 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 0 | 0 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 12 | 28 | 28 | 28 | 28 | Machine problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 1 | 70 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 15 | 70 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.49 | 0 | 4.6 | 0 | 4.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 764 | 759 | 748 | 748 | 748 | 748 | U#1 Under AOH
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 54.8 | 0 | 53 | 0 | 53 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 76 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1560.21 | 1595 | 2394.59 | 2193.99 | 1526.4 | 1325.8
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 56 | 56 | 55 | 55 | 58 | 58 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.2 | 0 | 4.8 | 0 | 4.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 133 | 0 | 142 | 0 | 142 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 293.2 | 196 | 491.8 | 317 | 460.8 | 286
System Total |  |  |  |  | 28823.2 | 28382.248 | 10272.22 | 11342.7 | 19943.7 | 19358.98 | 14478.35 | 13936.53
Forecast Scenario (25-01-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9640 |  | 0 |  | 9640
|  |  |  | 1:00 | 8930 |  | 0 |  | 8930
|  |  |  | 2:00 | 8480 |  | 0 |  | 8480
|  |  |  | 3:00 | 8160 |  | 0 |  | 8160
|  |  |  | 4:00 | 7930 |  | 0 |  | 7930
|  |  |  | 5:00 | 8000 |  | 0 |  | 8000
|  |  |  | 6:00 | 8410 |  | 0 |  | 8410
|  |  |  | 7:00 | 9110 |  | 0 |  | 9110
|  |  |  | 8:00 | 10400 |  | 0 |  | 10400
|  |  |  | 9:00 | 10730 |  | 0 |  | 10730
|  |  |  | 10:00 | 10340 |  | 0 |  | 10340
|  |  |  | 11:00 | 10460 |  | 0 |  | 10460
|  |  |  | 12:00 | 10900 |  | 0 |  | 10900
|  |  |  | 13:00 | 11250 |  | 0 |  | 11250
|  |  |  | 14:00 | 10860 |  | 0 |  | 10860
|  |  |  | 15:00 | 10410 |  | 0 |  | 10410
|  |  |  | 16:00 | 10090 |  | 0 |  | 10090
|  |  |  | 17:00 | 10220 |  | 0 |  | 10220
|  |  |  | 18:00 | 11120 |  | 0 |  | 11120
|  |  |  | 18:30 | 11200 |  | 0 |  | 11200
|  |  |  | 19:00 | 11390 |  | 0 |  | 11390
|  |  |  | 19:30 | 11510 |  | 0 |  | 11510
|  |  |  | 20:00 | 11530 |  | 0 |  | 11530
|  |  |  | 21:00 | 11310 |  | 0 |  | 11310
|  |  |  | 22:00 | 10880 |  | 0 |  | 10880
|  |  |  | 23:00 | 10240 |  | 0 |  | 10240
Probable Maximum Temperature: |  |  | 26.70°C
Probable Maximum Demand at Day Peak: |  |  | 10900.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11530.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11530.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 240.79 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:02 hrs on 25-01-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 24-01-2026 | [28 empty] | Date: | 24-01-2026 | [28 empty] | Date: | 24-01-2026 | [28 empty] | Date: | 24-01-2026 | [28 empty] | Date: | 24-01-2026 | [17 empty] | Date: | 24-01-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 42 | 155 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1170 | 0 | 0 | 0 | 255 | 280 | 0 | 0 | 0 | 225 | 0 | 0 | 106 | 17 | 0 | 13 | 0 | 100 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 160 | 0 | 21 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 16 | 0 | 50 | 0 | 0 | 0 | 4511 | 473 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1132 | 0 | 0 | 0 | 759.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 560 | 0 | 4381.7 | 8892.7 | 95.89
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 42 | 155 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1015 | 0 | 0 | 0 | 255 | 280 | 0 | 0 | 0 | 219 | 0 | 0 | 105 | 0 | 0 | 12 | 0 | 92 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 144 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 101 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 4212 | 473 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1027 | 0 | 0 | 0 | 757.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 130 | 220 | 0 | 0 | 500 | 0 | 4145.86 | 8357.86 | 95.88
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 42 | 155 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1005 | 0 | 0 | 0 | 255 | 280 | 0 | 0 | 0 | 218 | 0 | 0 | 105 | 0 | 0 | 11 | 0 | 82 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 0 | 143 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 101 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 4201 | 473 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 842 | 0 | 0 | 0 | 694.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 130 | 220 | 0 | 0 | 440 | 0 | 3825.91 | 8026.91 | 95.88
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 42 | 155 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 910 | 0 | 0 | 0 | 255 | 280 | 0 | 0 | 0 | 216 | 0 | 0 | 105 | 0 | 0 | 11 | 0 | 82 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 142 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 101 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 4075 | 474 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 793 | 0 | 0 | 0 | 531.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 130 | 220 | 0 | 0 | 380 | 0 | 3538.7 | 7613.7 | 95.88
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 42 | 155 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 870 | 0 | 0 | 0 | 255 | 280 | 0 | 0 | 0 | 213 | 0 | 0 | 105 | 0 | 0 | 11 | 0 | 76 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 144 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 4093 | 473 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 804 | 0 | 0 | 0 | 425.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 130 | 220 | 0 | 0 | 320 | 0 | 3381.71 | 7474.71 | 95.87
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 42 | 155 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 845 | 0 | 0 | 0 | 255 | 280 | 0 | 0 | 0 | 218 | 0 | 0 | 105 | 0 | 0 | 11 | 0 | 82 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 144 | 0 | 17 | 0 | 42 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 4061 | 474 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802 | 0 | 0 | 0 | 428.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 130 | 220 | 0 | 0 | 300 | 0 | 3358.38 | 7419.38 | 95.87
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 42 | 155 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1021 | 0 | 0 | 0 | 255 | 280 | 0 | 0 | 0 | 221 | 0 | 0 | 108 | 0 | 0 | 11 | 0 | 92 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 150 | 0 | 17 | 0 | 60 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 4286 | 474 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 827 | 0 | 0 | 0 | 561.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224 | 130 | 220 | 0 | 0 | 310 | 0 | 3572.17 | 7858.17 | 95.87
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 300 | 0 | 0 | 1 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0.1 | 86 | 0 | 25 | 155 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1170 | 1 | 0 | 0 | 265 | 280 | 0 | 0 | 0 | 220 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 86 | 0 | 2 | 0 | 310 | 0 | 0 | 0 | 0 | 157 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 100 | 0 | 0.79 | 0 | 4430.89 | 473 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1038 | 0 | 0 | 0 | 741.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52 | 0 | 0 | 0 | 0.61 | 186 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.06 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.01 | 0 | 282 | 100 | 180 | 0 | 0 | 395 | 0 | 4093.08 | 8523.97 | 95.86
08:00 | 0 | 12 | 16 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 10 | 0 | 40 | 16 | 95 | 4 | 5 | 49 | 0 | 0 | 0 | 370 | 0 | 17 | 300 | 0 | 0 | 5 | 52 | 16 | 22 | 0 | 0 | 8 | 30 | 0 | 0 | 2 | 0 | 0 | 6 | 36 | 25 | 0.4 | 86 | 5 | 8 | 155 | 52 | 0 | 5 | 1 | 18 | 185 | 0 | 0 | 0 | 1160 | 6 | 0 | 0 | 260 | 280 | 0 | 0 | 0 | 217 | 0 | 0 | 109 | 14 | 0 | 11 | 0 | 110 | 0 | 17 | 0 | 320 | 0 | 0 | 0 | 0 | 154 | 2 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 1 | 35 | 19 | 71 | 0 | 8.57 | 1 | 5005.97 | 473 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 1130 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 20 | 13 | 0 | 0 | 0 | 6 | 7.5 | 0 | 0 | 0 | 8.02 | 177 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0.78 | 0 | 56 | 30 | 5 | 34 | 0 | 0 | 0 | 0.9 | 26 | 0.1 | 0.76 | 279 | 100 | 220 | 0 | 0 | 472 | 0 | 4430.06 | 9436.03 | 95.86
09:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 15 | 0 | 52 | 32 | 45 | 15 | 17 | 54 | 0 | 0 | 0 | 349 | 0 | 17 | 300 | 0 | 0 | 0 | 35 | 23 | 22 | 0 | 0 | 28 | 15 | 7 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 1.05 | 86 | 33 | 7 | 155 | 17 | 0 | 19 | 2 | 32 | 185 | 0 | 0 | 0 | 1174 | 12 | 0 | 0 | 260 | 280 | 0 | 0 | 0 | 206 | 0 | 13 | 106 | 17 | 0 | 11 | 0 | 108 | 0 | 35 | 0 | 300 | 0 | 0 | 0 | 0 | 136 | 6 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 17 | 35 | 19 | 70 | 1 | 20.74 | 6 | 4976.79 | 473 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1116 | 0 | 0 | 0 | 762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 20.33 | 0 | 0 | 0 | 22.58 | 169 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 2.02 | 0 | 56 | 35 | 13 | 34 | 0 | 0 | 0 | 2.3 | 66 | 0.11 | 31 | 278 | 130 | 180 | 0 | 0 | 530 | 16 | 4542.34 | 9519.13 | 95.86
10:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 15.7 | 0 | 52 | 32 | 45 | 15 | 17 | 17 | 0 | 0 | 0 | 345 | 0 | 17 | 300 | 0 | 0 | 0 | 35 | 24 | 15 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 2.64 | 86 | 17 | 3 | 210 | 14 | 0 | 19 | 8 | 17 | 186 | 0 | 0 | 0 | 1145 | 17 | 0 | 0 | 215 | 280 | 0 | 0 | 0 | 212 | 0 | 0 | 105 | 17 | 0 | 11 | 0 | 118 | 0 | 50 | 8 | 305 | 0 | 0 | 0 | 0 | 139 | 9 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 17 | 35 | 19 | 62 | 0 | 31.8 | 6 | 4914.14 | 473 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1118 | 0 | 0 | 0 | 764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 30.9 | 0 | 0 | 0 | 35.54 | 174 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 3.11 | 0 | 56 | 35 | 22 | 34 | 0 | 0 | 0 | 3.8 | 100 | 0.29 | 32 | 271 | 130 | 220 | 0 | 0 | 560 | 0 | 4633.64 | 9547.78 | 95.85
11:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 15 | 17 | 51 | 32 | 45 | 15 | 0 | 15 | 0 | 0 | 0 | 340 | 0 | 0 | 250 | 0 | 0 | 0 | 35 | 29 | 22 | 0 | 0 | 0 | 15 | 30 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 3.15 | 86 | 14 | 6 | 355 | 15 | 0 | 19 | 8 | 15 | 187 | 0 | 0 | 0 | 1160 | 19 | 0 | 0 | 215 | 280 | 0 | 0 | 0 | 207 | 0 | 0 | 102 | 16 | 0 | 11 | 0 | 118 | 0 | 60 | 7 | 310 | 0 | 0 | 0 | 0 | 137 | 11 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 17 | 35 | 19 | 62 | 0 | 38.01 | 6 | 5028.16 | 474 | 231 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1115 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 35.35 | 73 | 0 | 0 | 44.49 | 172 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 3.91 | 0 | 56 | 35 | 28 | 34 | 0 | 0 | 0 | 4.7 | 126 | 0.48 | 32 | 276 | 130 | 180 | 0 | 0 | 560 | 0 | 4724.93 | 9753.09 | 95.85
12:00 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 16.5 | 17 | 51 | 38 | 75 | 15 | 0 | 45 | 0 | 0 | 0 | 360 | 0 | 0 | 300 | 0 | 0 | 0 | 35 | 21 | 22 | 0 | 0 | 7 | 15 | 30 | 0 | 0 | 0 | 8 | 0 | 36 | 25 | 3.29 | 86 | 17 | 10 | 415 | 16 | 0 | 19 | 8 | 20 | 187 | 0 | 0 | 0 | 1160 | 19 | 0 | 0 | 215 | 280 | 0 | 0 | 0 | 204 | 0 | 1 | 102 | 19 | 0 | 11 | 2 | 126 | 0 | 65 | 7 | 315 | 0 | 0 | 0 | 0 | 153 | 11 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 17 | 35 | 19 | 63 | 0 | 35.5 | 6 | 5354.29 | 474 | 230 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1119 | 0 | 0 | 0 | 764 | 0 | 0 | 0 | 15 | 1 | 0 | 0 | 0 | 8 | 41.92 | 76 | 0 | 0 | 54.8 | 181 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.49 | 0 | 56 | 35 | 30 | 34 | 0 | 0 | 0 | 5.2 | 133 | 0.52 | 32 | 276 | 130 | 220 | 0 | 0 | 556 | 17 | 4917.93 | 10272.22 | 95.84
13:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 16.5 | 17 | 51 | 48 | 95 | 15 | 0 | 52 | 0 | 0 | 0 | 385 | 0 | 0 | 300 | 0 | 0 | 0 | 35 | 29 | 21 | 0 | 0 | 31 | 15 | 32 | 0 | 0 | 16 | 8 | 15 | 36 | 25 | 3.2 | 86 | 33 | 18 | 415 | 14 | 0 | 19 | 8 | 33 | 187 | 0 | 0 | 0 | 1160 | 19 | 0 | 0 | 215 | 280 | 0 | 0 | 0 | 192 | 0 | 25 | 100 | 50 | 0 | 11 | 33 | 136 | 0 | 61 | 7 | 330 | 0 | 0 | 0 | 0 | 162 | 10 | 20 | 0 | 80 | 30 | 0 | 0 | 100 | 17 | 35 | 19 | 32 | 0 | 36.1 | 6 | 5607.8 | 474 | 229 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 0 | 0 | 769 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 8 | 43.3 | 78 | 0 | 0 | 53.8 | 183 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.93 | 0 | 55 | 35 | 30 | 34 | 0 | 0 | 0 | 5.1 | 133 | 0.48 | 32 | 282 | 130 | 220 | 0 | 0 | 555 | 17 | 4977.61 | 10585.41 | 95.84
14:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 15.7 | 17 | 51 | 48 | 30 | 15 | 0 | 52 | 0 | 0 | 0 | 375 | 0 | 17 | 300 | 0 | 0 | 0 | 17 | 29 | 21 | 0 | 0 | 15 | 15 | 19 | 0 | 0 | 16 | 8 | 0 | 12 | 25 | 2.7 | 86 | 28 | 8 | 415 | 0 | 0 | 19 | 0 | 31 | 187 | 0 | 0 | 0 | 1160 | 18 | 0 | 0 | 215 | 280 | 0 | 0 | 0 | 183 | 0 | 30 | 100 | 50 | 0 | 13 | 17 | 130 | 0 | 52 | 7 | 315 | 0 | 0 | 0 | 0 | 159 | 8 | 20 | 0 | 80 | 30 | 0 | 0 | 100 | 17 | 35 | 19 | 32 | 0 | 32.78 | 6 | 5355.18 | 474 | 230 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1109 | 0 | 0 | 0 | 763 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 39.64 | 67 | 0 | 0 | 43.34 | 188 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.2 | 0 | 55 | 35 | 26 | 34 | 0 | 0 | 0 | 4.4 | 111 | 0.41 | 16 | 279 | 130 | 220 | 0 | 0 | 555 | 17 | 4894.99 | 10250.17 | 95.83
15:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 15.7 | 17 | 51 | 48 | 30 | 15 | 0 | 50 | 0 | 0 | 0 | 370 | 0 | 35 | 300 | 0 | 0 | 0 | 17 | 29 | 21 | 0 | 0 | 15 | 15 | 12 | 0 | 0 | 16 | 8 | 0 | 12 | 25 | 2.03 | 86 | 29 | 6 | 415 | 0 | 0 | 19 | 0 | 16 | 187 | 0 | 0 | 0 | 1160 | 14 | 0 | 0 | 215 | 280 | 0 | 0 | 0 | 179 | 0 | 16 | 100 | 17 | 0 | 13 | 17 | 128 | 0 | 36 | 7 | 315 | 0 | 0 | 0 | 0 | 155 | 6 | 20 | 0 | 80 | 30 | 0 | 0 | 99 | 17 | 35 | 19 | 34 | 1 | 23.87 | 6 | 5251.6 | 474 | 230 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1108 | 0 | 0 | 0 | 767 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 24.07 | 49 | 0 | 0 | 30.61 | 178 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 2.88 | 0 | 55 | 35 | 17 | 34 | 0 | 0 | 0 | 3.1 | 83 | 0.39 | 16 | 276 | 130 | 220 | 0 | 0 | 555 | 17 | 4736.05 | 9987.65 | 95.83
16:00 | 0 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 15.4 | 17 | 51 | 64 | 30 | 15 | 0 | 15 | 0 | 0 | 0 | 360 | 0 | 35 | 300 | 0 | 0 | 0 | 17 | 29 | 20 | 0 | 0 | 15 | 15 | 12 | 0 | 0 | 16 | 8 | 0 | 12 | 25 | 1.07 | 86 | 28 | 7 | 415 | 0 | 0 | 19 | 0 | 15 | 187 | 0 | 0 | 0 | 1160 | 8 | 0 | 0 | 215 | 280 | 0 | 5 | 0 | 176 | 0 | 16 | 100 | 15 | 0 | 13 | 0 | 124 | 0 | 18 | 7 | 310 | 0 | 0 | 0 | 0 | 148 | 3 | 20 | 0 | 80 | 30 | 0 | 0 | 98 | 17 | 35 | 19 | 34 | 0 | 12.12 | 6 | 5131.59 | 473 | 230 | 0 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 1080 | 0 | 0 | 0 | 759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.14 | 23 | 0 | 0 | 12.78 | 173 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 1.48 | 0 | 55 | 0 | 9 | 0 | 0 | 0 | 0 | 1.9 | 43 | 0.16 | 16 | 279 | 130 | 220 | 0 | 0 | 555 | 17 | 4488.46 | 9620.05 | 95.82
17:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 26 | 0 | 68 | 64 | 105 | 15 | 17 | 81 | 0 | 0 | 0 | 378 | 0 | 35 | 300 | 0 | 0 | 0 | 52 | 27 | 17 | 0 | 0 | 16 | 15 | 12 | 0 | 0 | 16 | 8 | 4 | 40 | 25 | 0.15 | 86 | 33 | 11 | 415 | 30 | 0 | 20 | 1 | 21 | 187 | 0 | 0 | 0 | 1160 | 2 | 0 | 0 | 215 | 280 | 0 | 0 | 0 | 173 | 0 | 18 | 102 | 23 | 0 | 13 | 0 | 124 | 5 | 4 | 15 | 320 | 0 | 0 | 0 | 0 | 153 | 1 | 20 | 0 | 80 | 30 | 0 | 0 | 98 | 17 | 57 | 19 | 34 | 0 | 2.75 | 6 | 5424.9 | 473 | 230 | 0 | 13 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 1085 | 0 | 0 | 0 | 761 | 0 | 0 | 0 | 15 | 1 | 0 | 0 | 0 | 16 | 2.63 | 6 | 0 | 0 | 2.04 | 190 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0.19 | 0 | 56 | 17 | 2 | 18 | 0 | 0 | 0 | 0.3 | 10 | 0.54 | 16 | 273 | 130 | 180 | 0 | 0 | 555 | 17 | 4493.7 | 9918.6 | 95.82
18:00 | 0 | 46 | 19 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 34.4 | 0 | 78 | 64 | 195 | 22 | 35 | 83 | 0 | 0 | 0 | 370 | 0 | 35 | 335 | 0 | 0 | 0 | 90 | 29 | 16 | 0 | 0 | 57 | 32 | 17 | 0 | 0 | 16 | 8 | 34 | 50 | 25 | 0 | 86 | 63 | 16 | 415 | 86 | 0 | 25 | 0 | 49 | 187 | 0 | 0 | 0 | 1205 | 0 | 0 | 0 | 215 | 280 | 0 | 0 | 0 | 167 | 0 | 45 | 103 | 90 | 0 | 13 | 50 | 130 | 19 | 0 | 23 | 320 | 0 | 0 | 0 | 0 | 149 | 0 | 20 | 0 | 80 | 30 | 0 | 0 | 99 | 17 | 57 | 19 | 34 | 0 | 0 | 9 | 6025.4 | 473 | 230 | 0 | 30 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 0 | 0 | 757 | 0 | 0 | 0 | 50 | 45 | 0 | 0 | 0 | 25 | 0 | 0 | 6 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 70 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 307 | 130 | 220 | 0 | 0 | 545 | 37 | 4849 | 10874.4 | 95.81
19:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 30.8 | 0 | 80 | 64 | 195 | 30 | 35 | 81 | 0 | 0 | 0 | 405 | 0 | 35 | 335 | 0 | 0 | 0 | 90 | 28 | 15 | 0 | 0 | 60 | 16 | 44 | 0 | 0 | 16 | 8 | 35 | 50 | 25 | 0 | 86 | 68 | 18 | 415 | 86 | 0 | 26 | 2 | 48 | 187 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 215 | 280 | 0 | 0 | 0 | 162 | 0 | 47 | 105 | 97 | 0 | 13 | 47 | 128 | 25 | 0 | 25 | 315 | 0 | 0 | 0 | 0 | 149 | 0 | 20 | 0 | 80 | 30 | 0 | 0 | 99 | 17 | 56 | 19 | 34 | 0 | 0 | 12 | 6220.8 | 473 | 230 | 0 | 30 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 0 | 0 | 761 | 0 | 31 | 0 | 70 | 70 | 4 | 0 | 0 | 25 | 0 | 0 | 6 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 56 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 307 | 130 | 220 | 0 | 0 | 585 | 54 | 4999 | 11219.8 | 95.8
19:30 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 34 | 0 | 80 | 64 | 195 | 30 | 35 | 86 | 0 | 0 | 0 | 400 | 0 | 35 | 335 | 0 | 0 | 0 | 90 | 28 | 15 | 0 | 0 | 60 | 16 | 55 | 0 | 0 | 16 | 8 | 35 | 50 | 25 | 0 | 46 | 68 | 19 | 415 | 86 | 0 | 26 | 8 | 49 | 187 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 215 | 280 | 0 | 0 | 0 | 161 | 0 | 51 | 105 | 99 | 0 | 13 | 51 | 122 | 25 | 0 | 30 | 320 | 0 | 0 | 20 | 0 | 160 | 0 | 20 | 0 | 80 | 30 | 0 | 0 | 100 | 17 | 59 | 19 | 34 | 0 | 0 | 12 | 6245 | 473 | 230 | 0 | 30 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1108 | 0 | 0 | 0 | 757 | 0 | 31 | 0 | 70 | 70 | 0 | 0 | 0 | 25 | 0 | 0 | 6 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 56 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 307 | 130 | 220 | 0 | 0 | 610 | 54 | 5026 | 11271
20:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 33.7 | 0 | 80 | 64 | 195 | 30 | 35 | 86 | 0 | 0 | 0 | 395 | 0 | 35 | 335 | 0 | 0 | 0 | 90 | 28 | 15 | 0 | 0 | 65 | 16 | 62 | 0 | 0 | 16 | 8 | 35 | 50 | 25 | 0 | 46 | 67 | 19 | 415 | 87 | 0 | 24 | 8 | 49 | 187 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 215 | 280 | 0 | 0 | 0 | 152 | 0 | 50 | 105 | 100 | 0 | 13 | 48 | 126 | 25 | 0 | 30 | 320 | 0 | 0 | 30 | 20 | 161 | 0 | 20 | 0 | 80 | 30 | 0 | 0 | 100 | 17 | 59 | 18 | 34 | 0 | 0 | 12 | 6271.7 | 473 | 230 | 0 | 30 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1130 | 0 | 0 | 0 | 759 | 0 | 31 | 0 | 70 | 70 | 0 | 0 | 0 | 25 | 0 | 0 | 12 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 56 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 307 | 130 | 220 | 0 | 0 | 622 | 54 | 5071 | 11342.7 | 95.79
21:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 80 | 64 | 195 | 30 | 35 | 82 | 0 | 0 | 0 | 370 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 20 | 18 | 0 | 0 | 63 | 16 | 63 | 0 | 1 | 16 | 8 | 35 | 50 | 25 | 0 | 46 | 66 | 32 | 415 | 76 | 0 | 26 | 8 | 48 | 186 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 215 | 280 | 0 | 0 | 0 | 148 | 0 | 49 | 105 | 96 | 0 | 13 | 50 | 120 | 25 | 0 | 22 | 315 | 0 | 0 | 30 | 20 | 157 | 0 | 20 | 0 | 80 | 30 | 0 | 0 | 100 | 17 | 59 | 18 | 34 | 0 | 0 | 12 | 6141 | 474 | 230 | 0 | 30 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1118 | 0 | 0 | 0 | 759 | 0 | 31 | 0 | 70 | 70 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 307 | 130 | 220 | 0 | 0 | 622 | 54 | 5045 | 11186 | 95.78
22:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 75 | 16 | 145 | 30 | 35 | 72 | 0 | 0 | 0 | 345 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 20 | 17 | 0 | 0 | 45 | 16 | 52 | 0 | 0 | 16 | 8 | 17 | 50 | 25 | 0 | 46 | 51 | 35 | 415 | 68 | 0 | 26 | 8 | 47 | 186 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 215 | 280 | 0 | 0 | 0 | 143 | 0 | 40 | 106 | 96 | 0 | 13 | 44 | 118 | 8 | 0 | 15 | 310 | 0 | 0 | 30 | 20 | 156 | 0 | 20 | 0 | 80 | 30 | 0 | 0 | 100 | 17 | 59 | 18 | 34 | 0 | 0 | 9 | 5859 | 474 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1116 | 0 | 0 | 0 | 766 | 0 | 31 | 0 | 50 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 70 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 307 | 130 | 220 | 0 | 0 | 622 | 54 | 4898 | 10757 | 95.77
23:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 62 | 0 | 145 | 30 | 17 | 62 | 0 | 0 | 0 | 335 | 0 | 0 | 335 | 0 | 0 | 0 | 34 | 14.5 | 17 | 0 | 0 | 45 | 16 | 0 | 0 | 0 | 0 | 8 | 17 | 50 | 25 | 0 | 46 | 51 | 36 | 415 | 17 | 0 | 26 | 0 | 48 | 186 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 215 | 280 | 0 | 0 | 0 | 147 | 0 | 16 | 106 | 98 | 0 | 10 | 21 | 116 | 0 | 0 | 16 | 310 | 0 | 0 | 30 | 20 | 156 | 0 | 20 | 0 | 80 | 30 | 0 | 0 | 100 | 17 | 58 | 18 | 29 | 0 | 0 | 11 | 5450.5 | 473 | 218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1118 | 0 | 0 | 0 | 761 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 54 | 70 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 278 | 130 | 220 | 0 | 0 | 622 | 54 | 4799 | 10249.5 | 95.76
Total KWH | 0 | 547200 | 300480 | 0 | 0 | 0 | 0 | 0 | 7732800 | 0 | 0 | 259560 | 111960 | 1063440 | 726240 | 1770916 | 335157 | 266111 | 889920 | 0 | 0 | 0 | 8910958 | 0 | 270218 | 7366485 | 0 | 0 | 8438 | 786000 | 444000 | 447840 | 0 | 0 | 541964 | 333709 | 428160 | 0 | 44160 | 154013 | 111360 | 274833 | 511680 | 339840 | 20043 | 1867380 | 741000 | 554400 | 7236363.64 | 545309 | 0 | 358080 | 82542.6 | 593818 | 4401879 | 0 | 0 | 0 | 26885452 | 133785 | 0 | 0 | 5636500 | 7082800 | 0 | 12114 | 0 | 4715000 | 0 | 414720 | 2496036 | 969120 | 0 | 316600 | 344280 | 2633280 | 129878 | 399155 | 200768 | 7671000 | 0 | 0 | 116000 | 76080 | 3605564 | 67721 | 471432 | 0 | 1822080 | 717792 | 0 | 0 | 2407380 | 284040 | 769200 | 309600 | 1201920 | 3250 | 241440 | 135360 | 123647604.24 | 11440000 | 5516928 | 0 | 176640 | 165888 | 0 | 0 | 0 | 0 | 0 | 0 | 43200 | 25018200 | 0 | 0 | 0 | 17087909 | 0 | 120956 | 0 | 636288 | 656448 | 6359 | 6256 | 0 | 174806 | 249732 | 357990 | 15585 | 0 | 314992 | 4597909 | 0 | 0 | 0 | 0 | 0 | 9310400 | 0 | 27120 | 0 | 1304727 | 813889 | 183495 | 714576 | 0 | 0 | 0 | 31542.84 | 836640 | 2896 | 532704 | 6414000 | 3078000 | 5490080 | 0 | 0 | 12753454.55 | 439200 | 108518810.39 | 232166414.63

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 24-01-2026
Power Supply Scenario
| Day Peak Generation |  |  | 10272.22 | MW | 12:00 Hr. | Energy Generated |  |  | 232.1664 |  | MKWHr.
| Day Peak Demand |  |  | 10272.22 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.996 |  | MKWHr.
| Evening Peak Generation |  |  | 11342.7 | MW | 20:00 Hr. | Energy Demand |  |  | 233.1624 |  | MKWHr.
| Evening Peak Demand |  |  | 11548.97 | MW | 19:30 Hr. | Maximum Temperature |  |  | 26.3 |  | °C
| Minimum Generation of the Day |  |  | 7419.38 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 709.62 |  | MMCFD
| Maximum Generation of the Day |  |  | 11342.7 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 6.2703 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 24.9021 | 0 | 7.3272 | 0 | 0 | 0.008438 | 0 | 0 | 32.2377 | Gas | 96.2 | Gas | 335593377.35
| Chattogram Zone |  |  | 4.9563 | 34.1218 | 5.0163 | 0 | 1.8674 | 0.15383 | 0 | 0.04416 | 46.1598 | Coal | 79.6122 | Coal | 521484252.7582
| Cumilla Zone |  |  | 20.259 | 0 | 2.0588 | 0 | 0 | 0.39915 | 2.6333 | 0 | 25.3503 | HFO | 20.3601 | HFO | 362411132.712
| Mymensingh Zone |  |  | 1.2019 | 0 | 1.4982 | 0 | 0 | 0.24469 | 0 | 0 | 2.9448 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 16.8873 | 0 | 0 | 0 | 0 | 0.067721 | 0 | 0 | 16.955 | Hydro | 1.8674 | Hydro | 186738
| Khulna Zone |  |  | 5.5169 | 25.0182 | 0.34253 | 0 | 0 | 0.0432 | 11.44 | 0 | 42.3609 | Solar | 2.9214 | Solar | 45252219.958
| Barishal Zone |  |  | 8.5681 | 19.1675 | 0.9719 | 0 | 0 | 0.002896 | 0 | 0 | 28.7103 | Import | 31.1612 | Import | 190176004.76
| Rajshahi Zone |  |  | 13.9083 | 0 | 1.6167 | 0 | 0 | 0.94983 | 17.0879 | 0 | 33.5628 | Wind | 0.04416 | Wind | 649593.6
| Rangpur Zone |  |  | 0 | 1.3047 | 1.5285 | 0 | 0 | 1.0517 | 0 | 0 | 3.8849
| Total |  |  | 96.2 | 79.6122 | 20.3601 | 0 | 1.8674 | 2.9214 | 31.1612 | 0.04416 | 232.1664
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 335593377.35 |  | Hydro | 186738
|  |  |  | Coal | 521484252.7582 |  | Solar | 45252219.958
|  |  |  | HFO | 362411132.712 |  | Import | 190176004.76
|  |  |  | HSD | 0 |  | Wind | 649593.6
[5 empty] | Total: | 145,57,53,319 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 11.44 | Peak Hr Flow | 473.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 6996328.03 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 17.0879 | Peak Hr Flow | 759.00 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1667 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.6333 | Peak Hr Flow | 126.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2015 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 31.1612 | Peak Hr Flow | 1358.00 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4092
|  |  |  | Chattogram |  | 0 |  | 1208
|  |  |  | Cumilla |  | 0 |  | 990
|  |  |  | Mymensingh |  | 31 |  | 966
|  |  |  | Sylhet |  | 0 |  | 405
|  |  |  | Khulna |  | 70 |  | 1267
|  |  |  | Barishal |  | 0 |  | 336
|  |  |  | Rajshahi |  | 40 |  | 1041
|  |  |  | Rangpur |  | 10 |  | 710
|  |  |  | Total |  | 151 |  | 11015
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 51 MW PP (Midland) |  |  | 51
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 51
|  |  |  | Total Unavailable Capacity |  |  |  | 351
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:02 | 16:37 | Tongi 230/132/33kV S/S T-1 HT Tripped showing REF Opdr LV relays Due to Trip | [7 empty] | 24.0MW load
interrup.
| 08:14 | 18:24 | Kabirpur 132/33kV S/S XFR, T-2 HT Scheduled S/D Due to 33 kV Bus Maintenance Work by | [7 empty] | 55.0MW load
|  |  | DPBS-1 | [7 empty] | interrup.
| 08:14 | 18:26 | Kabirpur 132/33kV S/S XFR, T-2 LT Scheduled S/D Due to 33 kV Bus Maintenance Work by | [7 empty] | 55.0MW load
|  |  | DPBS-1 | [7 empty] | interrup.
| 08:15 | 14:48 | Mongla 132/33kV S/S T-1 LT Scheduled S/D Due to Annual maintenances work | [7 empty] | 22.0MW load
interrup.
| 08:15 | 14:46 | Mongla 132/33kV S/S T-1 HT Scheduled S/D Due to Annual maintenances work | [7 empty] | 22.0MW load
interrup.
| 08:15 | 14:48 | Mongla 132/33kV S/S T-2 LT Scheduled S/D Due to Annual maintenances work | [7 empty] | 22.0MW load
interrup.
| 08:16 | 14:46 | Mongla 132/33kV S/S T-2 HT Scheduled S/D Due to Annual maintenances work | [7 empty] | 22.0MW load
interrup.
| 08:16 | 16:33 | Fenchuganj-Sreemangal 132kV Ckt-2 Scheduled S/D from Sreemongol 132/33kV end Due to Dead
Line checking at Fenchuganj End. and from Fenchuganj 230/132/33kV end Due to Deadline
Checking.
| 08:17 | 18:24 | Kabirpur 132/33kV S/S XFR, T-I HT Scheduled S/D Due to 33 kV Bus Maintenance Work by | [7 empty] | 55.0MW load
|  |  | DPBS-1 | [7 empty] | interrup.
| 08:17 | 18:25 | Kabirpur 132/33kV S/S XFR, T-I LT Scheduled S/D Due to 33 kV Bus Maintenance Work by | [7 empty] | 55.0MW load
|  |  | DPBS-1 | [7 empty] | interrup.
| 08:17 | 10:36 | Natore-Rajshahi 132kV Ckt-2 Scheduled S/D from Natore 132/33kV end.
| 08:24 | 17:30 | Ashuganj-Bhulta 400 kV Ckt-2 Scheduled S/D from Bhulta 400/230kV end Due to Annual
maintenance work
| 08:24 | 14:42 | Mongla 132/33kV S/S 100MW ERBL Solar PS Scheduled S/D Due to Annual maintenances work
| 08:24 | 14:40 | Bagerhat-Mongla 132 kV Ckt-1 Scheduled S/D from Mongla 132/33kV end Due to Annual
maintenances work
| 08:25 | 14:40 | Mongla 132/33kV S/S Main Bus Scheduled S/D Due to Annual maintenances work | [7 empty] | 22.0MW load
interrup.
| 08:27 | 08:31 | Kalurghat 132/33kV S/S TRFO-02(516T) HT Forced S/D | [7 empty] | 14.0MW load
interrup.
| 08:28 | 14:53 | Chandraghona 132/33kV S/S MAIN BUS-1 Scheduled S/D Due to Annual maintenance
| 08:29 | 14:14 | Agargaon 230/132kV S/S 132kV Transformer-2 (415T2) LT Scheduled S/D Due to Annual
Maintenance
| 08:30 | 14:09 | Agargaon 230/132kV S/S 132kV Transformer-2 (415T2) HT Scheduled S/D Due to Annual
Maintenance
| 08:33 | 14:35 | Bagerhat 132/33kV S/S 132 kV BUS Scheduled S/D Due to 132KV Bus Shutdown for annual | [7 empty] | 53.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 08:36 | 14:33 | Bagerhat-Goalpara 132 kV Ckt-1 Scheduled S/D from Goalpara 132/33kV end Due to For annual
Maintenance work
| 08:46 | 20:41 | BIPTC S/S Baharampur-3 Scheduled S/D Due to Annual maintenance
| 08:49 | 15:28 | Purbasadipur-Saidpur 132kV Ckt-2 Scheduled S/D from Saidpur 132/33kV end Due to Annual
Maintenance
| 08:50 | 17:02 | Rampal 400/230kV S/S Gopalganj Line-2 Reactor Scheduled S/D Due to Maintenance work at
Khulna-ALDC.
| 08:53 | 17:00 | Gopalganj 400/132kV S/S 400kV Rampal Ckt-2 Scheduled S/D
| 08:53 | 17:01 | Gopalganj(N)-Rampal Ckt-2 Scheduled S/D from Rampal 400/230kV end Due to Maintenance work
at Khulna-ALDC.
| 08:58 | 17:26 | KSRM 132/33kV S/S Transformer-01 HT Scheduled S/D Due to for DS Removal and LA
Modification work on the 33KV KBIL Phase-02 Feeder
| 09:01 | 15:25 | Cumilla(N)-Daudkandi 132 kV Ckt-1 Scheduled S/D from Daudkandi 132/33kV end Due to Annual
Maintenance work.
| 09:02 | 15:25 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Daudkandi Ckt-01 Scheduled S/D
| 09:03 | 17:37 | Kaliakoir 400/230/132kV S/S 400/132kV TR1 LT Scheduled S/D Due to Annual maintenance.
| 09:03 | 17:37 | Kaliakoir 400/230/132kV S/S 400/132kV TR1 HT Scheduled S/D Due to annual maintenance
| 09:11 | 15:54 | Faridpur-Gopalganj(N) 132 kV Ckt-1 Scheduled S/D from Faridpur 132/33kV end Due to Annual
maintenance and from Gopalganj 400/132kVend.
| 09:12 | 17:03 | Mymensingh RPCL-Tangail 132kV Ckt-1 Scheduled S/D from Muktagacha 132/33kV end Due to
Piling Work of RHD
| 09:13 | 15:55 | Faridpur-Gopalganj(N) 132 kV Ckt-2 Scheduled S/D from Gopalganj 400/132kV end. and from
Faridpur 132/33kV end Due to Annual maintenance
| 09:19 | 14:21 | Barishal 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to Wzpdcl annual maintenance work | [7 empty] | 10.0MW load
|  |  | at 33kv bus | [7 empty] | interrup.
| 09:20 | 14:20 | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to Wzpdcl annual maintenance work | [7 empty] | 10.0MW load
interrup.
| 09:27 | 13:59 | Jaldhaka 132/33kV S/S 416T-2 LT Scheduled S/D Due to annual maintenance of 33 KV Bus | [7 empty] | 20.0MW load
|  |  | section -02 & Bus section -03 related 33 KV Feeder of NESCO & PBS. | [7 empty] | interrup.
| 09:28 | 13:58 | Jaldhaka 132/33kV S/S 416T-2 HT Scheduled S/D Due to annual maintenance of 33 KV Bus | [7 empty] | 20.0MW load
|  |  | section -02 & Bus section -03 related 33 KV Feeder of NESCO & PBS | [7 empty] | interrup.
| 09:34 | 16:42 | Khulna (C) S/S North-WestCkt-1 Scheduled S/D Due to S/D by ALDC
| 09:47 |  | BSRM 230/33kV S/S 230/33 kV Transformer-3 (125/140 MVA) HT Scheduled S/D Due to Annual
Maintenance
| 09:55 | 14:59 | Chauddagram 132/33kV S/S 132 kv T-1 HT Scheduled S/D Due to Maintanance work
| 09:55 | 14:58 | Chauddagram 132/33kV S/S 132 kv T-1 LT Scheduled S/D Due to Maintanence work
| 09:57 |  | Chapai 132/33kV S/S T-3 (425T) HT Scheduled S/D Due to T3 -132 kv CB change
| 09:57 | 15:01 | Madunaghat 400/230kV S/S Madunaghat-Hathazari 230kV Ckt.-1 Scheduled S/D
|  | 10:04 | Fenchuganj -Sylhet 132kV Ckt-1 is restored.
|  | 10:08 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 is restored.
| 10:08 | 15:02 | Hathazari-Madunaghat 132kV Ckt-1 Scheduled S/D from Hathazari 230/132/33kV end Due to
Annual dead line Check
| 10:19 | 18:38 | Kabirpur -Tongi 132kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end. and from
Kabirpur 132/33kV end Due to Annual Maintenance (Deadline Checking)
| 10:21 | 17:06 | Monakasha-Rahanpur 400kV Ckt-1 Scheduled S/D from Rahanpur 400/132kV end Due to Annual
maintenance
| 10:42 |  | Bhola Nutan Biddut BD LTD record a general event:- NBBL GIS Outgoing Bus-2 CB(DTCB-2)
Opeened
| 10:52 | 20:32 | Lakshmipur 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Shutdown taken for change
the rusted 33kv Circuit breaker.
| 10:55 |  | Bhola Nutan Biddut BD LTD record a general event:- NBBL GIS Outgoing Bus-2 CB (DTCB-2)
Before And After DS Opened
| 10:58 | 20:29 | Lakshmipur 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Shutdown taken for change
the 33kv circuit breaker.
| 11:00 |  | Bhola Nutan Biddut BD LTD record a general event:- NBBL GIS Outgoing Bus-2 CB (DTCB-2)
Before And After Earth Switch Applied.
|  | 11:40 | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-2 is restored.
|  | 11:41 | Baghabari-Roppur 230kV Ckt-2 is restored.
| 12:00 |  | Day Peak Generation: 10268 MW.
| 12:02 | 19:20 | Sylhet-Sylhet (South) 132KV Ckt-2 Scheduled S/D from Sylhet 132/33kV end Due to OPGW
Replacement work by OFCN.
|  | 12:04 | Baghabari-Roppur 230kV Ckt-1 is restored.
| 13:33 |  | Sirajgonj 225MW CCPP Unit-1, FGMO is ON with remarks:- From 06:25 AM.
| 13:45 | 14:04 | Taraganj 132/33kV S/S Taraganj-Rangpur CKT-01 Project Work S/D Due to ordered by ALDC
Bogura
| 14:17 | 17:25 | Kaliakoir 400/230/132kV S/S 132kV Bus 2 Scheduled S/D Due to Annual Maintenance.
|  | 14:22 | Bakulia 132/33kV S/S T-3 (422T) HT is restored.
|  | 14:23 | Bakulia 132/33kV S/S T-3 (422T) LT is restored.
| 14:33 | 17:38 | Barishal 132/33kV S/S T-1 (405T) LT Scheduled S/D Due to Maintenance work by WZPDCL. | [7 empty] | 24.0MW load
interrup.
| 14:34 | 17:37 | Barishal 132/33kV S/S T-1 (405T) HT Scheduled S/D Due to Maintenance work by WZPDCL. | [7 empty] | 24.0MW load
interrup.
|  | 14:34 | Keranigonj 230/132/33kV S/S 132 kV Lalbagh Ckt. 3 is restored.
| 14:50 | 15:24 | Madunaghat-Meghnaghat 400kV Ckt-2 Tripped from Meghnaghat 400/230kV end showing Relay
86.1, Relay 86.2 relays Due to 400 kV Madunaghat ckt- 02 Tripped.
|  | 15:03 | Kushtia 132/33kV S/S T2 HT is restored.
|  | 15:04 | Kushtia 132/33kV S/S T2 LT is restored.
|  | 15:07 | Jhenaidah-Kushtia 132kV Ckt-1 is restored.
|  | 15:08 | Jhenaidah 132/33kV S/S Jhenaidah-Kushtia 132kV Circuit-1(L1) is restored.
|  | 15:15 | Mirpur-Uttara 132kV Ckt-1 is restored.
| 15:26 | 15:42 | Halishahar-Julda 132kV Ckt-1 Tripped from Juldah 132/33kV end showing Distance relay
falut 1.00 Km. Over Current Flow. relays.
|  | 15:35 | Aminbazar-Mirpur 132kV Ckt-2 is restored.
|  | 15:59 | Bagerhat-Mongla 132 kV Ckt-2 is restored.
| 16:33 | 17:34 | Mirpur-Uttara 132kV Ckt-1 Project Work S/D from Mirpur 132/33kV end Due to CT Connection
Check
| 17:20 | 19:44 | Tongi 230/132/33kV S/S T-2 LT Scheduled S/D Due to Testing work
| 17:21 | 19:42 | Tongi 230/132/33kV S/S T-2 HT Scheduled S/D Due to Testing work
| 19:51 | 20:47 | Tongi 230/132/33kV S/S T-3 LT Scheduled S/D Due to Transformer Testing Work.
| 19:51 | 20:47 | Tongi 230/132/33kV S/S T-3 HT Scheduled S/D Due to Transformer Testing Work
| 20:00 |  | Evening peak generation 11342 MW
| 05:00 |  | Minimum Generation: 8008 MW
| 07:28 |  | Madartek-Rampura 132kV Ckt-1 Scheduled S/D from Rampura 230/132kV end Due to Annual
Maintenance
| 07:44 |  | Fenchuganj-Sreemangal 132kV Ckt-2 Forced S/D from Sreemongol 132/33kV end Due to Order
by Back Up NLDC. and from Fenchuganj 230/132/33kV end Due to Deadline Checking
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 24-01-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 326 | 7732800 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 335157 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7366485 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 33.7 | 259560 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 64 | 726240 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 266111 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 270218 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 28 | 444000 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 447840 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 300480 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 1770916 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 80 | 1063440 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 51 | 547200 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 86 | 889920 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 8438 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 111960 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 395 | 8910958 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 90 | 786000 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1823.7 | 32237723
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 82542.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 133785 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 24 | 358080 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1867380 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 187 | 4401879 | Plant availability less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 49 | 593818 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 8 | 111360 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 16 | 154013 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 511680 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 19 | 554400 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 62 | 428160 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20043 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 333709 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 35 | 274833 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 67 | 741000 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 339840 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 65 | 541964 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 87 | 545309 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 26885452 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 44160 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 415 | 7236363.64 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4898.863 | 2403 | 46159771.24
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 152 | 4715000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 280 | 7082800 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 215 | 5636500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 0 | 12114 | Gas shortage
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 30 | 200768 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 105 | 2496036 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 969120 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 126 | 2633280 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 129878 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 316600 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 48 | 344280 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 50 | 414720 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 399155 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1144 | 25350251
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 34 | 1201920 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 3250 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 18 | 309600 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 769200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 241440 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 135360 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 284040 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 140 | 2944810
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 67721 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 116000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 20 | 76080 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 161 | 3605564 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 717792 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1822080 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2407380 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 20 | 471432 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7671000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 761 | 16955049
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 473 | 11440000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 30 | 176640 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 37 | 165888 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 230 | 5516928 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 43200 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1130 | 25018200 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1900 | 42360856
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 47 | 532704 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 3078000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 622 | 12753454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5490080 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 439200 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6414000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2896 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1380 | 28710334.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 249732 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 31 | 120956 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 6359 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Shutdown for Pond Cleaning.
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 214 | 4597909 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9310400 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 12 | 15585 | machine problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 25 | 174806 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 6256 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 656448 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 70 | 636288 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 27120 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 759 | 17087909 | U#1 Under AOH
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 314992 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 357990 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1595 | 33562750
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 56 | 1304727 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 714576 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 31542.84 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 813889 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 183495 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 836640 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 196 | 3884869.84
Eastern Grid Total |  |  |  |  | 17398.245 | 6271.7 | 123647604.24
Western Grid Total |  |  |  |  | 10984.003 | 5071 | 108518810.39
National Grid Total |  |  |  |  | 28382.248 | 11342.7 | 232166414.63
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 24-01-2026
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7630.07 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3233.5 | MW
i) Dhaka area |  |  | 4091.97 |  | MW | i) Khulna area |  |  |  | 1197 | MW
ii) Chattogram area |  |  | 1208.1 |  | MW | ii) Barishal area |  |  |  | 335.5 | MW
iii) Cumilla area |  |  | 990 |  | MW | iii) Rajshahi area |  |  |  | 1001 | MW
iv) Mymensingh area |  |  | 935 |  | MW | iv) Rangpur area |  |  |  | 700 | MW
v) Sylhet area |  |  | 405 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10863.57 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 14 | 17:00 | 67 | Hasnabad | 82 | 13:00 | 133 | Netrakona | 130 | 18:00
2 | AKSML | 131 | 09:00 | 68 | Hathazari | 57 | 19:00 | 134 | New | 74 | 12:00
3 | Aftabnagar | 26 | 13:00 | 69 | Hatirjheel | 28 | 13:00 | 135 | Niamatpur | 86 | 08:00
4 | Agargaon | 73 | 18:30 | 70 | Ishurdi | 50 | 18:30 | 136 | Noapara | 35 | 13:00
5 | Agrabad | 32 | 11:00 | 71 | Jaldhaka | 50 | 08:00 | 137 | PHP | 9 | 18:00
6 | Amnura | 32 | 08:00 | 72 | Jamalpur | 84 | 07:00 | 138 | Pabna | 74 | 20:00
7 | Ashuganj | 65 | 19:30 | 73 | Jashore | 99 | 12:00 | 139 | Palashbari | 78 | 19:30
8 | BSRM | 191 | 19:30 | 74 | Jhenaidah | 99 | 08:00 | 140 | Panchagarh | 39 | 09:00
9 | Bagerhat | 75 | 18:30 | 75 | Joydebpur | 106 | 18:00 | 141 | Patiya | 6.6 | 20:00
10 | Bajitpur | 66 | 18:30 | 76 | Joypurhat | 42 | 08:00 | 142 | Patuakhali | 39.6 | 21:00
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 13 | 11:00 | 143 | Payra | 28 | 19:30
12 | Bakulia | 65 | 18:00 | 78 | KSRM | 19 | 09:00 | 144 | Postogola | 42 | 13:00
13 | Banani | 34.6 | 13:00 | 79 | Kabirpur | 209 | 19:30 | 145 | Purbachal | 22 | 13:00
14 | Bangabhaban | 5 | 11:00 | 80 | Kachua | 63 | 18:00 | 146 | Purbasadipur | 114 | 12:00
15 | Barapukuria | 52 | 12:00 | 81 | Kallyanpur | 72 | 13:00 | 147 | Rahanpur | 24 | 08:00
16 | Barguna | 16 | 19:00 | 82 | Kalurghat | 42 | 14:00 | 148 | Rahim | 51 | 15:00
17 | Barishal | 87 | 18:30 | 83 | Kamrangirchar | 65 | 12:00 | 149 | Rajbari | 49 | 17:00
18 | Barishal-230 | 72 | 19:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 105 | 10:00
19 | Baroaulia | 59 | 10:00 | 85 | Kasba | 24 | 13:00 | 151 | Rajshahi | 72 | 13:00
20 | Baroirhat | 56 | 13:00 | 86 | Kazla | 105 | 13:00 | 152 | Rajshahi-230 | 72 | 13:00
21 | Bashundhara | 164 | 13:00 | 87 | Keranigonj | 71 | 13:00 | 153 | Ramganj | 72 | 13:00
22 | BashundharaCement | 1 | 00:00 | 88 | Khagrachori | 30 | 18:30 | 154 | Rampur | 28 | 15:00
23 | Beanibazar | 50 | 18:00 | 89 | Khulna | 48 | 13:00 | 155 | Rangamati | 14 | 18:00
24 | Benapole | 68 | 08:00 | 90 | Khulshi | 159 | 14:00 | 156 | Rangpur | 103 | 13:00
25 | Bhaluka | 136 | 18:30 | 91 | Kishoreganj | 102 | 18:00 | 157 | Ruppur | 1.4 | 10:00
26 | Bhandaria | 37 | 21:00 | 92 | Kodda | 254 | 17:00 | 158 | SSM | 9 | 23:00
27 | Bhangura | 23 | 20:00 | 93 | Kulaura | 30 | 18:30 | 159 | Saidpur | 91 | 09:00
28 | Bheramara(GK) | 39 | 18:00 | 94 | Kurigram | 52 | 07:00 | 160 | Satkhira | 95 | 08:00
29 | Bhulta | 184 | 21:00 | 95 | Kushtia | 121 | 21:00 | 161 | Satmasjid | 84 | 13:00
30 | Bog-Sherpur | 50 | 08:00 | 96 | Laksam | 13 | 13:00 | 162 | Savar | 176 | 15:00
31 | Bogura | 108 | 17:00 | 97 | Lakshmipur | 24 | 22:00 | 163 | SevenRings | 14.95 | 00:00
32 | Borhanuddin | 68 | 21:00 | 98 | Lalbag | 54 | 13:00 | 164 | ShahCement | 36 | 16:00
33 | Brahmanbaria | 92 | 20:00 | 99 | Lalmonirhat | 40 | 19:30 | 165 | Shahjadpur | 52 | 12:00
34 | Cantonment | 88 | 12:00 | 100 | MI_Cement | 12 | 23:00 | 166 | Shahjibazar | 99 | 18:00
35 | Chandina | 15 | 22:00 | 101 | Madanganj | 30 | 13:00 | 167 | Shahmirpur | 39 | 18:00
36 | Chandpur | 54 | 15:00 | 102 | Madaripur | 73 | 22:00 | 168 | Shariatpur | 56 | 20:00
37 | Chandraghona | 28 | 18:00 | 103 | Madartek | 54 | 13:00 | 169 | Sherpur | 112 | 07:00
38 | Chapai | 49 | 08:00 | 104 | Madunaghat | 39 | 18:00 | 170 | Shikalbaha | 23 | 13:00
39 | Charsaidpur | 43 | 18:30 | 105 | Magura | 53 | 18:00 | 171 | Shitalakhya | 66.5 | 12:00
40 | Chauddagram | 55 | 13:00 | 106 | Mahasthangarh | 48 | 19:30 | 172 | Sholosohor | 34 | 13:00
41 | Chhatak | 24 | 00:00 | 107 | Maijdee | 35 | 19:30 | 173 | Shyampur | 148 | 13:00
42 | Chowmuhani | 111 | 18:00 | 108 | Manikganj | 94 | 19:00 | 174 | Siddhirganj | 110 | 12:00
43 | Chuadanga | 85 | 12:00 | 109 | Maniknagar | 40 | 13:00 | 175 | Sirajganj | 72 | 12:00
44 | Coxsbazar | 111 | 18:00 | 110 | Matarbari | 41 | 18:00 | 176 | Sonargaon | 140 | 16:00
45 | Cumilla(N) | 101 | 19:00 | 111 | Matuail | 58 | 12:00 | 177 | Sreemongol | 58 | 15:00
46 | Cumilla(S) | 136 | 13:00 | 112 | Metrorail_Motijheel | 22 | 20:00 | 178 | Sreepur | 102 | 18:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 0 | 00:00 | 179 | Srinagar | 31.2 | 14:00
48 | Daudkandi | 114 | 19:00 | 114 | Millgate | 76 | 12:00 | 180 | Sunamganj | 41 | 18:00
49 | DhakaUniversity | 54 | 13:00 | 115 | Mirpur | 113 | 15:00 | 181 | Sylhet | 43 | 18:00
50 | Dhamrai | 104 | 18:00 | 116 | Mirsorai | 38 | 07:00 | 182 | Sylhet-132 | 73 | 18:00
51 | Dhanmondi | 76.4 | 13:00 | 117 | Mirzapur | 45 | 12:00 | 183 | TK | 17 | 19:00
52 | Dohazari | 83 | 20:00 | 118 | Mithapukur | 44 | 08:00 | 184 | Tangail | 124 | 07:00
53 | Faridpur | 113 | 18:30 | 119 | Modern | N/A | N/A | 185 | Taraganj | 19 | 12:00
54 | Fatullah | 92 | 12:00 | 120 | Mogbazar | 41.1 | 10:00 | 186 | Tasnim | 26 | 00:00
55 | Fenchuganj | 28 | 18:00 | 121 | Mongla | 32 | 23:00 | 187 | Thakurgaon | 72 | 20:00
56 | Feni | 73 | 18:30 | 122 | Motijheel | 35 | 13:00 | 188 | Tongi | 105 | 09:00
57 | GPH | 94 | 16:00 | 123 | Muktagacha | 30 | 13:00 | 189 | Ullahpara | 25 | 20:00
58 | Ghatail | 68 | 07:00 | 124 | Munshiganj | 71 | 19:30 | 190 | Ullon | 46 | 14:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 0 | 00:00 | 191 | Uttara | 61 | 13:00
60 | Ghorashal-230 | 96 | 13:00 | 126 | Mymensingh | 158 | 08:00 | 192 | UttaraNew | 27 | 13:00
61 | Goalpara | 33 | 13:00 | 127 | Naogaon | 95 | 08:00 | 193 | Zigatola | 76 | 13:00
62 | Gollamari | 78 | 13:00 | 128 | Narail | 40 | 08:00
63 | Gopalganj | 73 | 08:00 | 129 | Narinda | 55 | 13:00
64 | Gulshan | 64 | 13:00 | 130 | Narshingdi | 148 | 19:00
65 | Halishahar | 59 | 18:00 | 131 | Natore | 99 | 08:00
66 | HaripurSBU | 125 | 12:00 | 132 | Nawabganj | 30.4 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 24-01-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 8892.7 | 0 |  | 8892.7
1:00 | 8357.86 | 0 |  | 8357.86
2:00 | 8026.91 | 0 |  | 8026.91
3:00 | 7613.7 | 0 |  | 7613.7
4:00 | 7474.71 | 0 |  | 7474.71
5:00 | 7419.38 | 0 |  | 7419.38
6:00 | 7858.17 | 0 |  | 7858.17
7:00 | 8523.97 | 0 |  | 8523.97
8:00 | 9436.03 | 46 |  | 9484.03
9:00 | 9519.13 | 0 |  | 9519.13
10:00 | 9547.78 | 0 |  | 9547.78
11:00 | 9753.09 | 0 |  | 9753.09
12:00 | 10272.22 | 0 |  | 10272.22
13:00 | 10585.41 | 55 |  | 10642.41
14:00 | 10250.17 | 0 |  | 10250.17
15:00 | 9987.65 | 0 |  | 9987.65
16:00 | 9620.05 | 0 |  | 9620.05
17:00 | 9918.6 | 0 |  | 9918.6
18:00 | 10874.4 | 264 |  | 11150.28
19:00 | 11219.8 | 268 |  | 11499.8
19:30 | 11271 | 266 |  | 11548.97
20:00 | 11342.7 | 151 |  | 11500.5
21:00 | 11186 | 157 |  | 11350.07
22:00 | 10757 | 32 |  | 10790
23:00 | 10249.5 | 23 |  | 10273.54
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 24-01-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4511 | 4381.7 | 8892.7 | DAILY GENERATION CURVE
00:30 | 4361.5 | 4263.78 | 8625.28
01:00 | 4212 | 4145.86 | 8357.86 | 24-01-2026
01:30 | 4206.5 | 3985.885 | 8192.385
02:00 | 4201 | 3825.91 | 8026.91
02:30 | 4138 | 3682.305 | 7820.305
03:00 | 4075 | 3538.7 | 7613.7
03:30 | 4084 | 3460.205 | 7544.205
04:00 | 4093 | 3381.71 | 7474.71
04:30 | 4077 | 3370.045 | 7447.045
05:00 | 4061 | 3358.38 | 7419.38
05:30 | 4173.5 | 3465.275 | 7638.775
06:00 | 4286 | 3572.17 | 7858.17
06:30 | 4358.445 | 3832.625 | 8191.07
07:00 | 4430.89 | 4093.08 | 8523.97
07:30 | 4718.43 | 4261.57 | 8980
08:00 | 5005.97 | 4430.06 | 9436.03
08:30 | 4991.38 | 4486.2 | 9477.58
09:00 | 4976.79 | 4542.34 | 9519.13
09:30 | 4945.465 | 4587.99 | 9533.455
10:00 | 4914.14 | 4633.64 | 9547.78
10:30 | 4971.15 | 4679.285 | 9650.435
11:00 | 5028.16 | 4724.93 | 9753.09
11:30 | 5191.225 | 4821.43 | 10012.655
12:00 | 5354.29 | 4917.93 | 10272.22
12:30 | 5481.045 | 4947.77 | 10428.815
13:00 | 5607.8 | 4977.61 | 10585.41
13:30 | 5481.49 | 4936.3 | 10417.79
14:00 | 5355.18 | 4894.99 | 10250.17
14:30 | 5303.39 | 4815.52 | 10118.91
15:00 | 5251.6 | 4736.05 | 9987.65
15:30 | 5191.595 | 4612.255 | 9803.85
16:00 | 5131.59 | 4488.46 | 9620.05
16:30 | 5278.245 | 4491.08 | 9769.325
17:00 | 5424.9 | 4493.7 | 9918.6
17:30 | 5725.15 | 4671.35 | 10396.5
18:00 | 6025.4 | 4849 | 10874.4
18:30 | 6123.1 | 4924 | 11047.1
19:00 | 6220.8 | 4999 | 11219.8
19:30 | 6245 | 5026 | 11271
20:00 | 6271.7 | 5071 | 11342.7
20:30 | 6206.35 | 5058 | 11264.35 |  | Executive Engineer
21:00 | 6141 | 5045 | 11186 |  | Network Operation Division
21:30 | 6000 | 4971.5 | 10971.5
22:00 | 5859 | 4898 | 10757
22:30 | 5654.75 | 4848.5 | 10503.25
23:00 | 5450.5 | 4799 | 10249.5

## En-Curve
QF-LDC-12
Date | 24-01-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2744 | 1300 | 473 | 0 | 100 | 759.7 | 86 | 3380 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2747.5 | 1272 | 473 | 0 | 96 | 758.78 | 86 | 3167 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 24-01-2026
01:00 | 2751 | 1244 | 473 | 0 | 92 | 757.86 | 86 | 2954 | 0 | 0 | 0 | 0 | 0 | 0 | 0
01:30 | 2746.5 | 1244 | 473 | 0 | 87 | 726.385 | 86 | 2827 | 0 | 0 | 0 | 0 | 0 | 2.5 | 0 | Energy Generated | 232.1664 |  | MKWHr
02:00 | 2742 | 1244 | 473 | 0 | 82 | 694.91 | 86 | 2700 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | Energy not Served | 0.996 |  | MKWHr
02:30 | 2745.5 | 1231 | 473.5 | 0 | 82 | 613.305 | 86 | 2583.5 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0 | Total Energy Requirement | 233.1624 |  | MKWHr
03:00 | 2749 | 1218 | 474 | 0 | 82 | 531.7 | 86 | 2467 | 0 | 0 | 0 | 0 | 0 | 6 | 0
03:30 | 2761 | 1237.5 | 473.5 | 0 | 79 | 478.705 | 86 | 2422.5 | 0 | 0 | 0 | 0 | 0 | 6 | 0
04:00 | 2773 | 1257 | 473 | 0 | 76 | 425.71 | 86 | 2378 | 0 | 0 | 0 | 0 | 0 | 6 | 0
04:30 | 2788.5 | 1233 | 473.5 | 0 | 79 | 427.045 | 86 | 2354 | 0 | 0 | 0 | 0 | 0 | 6 | 0
05:00 | 2804 | 1209 | 474 | 0 | 82 | 428.38 | 86 | 2330 | 0 | 0 | 0 | 0 | 0 | 6 | 0
05:30 | 2809.5 | 1218.5 | 474 | 0 | 87 | 494.775 | 86 | 2461 | 0 | 0 | 0 | 0 | 0 | 8 | 0
06:00 | 2815 | 1228 | 474 | 0 | 92 | 561.17 | 86 | 2592 | 0 | 0 | 0 | 0 | 0 | 10 | 0
06:30 | 2828.5 | 1206 | 473.5 | 0 | 89 | 651.525 | 86 | 2844 | 5.045 | 0 | 0 | 0 | 0 | 7.5 | 0
07:00 | 2842 | 1184 | 473 | 0 | 86 | 741.88 | 86 | 3096 | 10.09 | 0 | 0 | 0 | 0 | 5 | 0
07:30 | 2799 | 1201 | 473 | 0 | 98 | 750.94 | 86 | 3174 | 56.68 | 48 | 289.88 | 0 | 0 | 3.5 | 23
08:00 | 2756 | 1218 | 473 | 0 | 110 | 760 | 86 | 3252 | 103.27 | 96 | 579.76 | 0 | 0 | 2 | 46
08:30 | 2747 | 1171.5 | 473 | 0 | 109 | 761 | 86 | 3280.5 | 152.7 | 98 | 597.88 | 0 | 0 | 1 | 23
09:00 | 2738 | 1125 | 473 | 0 | 108 | 762 | 86 | 3309 | 202.13 | 100 | 616 | 0 | 0 | 0 | 0
09:30 | 2705 | 1142 | 473 | 0 | 113 | 763 | 86 | 3334.5 | 254.105 | 108 | 554.85 | 0 | 0 | 0 | 0
10:00 | 2672 | 1159 | 473 | 0 | 118 | 764 | 86 | 3360 | 306.08 | 116 | 493.7 | 0 | 0 | 0 | 0
10:30 | 2646 | 1145.5 | 473.5 | 0 | 118 | 761 | 86 | 3441 | 376.585 | 118 | 484.85 | 0 | 0 | 0 | 0
11:00 | 2620 | 1132 | 474 | 0 | 118 | 758 | 86 | 3522 | 447.09 | 120 | 476 | 0 | 0 | 0 | 0
11:30 | 2692 | 1170.5 | 474 | 0 | 122 | 761 | 86 | 3552 | 463.405 | 127 | 564.75 | 0 | 0 | 0 | 0
12:00 | 2764 | 1209 | 474 | 0 | 126 | 764 | 86 | 3582 | 479.72 | 134 | 653.5 | 0 | 0 | 0 | 0
12:30 | 2744.5 | 1242.5 | 474 | 0 | 131 | 766.5 | 86 | 3580.5 | 478.815 | 154 | 771 | 0 | 0 | 0 | 27.5
13:00 | 2725 | 1276 | 474 | 0 | 136 | 769 | 86 | 3579 | 477.91 | 174 | 888.5 | 0 | 0 | 0 | 55
13:30 | 2718 | 1258 | 474 | 0 | 133 | 766 | 86 | 3576 | 443.69 | 165 | 798.1 | 0 | 0 | 0 | 27.5
14:00 | 2711 | 1240 | 474 | 0 | 130 | 763 | 86 | 3573 | 409.47 | 156 | 707.7 | 0 | 0 | 0 | 0
14:30 | 2670.5 | 1234.5 | 474 | 0 | 129 | 765 | 86 | 3571 | 351.21 | 156 | 681.7 | 0 | 0 | 0 | 0
15:00 | 2630 | 1229 | 474 | 0 | 128 | 767 | 86 | 3569 | 292.95 | 156 | 655.7 | 0 | 0 | 0 | 0
15:30 | 2631.5 | 1220.5 | 473.5 | 0 | 126 | 763 | 86 | 3556.5 | 229.8 | 159 | 558.05 | 0 | 0 | 0 | 0
16:00 | 2633 | 1212 | 473 | 0 | 124 | 759 | 86 | 3544 | 166.65 | 162 | 460.4 | 0 | 0 | 0 | 0
16:30 | 2637.5 | 1205.5 | 473 | 0 | 124 | 760 | 86 | 3544 | 103.125 | 201.5 | 634.7 | 0 | 0 | 0 | 0
17:00 | 2642 | 1199 | 473 | 0 | 124 | 761 | 86 | 3544 | 39.6 | 241 | 809 | 0 | 0 | 0 | 0
17:30 | 2652.5 | 1216 | 473 | 0 | 127 | 759 | 86 | 3591.5 | 19.8 | 289 | 1182.7 | 0 | 0 | 0 | 132
18:00 | 2663 | 1233 | 473 | 0 | 130 | 757 | 86 | 3639 | 0 | 337 | 1556.4 | 0 | 0 | 0 | 264
18:30 | 2714.5 | 1248 | 473 | 0 | 129 | 759 | 86 | 3660.5 | 0 | 364 | 1613.1 | 0 | 0 | 0 | 266
19:00 | 2766 | 1263 | 473 | 0 | 128 | 761 | 86 | 3682 | 0 | 391 | 1669.8 | 0 | 0 | 0 | 268
19:30 | 2780 | 1275 | 473 | 0 | 122 | 757 | 46 | 3720 | 0 | 389 | 1709 | 0 | 0 | 0 | 266
20:00 | 2802 | 1271 | 473 | 0 | 126 | 759 | 46 | 3754 | 0 | 394 | 1717.7 | 0 | 0 | 0 | 151
20:30 | 2800 | 1258 | 473.5 | 0 | 123 | 759 | 46 | 3747.5 | 0 | 384 | 1672.85 | 0 | 0 | 0.5 | 154
21:00 | 2798 | 1245 | 474 | 0 | 120 | 759 | 46 | 3741 | 0 | 374 | 1628 | 0 | 0 | 1 | 157
21:30 | 2793 | 1230.5 | 474 | 0 | 119 | 762.5 | 46 | 3740 | 0 | 303 | 1503 | 0 | 0 | 0.5 | 94.5
22:00 | 2788 | 1216 | 474 | 0 | 118 | 766 | 46 | 3739 | 0 | 232 | 1378 | 0 | 0 | 0 | 32
22:30 | 2773 | 1207.25 | 473.5 | 0 | 117 | 763.5 | 46 | 3693 | 0 | 157.5 | 1272.5 | 0 | 0 | 0 | 27.5
23:00 | 2758 | 1198.5 | 473 | 0 | 116 | 761 | 46 | 3647 | 0 | 83 | 1167 | 0 | 0 | 0 | 23
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 24-01-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 424 | 05:00 | 402 | 11:00 | Madunaghat | 418 | 05:00 | 409 | 12:00
Amtali | 427 | 05:00 | 416 | 12:00 | Meghnaghat | 427 | 05:00 | 405 | 12:00
Ashuganj | 414 | 5:00 | 394 | 12:00 | Payra | 427 | 03:00 | 416 | 12:00
Bhulta | 407 | 05:00 | 381 | 12:00 | Rahanpur | 421 | 04:00 | 400 | 09:00
Bibiana | 423 | 05:00 | 411 | 12:00 | Rampal | 418 | 02:00 | 403 | 12:00
BIPTC | 407 | 03:00 | 392 | 10:00
Bogura | 419 | 04:00 | 398 | 09:00
Gopalganj | 423 | 04:00 | 407 | 12:00
Kaliakoir | 418 | 05:00 | 399 | 12:00
Korerhat | 427 | 05:00 | 413 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 246 | 05:00 | 231 | 12:00 | Jhenaidah | 244 | 04:00 | 232 | 12:00
AKSML | 240 | 08:00 | 233 | 13:00 | Kachua | 244 | 18:30 | 233 | 11:00
Aminbazar | 244 | 05:00 | 231 | 11:00 | Kaliakoir | 246 | 05:00 | 233 | 12:00
Ashuganj | 239 | 02:00 | 228 | 11:00 | Keranigonj | 244 | 05:00 | 229 | 12:00
Ashuganj-400 | 238 | 5:00 | 228 | 12:00 | Khulna(S) | 246 | 04:00 | 235 | 12:00
Baghabari | 243 | 02:00 | 233 | 16:00 | Korerhat | 242 | 18:30 | 234 | 11:00
Barapukuria | 233 | 18:30 | 222 | 09:00 | Madunaghat | 241 | 07:00 | 234 | 11:00
Barapukuria-230 | 233 | 18:00 | 220 | 10:00 | Madunaghat-400 | 241 | 09:00 | 235 | 12:00
Barishal | 241 | 04:00 | 232 | 13:00 | Maniknagar | 242 | 03:00 | 229 | 12:00
Bheramara | 242 | 03:00 | 232 | 12:00 | Meghnaghat | 248 | 04:00 | 240 | 09:00
Bhulta | 244 | 04:00 | 229 | 12:00 | Meghnaghat-400 | 243 | 04:00 | 229 | 12:00
Bibiana | 242 | 04:00 | 236 | 12:00 | Mirsorai | 244 | 18:30 | 234 | 12:00
BIPTC | 244 | 05:00 | 231 | 12:00 | Rajshahi | 242 | 05:00 | 230 | 12:00
Bogura | 245 | 05:00 | 233 | 09:00 | Rampal | 243 | 04:00 | 232 | 12:00
Bogura-400 | 244 | 04:00 | 232 | 09:00 | Rampur | N/A | N/A | N/A | N/A
Borhanuddin | 240 | 05:00 | 236 | 12:00 | Rampura | 244 | 05:00 | 229 | 12:00
BSRM | 242 | 05:00 | 234 | 12:00 | Shikalbaha | 239 | 08:00 | 232 | 16:00
Chowmuhani | N/A | N/A | N/A | N/A | Shyampur | 243 | 05:00 | 228 | 12:00
Cumilla(N) | 239 | 04:00 | 230 | 11:00 | Siddhirganj | 241 | 03:00 | 231 | 11:00
Faridpur | 240 | 04:00 | 226 | 12:00 | Sirajgonj | 246 | 02:00 | 240 | 18:30
Fenchuganj | 246 | 04:00 | 240 | 11:00 | Sreepur | 238 | 05:00 | 225 | 12:00
Feni | 243 | 05:00 | 233 | 11:00 | Tongi | 241 | 04:00 | 230 | 11:00
Ghorashal | 245 | 02:00 | 230 | 18:00
Ghorashal-230 | 242 | 03:00 | 228 | 12:00
Gopalganj | 238 | 05:00 | 227 | 12:00
GPH | 241 | 04:00 | 233 | 12:00
Haripur | 243 | 04:00 | 230 | 12:00
Hasnabad | 242 | 02:00 | 230 | 11:00
Hathazari | 240 | 07:00 | 231 | 14:00
Ishurdi | 245 | 04:00 | 234 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 05:00 | 126 | 12:00 | Maijdee | 136 | 04:00 | 131 | 12:00
Agargaon | 137 | 8:00 | 130 | 12:00 | Manikganj | 133 | 04:00 | 122 | 12:00
Agrabad | 140 | 08:00 | 135 | 11:00 | Maniknagar | 141 | 05:00 | 131 | 10:00
AKS | 137 | 03:00 | 133 | 11:00 | Matarbari | 131 | 02:00 | 125 | 15:00
Aminbazar | 140 | 00:00 | 132 | 11:00 | Matuail | 139.5 | 04:00 | 132 | 12:00
Amnura | 140 | 05:00 | 131 | 09:00 | Metrorail_Motijheel | 141 | 06:00 | 131 | 12:00
Ashuganj | 139 | 04:00 | 135 | 12:00 | Metrorail_Uttara | 141 | 04:00 | 131 | 11:00
Bagerhat | 137 | 04:00 | 127 | 18:00 | Millgate | 135 | 02:00 | 126 | 12:00
Bajitpur | 136 | 02:00 | 130 | 12:00 | Mirpur | 140 | 04:00 | 130 | 12:00
Bakerganj | 141 | 01:00 | 137 | 10:00 | Mirzapur | 136 | 05:00 | 128 | 07:00
Bakulia | 141 | 08:00 | 136 | 16:00 | Mithapukur | 136 | 04:00 | 128 | 16:00
Banani | 136 | 03:00 | 125 | 12:00 | MI_Cement | 138 | 04:00 | 125 | 12:00
Bangabhaban | 141 | 06:00 | 131 | 12:00 | Modern | N/A | N/A | N/A | N/A
Barapukuria | 138 | 13:00 | 128 | 09:00 | Mogbazar | 136 | 00:00 | 127 | 13:00
Barguna | 141 | 01:00 | 137 | 10:00 | Mongla | 137 | 05:00 | 128 | 18:00
Barishal | 141 | 03:00 | 138 | 12:00 | Motijheel | 141 | 06:00 | 131 | 12:00
Barishal-230 | 141 | 02:00 | 135 | 13:00 | Muktagacha | 133 | 11:00 | 120 | 06:00
Baroaulia | 140 | 18:30 | 136 | 11:00 | Munshiganj | 137 | 02:00 | 132 | 11:00
Baroirhat | 136 | 01:00 | 132 | 12:00 | Muradnagar | 140 | 04:00 | 132 | 12:00
Bashundhara | 135 | 03:00 | 126 | 12:00 | Mymensingh | 134 | 11:00 | 120 | 05:00
BashundharaCement | 137 | 00:00 | 133 | 16:00 | Naogaon | 135 | 04:00 | 127 | 09:00
Beanibazar | 134 | 03:00 | 130 | 15:00 | Narail | 140 | 04:00 | 131 | 08:00
Benapole | 137 | 03:00 | 126 | 12:00 | Narinda | 141 | 5:00 | 131 | 10:00
Bhaluka | 132 | 18:30 | 125 | 12:00 | Narshingdi | 136 | 00:00 | 119 | 12:00
Bhandaria | 139 | 06:00 | 135 | 11:00 | Natore | 138 | 18:30 | 133 | 12:00
Bhangura | 140 | 00:00 | 134 | 11:00 | Nawabganj | 138 | 04:00 | 128 | 12:00
Bheramara | 140 | 04:00 | 135 | 12:00 | Netrakona | 127 | 03:00 | 116 | 13:00
Bheramara(GK) | 139 | 03:00 | 135 | 12:00 | New | 135 | 05:00 | 126 | 12:00
Bhulta | 132 | 00:00 | 128 | 12:00 | Niamatpur | 141 | 04:00 | 132 | 09:00
Bog-Sherpur | 139 | 03:00 | 132 | 09:00 | Noapara | 138 | 05:00 | 129 | 12:00
Bogura | 139 | 18:00 | 132 | 09:00 | Pabna | 140 | 02:00 | 134 | 12:00
Bogura-230 | 140 | 18:30 | 132 | 09:00 | Palashbari | 135 | 03:00 | 127 | 09:00
Brahmanbaria | 133 | 04:00 | 123 | 16:00 | Panchagarh | 138 | 18:30 | 128 | 08:00
Cantonment | 138 | 00:00 | 130 | 12:00 | Patiya | 140 | 08:00 | 136 | 11:00
Chandina | 141 | 04:00 | 133 | 12:00 | Patuakhali | 141 | 18:00 | 135 | 12:00
Chandpur | 141 | 18:00 | 135 | 11:00 | Payra | 143 | 05:00 | 137 | 11:00
Chandraghona | 141 | 08:00 | 137 | 16:00 | PHP | 136 | 02:00 | 131 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 139 | 01:00 | 132 | 09:00 | Postogola | 139 | 05:00 | 127 | 12:00
Charsaidpur | 139 | 03:00 | 131 | 12:00 | Purbachal | 136 | 03:00 | 126 | 12:00
Chauddagram | 138 | 02:00 | 132 | 11:00 | Purbasadipur | 134 | 05:00 | 126 | 16:00
Chhatak | 132 | 01:00 | 127 | 13:00 | Rahanpur | 141 | 05:00 | 134 | 09:00
Chowmuhani | 136 | 02:00 | 130 | 16:00 | Rahanpur-400 | 142 | 04:00 | 134 | 09:00
Chuadanga | 140 | 03:00 | 130 | 12:00 | Rahim | 138 | 03:00 | 132 | 13:00
Coxsbazar | 132 | 04:00 | 125 | 18:00 | Rajbari | 139 | 03:00 | 129 | 13:00
Cumilla(N) | 139 | 00:00 | 133 | 11:00 | Rajendrapur | 135 | 04:00 | 125 | 12:00
Cumilla(S) | 139 | 05:00 | 124 | 10:00 | Rajshahi | 139 | 02:00 | 132 | 13:00
Daganbhuiyan | 137 | 05:00 | 132 | 11:00 | Rajshahi-230 | 140 | 04:00 | 132 | 12:00
Daudkandi | 137 | 02:00 | 129 | 12:00 | Ramganj | 137 | 18:00 | 132 | 14:00
DhakaUniversity | 135 | 03:00 | 126 | 12:00 | Rampur | 139 | 19:30 | 135 | 11:00
Dhamrai | 138 | 00:00 | 132 | 12:00 | Rampura | 135 | 03:00 | 126 | 12:00
Dhanmondi | 140 | 04:00 | 133 | 12:00 | Rangamati | 139 | 03:00 | 134 | 08:00
Dohazari | 136 | 08:00 | 133 | 00:00 | Rangpur | 136 | 18:30 | 127 | 17:00
Faridpur | 139 | 04:00 | 128 | 12:00 | Ruppur | 140 | 00:00 | 136 | 09:00
Fatullah | 140 | 03:00 | 126 | 12:00 | Saidpur | 135 | 05:00 | 127 | 09:00
Fenchuganj | 139 | 05:00 | 134 | 11:00 | Satkhira | 137 | 05:00 | 127 | 12:00
Feni | 135 | 04:00 | 130 | 12:00 | Satmasjid | 139 | 04:00 | 130 | 13:00
Feni-230 | 136 | 03:00 | 130 | 11:00 | Savar | 140 | 18:30 | 130 | 12:00
Ghatail | 130 | 10:00 | 118 | 07:00 | SevenRings | 135 | 04:00 | 128 | 12:00
Ghorashal | 134 | 01:00 | 128 | 11:00 | ShahCement | 139 | 03:00 | 131 | 12:00
Goalpara | 137 | 04:00 | 131 | 12:00 | Shahjadpur | 142 | 01:00 | 136 | 09:00
Gollamari | 138 | 03:00 | 131 | 12:00 | Shahjibazar | 133 | 01:00 | 126 | 12:00
Gopalganj | 141 | 03:00 | 135 | 12:00 | Shahmirpur | 141 | 08:00 | 137 | 03:00
Gopalganj-400 | 144 | 05:00 | 139 | 12:00 | Shariatpur | 143 | 04:00 | 137 | 12:00
Gulshan | 134 | 04:00 | 126 | 12:00 | Sherpur | 130 | 09:00 | 110 | 07:00
Halishahar | 140 | 05:00 | 136 | 16:00 | Shikalbaha | 130 | 08:00 | 125 | 16:00
Haripur | 139 | 03:00 | 132 | 12:00 | Shikalbaha-230 | 142 | 21:00 | 137 | 11:00
HaripurSBU | 139 | 03:00 | 131 | 12:00 | Shitalakhya | 138 | 04:00 | 125 | 12:00
Hasnabad | 137 | 01:00 | 127 | 12:00 | Sholosohor | 140 | 04:00 | 137 | 11:00
Hathazari | 140 | 03:00 | 136 | 11:00 | Shyampur | 139 | 02:00 | 130 | 13:00
Hatirjheel | 136 | 05:00 | 126 | 12:00 | Shyampur-230 | 141 | 05:00 | 131 | 12:00
Ishurdi | 142 | 02:00 | 137 | 09:00 | Siddhirganj | 139 | 02:00 | 132 | 12:00
Jaldhaka | 133 | 04:00 | 124 | 09:00 | Sirajganj | 139 | 04:00 | 131 | 09:00
Jamalpur | 133 | 10:00 | 112 | 07:00 | Sonargaon | 136 | 00:00 | 132 | 15:00
Jashore | 137 | 03:00 | 128 | 12:00 | Sreemongol | 135 | 05:00 | 127 | 12:00
Jhenaidah | 141 | 04:00 | 125 | 08:00 | Sreepur | 136 | 04:00 | 128 | 11:00
Jhenaidah-230 | 142 | 05:00 | 132 | 10:00 | Srinagar | 138 | 05:00 | 128 | 12:00
Joydebpur | 133 | 01:00 | 124 | 12:00 | SSM | 143 | 18:30 | 140 | 00:00
Joypurhat | 134 | 05:00 | 125 | 09:00 | Sunamganj | 132 | 06:00 | 126 | 13:00
Juldah | 141 | 21:00 | 137 | 00:00 | Sylhet | 134 | 03:00 | 129 | 11:00
Kabirpur | 139 | 01:00 | 123 | 12:00 | Sylhet-132 | 133 | 01:00 | 130 | 12:00
Kachua | 139 | 18:30 | 134 | 11:00 | Tangail | 130 | 05:00 | 125 | 12:00
Kaliakoir | 142 | 04:00 | 134 | 13:00 | Taraganj | 134 | 04:00 | 126 | 10:00
Kallyanpur | 141 | 06:00 | 131 | 12:00 | Tasnim | 138 | 02:00 | 132 | 13:00
Kalurghat | 140 | 03:00 | 137 | 11:00 | Thakurgaon | 138 | 18:30 | 129 | 07:00
Kamrangirchar | 137 | 05:00 | 128 | 12:00 | TK | 140 | 21:00 | 136 | 11:00
Kaptai | N/A | N/A | N/A | N/A | Tongi | 136 | 01:00 | 128 | 11:00
Kasba | 140 | 04:00 | 136 | 20:00 | Ullahpara | 139 | 03:00 | 132 | 12:00
Kazla | 141 | 06:00 | 130 | 13:00 | Ullon | 136 | 04:00 | 126 | 12:00
Keranigonj | 138 | 05:00 | 128 | 12:00 | Uttara | 135 | 03:00 | 125 | 12:00
Khagrachori | 140 | 08:00 | 137 | 11:00 | UttaraNew | 141 | 04:00 | 130 | 12:00
Khulna | 136 | 00:00 | 131 | 12:00 | Zigatola | 138 | 05:00 | 128 | 12:00
Khulna(S) | 139 | 04:00 | 131 | 12:00
Khulshi | 139 | 08:00 | 135 | 11:00
Kishoreganj | 134 | 03:00 | 128 | 12:00
Kodda | 138 | 08:00 | 132 | 12:00
KSRM | 140 | 21:00 | 136 | 10:00
Kulaura | 138 | 04:00 | 134 | 12:00
Kurigram | 132 | 04:00 | 123 | 07:00
Kushtia | 138 | 01:00 | 132 | 12:00
Laksam | 139 | 03:00 | 135 | 10:00
Lakshmipur | 136 | 03:00 | 131 | 12:00
Lalbag | 139 | 08:00 | 130 | 12:00
Lalmonirhat | 132 | 21:00 | 121 | 12:00
Madanganj | 137 | 00:00 | 133 | 16:00
Madaripur | 141 | 02:00 | 138 | 15:00
Madartek | 135 | 08:00 | 125 | 12:00
Madunaghat | 141 | 07:00 | 137 | 11:00
Magura | 140 | 03:00 | 131 | 12:00
Mahasthangarh | 138 | 05:00 | 130 | 09:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division