## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 29-01-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-01-2026 | during | 29-01-2026 | during | 29-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 306 | 301 | 412 | 412 | 412 | 412 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 240 | 240 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 33 | 53.97 | 53.97 | 53.97 | 53.97 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 48 | 80 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 22.8 | 23 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 20 | 20 | 22.5 | 22.5 | 15.1 | 15.1 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 25 | 52.19 | 52.19 | 25 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 95 | 160 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 51 | 86 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 51 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 50 | 86 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 29 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Under shutdown
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 463 | 464 | 718 | 718 | 680 | 680 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 90 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1458.8 | 1746 | 5357.85 | 5329.85 | 2735.43 | 2772.43
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 32 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 184 | 184 | 150 | 150 | 150 | 150 | Plant availability less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 33 | 66 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 8 | 8 | 16 | 16 | 8 | 8 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 34 | 34 | 34 | 34 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 36 | 60 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 11 | 20 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 39 | 60 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.45 | 0 | 3.41 | 0 | 3.41 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 35 | 54.36 | 54.36 | 54.36 | 54.36 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 34 | 67 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 60 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 52 | 85 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1147 | 1170 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 395 | 395 | 395 | 395 | 395 | 395 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2120.45 | 2374 | 3118.27 | 3110.86 | 2743.27 | 2735.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 180 | 171 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 280 | 280 | 353.35 | 353.35 | 317 | 317 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 215 | 215 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 3 | 3 | 46.7 | 46.7 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 45 | 85 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 16 | 22 | 42 | 42 | 42 | 42 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 99 | 103 | 163 | 163 | 110 | 110 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 68 | 120 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 124 | 124 | 84 | 80 | 146 | 146 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 16 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 13 | 24.5 | 24.5 | 24.5 | 24.5 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 33 | 68 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 34 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1237 | 1323 | 2437.75 | 2368.75 | 1967.7 | 1902.7
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-01-2026 | during | 29-01-2026 | during | 29-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 9 | 12 | 157.5 | 157.5 | 35 | 35 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 19 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 35 | 58 | 60 | 60 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 41.46 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 22 | 22 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 112.46 | 112 | 358.1 | 314 | 235.6 | 191.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 30 | 30 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 53 | 53 | 53 | 53 | 53 | 53 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 158 | 155 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 83 | 83 | 83 | 83 | 83 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 97 | 100 | 100 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 20 | 21 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 325 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 816 | 806 | 837 | 837 | 767 | 767
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 894 | 893 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 13 | 26 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 35 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 190 | 164 | 410 | 410 | 369 | 369 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 73 | 0 | 82 | 0 | 82 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 606 | 601 | 617.1 | 617.1 | 617.1 | 617.1 | U#1 Under Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1776 | 1719 | 2971.1 | 2889.1 | 2175.2 | 2093.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 32 | 44 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 128 | 130 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 600 | 622 | 622 | 622 | 622 | 622 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 35 | 150 | 150 | 150 | 150 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 279 | 280 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.56 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1276.56 | 1331 | 1540 | 1539 | 1520 | 1519
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 47.61 | 0 | 43.5 | 0 | 43.5 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 0 | 40 | 40 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Machine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 15 | 32 | 32 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 187 | 172 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 21 | 20 | 20 | 24 | 24 | machine problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 16 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 70 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 70 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.53 | 0 | 5.1 | 0 | 5.1 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 756.64 | 765 | 748 | 748 | 748 | 748 | U#1 Under AOH
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 53.49 | 0 | 52 | 0 | 52 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 95 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1644.27 | 1561 | 2378.59 | 2177.99 | 1908.8 | 1708.2
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 55 | 55 | 55 | 55 | 55 | 55 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 62 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.6 | 0 | 4.8 | 0 | 4.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 150 | 0 | 143.78 | 0 | 143.78 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 309.6 | 187 | 495.58 | 317 | 461.58 | 283
System Total |  |  |  |  | 28823.2 | 28382.248 | 10751.14 | 11159 | 19494.24 | 18883.55 | 14514.58 | 13972.89
Forecast Scenario (29-01-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9690 |  | 0 |  | 9690
|  |  |  | 1:00 | 8960 |  | 0 |  | 8960
|  |  |  | 2:00 | 8740 |  | 0 |  | 8740
|  |  |  | 3:00 | 8360 |  | 0 |  | 8360
|  |  |  | 4:00 | 8200 |  | 0 |  | 8200
|  |  |  | 5:00 | 8030 |  | 0 |  | 8030
|  |  |  | 6:00 | 8550 |  | 0 |  | 8550
|  |  |  | 7:00 | 9180 |  | 0 |  | 9180
|  |  |  | 8:00 | 10320 |  | 0 |  | 10320
|  |  |  | 9:00 | 10700 |  | 0 |  | 10700
|  |  |  | 10:00 | 10620 |  | 0 |  | 10620
|  |  |  | 11:00 | 10950 |  | 0 |  | 10950
|  |  |  | 12:00 | 11300 |  | 0 |  | 11300
|  |  |  | 13:00 | 11400 |  | 0 |  | 11400
|  |  |  | 14:00 | 11060 |  | 0 |  | 11060
|  |  |  | 15:00 | 10900 |  | 0 |  | 10900
|  |  |  | 16:00 | 10560 |  | 0 |  | 10560
|  |  |  | 17:00 | 10750 |  | 0 |  | 10750
|  |  |  | 18:00 | 11490 |  | 0 |  | 11490
|  |  |  | 18:30 | 11525 |  | 0 |  | 11525
|  |  |  | 19:00 | 11540 |  | 0 |  | 11540
|  |  |  | 19:30 | 11670 |  | 0 |  | 11670
|  |  |  | 20:00 | 11620 |  | 0 |  | 11620
|  |  |  | 21:00 | 11490 |  | 0 |  | 11490
|  |  |  | 22:00 | 11010 |  | 0 |  | 11010
|  |  |  | 23:00 | 10400 |  | 0 |  | 10400
Probable Maximum Temperature: |  |  | 27.50°C
Probable Maximum Demand at Day Peak: |  |  | 11300.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11670.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11670.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 245.82 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:24 hrs on 29-01-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 28-01-2026 | [28 empty] | Date: | 28-01-2026 | [28 empty] | Date: | 28-01-2026 | [28 empty] | Date: | 28-01-2026 | [28 empty] | Date: | 28-01-2026 | [17 empty] | Date: | 28-01-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [17 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 488 | 18 | 0 | 78 | 0 | 0 | 0 | 17 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 19 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 51 | 36 | 395 | 0 | 0 | 6 | 0 | 63 | 185 | 0 | 0 | 0 | 1160 | 0 | 70 | 0 | 215 | 280 | 0 | 51 | 0 | 181 | 0 | 17 | 105 | 115 | 0 | 13 | 0 | 104 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 53 | 143 | 0 | 20 | 0 | 83 | 32 | 0 | 0 | 100 | 0 | 59 | 0 | 28 | 0 | 0 | 0 | 5268 | 894 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 598 | 0 | 0 | 0 | 765.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 622 | 0 | 4421.96 | 9689.96 | 95.3
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 19 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 395 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 215 | 280 | 0 | 51 | 0 | 186 | 0 | 0 | 106 | 0 | 0 | 13 | 0 | 96 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 53 | 155 | 0 | 20 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 4678 | 894 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 596 | 0 | 0 | 0 | 763.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 130 | 220 | 0 | 0 | 600 | 0 | 4290.21 | 8968.21 | 95.3
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 13.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 395 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 215 | 280 | 0 | 51 | 0 | 185 | 0 | 0 | 105 | 0 | 0 | 13 | 0 | 100 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 53 | 143 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 4608.5 | 894 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 554 | 0 | 0 | 0 | 760.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 130 | 220 | 0 | 0 | 560 | 0 | 4134.43 | 8742.93 | 95.29
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 13.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 395 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1120 | 0 | 0 | 0 | 215 | 280 | 0 | 51 | 0 | 192 | 0 | 0 | 106 | 0 | 0 | 13 | 0 | 98 | 0 | 0 | 0 | 320 | 0 | 0 | 42 | 53 | 142 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 4637.5 | 894 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 442 | 0 | 0 | 0 | 599.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 130 | 220 | 0 | 0 | 450 | 0 | 3728.7 | 8366.2 | 95.29
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 13.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 395 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1060 | 0 | 0 | 0 | 215 | 280 | 0 | 51 | 0 | 195 | 0 | 0 | 107 | 0 | 0 | 13 | 0 | 96 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 53 | 159 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 4564.5 | 894 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 572.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 130 | 220 | 0 | 0 | 400 | 0 | 3638.22 | 8202.72 | 95.29
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 14.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 395 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1058 | 0 | 0 | 0 | 215 | 280 | 0 | 51 | 0 | 199 | 0 | 0 | 108 | 0 | 0 | 13 | 0 | 88 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 53 | 157 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 4520.5 | 894 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 0 | 0 | 515.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 130 | 220 | 0 | 0 | 350 | 0 | 3513.77 | 8034.27 | 95.28
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 14.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 395 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1128 | 0 | 0 | 0 | 215 | 280 | 0 | 51 | 0 | 199 | 0 | 0 | 108 | 0 | 0 | 13 | 0 | 102 | 0 | 0 | 0 | 320 | 0 | 0 | 41 | 53 | 159 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 102 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 4672.5 | 894 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 626.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 130 | 220 | 0 | 0 | 375 | 0 | 3755.62 | 8428.12 | 95.28
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 1 | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 40 | 0 | 39 | 395 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 1187 | 1 | 0 | 0 | 215 | 280 | 0 | 51 | 0 | 192 | 0 | 0 | 108 | 0 | 0 | 13 | 0 | 104 | 0 | 2 | 0 | 325 | 0 | 0 | 41 | 53 | 163 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 31 | 0 | 0.74 | 0 | 4750.84 | 894 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.93 | 488 | 0 | 0 | 0 | 763.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69 | 2 | 0 | 0 | 0.75 | 185 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.08 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.01 | 0 | 307 | 130 | 220 | 0 | 0 | 500 | 0 | 4165.36 | 8916.2 | 95.28
08:00 | 0 | 8 | 14 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 469 | 0 | 0 | 34 | 48 | 95 | 13 | 9 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 260 | 0 | 0 | 7 | 52 | 24 | 21 | 0 | 0 | 25 | 16 | 10 | 0 | 0 | 0 | 0 | 0 | 36 | 25 | 0.43 | 40 | 21 | 13 | 395 | 52 | 0 | 14 | 3 | 31 | 185 | 0 | 0 | 0 | 1110 | 7 | 45 | 0 | 215 | 280 | 0 | 51 | 0 | 192 | 0 | 18 | 108 | 38 | 0 | 13 | 34 | 104 | 15 | 22 | 1 | 315 | 0 | 0 | 41 | 53 | 156 | 3 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 35 | 19 | 29 | 0 | 9.82 | 4 | 5442.25 | 894 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.27 | 596 | 0 | 0 | 0 | 757.01 | 0 | 0 | 0 | 20 | 20 | 0 | 0 | 0 | 16 | 9.02 | 18 | 0 | 0 | 9.19 | 185 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0.97 | 0 | 51 | 35 | 6 | 34 | 0 | 0 | 0 | 0.8 | 32 | 0.03 | 24 | 307 | 130 | 220 | 0 | 0 | 590 | 16 | 4562.29 | 10004.54 | 95.27
09:00 | 0 | 31 | 16 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 450 | 0 | 0 | 51 | 48 | 95 | 15 | 17 | 52 | 0 | 0 | 0 | 0 | 0 | 17 | 260 | 0 | 0 | 15 | 52 | 24 | 21 | 0 | 0 | 34 | 16 | 32 | 0 | 0 | 0 | 0 | 0 | 36 | 25 | 1.93 | 40 | 32 | 5 | 395 | 48 | 0 | 19 | 8 | 33 | 183 | 0 | 0 | 0 | 1120 | 13 | 45 | 0 | 215 | 280 | 0 | 51 | 0 | 179 | 3 | 34 | 105 | 68 | 0 | 13 | 33 | 108 | 16 | 42 | 4 | 320 | 0 | 0 | 42 | 53 | 161 | 6 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 35 | 19 | 28 | 1 | 23.63 | 6 | 5657.56 | 894 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 602 | 0 | 0 | 0 | 753.86 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 16 | 24.39 | 44 | 0 | 0 | 24.66 | 186 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 2.25 | 0 | 52 | 35 | 13 | 37 | 0 | 0 | 0 | 1.6 | 74 | 0.14 | 32 | 307 | 130 | 220 | 0 | 0 | 600 | 17 | 4731.9 | 10389.46 | 95.27
10:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 452 | 0 | 0 | 51 | 48 | 95 | 15 | 17 | 51 | 0 | 0 | 0 | 0 | 0 | 17 | 260 | 0 | 0 | 22 | 52 | 23 | 20 | 0 | 0 | 34 | 16 | 32 | 0 | 0 | 0 | 0 | 0 | 36 | 25 | 2.71 | 40 | 33 | 6 | 395 | 50 | 0 | 19 | 8 | 32 | 184 | 0 | 0 | 0 | 1137 | 16 | 45 | 0 | 215 | 280 | 0 | 43 | 0 | 180 | 3 | 34 | 102 | 67 | 0 | 13 | 32 | 114 | 16 | 56 | 8 | 320 | 0 | 0 | 42 | 53 | 159 | 9 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 35 | 19 | 10 | 2 | 34.24 | 6 | 5696.95 | 894 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 605 | 0 | 0 | 0 | 756.02 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 16 | 36.07 | 69 | 0 | 0 | 40.05 | 187 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 3.62 | 0 | 53 | 35 | 23 | 34 | 0 | 0 | 0 | 3 | 107 | 0.4 | 32 | 275 | 130 | 220 | 0 | 0 | 600 | 17 | 4822.16 | 10519.11 | 95.27
11:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 455 | 0 | 0 | 51 | 48 | 95 | 15 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 17 | 260 | 0 | 0 | 27 | 52 | 23 | 20 | 0 | 0 | 34 | 16 | 43 | 0 | 0 | 0 | 8 | 0.09 | 36 | 25 | 3.26 | 40 | 33 | 3 | 395 | 48 | 0 | 19 | 8 | 34 | 184 | 0 | 0 | 0 | 1121 | 18 | 45 | 0 | 215 | 280 | 0 | 43 | 0 | 182 | 3 | 34 | 100 | 68 | 0 | 13 | 33 | 126 | 16 | 66 | 16 | 325 | 0 | 0 | 42 | 53 | 161 | 11 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 35 | 19 | 10 | 2 | 39.91 | 6 | 5750.26 | 894 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 605 | 0 | 0 | 0 | 756.41 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 16 | 45.21 | 87 | 0 | 0 | 50.23 | 186 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 4.54 | 0 | 55 | 35 | 29 | 34 | 0 | 0 | 0 | 5 | 141 | 0.47 | 32 | 278 | 128 | 220 | 0 | 0 | 600 | 17 | 4906.86 | 10657.12 | 95.27
12:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 463 | 0 | 0 | 51 | 48 | 95 | 15 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 29 | 52 | 22.8 | 20 | 0 | 0 | 34 | 16 | 39 | 0 | 0 | 0 | 8 | 17 | 36 | 25 | 3.45 | 40 | 34 | 11 | 395 | 52 | 0 | 19 | 8 | 33 | 184 | 0 | 0 | 0 | 1147 | 19 | 45 | 0 | 215 | 280 | 0 | 43 | 0 | 180 | 3 | 34 | 99 | 68 | 0 | 13 | 33 | 124 | 16 | 68 | 16 | 320 | 0 | 0 | 42 | 53 | 158 | 11 | 20 | 0 | 82 | 30 | 0 | 0 | 100 | 0 | 35 | 19 | 9 | 2 | 41.46 | 6 | 5744.71 | 894 | 190 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 606 | 0 | 0 | 0 | 756.64 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 16 | 47.61 | 95 | 0 | 0 | 53.49 | 187 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.53 | 0 | 55 | 35 | 30 | 34 | 0 | 0 | 0 | 5.6 | 150 | 0.56 | 32 | 279 | 128 | 220 | 0 | 0 | 600 | 17 | 5006.43 | 10751.14 | 95.26
13:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 461 | 13.5 | 0 | 51 | 48 | 95 | 15 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 31 | 52 | 14.5 | 20 | 0 | 0 | 34 | 16 | 39 | 0 | 0 | 0 | 8 | 17 | 36 | 25 | 3.15 | 40 | 33 | 14 | 395 | 50 | 0 | 19 | 8 | 32 | 185 | 0 | 0 | 0 | 1130 | 19 | 45 | 0 | 215 | 280 | 0 | 43 | 0 | 177 | 3 | 34 | 98 | 68 | 0 | 19 | 32 | 128 | 16 | 65 | 16 | 320 | 0 | 0 | 42 | 53 | 159 | 10 | 20 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 35 | 19 | 9 | 2 | 40.64 | 6 | 5731.79 | 894 | 180 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 607 | 0 | 0 | 0 | 758.61 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 16 | 46.3 | 92 | 0 | 0 | 54.63 | 186 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.54 | 0 | 55 | 35 | 29 | 34 | 0 | 0 | 0 | 4.8 | 143 | 0.53 | 32 | 275 | 128 | 220 | 0 | 0 | 615 | 17 | 5000.41 | 10732.2 | 95.26
14:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 434 | 16.1 | 0 | 51 | 48 | 95 | 15 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 25 | 52 | 14.5 | 20 | 0 | 0 | 34 | 16 | 36 | 0 | 5 | 0 | 8 | 17 | 36 | 25 | 2.82 | 40 | 31 | 6 | 395 | 50 | 0 | 19 | 8 | 32 | 183 | 0 | 0 | 0 | 1130 | 17 | 45 | 0 | 215 | 280 | 0 | 43 | 0 | 174 | 3 | 34 | 100 | 67 | 0 | 19 | 30 | 136 | 16 | 58 | 15 | 315 | 0 | 0 | 42 | 53 | 156 | 8 | 20 | 0 | 83 | 30 | 0 | 0 | 98 | 0 | 35 | 19 | 8 | 1.6 | 35.52 | 6 | 5666.54 | 894 | 180 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 608 | 0 | 0 | 0 | 763 | 0 | 0 | 0 | 35 | 32 | 0 | 0 | 0 | 16 | 41.3 | 78 | 0 | 0 | 39.52 | 182 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 3.21 | 0 | 55 | 35 | 17 | 34 | 0 | 0 | 0 | 4.2 | 124 | 0.45 | 32 | 274 | 127 | 180 | 0 | 0 | 622 | 17 | 4877.68 | 10544.22 | 95.26
15:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 425 | 15.7 | 0 | 52 | 48 | 95 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 18 | 52 | 23 | 20 | 0 | 0 | 34 | 16 | 38 | 0 | 5 | 0 | 8 | 17 | 36 | 25 | 2.06 | 40 | 33 | 0 | 395 | 45 | 0 | 19 | 8 | 31 | 184 | 0 | 0 | 0 | 1135 | 13 | 45 | 0 | 215 | 280 | 0 | 43 | 0 | 174 | 3 | 34 | 100 | 67 | 0 | 19 | 32 | 132 | 16 | 46 | 15 | 320 | 0 | 0 | 42 | 53 | 156 | 5 | 20 | 0 | 83 | 30 | 0 | 0 | 97 | 0 | 35 | 19 | 8 | 1 | 26.79 | 6 | 5614.55 | 894 | 180 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 607 | 0 | 0 | 0 | 769 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 16 | 31.24 | 61 | 0 | 0 | 27.62 | 178 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 2.48 | 0 | 54 | 35 | 13 | 34 | 0 | 0 | 0 | 2.4 | 81 | 0 | 32 | 275 | 127 | 220 | 0 | 0 | 610 | 17 | 4789.74 | 10404.29 | 95.26
16:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 453 | 16 | 17 | 52 | 48 | 95 | 0 | 17 | 52 | 0 | 0 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 9 | 52 | 23 | 20 | 0 | 0 | 34 | 16 | 38 | 0 | 2 | 0 | 8 | 17 | 12 | 25 | 1 | 40 | 34 | 0 | 395 | 53 | 0 | 19 | 8 | 32 | 184 | 0 | 0 | 0 | 1160 | 8 | 45 | 0 | 215 | 280 | 0 | 43 | 0 | 182 | 3 | 34 | 100 | 65 | 0 | 19 | 32 | 124 | 16 | 26 | 15 | 315 | 0 | 0 | 42 | 53 | 152 | 2 | 20 | 0 | 83 | 30 | 0 | 0 | 97 | 4 | 35 | 19 | 8 | 1 | 14.27 | 6 | 5629.27 | 894 | 172 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 609 | 0 | 0 | 0 | 763 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 16 | 16.46 | 28 | 0 | 0 | 15.65 | 177 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.2 | 0 | 55 | 35 | 9 | 34 | 0 | 0 | 0 | 1.9 | 41 | 0.15 | 32 | 278 | 127 | 220 | 0 | 0 | 600 | 17 | 4669.36 | 10298.63 | 95.25
17:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 439 | 19 | 17 | 56 | 80 | 160 | 0 | 17 | 82 | 0 | 0 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 2 | 90 | 23 | 20 | 0 | 0 | 46 | 16 | 38 | 0 | 3 | 16 | 8 | 17 | 60 | 25 | 0.2 | 40 | 44 | 6 | 395 | 75 | 0 | 19 | 8 | 49 | 184 | 0 | 0 | 0 | 1120 | 2 | 63 | 0 | 215 | 280 | 0 | 43 | 0 | 177 | 3 | 34 | 100 | 68 | 0 | 13 | 70 | 116 | 16 | 5 | 15 | 320 | 0 | 0 | 42 | 53 | 157 | 0 | 20 | 0 | 83 | 30 | 0 | 0 | 97 | 17 | 47 | 19 | 11 | 0 | 2.9 | 6 | 5908.1 | 893 | 169 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 607 | 0 | 0 | 0 | 762 | 0 | 0 | 0 | 70 | 36 | 0 | 0 | 0 | 34 | 3.15 | 7 | 14 | 0 | 3.21 | 174 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.29 | 0 | 55 | 50 | 3 | 50 | 0 | 0 | 0 | 0.5 | 12 | 0.04 | 31 | 275 | 127 | 220 | 0 | 0 | 600 | 17 | 4654.19 | 10562.29 | 95.25
18:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 478 | 34 | 17 | 86 | 80 | 160 | 0 | 35 | 85 | 0 | 0 | 0 | 0 | 0 | 35 | 240 | 0 | 0 | 0 | 90 | 23 | 20 | 0 | 0 | 61 | 16 | 52 | 0 | 0 | 34 | 8 | 22 | 60 | 25 | 0 | 40 | 68 | 14 | 395 | 85 | 0 | 32 | 16 | 66 | 184 | 0 | 0 | 0 | 1169 | 0 | 85 | 0 | 215 | 280 | 0 | 51 | 0 | 176 | 3 | 35 | 101 | 101 | 0 | 13 | 68 | 130 | 34 | 0 | 15 | 310 | 0 | 0 | 42 | 53 | 156 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 97 | 17 | 57 | 19 | 10 | 0 | 0 | 6 | 6316 | 894 | 164 | 0 | 27 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 0 | 0 | 0 | 765 | 0 | 0 | 0 | 70 | 60 | 0 | 0 | 10 | 34 | 0 | 0 | 21 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 70 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 281 | 127 | 220 | 0 | 0 | 575 | 35 | 4691 | 11007 | 95.25
19:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 435 | 33 | 21 | 86 | 80 | 160 | 0 | 35 | 90 | 0 | 0 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 0 | 90 | 23 | 20 | 0 | 0 | 63 | 16 | 60 | 0 | 0 | 34 | 8 | 35 | 60 | 25 | 0 | 40 | 67 | 17 | 395 | 80 | 0 | 32 | 16 | 66 | 184 | 0 | 0 | 0 | 1154 | 0 | 85 | 0 | 215 | 280 | 0 | 51 | 0 | 171 | 3 | 32 | 102 | 119 | 0 | 13 | 66 | 130 | 34 | 0 | 22 | 315 | 0 | 0 | 42 | 53 | 157 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 97 | 17 | 58 | 19 | 12 | 0 | 0 | 6 | 6292 | 894 | 164 | 0 | 26 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 599 | 0 | 0 | 0 | 752 | 0 | 0 | 0 | 70 | 70 | 0 | 0 | 15 | 34 | 0 | 0 | 21 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 70 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 273 | 129 | 220 | 0 | 0 | 580 | 35 | 4733 | 11025 | 95.25
19:30 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 464 | 33 | 35 | 86 | 80 | 160 | 0 | 35 | 86 | 0 | 0 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 0 | 90 | 23 | 20 | 0 | 0 | 60 | 16 | 60 | 0 | 0 | 34 | 8 | 35 | 60 | 25 | 0 | 40 | 67 | 20 | 395 | 85 | 0 | 32 | 17 | 66 | 184 | 0 | 0 | 0 | 1170 | 0 | 85 | 0 | 215 | 280 | 0 | 51 | 0 | 171 | 3 | 34 | 103 | 120 | 0 | 13 | 68 | 124 | 34 | 0 | 22 | 325 | 0 | 0 | 42 | 53 | 155 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 97 | 17 | 58 | 19 | 12 | 0 | 0 | 6 | 6361 | 893 | 164 | 0 | 26 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 601 | 0 | 0 | 0 | 765 | 0 | 0 | 0 | 70 | 70 | 0 | 0 | 15 | 34 | 0 | 0 | 21 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 70 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 280 | 130 | 220 | 0 | 0 | 622 | 35 | 4798 | 11159
20:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 456 | 32 | 35 | 86 | 80 | 160 | 0 | 35 | 88 | 0 | 0 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 0 | 90 | 23 | 20 | 0 | 0 | 62 | 16 | 60 | 0 | 0 | 34 | 8 | 35 | 60 | 25 | 0 | 40 | 67 | 20 | 395 | 85 | 0 | 32 | 17 | 67 | 184 | 0 | 0 | 0 | 1160 | 0 | 85 | 0 | 215 | 280 | 0 | 51 | 0 | 169 | 3 | 33 | 104 | 117 | 0 | 13 | 68 | 122 | 34 | 0 | 22 | 310 | 0 | 0 | 42 | 53 | 159 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 97 | 17 | 58 | 19 | 12 | 0 | 0 | 6 | 6328 | 894 | 164 | 0 | 26 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 603 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 70 | 70 | 0 | 0 | 17 | 34 | 0 | 0 | 21 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 70 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 278 | 130 | 220 | 0 | 0 | 622 | 35 | 4798 | 11126 | 95.24
21:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 461 | 18.5 | 17 | 86 | 80 | 160 | 0 | 17 | 86 | 0 | 0 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 0 | 90 | 23 | 20 | 0 | 0 | 65 | 16 | 61 | 0 | 0 | 34 | 8 | 35 | 60 | 25 | 0 | 40 | 68 | 20 | 395 | 85 | 0 | 32 | 17 | 68 | 184 | 0 | 0 | 0 | 1160 | 0 | 85 | 0 | 215 | 280 | 0 | 51 | 0 | 167 | 3 | 32 | 106 | 120 | 0 | 13 | 68 | 126 | 34 | 0 | 23 | 320 | 0 | 0 | 42 | 53 | 161 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 98 | 17 | 58 | 19 | 12 | 0 | 0 | 6 | 6307.5 | 893 | 164 | 0 | 26 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 0 | 0 | 0 | 756.97 | 0 | 0 | 0 | 70 | 70 | 0 | 0 | 10 | 34 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 70 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 307 | 130 | 220 | 0 | 0 | 622 | 35 | 4798.97 | 11106.47 | 95.24
22:00 | 0 | 51 | 8 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 451 | 18 | 17 | 86 | 80 | 160 | 0 | 17 | 87 | 0 | 0 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 0 | 90 | 21 | 20 | 0 | 0 | 67 | 16 | 63 | 0 | 0 | 34 | 8 | 35 | 60 | 25 | 0 | 40 | 68 | 23 | 395 | 83 | 0 | 32 | 17 | 68 | 184 | 0 | 0 | 0 | 1160 | 0 | 85 | 0 | 215 | 280 | 0 | 51 | 0 | 171 | 3 | 33 | 106 | 85 | 0 | 11 | 67 | 122 | 34 | 0 | 23 | 320 | 0 | 0 | 42 | 53 | 162 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 98 | 17 | 58 | 19 | 12 | 0 | 0 | 6 | 6248 | 894 | 163 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608 | 0 | 0 | 0 | 772.72 | 0 | 0 | 0 | 70 | 50 | 0 | 0 | 10 | 34 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 53 | 70 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 130 | 220 | 0 | 0 | 622 | 35 | 4761.72 | 11009.72 | 95.24
23:00 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 425 | 18 | 17 | 86 | 0 | 160 | 0 | 17 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 90 | 22 | 20 | 0 | 0 | 58 | 16 | 0 | 0 | 0 | 0 | 8 | 17 | 60 | 25 | 0 | 40 | 67 | 26 | 395 | 76 | 0 | 33 | 17 | 64 | 179 | 0 | 0 | 0 | 1146 | 0 | 85 | 0 | 215 | 280 | 0 | 51 | 0 | 178 | 0 | 17 | 106 | 76 | 0 | 11 | 0 | 114 | 34 | 0 | 24 | 310 | 0 | 0 | 42 | 53 | 154 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 99 | 17 | 59 | 19 | 12 | 0 | 0 | 6 | 5856 | 894 | 156 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 609 | 0 | 0 | 0 | 762.93 | 0 | 0 | 0 | 70 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 70 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 277 | 130 | 220 | 0 | 0 | 622 | 35 | 4648.93 | 10504.93 | 95.24
Total KWH | 0 | 660480 | 298080 | 0 | 0 | 0 | 0 | 0 | 7650000 | 0 | 11100925 | 265680 | 204120 | 1197648 | 935040 | 2125200 | 124135 | 265375 | 1195200 | 0 | 0 | 0 | 0 | 0 | 270658 | 5960557 | 0 | 0 | 186418 | 1094400 | 483000 | 487440 | 0 | 0 | 785345 | 281018 | 687360 | 0 | 20640 | 178120 | 97680 | 329431 | 744000 | 396480 | 20926 | 972000 | 894900 | 476640 | 9534545.46 | 1015345 | 0 | 424320 | 186168.6 | 872327 | 4352099 | 0 | 0 | 0 | 27398179 | 133515 | 1119054 | 0 | 5266500 | 7088600 | 0 | 1218893 | 0 | 4683000 | 48096 | 559680 | 2465693 | 1470240 | 0 | 356440 | 718200 | 2765760 | 375326 | 459582 | 245600 | 7730000 | 0 | 0 | 993000 | 1334040 | 3771164 | 66498 | 479928 | 0 | 1944960 | 713376 | 0 | 0 | 2385020 | 140400 | 849600 | 309600 | 383040 | 12350 | 269530 | 100080 | 134628645.06 | 21617454 | 4518144 | 0 | 224160 | 118784 | 0 | 0 | 0 | 0 | 0 | 0 | 480240 | 14014500 | 0 | 0 | 0 | 17539431.07 | 0 | 0 | 0 | 881280 | 794400 | 0 | 0 | 42471 | 363504 | 300840 | 587460 | 75056 | 0 | 321008 | 4351182 | 0 | 0 | 0 | 0 | 0 | 9833963 | 0 | 28080 | 0 | 1244509 | 863086 | 180985 | 804643 | 0 | 0 | 0 | 30152.16 | 920880 | 3093 | 590976 | 6523000 | 3103000 | 5546020 | 0 | 0 | 13905454.55 | 411600 | 110219355.78 | 244848000.84

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 28-01-2026
Power Supply Scenario
| Day Peak Generation |  |  | 10751.14 | MW | 12:00 Hr. | Energy Generated |  |  | 244.848 |  | MKWHr.
| Day Peak Demand |  |  | 11304.14 | MW | 12:00 Hr. | Energy Unserverd |  |  | 5.806 |  | MKWHr.
| Evening Peak Generation |  |  | 11159 | MW | 19:30 Hr. | Energy Demand |  |  | 250.654 |  | MKWHr.
| Evening Peak Demand |  |  | 11679 | MW | 19:30 Hr. | Maximum Temperature |  |  | 29.2 |  | °C
| Minimum Generation of the Day |  |  | 8034.27 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 741.17 |  | MMCFD
| Maximum Generation of the Day |  |  | 11159 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.4025 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 25.6819 | 0 | 8.636 | 0 | 0 | 0.18642 | 0 | 0 | 34.5044 | Gas | 98.7247 | Gas | 350497786.79
| Chattogram Zone |  |  | 4.8287 | 36.9327 | 6.8925 | 0 | 0.972 | 0.15444 | 0 | 0.02064 | 49.801 | Coal | 72.6202 | Coal | 464918126.0728
| Cumilla Zone |  |  | 21.1272 | 0 | 4.4881 | 0 | 0 | 0.45958 | 2.7658 | 0 | 28.8407 | HFO | 26.5863 | HFO | 462705691.892
| Mymensingh Zone |  |  | 0.38304 | 0 | 1.3997 | 0 | 0 | 0.28188 | 0 | 0 | 2.0646 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 19.3515 | 0 | 0 | 0 | 0 | 0.066498 | 0 | 0 | 19.418 | Hydro | 0.972 | Hydro | 97200
| Khulna Zone |  |  | 4.5181 | 14.0145 | 0.34294 | 0 | 0 | 0.48024 | 21.6175 | 0 | 40.9733 | Solar | 4.0016 | Solar | 63635585.112
| Barishal Zone |  |  | 8.649 | 20.4285 | 1.0026 | 0 | 0 | 0.003093 | 0 | 0 | 30.0831 | Import | 41.9226 | Import | 225489323.9806
| Rajshahi Zone |  |  | 14.1851 | 0 | 2.1567 | 0 | 0 | 1.2374 | 17.5394 | 0 | 35.1187 | Wind | 0.02064 | Wind | 303614.4
| Rangpur Zone |  |  | 0 | 1.2445 | 1.6677 | 0 | 0 | 1.132 | 0 | 0 | 4.0443
| Total |  |  | 98.7247 | 72.6202 | 26.5863 | 0 | 0.972 | 4.0016 | 41.9226 | 0.02064 | 244.848
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 350497786.79 |  | Hydro | 97200
|  |  |  | Coal | 464918126.0728 |  | Solar | 63635585.112
|  |  |  | HFO | 462705691.892 |  | Import | 225489323.9806
|  |  |  | HSD | 0 |  | Wind | 303614.4
[5 empty] | Total: | 156,76,47,328 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.6175 | Peak Hr Flow | 893.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 33424874.01 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 17.5394 | Peak Hr Flow | 765.00 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1597 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.7658 | Peak Hr Flow | 124.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1979 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 41.9226 | Peak Hr Flow | 1782.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 115 |  | 4349
|  |  |  | Chattogram |  | 0 |  | 1221
|  |  |  | Cumilla |  | 8 |  | 1000
|  |  |  | Mymensingh |  | 56 |  | 998
|  |  |  | Sylhet |  | 31 |  | 400
|  |  |  | Khulna |  | 137 |  | 1232
|  |  |  | Barishal |  | 36 |  | 322
|  |  |  | Rajshahi |  | 65 |  | 1047
|  |  |  | Rangpur |  | 50 |  | 728
|  |  |  | Total |  | 498 |  | 11297
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:11 | 17:18 | Cumilla(N)-Cumilla(S) 132 kV Ckt-3 Scheduled S/D from Cumilla(S) 132/33kV end Due to
Annual Maintenance
| 08:25 | 14:55 | Madartek-Rampura 132kV Ckt-2 Scheduled S/D from Rampura 230/132kV end Due to Annual
Maintenance
| 08:29 | 15:51 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 HT Scheduled S/D Due to Annual
Maintenance
| 08:29 | 15:50 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 LT Scheduled S/D Due to Annual
Maintenance
| 08:41 | 15:37 | Daudkandi-Sonargaon 132 kV Ckt-2 Scheduled S/D from Daudkandi 132/33kV end Due to 132 KV
Sonargaon-2 Line Shutdown for annual maintenance work
| 08:42 | 15:51 | BIPTC S/S Baharampur-4 Scheduled S/D Due to Annual Maintenance
| 08:44 | 14:49 | Madanganj-Munsiganj 132 kV Ckt-2 Project Work S/D from Madanganj 132/33kV end. and from
Munshiganj 132/33kV end Due to Insulator Replacement
| 08:46 | 14:47 | Kabirpur -Tongi 132kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Shutdown
taken by Kabirpur
| 08:47 | 16:57 | Gollamari 132/33kV S/S E01 Gollamari-Gopalgonj Line - 1 Scheduled S/D Due to Annual
Maintenance work
| 08:47 | 17:00 | Gollamari 132/33kV S/S E07 Gollamari-Gopalgonj Line - 2 Scheduled S/D Due to Annual
Maintenance work
| 08:48 | 16:59 | Gopalganj 132/33kV S/S Gallamari-1 Scheduled S/D Due to Annual maintenance
| 08:48 | 17:03 | Gopalganj 132/33kV S/S Gallamari-2 Scheduled S/D Due to Annual maintenance
| 08:57 | 16:41 | Fenchuganj-Fenchuganj 132 kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
For deadline checking
| 09:00 | 15:16 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-01 Scheduled S/D
| 09:00 | 15:39 | Daudkandi-Sonargaon 132 kV Ckt-2 Forced S/D from Sonargaon 132/33kV end Due to According
to NLDC instruction.
| 09:01 | 15:16 | Faridpur 132/33kV S/S 230kV Faridpur-Gopalganj CKT-1 Scheduled S/D
| 09:01 | 17:40 | Aminbazar-Meghnaghat 400kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Disc cleaning and from Meghnaghat 400/230kV end Due to None
| 09:08 | 15:20 | Meghnaghat-Shyampur 230kV Ckt-1 Scheduled S/D from Meghnaghat 400/230kV end Due to
Annual Maintenance work and from Shyampur 230/132kV end Due to Annual maintenane work at
Meghnaghat SS and insulator disc cleaning at tower no 22 an 23.
| 09:29 | 17:12 | Bibiyana-Shahjibazar 230 kV Ckt-1 Scheduled S/D from Bibiana 400/230kV end.
| 09:34 | 17:53 | Sirajganj-Sreepur 230 kV Ckt-1 Scheduled S/D from Sirajgonj 230 end Due to Annual
Maintenance
| 09:43 | 14:37 | Baroaulia-Hathazari 132 kV Ckt-1 Scheduled S/D from Baroaulia 132/33kV end Due to Annual
maintanance
| 09:46 | 17:52 | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-1 Scheduled S/D Due to Annual Maintenance
(Dead Line Check)
| 10:00 | 14:35 | Baroaulia-Hathazari 132 kV Ckt-1 Scheduled S/D from Hathazari 230/132/33kV end.
| 10:15 | 14:28 | Chowmuhani-Feni 132 kV Ckt-1 Project Work S/D from Feni 230/132kV end Due to Line
parameter test and from Daganbhuiyan 132/33kV end Due to Parameter test
| 10:40 | 15:05 | Shahmirpur-Sikalbaha 132kV Ckt-1 Scheduled S/D from Shahmirpur 132/33kV end Due to annual
maintenance
|  | 10:58 | Khulna(S) 230/132kV S/S TR-1 HT is restored.
| 11:01 |  | Kabirpur-Kaliakoir 132kV Ckt-1 Scheduled S/D from Kaliakoir 400/230/132kV end Due to
‍Annual Maintenance.
|  | 11:06 | Khulna(S) 230/132kV S/S TR-1 LT is restored.
| 11:22 |  | Kaliakoir 400/230/132kV S/S 132kV Bus 2 Scheduled S/D Due to Annual Maintenance.
| 11:26 | 19:21 | Kasba 132/33kV S/S TR-1 LT Project Work S/D
| 11:26 | 19:21 | Kasba 132/33kV S/S TR-1 HT Project Work S/D
| 12:10 | 14:02 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Kosba Ckt-01 Project Work S/D Due to
Maintenance Work
| 12:14 | 14:03 | Kasba 132/33kV S/S Muradnagar-Kasba Ckt-1 Project Work S/D Due to check phase sequence
|  | 12:52 | BSRM 230/33kV S/S 230/33 kV Transformer-3 (125/140 MVA) HT is restored.
|  | 13:38 | Chowmuhani-Feni 132 kV Ckt-2 is restored.
|  | 13:38 | Chowmuhani-Feni 132 kV Ckt-2 is restored.
| 14:38 | 17:35 | Chowmuhani-Feni 132 kV Ckt-1 Scheduled S/D from Daganbhuiyan 132/33kV end Due to Project
work and from Chowmuhani 132/33kV end Due to Request by Daganbhuiyan Grid
| 14:48 | 17:50 | Kabirpur -Tongi 132kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Annual
maintenance by kabirpur grid
| 14:58 | 17:45 | Chowmuhani-Feni 132 kV Ckt-2 Scheduled S/D from Daganbhuiyan 132/33kV end Due to Project
work and from Chowmuhani 132/33kV end Due to Request by Daganbhuiyan Grid
| 15:14 | 17:18 | Niamatpur 132/33kV S/S Transformer-2 (417T) LT Tripped showing OC/ Earth fault relays.
|  | 15:31 | BSRM-Cumilla(N) 230 kV Ckt-1 is restored.
|  | 15:50 | Madanganj 132/33kV S/S GT-2 HT is restored.
|  | 15:56 | Madanganj 132/33kV S/S GT-2 LT is restored.
|  | 16:54 | Rajshahi 132/33kV S/S Transformer T-2(415T) HT is restored.
|  | 16:56 | Rajshahi 132/33kV S/S Transformer T-2(415T) LT is restored.
|  | 17:10 | Maniknagar-Siddhirganj 230kV Ckt-2 is restored.
|  | 17:12 | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) HT is restored.
|  | 17:17 | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) LT is restored.
|  | 17:22 | Purbasadipur 132/33kV S/S T-3 Transformer (423T) HT is restored.
|  | 17:44 | Purbasadipur 132/33kV S/S T-3 Transformer (423T) LT is restored.
| 19:05 | 19:20 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing Gen. Trip, Non Dir OC DMT Trip. relays | [7 empty] | 8.0MW load
|  |  | Due to Shaistaganj Feeder Flashing. | [7 empty] | interrup.
| 05:00 |  | Minimum Generation is 8151 MW
| 07:46 |  | Khulshi 132/33kV S/S 405T (T1) HT Scheduled S/D Due to 132/33kV TR-01 given Shutdown due
to Annual maintenance work.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 28-01-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 301 | 7650000 | Gas (RMS) problem
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 124135 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 240 | 5960557 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 33 | 265680 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 80 | 935040 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 265375 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 270658 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 483000 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 487440 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 298080 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 160 | 2125200 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 86 | 1197648 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 51 | 660480 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 86 | 1195200 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 186418 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 204120 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 464 | 11100925 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 90 | 1094400 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1746 | 34504356
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 186168.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 133515 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 32 | 424320 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 972000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 184 | 4352099 | Plant availability less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 66 | 872327 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 8 | 97680 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 178120 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 60 | 744000 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 476640 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 60 | 687360 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20926 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 281018 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 35 | 329431 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 67 | 894900 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 396480 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 60 | 785345 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 85 | 1015345 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1170 | 27398179 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 20640 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 395 | 9534545.46 | U2 S/D 9/Jan/26 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4898.863 | 2374 | 49801039.06
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 171 | 4683000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 280 | 7088600 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 215 | 5266500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 3 | 48096 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1218893 | Gas shortage
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 85 | 1119054 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 22 | 245600 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 103 | 2465693 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 120 | 1470240 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 124 | 2765760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 34 | 375326 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 356440 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 68 | 718200 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 34 | 559680 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 459582 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1323 | 28840664
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 12 | 383040 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12350 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 309600 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 58 | 849600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 269530 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 100080 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 140400 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 112 | 2064600
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 66498 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 993000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 53 | 1334040 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3771164 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 713376 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1944960 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 97 | 2385020 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 479928 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 325 | 7730000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | plant will be shutdown due to 3rd Minor Inspection
Sylhet Area Total |  |  |  |  | 2325 | 806 | 19417986
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 893 | 21617454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 26 | 224160 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 35 | 118784 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 164 | 4518144 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 480240 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 601 | 14014500 | U#1 Under Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1719 | 40973282
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 44 | 590976 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 3103000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 622 | 13905454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5546020 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 411600 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 280 | 6523000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3093 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1331 | 30083143.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 300840 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Machine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 15 | 42471 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 172 | 4351182 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9833963 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 75056 | machine problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 34 | 363504 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 794400 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 70 | 881280 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 28080 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 765 | 17539431.07 | U#1 Under AOH
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 321008 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 587460 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1561 | 35118675.07
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 55 | 1244509 | plant availability zero
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 62 | 804643 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 30152.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 863086 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 180985 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 920880 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 187 | 4044255.16
Eastern Grid Total |  |  |  |  | 17398.245 | 6361 | 134628645.06
Western Grid Total |  |  |  |  | 10984.003 | 4798 | 110219355.78
National Grid Total |  |  |  |  | 28382.248 | 11159 | 244848000.84
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 28-01-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7758.34 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3040.5 | MW
i) Dhaka area |  |  | 4234.44 |  | MW | i) Khulna area |  |  |  | 1095.4 | MW
ii) Chattogram area |  |  | 1220.9 |  | MW | ii) Barishal area |  |  |  | 285.5 | MW
iii) Cumilla area |  |  | 992 |  | MW | iii) Rajshahi area |  |  |  | 981.6 | MW
iv) Mymensingh area |  |  | 942 |  | MW | iv) Rangpur area |  |  |  | 678 | MW
v) Sylhet area |  |  | 369 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10798.84 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 12 | 21:00 | 67 | Hasnabad | 70 | 21:00 | 133 | Netrakona | 130 | 20:00
2 | AKSML | 124.6 | 06:00 | 68 | Hathazari | 55 | 21:00 | 134 | New | 64 | 12:00
3 | Aftabnagar | 26 | 15:00 | 69 | Hatirjheel | 32 | 14:00 | 135 | Niamatpur | 84 | 10:00
4 | Agargaon | 85 | 13:00 | 70 | Ishurdi | 51 | 18:30 | 136 | Noapara | 34 | 22:00
5 | Agrabad | 28 | 15:00 | 71 | Jaldhaka | 48 | 10:00 | 137 | PHP | 7 | 10:00
6 | Amnura | 33 | 10:00 | 72 | Jamalpur | 91 | 14:00 | 138 | Pabna | 77 | 18:30
7 | Ashuganj | 63 | 19:00 | 73 | Jashore | 101 | 14:00 | 139 | Palashbari | 84 | 22:00
8 | BSRM | 198 | 19:30 | 74 | Jhenaidah | 85 | 21:00 | 140 | Panchagarh | 38 | 18:30
9 | Bagerhat | 63 | 22:00 | 75 | Joydebpur | 106 | 17:00 | 141 | Patiya | 7 | 18:00
10 | Bajitpur | 59 | 19:30 | 76 | Joypurhat | 46 | 10:00 | 142 | Patuakhali | 36.5 | 20:00
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 18 | 15:00 | 143 | Payra | 28 | 19:30
12 | Bakulia | 69 | 13:00 | 78 | KSRM | 12 | 05:00 | 144 | Postogola | 43 | 13:00
13 | Banani | 40 | 12:00 | 79 | Kabirpur | 210 | 08:00 | 145 | Purbachal | 24 | 13:00
14 | Bangabhaban | 11 | 11:00 | 80 | Kachua | 63 | 19:30 | 146 | Purbasadipur | 107 | 18:00
15 | Barapukuria | 59 | 19:30 | 81 | Kallyanpur | 78 | 13:00 | 147 | Rahanpur | 25 | 11:00
16 | Barguna | 14 | 18:00 | 82 | Kalurghat | 34 | 12:00 | 148 | Rahim | 44 | 08:00
17 | Barishal | 80 | 22:00 | 83 | Kamrangirchar | 72 | 13:00 | 149 | Rajbari | 55 | 22:00
18 | Barishal-230 | 62 | 18:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 112 | 19:00
19 | Baroaulia | 62 | 13:00 | 85 | Kasba | 24 | 13:00 | 151 | Rajshahi | 70 | 18:30
20 | Baroirhat | 44 | 18:00 | 86 | Kazla | 91 | 12:00 | 152 | Rajshahi-230 | 70 | 13:00
21 | Bashundhara | 159 | 13:00 | 87 | Keranigonj | 60 | 10:00 | 153 | Ramganj | 68 | 21:00
22 | BashundharaCement | 7 | 00:00 | 88 | Khagrachori | 28 | 18:00 | 154 | Rampur | 30 | 14:00
23 | Beanibazar | 50 | 23:00 | 89 | Khulna | 47 | 12:00 | 155 | Rangamati | 15 | 18:00
24 | Benapole | 52 | 22:00 | 90 | Khulshi | 175 | 18:30 | 156 | Rangpur | 104 | 20:00
25 | Bhaluka | 120 | 10:00 | 91 | Kishoreganj | 107 | 19:30 | 157 | Ruppur | 3 | 16:00
26 | Bhandaria | 34 | 22:00 | 92 | Kodda | 264 | 10:00 | 158 | SSM | 0 | 00:00
27 | Bhangura | 25 | 13:00 | 93 | Kulaura | 29 | 18:00 | 159 | Saidpur | 86 | 11:00
28 | Bheramara(GK) | 37 | 14:00 | 94 | Kurigram | 50 | 10:00 | 160 | Satkhira | 81 | 22:00
29 | Bhulta | 204 | 19:30 | 95 | Kushtia | 102 | 13:00 | 161 | Satmasjid | 85 | 13:00
30 | Bog-Sherpur | 52 | 18:00 | 96 | Laksam | 13 | 13:00 | 162 | Savar | 182 | 16:00
31 | Bogura | 116 | 18:30 | 97 | Lakshmipur | 25 | 20:00 | 163 | SevenRings | 16.58 | 00:00
32 | Borhanuddin | 64 | 22:00 | 98 | Lalbag | 56 | 18:00 | 164 | ShahCement | 36 | 13:00
33 | Brahmanbaria | 96 | 18:00 | 99 | Lalmonirhat | 39 | 18:30 | 165 | Shahjadpur | 52 | 11:00
34 | Cantonment | 72 | 13:00 | 100 | MI_Cement | 17.3 | 02:00 | 166 | Shahjibazar | 96 | 23:00
35 | Chandina | 13 | 18:00 | 101 | Madanganj | 32 | 18:00 | 167 | Shahmirpur | 37 | 19:30
36 | Chandpur | 50 | 18:30 | 102 | Madaripur | 75 | 22:00 | 168 | Shariatpur | 58 | 22:00
37 | Chandraghona | 27 | 19:30 | 103 | Madartek | 62 | 13:00 | 169 | Sherpur | 124 | 00:00
38 | Chapai | 56 | 10:00 | 104 | Madunaghat | 38 | 13:00 | 170 | Shikalbaha | 22 | 19:30
39 | Charsaidpur | 43 | 07:00 | 105 | Magura | 40 | 13:00 | 171 | Shitalakhya | 70.7 | 12:00
40 | Chauddagram | 50 | 13:00 | 106 | Mahasthangarh | 50 | 18:30 | 172 | Sholosohor | 34 | 12:00
41 | Chhatak | 24 | 21:00 | 107 | Maijdee | 34 | 19:30 | 173 | Shyampur | 156 | 13:00
42 | Chowmuhani | 107 | 19:30 | 108 | Manikganj | 98 | 19:30 | 174 | Siddhirganj | 117 | 12:00
43 | Chuadanga | 69 | 13:00 | 109 | Maniknagar | 43 | 13:00 | 175 | Sirajganj | 80 | 19:00
44 | Coxsbazar | 114 | 18:00 | 110 | Matarbari | 41 | 19:30 | 176 | Sonargaon | 142 | 09:00
45 | Cumilla(N) | 89 | 12:00 | 111 | Matuail | 56 | 12:00 | 177 | Sreemongol | 59 | 21:00
46 | Cumilla(S) | 137 | 14:00 | 112 | Metrorail_Motijheel | 32 | 20:00 | 178 | Sreepur | 101 | 09:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 0 | 00:00 | 179 | Srinagar | 30.52 | 22:00
48 | Daudkandi | 117 | 19:30 | 114 | Millgate | 78 | 15:00 | 180 | Sunamganj | 40 | 21:00
49 | DhakaUniversity | 66 | 13:00 | 115 | Mirpur | 115 | 12:00 | 181 | Sylhet | 33 | 21:00
50 | Dhamrai | 110 | 08:00 | 116 | Mirsorai | 11 | 15:00 | 182 | Sylhet-132 | 76 | 21:00
51 | Dhanmondi | 83 | 13:00 | 117 | Mirzapur | 38 | 07:00 | 183 | TK | 15 | 10:00
52 | Dohazari | 78 | 19:00 | 118 | Mithapukur | 38 | 18:30 | 184 | Tangail | 134 | 18:00
53 | Faridpur | 105 | 21:00 | 119 | Modern | N/A | N/A | 185 | Taraganj | 20 | 18:00
54 | Fatullah | 80 | 15:00 | 120 | Mogbazar | 65.2 | 14:00 | 186 | Tasnim | 29 | 08:00
55 | Fenchuganj | 25 | 18:00 | 121 | Mongla | 37 | 18:00 | 187 | Thakurgaon | 70 | 18:30
56 | Feni | 83 | 18:00 | 122 | Motijheel | 38 | 13:00 | 188 | Tongi | 114 | 18:00
57 | GPH | 97 | 06:00 | 123 | Muktagacha | 27 | 12:00 | 189 | Ullahpara | 28 | 18:30
58 | Ghatail | 66 | 18:00 | 124 | Munshiganj | 69 | 22:00 | 190 | Ullon | 48 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 27 | 19:30 | 191 | Uttara | 55 | 13:00
60 | Ghorashal-230 | 96 | 19:30 | 126 | Mymensingh | 178 | 18:30 | 192 | UttaraNew | 24 | 13:00
61 | Goalpara | 27 | 18:00 | 127 | Naogaon | 99 | 10:00 | 193 | Zigatola | 62 | 14:00
62 | Gollamari | 70 | 22:00 | 128 | Narail | 39 | 22:00
63 | Gopalganj | 71 | 18:30 | 129 | Narinda | 62 | 13:00
64 | Gulshan | 78 | 13:00 | 130 | Narshingdi | 144 | 21:00
65 | Halishahar | 71 | 15:00 | 131 | Natore | 99 | 10:00
66 | HaripurSBU | 125 | 10:00 | 132 | Nawabganj | 41.8 | 15:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 28-01-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 9689.96 | 0 |  | 9689.96
1:00 | 8968.21 | 0 |  | 8968.21
2:00 | 8742.93 | 0 |  | 8742.93
3:00 | 8366.2 | 0 |  | 8366.2
4:00 | 8202.72 | 0 |  | 8202.72
5:00 | 8034.27 | 0 |  | 8034.27
6:00 | 8428.12 | 117 |  | 8550.12
7:00 | 8916.2 | 256 |  | 9184.2
8:00 | 10004.54 | 305 |  | 10323.54
9:00 | 10389.46 | 301 |  | 10704.46
10:00 | 10519.11 | 98 |  | 10621.11
11:00 | 10657.12 | 283 |  | 10953.12
12:00 | 10751.14 | 529 |  | 11304.14
13:00 | 10732.2 | 643 |  | 11404.2
14:00 | 10544.22 | 497 |  | 11063.22
15:00 | 10404.29 | 477 |  | 10902.29
16:00 | 10298.63 | 259 |  | 10569.29
17:00 | 10562.29 | 181 |  | 10751.29
18:00 | 11007 | 471 |  | 11499.2
19:00 | 11025 | 501 |  | 11548.55
19:30 | 11159 | 498 |  | 11679
20:00 | 11126 | 481 |  | 11629
21:00 | 11106.47 | 368 |  | 11491.03
22:00 | 11009.72 | 39 |  | 11050.72
23:00 | 10504.93 | 0 |  | 10504.93
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 28-01-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5268 | 4421.96 | 9689.96 | DAILY GENERATION CURVE
00:30 | 4973 | 4356.085 | 9329.085
01:00 | 4678 | 4290.21 | 8968.21 | 28-01-2026
01:30 | 4643.25 | 4212.32 | 8855.57
02:00 | 4608.5 | 4134.43 | 8742.93
02:30 | 4623 | 3931.565 | 8554.565
03:00 | 4637.5 | 3728.7 | 8366.2
03:30 | 4601 | 3683.46 | 8284.46
04:00 | 4564.5 | 3638.22 | 8202.72
04:30 | 4542.5 | 3575.995 | 8118.495
05:00 | 4520.5 | 3513.77 | 8034.27
05:30 | 4596.5 | 3634.695 | 8231.195
06:00 | 4672.5 | 3755.62 | 8428.12
06:30 | 4711.67 | 3960.49 | 8672.16
07:00 | 4750.84 | 4165.36 | 8916.2
07:30 | 5096.545 | 4363.825 | 9460.37
08:00 | 5442.25 | 4562.29 | 10004.54
08:30 | 5549.905 | 4647.095 | 10197
09:00 | 5657.56 | 4731.9 | 10389.46
09:30 | 5677.255 | 4777.03 | 10454.285
10:00 | 5696.95 | 4822.16 | 10519.11
10:30 | 5723.605 | 4864.51 | 10588.115
11:00 | 5750.26 | 4906.86 | 10657.12
11:30 | 5747.485 | 4956.645 | 10704.13
12:00 | 5744.71 | 5006.43 | 10751.14
12:30 | 5738.25 | 5003.42 | 10741.67
13:00 | 5731.79 | 5000.41 | 10732.2
13:30 | 5699.165 | 4939.045 | 10638.21
14:00 | 5666.54 | 4877.68 | 10544.22
14:30 | 5640.545 | 4833.71 | 10474.255
15:00 | 5614.55 | 4789.74 | 10404.29
15:30 | 5621.91 | 4729.55 | 10351.46
16:00 | 5629.27 | 4669.36 | 10298.63
16:30 | 5768.685 | 4661.775 | 10430.46
17:00 | 5908.1 | 4654.19 | 10562.29
17:30 | 6112.05 | 4672.595 | 10784.645
18:00 | 6316 | 4691 | 11007
18:30 | 6304 | 4712 | 11016
19:00 | 6292 | 4733 | 11025
19:30 | 6361 | 4798 | 11159
20:00 | 6328 | 4798 | 11126
20:30 | 6317.75 | 4798.485 | 11116.235 |  | Executive Engineer
21:00 | 6307.5 | 4798.97 | 11106.47 |  | Network Operation Division
21:30 | 6277.75 | 4780.345 | 11058.095
22:00 | 6248 | 4761.72 | 11009.72
22:30 | 6052 | 4705.325 | 10757.325
23:00 | 5856 | 4648.93 | 10504.93

## En-Curve
QF-LDC-12
Date | 28-01-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2711 | 1409 | 894 | 0 | 104 | 765.96 | 40 | 3137 | 0 | 0 | 629 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2687.5 | 1408 | 894 | 0 | 100 | 764.585 | 40 | 3118 | 0 | 0 | 314.5 | 0 | 0 | 2.5 | 0 | 28-01-2026
01:00 | 2664 | 1407 | 894 | 0 | 96 | 763.21 | 40 | 3099 | 0 | 0 | 0 | 0 | 0 | 5 | 0
01:30 | 2649.5 | 1376.25 | 894 | 0 | 98 | 761.82 | 40 | 3032 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | Energy Generated | 244.848 |  | MKWHr
02:00 | 2635 | 1345.5 | 894 | 0 | 100 | 760.43 | 40 | 2965 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | Energy not Served | 5.806 |  | MKWHr
02:30 | 2661 | 1378 | 894 | 0 | 99 | 680.065 | 40 | 2800.5 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | Total Energy Requirement | 250.654 |  | MKWHr
03:00 | 2687 | 1410.5 | 894 | 0 | 98 | 599.7 | 40 | 2636 | 0 | 0 | 0 | 0 | 0 | 1 | 0
03:30 | 2709.5 | 1398 | 894 | 0 | 97 | 585.96 | 40 | 2559 | 0 | 0 | 0 | 0 | 0 | 1 | 0
04:00 | 2732 | 1385.5 | 894 | 0 | 96 | 572.22 | 40 | 2482 | 0 | 0 | 0 | 0 | 0 | 1 | 0
04:30 | 2725 | 1373.5 | 894 | 0 | 92 | 543.995 | 40 | 2449.5 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0
05:00 | 2718 | 1361.5 | 894 | 0 | 88 | 515.77 | 40 | 2417 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 2730.5 | 1387.5 | 894 | 0 | 95 | 571.195 | 40 | 2513 | 0 | 0 | 0 | 0 | 0 | 0 | 58.5
06:00 | 2743 | 1413.5 | 894 | 0 | 102 | 626.62 | 40 | 2609 | 0 | 0 | 0 | 0 | 0 | 0 | 117
06:30 | 2744 | 1420.75 | 894 | 0 | 103 | 695.26 | 40 | 2769 | 6.15 | 0 | 0 | 0 | 0 | 0 | 186.5
07:00 | 2745 | 1428 | 894 | 0 | 104 | 763.9 | 40 | 2929 | 12.3 | 0 | 0 | 0 | 0 | 0 | 256
07:30 | 2720 | 1403.5 | 894 | 0 | 104 | 760.455 | 40 | 2989 | 76.915 | 61.5 | 411 | 0 | 0 | 0 | 280.5
08:00 | 2695 | 1379 | 894 | 0 | 104 | 757.01 | 40 | 3049 | 141.53 | 123 | 822 | 0 | 0 | 0 | 305
08:30 | 2690.5 | 1370.5 | 894 | 0 | 106 | 755.435 | 40 | 3062.5 | 233.565 | 137 | 907.5 | 0 | 0 | 0 | 303
09:00 | 2686 | 1362 | 894 | 0 | 108 | 753.86 | 40 | 3076 | 325.6 | 151 | 993 | 0 | 0 | 0 | 301
09:30 | 2677 | 1357.5 | 894 | 0 | 111 | 754.94 | 40 | 3070.5 | 403.845 | 154.5 | 991 | 0 | 0 | 0 | 199.5
10:00 | 2668 | 1353 | 894 | 0 | 114 | 756.02 | 40 | 3065 | 482.09 | 158 | 989 | 0 | 0 | 0 | 98
10:30 | 2665 | 1358 | 894 | 0 | 120 | 756.215 | 40 | 3059.5 | 541.355 | 166 | 988.045 | 0 | 0 | 0 | 190.5
11:00 | 2662 | 1363 | 894 | 0 | 126 | 756.41 | 40 | 3054 | 600.62 | 174 | 987.09 | 0 | 0 | 0 | 283
11:30 | 2661 | 1367.9 | 894 | 0 | 125 | 756.525 | 40 | 3068 | 617.16 | 180.5 | 994.045 | 0 | 0 | 0 | 406
12:00 | 2660 | 1372.8 | 894 | 0 | 124 | 756.64 | 40 | 3082 | 633.7 | 187 | 1001 | 0 | 0 | 0 | 529
12:30 | 2650 | 1373.15 | 894 | 0 | 126 | 757.625 | 40 | 3079.5 | 626.145 | 188.5 | 1006.75 | 0 | 0 | 0 | 586
13:00 | 2640 | 1373.5 | 894 | 0 | 128 | 758.61 | 40 | 3077 | 618.59 | 190 | 1012.5 | 0 | 0 | 0 | 643
13:30 | 2630.5 | 1332 | 894 | 0 | 132 | 760.805 | 40 | 3080.5 | 570.105 | 188.5 | 1007.3 | 0 | 0 | 2.5 | 570
14:00 | 2621 | 1290.5 | 894 | 0 | 136 | 763 | 40 | 3084 | 521.62 | 187 | 1002.1 | 0 | 0 | 5 | 497
14:30 | 2612.5 | 1309.75 | 894 | 0 | 134 | 766 | 40 | 3080 | 450.105 | 187 | 995.9 | 0 | 0 | 5 | 487
15:00 | 2604 | 1329 | 894 | 0 | 132 | 769 | 40 | 3076 | 378.59 | 187 | 989.7 | 0 | 0 | 5 | 477
15:30 | 2615 | 1338.5 | 894 | 0 | 128 | 766 | 40 | 3086.5 | 289.11 | 189 | 1001.85 | 0 | 0 | 3.5 | 368
16:00 | 2626 | 1348 | 894 | 0 | 124 | 763 | 40 | 3097 | 199.63 | 191 | 1014 | 0 | 0 | 2 | 259
16:30 | 2622 | 1346 | 893.5 | 0 | 120 | 762.5 | 40 | 3074.5 | 124.46 | 241.5 | 1203.5 | 0 | 0 | 2.5 | 220
17:00 | 2618 | 1344 | 893 | 0 | 116 | 762 | 40 | 3052 | 49.29 | 292 | 1393 | 0 | 0 | 3 | 181
17:30 | 2614 | 1366.5 | 893.5 | 0 | 123 | 763.5 | 40 | 3050.5 | 24.645 | 343 | 1564.5 | 0 | 0 | 1.5 | 326
18:00 | 2610 | 1389 | 894 | 0 | 130 | 765 | 40 | 3049 | 0 | 394 | 1736 | 0 | 0 | 0 | 471
18:30 | 2610 | 1372 | 894 | 0 | 130 | 758.5 | 40 | 3052.5 | 0 | 404.5 | 1754.5 | 0 | 0 | 0 | 486
19:00 | 2610 | 1355 | 894 | 0 | 130 | 752 | 40 | 3056 | 0 | 415 | 1773 | 0 | 0 | 0 | 501
19:30 | 2611 | 1395 | 893 | 0 | 124 | 765 | 40 | 3123 | 0 | 407 | 1801 | 0 | 0 | 0 | 498
20:00 | 2609 | 1376 | 894 | 0 | 122 | 760 | 40 | 3113 | 0 | 409 | 1803 | 0 | 0 | 0 | 481
20:30 | 2609.5 | 1384.5 | 893.5 | 0 | 124 | 758.485 | 40 | 3129 | 0 | 395.5 | 1781.75 | 0 | 0 | 0 | 424.5
21:00 | 2610 | 1393 | 893 | 0 | 126 | 756.97 | 40 | 3145 | 0 | 382 | 1760.5 | 0 | 0 | 0 | 368
21:30 | 2612 | 1388 | 893.5 | 0 | 124 | 764.845 | 40 | 3145 | 0 | 356 | 1734.75 | 0 | 0 | 0 | 203.5
22:00 | 2614 | 1383 | 894 | 0 | 122 | 772.72 | 40 | 3145 | 0 | 330 | 1709 | 0 | 0 | 0 | 39
22:30 | 2612 | 1363 | 894 | 0 | 118 | 767.825 | 40 | 3124.5 | 0 | 261.5 | 1576.5 | 0 | 0 | 0 | 19.5
23:00 | 2610 | 1343 | 894 | 0 | 114 | 762.93 | 40 | 3104 | 0 | 193 | 1444 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 28-01-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 422 | 05:00 | 400 | 08:00 | Madunaghat | 417 | 08:00 | 403 | 11:00
Amtali | 427 | 05:00 | 415 | 12:00 | Meghnaghat | 426 | 05:00 | 411 | 12:00
Ashuganj | 411 | 5:00 | 393 | 12:00 | Payra | 428 | 05:00 | 418 | 11:00
Bhulta | 403 | 04:00 | 384 | 12:00 | Rahanpur | 420 | 05:00 | 409 | 10:00
Bibiana | 422 | 04:00 | 412 | 12:00 | Rampal | 418 | 03:00 | 402 | 12:00
BIPTC | 404 | 04:00 | 385 | 13:00
Bogura | 416 | 04:00 | 404 | 10:00
Gopalganj | 423 | 05:00 | 409 | 12:00
Kaliakoir | 415 | 03:00 | 401 | 12:00
Korerhat | 425 | 05:00 | 416 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 244 | 05:00 | 231 | 12:00 | Jhenaidah | 243 | 05:00 | 229 | 12:00
AKSML | 241 | 08:00 | 235 | 16:00 | Kachua | 242 | 00:00 | 239 | 01:00
Aminbazar | 243 | 03:00 | 231 | 12:00 | Kaliakoir | 243 | 04:00 | 232 | 12:00
Ashuganj | 239 | 03:00 | 229 | 12:00 | Keranigonj | 242 | 05:00 | 229 | 12:00
Ashuganj-400 | 239 | 03:00 | 229 | 12:00 | Khulna(S) | 245 | 04:00 | 232 | 12:00
Baghabari | 242 | 04:00 | 235 | 10:00 | Korerhat | 242 | 05:00 | 233 | 12:00
Barapukuria | 233 | 19:00 | 223 | 10:00 | Madunaghat | 239 | 05:00 | 235 | 07:00
Barapukuria-230 | 233 | 19:00 | 223 | 10:00 | Madunaghat-400 | 240 | 09:00 | 237 | 02:00
Barishal | 239 | 05:00 | 235 | 00:00 | Maniknagar | 240 | 05:00 | 228 | 12:00
Bheramara | 240 | 05:00 | 230 | 12:00 | Meghnaghat | 247 | 03:00 | 236 | 13:00
Bhulta | 242 | 04:00 | 229 | 12:00 | Meghnaghat-400 | 241 | 05:00 | 231 | 12:00
Bibiana | 245 | 03:00 | 237 | 12:00 | Mirsorai | 242 | 08:00 | 237 | 07:00
BIPTC | 243 | 05:00 | 230 | 12:00 | Rajshahi | 241 | 05:00 | 229 | 12:00
Bogura | 244 | 05:00 | 237 | 10:00 | Rampal | 242 | 03:00 | 229 | 12:00
Bogura-400 | 242 | 04:00 | 235 | 10:00 | Rampur | N/A | N/A | N/A | N/A
Borhanuddin | 240 | 22:00 | 237 | 09:00 | Rampura | 242 | 05:00 | 229 | 12:00
BSRM | 242 | 22:00 | 237 | 13:00 | Shikalbaha | 239 | 21:00 | 235 | 00:00
Chowmuhani | N/A | N/A | N/A | N/A | Shyampur | 242 | 05:00 | 228 | 12:00
Cumilla(N) | 239 | 02:00 | 231 | 12:00 | Siddhirganj | 243 | 04:00 | 230 | 12:00
Faridpur | 239 | 05:00 | 232 | 12:00 | Sirajgonj | 246 | 04:00 | 240 | 14:00
Fenchuganj | 245 | 18:30 | 240 | 13:00 | Sreepur | 237 | 23:00 | 225 | 14:00
Feni | 242 | 05:00 | 237 | 13:00 | Tongi | 241 | 04:00 | 230 | 11:00
Ghorashal | 240 | 00:00 | 232 | 12:00
Ghorashal-230 | 240 | 04:00 | 229 | 12:00
Gopalganj | 237 | 04:00 | 230 | 12:00
GPH | 240 | 08:00 | 235 | 18:00
Haripur | 242 | 05:00 | 230 | 12:00
Hasnabad | 240 | 02:00 | 228 | 12:00
Hathazari | 238 | 07:00 | 232 | 16:00
Ishurdi | 244 | 05:00 | 233 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 133 | 03:00 | 125 | 12:00 | Maijdee | 135 | 00:00 | 133 | 13:00
Agargaon | 139 | 05:00 | 131 | 12:00 | Manikganj | 129 | 01:00 | 121 | 12:00
Agrabad | 139 | 08:00 | 132 | 12:00 | Maniknagar | 138 | 04:00 | 126 | 12:00
AKS | 136 | 18:00 | 134 | 10:00 | Matarbari | 137 | 18:00 | 126 | 19:30
Aminbazar | 140 | 00:00 | 132 | 12:00 | Matuail | 137 | 02:00 | 132 | 12:00
Amnura | 139 | 04:00 | 133 | 11:00 | Metrorail_Motijheel | 138 | 04:00 | 126 | 13:00
Ashuganj | 138 | 02:00 | 135 | 08:00 | Metrorail_Uttara | 133 | 03:00 | 125 | 12:00
Bagerhat | 135 | 03:00 | 125 | 12:00 | Millgate | 133 | 02:00 | 126 | 12:00
Bajitpur | 134 | 02:00 | 128 | 10:00 | Mirpur | 139 | 00:00 | 131 | 12:00
Bakerganj | 141 | 00:00 | 137 | 12:00 | Mirzapur | 133 | 04:00 | 129 | 10:00
Bakulia | 140 | 00:00 | 137 | 13:00 | Mithapukur | 136 | 19:00 | 127 | 10:00
Banani | 134 | 04:00 | 125 | 12:00 | MI_Cement | 136 | 00:00 | 126 | 12:00
Bangabhaban | 138 | 04:00 | 125 | 12:00 | Modern | N/A | N/A | N/A | N/A
Barapukuria | 136 | 23:00 | 129 | 10:00 | Mogbazar | 135 | 02:00 | 126 | 12:00
Barguna | 141 | 18:30 | 137 | 12:00 | Mongla | 135 | 05:00 | 125 | 12:00
Barishal | 140 | 00:00 | 137 | 13:00 | Motijheel | 138 | 04:00 | 125 | 12:00
Barishal-230 | 140 | 03:00 | 137 | 10:00 | Muktagacha | 127 | 08:00 | 117 | 14:00
Baroaulia | 140 | 17:00 | 137 | 16:00 | Munshiganj | 136 | 02:00 | 127 | 11:00
Baroirhat | 136 | 01:00 | 134 | 12:00 | Muradnagar | 138 | 04:00 | 133 | 12:00
Bashundhara | 134 | 03:00 | 125 | 12:00 | Mymensingh | 129 | 00:00 | 114 | 14:00
BashundharaCement | 134 | 01:00 | 132 | 00:00 | Naogaon | 136 | 19:00 | 129 | 10:00
Beanibazar | 134 | 04:00 | 130 | 13:00 | Narail | 138 | 05:00 | 129 | 12:00
Benapole | 137 | 04:00 | 124 | 12:00 | Narinda | 138 | 04:00 | 126 | 12:00
Bhaluka | 133 | 18:00 | 126 | 10:00 | Narshingdi | 135 | 18:00 | 125 | 11:00
Bhandaria | 140 | 08:00 | 136 | 13:00 | Natore | 138 | 19:00 | 134 | 10:00
Bhangura | 140 | 02:00 | 135 | 10:00 | Nawabganj | 136 | 03:00 | 127 | 12:00
Bheramara | 140 | 05:00 | 135 | 11:00 | Netrakona | 125 | 04:00 | 116 | 08:00
Bheramara(GK) | 140 | 03:00 | 136 | 10:00 | New | 133 | 01:00 | 126 | 10:00
Bhulta | 132 | 00:00 | 126 | 12:00 | Niamatpur | 141 | 05:00 | 136 | 13:00
Bog-Sherpur | 138 | 03:00 | 133 | 10:00 | Noapara | 136 | 03:00 | 126 | 13:00
Bogura | 139 | 00:00 | 134 | 10:00 | Pabna | 140 | 04:00 | 135 | 11:00
Bogura-230 | 139 | 18:00 | 134 | 10:00 | Palashbari | 134 | 00:00 | 127 | 10:00
Brahmanbaria | 132 | 06:00 | 126 | 13:00 | Panchagarh | 138 | 23:00 | 127 | 10:00
Cantonment | 138 | 03:00 | 130 | 12:00 | Patiya | 139 | 08:00 | 135 | 01:00
Chandina | 140 | 04:00 | 135 | 12:00 | Patuakhali | 141 | 18:30 | 135 | 09:00
Chandpur | 141 | 00:00 | 137 | 01:00 | Payra | 140 | 05:00 | 138 | 10:00
Chandraghona | 140 | 09:00 | 138 | 00:00 | PHP | 136 | 04:00 | 133 | 16:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 139 | 01:00 | 133 | 10:00 | Postogola | 136 | 04:00 | 128 | 12:00
Charsaidpur | 137 | 02:00 | 131 | 12:00 | Purbachal | 134 | 02:00 | 125 | 12:00
Chauddagram | 137 | 04:00 | 134 | 12:00 | Purbasadipur | 134 | 19:00 | 126 | 10:00
Chhatak | 133 | 05:00 | 128 | 16:00 | Rahanpur | 141 | 04:00 | 137 | 10:00
Chowmuhani | 136 | 22:00 | 132 | 15:00 | Rahanpur-400 | 141 | 03:00 | 137 | 10:00
Chuadanga | 140 | 04:00 | 129 | 11:00 | Rahim | 137 | 00:00 | 131 | 12:00
Coxsbazar | 131 | 11:00 | 125 | 07:00 | Rajbari | 139 | 05:00 | 134 | 12:00
Cumilla(N) | 140 | 00:00 | 135 | 12:00 | Rajendrapur | 134 | 04:00 | 125 | 10:00
Cumilla(S) | 139 | 08:00 | 124 | 10:00 | Rajshahi | 139 | 02:00 | 133 | 11:00
Daganbhuiyan | 136 | 04:00 | 133 | 13:00 | Rajshahi-230 | 140 | 04:00 | 132 | 12:00
Daudkandi | 136 | 05:00 | 130 | 13:00 | Ramganj | 138 | 00:00 | 135 | 12:00
DhakaUniversity | 134 | 03:00 | 125 | 12:00 | Rampur | 139 | 09:00 | 136 | 02:00
Dhamrai | 137 | 17:00 | 133 | 09:00 | Rampura | 134 | 05:00 | 125 | 12:00
Dhanmondi | 139 | 01:00 | 133 | 12:00 | Rangamati | 139 | 09:00 | 136 | 14:00
Dohazari | 136 | 09:00 | 133 | 00:00 | Rangpur | 136 | 23:00 | 126 | 09:00
Faridpur | 137 | 00:00 | 134 | 12:00 | Ruppur | 141 | 02:00 | 136 | 12:00
Fatullah | 139 | 03:00 | 127 | 12:00 | Saidpur | 133 | 19:00 | 127 | 10:00
Fenchuganj | 138 | 01:00 | 135 | 11:00 | Satkhira | 135 | 05:00 | 125 | 12:00
Feni | 135 | 00:00 | 132 | 12:00 | Satmasjid | 138 | 04:00 | 130 | 12:00
Feni-230 | 136 | 05:00 | 133 | 13:00 | Savar | 140 | 23:00 | 131 | 12:00
Ghatail | 128 | 00:00 | 118 | 14:00 | SevenRings | 139 | 19:30 | 127 | 09:00
Ghorashal | 133 | 01:00 | 128 | 08:00 | ShahCement | 137 | 02:00 | 131 | 12:00
Goalpara | 138 | 04:00 | 127 | 13:00 | Shahjadpur | 142 | 00:00 | 136 | 12:00
Gollamari | 138 | 05:00 | 128 | 12:00 | Shahjibazar | 133 | 03:00 | 128 | 12:00
Gopalganj | 141 | 05:00 | 137 | 12:00 | Shahmirpur | 140 | 07:00 | 137 | 16:00
Gopalganj-400 | 172 | 01:00 | 132 | 12:00 | Shariatpur | 142 | 04:00 | 137 | 13:00
Gulshan | 132 | 03:00 | 125 | 12:00 | Sherpur | 122 | 21:00 | 111 | 17:00
Halishahar | 140 | 05:00 | 137 | 07:00 | Shikalbaha | 129 | 00:00 | 125 | 07:00
Haripur | 138 | 04:00 | 132 | 12:00 | Shikalbaha-230 | 141 | 22:00 | 138 | 15:00
HaripurSBU | 138 | 05:00 | 132 | 12:00 | Shitalakhya | 136 | 00:00 | 126.1 | 12:00
Hasnabad | 138 | 03:00 | 128 | 11:00 | Sholosohor | 139 | 00:00 | 137 | 13:00
Hathazari | 140 | 07:00 | 137 | 16:00 | Shyampur | 138 | 00:00 | 129 | 12:00
Hatirjheel | 134 | 04:00 | 125 | 12:00 | Shyampur-230 | 139 | 04:00 | 131 | 12:00
Ishurdi | 142 | 03:00 | 137 | 12:00 | Siddhirganj | 137 | 00:00 | 132 | 12:00
Jaldhaka | 132 | 19:00 | 124 | 10:00 | Sirajganj | 139 | 04:00 | 132 | 10:00
Jamalpur | 126 | 08:00 | 112 | 14:00 | Sonargaon | 136 | 03:00 | 132 | 09:00
Jashore | 138 | 04:00 | 126 | 13:00 | Sreemongol | 134 | 03:00 | 130 | 12:00
Jhenaidah | 140 | 03:00 | 130 | 11:00 | Sreepur | 135 | 05:00 | 128 | 14:00
Jhenaidah-230 | 139 | 02:00 | 125 | 13:00 | Srinagar | 135 | 00:00 | 128 | 12:00
Joydebpur | 130 | 11:00 | 123 | 10:00 | SSM | 142 | 00:00 | 140 | 11:00
Joypurhat | 135 | 19:00 | 127 | 10:00 | Sunamganj | 132 | 03:00 | 128 | 14:00
Juldah | 140 | 00:00 | 135 | 07:00 | Sylhet | 134 | 02:00 | 130 | 16:00
Kabirpur | 139 | 01:00 | 123 | 10:00 | Sylhet-132 | 133 | 03:00 | 131 | 12:00
Kachua | 139 | 00:00 | 137 | 01:00 | Tangail | 129 | 07:00 | 124 | 12:00
Kaliakoir | 140 | 05:00 | 134 | 11:00 | Taraganj | 135 | 23:00 | 127 | 10:00
Kallyanpur | 140 | 00:00 | 132 | 10:00 | Tasnim | 137 | 04:00 | 131 | 09:00
Kalurghat | 139 | 01:00 | 137 | 00:00 | Thakurgaon | 139 | 23:00 | 128 | 10:00
Kamrangirchar | 136 | 04:00 | 127 | 12:00 | TK | 139 | 07:00 | 137 | 16:00
Kaptai | N/A | N/A | N/A | N/A | Tongi | 135 | 07:00 | 127 | 11:00
Kasba | 138 | 05:00 | 131 | 12:00 | Ullahpara | 139 | 04:00 | 133 | 12:00
Kazla | 139 | 04:00 | 125 | 13:00 | Ullon | 133 | 03:00 | 125 | 09:00
Keranigonj | 137 | 05:00 | 128 | 12:00 | Uttara | 134 | 05:00 | 123 | 13:00
Khagrachori | 139 | 22:00 | 136 | 07:00 | UttaraNew | 133 | 03:00 | 125 | 12:00
Khulna | 138 | 04:00 | 127 | 12:00 | Zigatola | 136 | 02:00 | 128 | 12:00
Khulna(S) | 138 | 04:00 | 129 | 13:00
Khulshi | 138 | 07:00 | 135 | 13:00
Kishoreganj | 132 | 01:00 | 127 | 14:00
Kodda | 137 | 17:00 | 129 | 07:00
KSRM | 139 | 08:00 | 136 | 00:00
Kulaura | 138 | 03:00 | 134 | 12:00
Kurigram | 132 | 23:00 | 122 | 10:00
Kushtia | 139 | 03:00 | 133 | 11:00
Laksam | 139 | 00:00 | 136 | 13:00
Lakshmipur | 136 | 05:00 | 133 | 12:00
Lalbag | 135 | 04:00 | 127 | 12:00
Lalmonirhat | 133 | 23:00 | 27 | 07:00
Madanganj | 134 | 01:00 | 132 | 00:00
Madaripur | 140 | 00:00 | 138 | 13:00
Madartek | 134 | 05:00 | 125 | 12:00
Madunaghat | 139 | 00:00 | 137 | 07:00
Magura | 139 | 03:00 | 129 | 12:00
Mahasthangarh | 137 | 18:00 | 132 | 10:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division