## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 01-02-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 31-01-2026 | during | 01-02-2026 | during | 01-02-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 329 | 305 | 412 | 412 | 350 | 350 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 335 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 32.7 | 53.97 | 53.97 | 53.97 | 53.97 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 80 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 18 | 22 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 20 | 20 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 33 | 52.19 | 52.19 | 25 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 160 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 85 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 50 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 45 | 68 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 25 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 3 | 35 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 548 | 548 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 90 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1305 | 1963.7 | 5361.35 | 5329.35 | 2750.83 | 2745.83
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 3 | 32 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 176 | 179 | 150 | 150 | 150 | 150 | Plant availability less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 5 | 66 | 105 | 105 | 95 | 95 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 8 | 8 | 8 | 8 | 8 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 34 | 34 | 34 | 34 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 50 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 7 | 28 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 50 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.81 | 0 | 3.24 | 0 | 3.24 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 16 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 35 | 54.36 | 54.36 | 54.36 | 54.36 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 59 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 25 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 62 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 75 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 8 | 0 | 15 | 0 | 15 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 435 | 430 | 430 | 430 | 570 | 570 | machine problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1838.81 | 2438 | 3145.1 | 3144.86 | 2918.1 | 2702.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 45 | 198 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 280 | 280 | 353.35 | 353.35 | 317 | 317 | FGMO
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 215 | 220 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 33 | 3 | 46.7 | 46.7 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 49 | 0 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 3 | 85 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 23 | 42 | 42 | 42 | 42 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 103 | 163 | 163 | 110 | 110 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 11 | 103 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 132 | 126 | 84 | 82 | 84 | 82 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 13 | 24.5 | 24.5 | 13 | 13 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 58 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 3 | 69 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 60 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 967 | 1366 | 2437.75 | 2370.75 | 1878.2 | 1811.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 31-01-2026 | during | 01-02-2026 | during | 01-02-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 7 | 9 | 157.5 | 157.5 | 35 | 35 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 19 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 57 | 58 | 60 | 60 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 41.14 | 0 | 41.5 | 0 | 41.5 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 3 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 126.14 | 106 | 357.6 | 314 | 235.1 | 191.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 42 | 42 | 42 | 42 | 42 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 53 | 53 | 53 | 53 | 53 | 53 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 158 | 156 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 83 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 97 | 100 | 100 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 15 | 15 | 18 | 18 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 20 | 25 | 25 | 20 | 21 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | -
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 825 | 811 | 855 | 855 | 782 | 783
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 897 | 883 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 34 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 15 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 236 | 410 | 410 | 250 | 250 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 85 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 580 | 610 | 617.1 | 617.1 | 617.1 | 617.1 | U#1 Under Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1812 | 1778 | 2964.1 | 2889.1 | 2049.2 | 1974.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 32 | 110 | 110 | 50 | 50 | Fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 65 | 65 | 65 | 65 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 1000 | 1085 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 150 | 150 | 150 | 150 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 277 | 307 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.55 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1562.55 | 1744 | 1938.32 | 1937.32 | 1943.32 | 1942.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 52.66 | 0 | 48 | 0 | 48 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Machine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 180 | 168 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 15 | 20 | 20 | 24 | 24 | Machine problem and fuel shortage
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 70 | 112 | 112 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.62 | 0 | 5.1 | 0 | 5.1 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 719.32 | 762.44 | 748 | 748 | 748 | 748 | U#1 Under AOH
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 56.18 | 0 | 58 | 0 | 58 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 105 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1531.78 | 1533.44 | 2428.09 | 2216.99 | 1919.71 | 1708.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 54 | 55 | 54 | 54 | 55 | 55 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.9 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 145 | 0 | 149.59 | 0 | 149.59 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 233.9 | 160 | 500.79 | 316 | 467.79 | 283
System Total |  |  |  |  | 28823.2 | 28382.248 | 10202.18 | 11900.14 | 19988.1 | 19373.37 | 14944.25 | 14142.52
Forecast Scenario (01-02-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9860 |  | 0 |  | 9860
|  |  |  | 1:00 | 9210 |  | 0 |  | 9210
|  |  |  | 2:00 | 8810 |  | 0 |  | 8810
|  |  |  | 3:00 | 8520 |  | 0 |  | 8520
|  |  |  | 4:00 | 8320 |  | 0 |  | 8320
|  |  |  | 5:00 | 8240 |  | 0 |  | 8240
|  |  |  | 6:00 | 8630 |  | 0 |  | 8630
|  |  |  | 7:00 | 9420 |  | 0 |  | 9420
|  |  |  | 8:00 | 10200 |  | 0 |  | 10200
|  |  |  | 9:00 | 10720 |  | 0 |  | 10720
|  |  |  | 10:00 | 10800 |  | 0 |  | 10800
|  |  |  | 11:00 | 11000 |  | 0 |  | 11000
|  |  |  | 12:00 | 11400 |  | 0 |  | 11400
|  |  |  | 13:00 | 11700 |  | 0 |  | 11700
|  |  |  | 14:00 | 11320 |  | 0 |  | 11320
|  |  |  | 15:00 | 10950 |  | 0 |  | 10950
|  |  |  | 16:00 | 10650 |  | 0 |  | 10650
|  |  |  | 17:00 | 10950 |  | 0 |  | 10950
|  |  |  | 18:00 | 11700 |  | 0 |  | 11700
|  |  |  | 18:30 | 11800 |  | 0 |  | 11800
|  |  |  | 19:00 | 11900 |  | 0 |  | 11900
|  |  |  | 19:30 | 11800 |  | 0 |  | 11800
|  |  |  | 20:00 | 11650 |  | 0 |  | 11650
|  |  |  | 21:00 | 11540 |  | 0 |  | 11540
|  |  |  | 22:00 | 11050 |  | 0 |  | 11050
|  |  |  | 23:00 | 10340 |  | 0 |  | 10340
Probable Maximum Temperature: |  |  | 28.10°C
Probable Maximum Demand at Day Peak: |  |  | 11400.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11900.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11900.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 248.88 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:18 hrs on 01-02-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 31-01-2026 | [28 empty] | Date: | 31-01-2026 | [28 empty] | Date: | 31-01-2026 | [28 empty] | Date: | 31-01-2026 | [28 empty] | Date: | 31-01-2026 | [17 empty] | Date: | 31-01-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 11 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 400 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 923 | 0 | 0 | 0 | 215 | 280 | 0 | 51 | 0 | 199 | 0 | 0 | 105 | 0 | 0 | 13 | 0 | 100 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 53 | 153 | 0 | 20 | 0 | 83 | 30 | 0 | 15 | 101 | 0 | 35 | 18 | 23 | 0 | 0 | 0 | 4631 | 896 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583 | 0 | 0 | 0 | 762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 130 | 180 | 0 | 0 | 950 | 0 | 4485 | 9116 | 95.12
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 11 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 2 | 535 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 886 | 0 | 0 | 0 | 215 | 280 | 0 | 5 | 0 | 200 | 0 | 0 | 105 | 0 | 0 | 13 | 0 | 90 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 53 | 156 | 0 | 0 | 0 | 5 | 20 | 0 | 15 | 100 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 4480 | 897 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 454 | 0 | 0 | 0 | 682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 65 | 180 | 0 | 0 | 800 | 0 | 4046 | 8526 | 95.12
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 11 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 2 | 535 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 842 | 0 | 0 | 0 | 215 | 280 | 0 | 5 | 0 | 206 | 0 | 0 | 106 | 0 | 0 | 13 | 0 | 88 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 53 | 157 | 0 | 0 | 0 | 5 | 20 | 0 | 15 | 100 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 4471 | 897 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 65 | 180 | 0 | 0 | 670 | 0 | 3696 | 8167 | 95.11
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 11 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 2 | 545 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 750 | 0 | 0 | 0 | 215 | 280 | 0 | 5 | 0 | 205 | 0 | 0 | 106 | 0 | 0 | 13 | 0 | 86 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 53 | 153 | 0 | 0 | 0 | 5 | 20 | 0 | 15 | 100 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 4345 | 897 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 65 | 180 | 0 | 0 | 600 | 0 | 3522 | 7867 | 95.11
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 11 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 2 | 545 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 605 | 0 | 0 | 0 | 215 | 280 | 0 | 5 | 0 | 205 | 0 | 0 | 106 | 0 | 0 | 13 | 0 | 82 | 0 | 0 | 0 | 305 | 0 | 0 | 41 | 53 | 152 | 0 | 0 | 0 | 5 | 20 | 0 | 15 | 100 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 4148 | 897 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 65 | 180 | 0 | 0 | 595 | 0 | 3483 | 7631 | 95.11
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 11 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 545 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 603 | 0 | 0 | 0 | 215 | 280 | 0 | 5 | 0 | 137 | 0 | 0 | 108 | 0 | 0 | 13 | 0 | 82 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 53 | 140 | 0 | 0 | 0 | 5 | 20 | 0 | 15 | 100 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 4080 | 896 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 65 | 180 | 0 | 0 | 587 | 0 | 3519 | 7599 | 95.11
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 11 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 545 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 700 | 0 | 0 | 0 | 215 | 280 | 0 | 5 | 0 | 137 | 0 | 0 | 108 | 0 | 0 | 13 | 0 | 92 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 53 | 146 | 0 | 0 | 0 | 79 | 20 | 0 | 15 | 100 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 4287 | 897 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 65 | 220 | 0 | 0 | 615 | 0 | 3729 | 8016 | 95.1
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 1 | 0 | 14 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 40 | 0 | 41 | 565 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 896 | 0 | 0 | 0 | 215 | 280 | 0 | 40 | 0 | 134 | 0 | 0 | 108 | 0 | 0 | 13 | 0 | 84 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 53 | 158 | 0 | 16 | 0 | 80 | 30 | 0 | 15 | 100 | 0 | 0 | 0 | 24 | 0 | 1.17 | 0 | 4606.27 | 897 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 464 | 0 | 0 | 0 | 581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88 | 0 | 0 | 0 | 0.87 | 168 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.09 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.02 | 0 | 286 | 65 | 220 | 0 | 0 | 715 | 0 | 4122.16 | 8728.43 | 95.1
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 466 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 6 | 17 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79 | 40 | 0 | 17 | 565 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 1145 | 0 | 0 | 0 | 215 | 280 | 0 | 51 | 0 | 130 | 0 | 0 | 106 | 0 | 0 | 13 | 0 | 104 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 53 | 163 | 2 | 17 | 0 | 80 | 30 | 0 | 15 | 101 | 0 | 35 | 19 | 24 | 1 | 10.51 | 0 | 4969.3 | 897 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 558 | 0 | 0 | 0 | 756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.54 | 22 | 0 | 0 | 11.05 | 167 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.18 | 0 | 55 | 0 | 3 | 0 | 0 | 0 | 0 | 0.6 | 26 | 0.16 | 0 | 278 | 65 | 220 | 0 | 0 | 810 | 0 | 4553.53 | 9522.83 | 95.1
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 439 | 0 | 0 | 34 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 18 | 17 | 19 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.87 | 40 | 0 | 0 | 560 | 0 | 0 | 0 | 0 | 16 | 176 | 0 | 0 | 0 | 1090 | 0 | 0 | 0 | 215 | 280 | 0 | 51 | 0 | 123 | 0 | 9 | 106 | 29 | 0 | 13 | 0 | 104 | 0 | 39 | 0 | 305 | 0 | 0 | 41 | 53 | 161 | 3 | 17 | 0 | 80 | 30 | 0 | 15 | 101 | 0 | 57 | 19 | 17 | 1 | 23 | 0 | 4923.87 | 896 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 607 | 0 | 0 | 0 | 759.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.37 | 46 | 0 | 0 | 30.5 | 168 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 2.67 | 0 | 56 | 0 | 8 | 0 | 0 | 0 | 0 | 1.6 | 74 | 0.25 | 0 | 254 | 65 | 180 | 0 | 0 | 900 | 0 | 4714.17 | 9638.04 | 95.1
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 26 | 17 | 18.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 40 | 0 | 5 | 570 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 1060 | 0 | 0 | 0 | 215 | 280 | 0 | 43 | 8 | 32 | 26 | 0 | 80 | 0 | 0 | 13 | 0 | 120 | 0 | 57 | 0 | 310 | 0 | 0 | 41 | 53 | 139 | 8 | 20 | 0 | 81 | 30 | 0 | 15 | 100 | 0 | 57 | 19 | 9 | 2 | 34.15 | 0 | 4740.45 | 896 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 567 | 0 | 0 | 0 | 723.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.79 | 78 | 0 | 0 | 44.5 | 179 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 3.88 | 0 | 54 | 0 | 21 | 0 | 0 | 0 | 0 | 4 | 116 | 0.44 | 0 | 214 | 65 | 180 | 0 | 0 | 1010 | 0 | 4852.96 | 9593.41 | 95.09
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 30 | 0 | 18.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.62 | 40 | 0 | 6 | 510 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 1056 | 0 | 0 | 0 | 215 | 280 | 0 | 43 | 36 | 47 | 30 | 0 | 80 | 0 | 0 | 13 | 0 | 120 | 0 | 56 | 0 | 315 | 0 | 0 | 42 | 53 | 142 | 10 | 17 | 0 | 81 | 30 | 0 | 15 | 100 | 0 | 57 | 19 | 9 | 2 | 39.9 | 0 | 4859.02 | 897 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 556 | 0 | 0 | 0 | 718.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.67 | 98 | 0 | 0 | 52.11 | 182 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.38 | 0 | 54 | 0 | 26 | 0 | 0 | 0 | 0 | 4.2 | 138 | 0.55 | 0 | 221 | 65 | 220 | 0 | 0 | 1010 | 0 | 5042.67 | 9901.69 | 95.09
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 548 | 17 | 3 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 25 | 0 | 18 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 2.81 | 40 | 0 | 7 | 435 | 0 | 0 | 3 | 0 | 5 | 176 | 0 | 0 | 0 | 1160 | 0 | 3 | 0 | 215 | 280 | 0 | 43 | 49 | 45 | 33 | 3 | 80 | 11 | 0 | 13 | 0 | 132 | 0 | 60 | 0 | 320 | 0 | 0 | 41 | 53 | 158 | 10 | 17 | 0 | 81 | 30 | 0 | 15 | 100 | 0 | 57 | 19 | 7 | 2 | 41.14 | 0 | 5061.95 | 897 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 580 | 0 | 0 | 0 | 719.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.66 | 105 | 0 | 0 | 56.18 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.62 | 0 | 54 | 0 | 30 | 0 | 0 | 0 | 0 | 4.9 | 145 | 0.55 | 0 | 277 | 65 | 220 | 0 | 0 | 1000 | 0 | 5140.23 | 10202.18 | 95.09
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 545 | 16.3 | 17 | 41 | 38 | 95 | 15 | 17 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 30 | 52 | 18 | 19 | 0 | 0 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 14 | 36 | 25 | 3.05 | 40 | 28 | 16 | 450 | 17 | 0 | 18 | 4 | 33 | 180 | 0 | 0 | 0 | 1165 | 0 | 45 | 0 | 215 | 280 | 0 | 43 | 49 | 40 | 31 | 32 | 80 | 61 | 0 | 13 | 30 | 134 | 8 | 62 | 1 | 320 | 0 | 0 | 41 | 53 | 158 | 9 | 20 | 0 | 83 | 30 | 0 | 15 | 100 | 2 | 59 | 19 | 7 | 2 | 38.06 | 2 | 5736.41 | 897 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 610 | 0 | 0 | 0 | 759.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.25 | 103 | 0 | 0 | 55.11 | 175 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.85 | 0 | 54 | 0 | 26 | 0 | 0 | 0 | 0 | 5.2 | 140 | 0.57 | 0 | 277 | 65 | 220 | 0 | 0 | 1065 | 0 | 5231.85 | 10968.26 | 95.09
14:00 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 456 | 15.6 | 17 | 50 | 48 | 15 | 15 | 17 | 49 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 28 | 52 | 18 | 20 | 0 | 0 | 17 | 16 | 12 | 0 | 0 | 0 | 0 | 17 | 12 | 12 | 3.1 | 40 | 33 | 4 | 430 | 17 | 0 | 19 | 8 | 32 | 180 | 0 | 0 | 0 | 1160 | 15 | 40 | 0 | 215 | 280 | 0 | 43 | 47 | 43 | 31 | 31 | 80 | 63 | 0 | 13 | 0 | 134 | 8 | 58 | 13 | 310 | 0 | 0 | 42 | 53 | 138 | 9 | 20 | 0 | 80 | 30 | 0 | 15 | 100 | 17 | 59 | 19 | 6 | 1 | 35.29 | 6 | 5497.99 | 897 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 568 | 0 | 0 | 0 | 764.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.26 | 75 | 0 | 0 | 48.73 | 171 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 4.15 | 0 | 55 | 0 | 25 | 0 | 0 | 0 | 0 | 3.5 | 114 | 0.45 | 0 | 230 | 65 | 220 | 0 | 0 | 1080 | 0 | 4994.49 | 10492.48 | 95.08
15:00 | 0 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 404 | 15.4 | 17 | 50 | 48 | 15 | 15 | 17 | 51 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 20 | 52 | 16 | 20 | 0 | 0 | 0 | 16 | 32 | 0 | 4 | 0 | 0 | 17 | 12 | 12 | 2.03 | 40 | 34 | 2 | 430 | 17 | 0 | 19 | 8 | 30 | 180 | 0 | 0 | 0 | 1160 | 12 | 12 | 0 | 215 | 280 | 0 | 43 | 49 | 54 | 32 | 30 | 80 | 64 | 0 | 13 | 0 | 132 | 8 | 42 | 13 | 310 | 0 | 0 | 42 | 53 | 144 | 7 | 20 | 0 | 83 | 30 | 0 | 15 | 99 | 17 | 59 | 19 | 6 | 1 | 22.11 | 6 | 5431.54 | 897 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 557 | 0 | 0 | 0 | 709.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.13 | 67 | 0 | 0 | 32 | 130 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 2.92 | 0 | 55 | 0 | 15 | 0 | 0 | 0 | 0 | 2.9 | 83 | 0.35 | 0 | 275 | 65 | 180 | 0 | 0 | 1070 | 0 | 4748.38 | 10179.92 | 95.08
16:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 413 | 16.5 | 17 | 50 | 48 | 15 | 15 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 17 | 270 | 0 | 0 | 10 | 52 | 22 | 20 | 0 | 0 | 0 | 16 | 10 | 0 | 5 | 0 | 8 | 0 | 0 | 0 | 1.27 | 40 | 17 | 2 | 430 | 17 | 0 | 19 | 8 | 17 | 179 | 0 | 0 | 0 | 1162 | 8 | 12 | 0 | 215 | 280 | 0 | 51 | 0 | 119 | 3 | 18 | 80 | 17 | 0 | 13 | 0 | 130 | 8 | 23 | 13 | 320 | 0 | 0 | 42 | 53 | 144 | 3 | 20 | 0 | 83 | 30 | 0 | 15 | 99 | 17 | 58 | 19 | 6 | 1 | 14.98 | 6 | 5246.75 | 897 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 560 | 0 | 0 | 0 | 673.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.45 | 48 | 0 | 0 | 21.05 | 130 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 55 | 0 | 9 | 0 | 0 | 0 | 0 | 1.5 | 45 | 0.21 | 0 | 279 | 65 | 180 | 0 | 0 | 1078 | 0 | 4610.71 | 9857.46 | 95.08
17:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 417 | 16 | 17 | 50 | 48 | 95 | 15 | 17 | 65 | 0 | 0 | 0 | 0 | 0 | 17 | 320 | 0 | 0 | 3 | 52 | 22 | 20 | 0 | 0 | 0 | 16 | 10 | 0 | 7 | 4 | 8 | 0 | 0 | 0 | 0.22 | 40 | 17 | 9 | 430 | 17 | 0 | 19 | 8 | 17 | 180 | 0 | 0 | 0 | 1120 | 3 | 12 | 0 | 215 | 290 | 0 | 51 | 0 | 188 | 3 | 16 | 102 | 23 | 0 | 13 | 0 | 112 | 8 | 5 | 13 | 320 | 0 | 0 | 42 | 53 | 146 | 1 | 20 | 0 | 80 | 30 | 0 | 15 | 97 | 17 | 58 | 19 | 6 | 0 | 2.06 | 4 | 5418.28 | 881 | 226 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 560 | 0 | 0 | 0 | 673.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.98 | 12 | 0 | 0 | 3.92 | 130 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0.37 | 0 | 55 | 0 | 2 | 0 | 0 | 0 | 0 | 0.5 | 13 | 0.06 | 0 | 270 | 65 | 180 | 0 | 0 | 1085 | 13 | 4468.03 | 9886.31 | 95.07
18:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 491 | 31.5 | 30 | 85 | 80 | 160 | 21 | 26 | 69 | 0 | 0 | 0 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 108 | 19 | 20 | 0 | 0 | 25 | 16 | 50 | 0 | 8 | 34 | 8 | 19 | 50 | 25 | 0 | 40 | 50 | 13 | 430 | 35 | 0 | 29 | 15 | 63 | 180 | 0 | 0 | 0 | 1160 | 0 | 76 | 0 | 260 | 315 | 0 | 51 | 0 | 197 | 3 | 40 | 103 | 65 | 0 | 13 | 63 | 126 | 27 | 0 | 17 | 310 | 0 | 0 | 42 | 53 | 141 | 0 | 20 | 0 | 83 | 30 | 0 | 15 | 97 | 17 | 58 | 19 | 6 | 0 | 0 | 5 | 6405.5 | 878 | 230 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 562 | 0 | 0 | 0 | 742.83 | 0 | 0 | 0 | 70 | 65 | 0 | 0 | 5 | 25 | 0 | 0 | 14 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 55 | 35 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 277 | 65 | 220 | 0 | 0 | 1070 | 35 | 4967.83 | 11373.33 | 95.07
19:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 548 | 32.7 | 35 | 85 | 80 | 160 | 30 | 35 | 68 | 0 | 0 | 0 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 90 | 22 | 20 | 0 | 0 | 62 | 16 | 50 | 0 | 8 | 34 | 8 | 35 | 50 | 25 | 0 | 40 | 59 | 28 | 430 | 75 | 0 | 32 | 17 | 66 | 179 | 0 | 0 | 0 | 1224 | 0 | 85 | 0 | 220 | 280 | 0 | 51 | 0 | 198 | 3 | 69 | 103 | 103 | 0 | 13 | 58 | 126 | 34 | 0 | 23 | 315 | 0 | 0 | 42 | 53 | 156 | 0 | 20 | 0 | 83 | 30 | 0 | 15 | 97 | 17 | 58 | 19 | 9 | 0 | 0 | 3 | 6684.7 | 883 | 236 | 0 | 34 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610 | 0 | 0 | 0 | 762.44 | 0 | 0 | 0 | 70 | 70 | 0 | 0 | 0 | 34 | 0 | 0 | 15 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 65 | 220 | 0 | 0 | 1085 | 35 | 5215.44 | 11900.14 | 95.07
19:30 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 608 | 32.7 | 35 | 85 | 62 | 160 | 30 | 35 | 69 | 0 | 0 | 0 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 90 | 22 | 20 | 0 | 0 | 60 | 16 | 0 | 0 | 10 | 34 | 8 | 0 | 50 | 25 | 0 | 40 | 68 | 28 | 430 | 17 | 0 | 32 | 0 | 65 | 179 | 0 | 0 | 0 | 1224 | 0 | 85 | 0 | 220 | 320 | 0 | 51 | 0 | 204 | 3 | 66 | 104 | 118 | 0 | 13 | 0 | 120 | 0 | 0 | 30 | 320 | 0 | 0 | 42 | 53 | 158 | 0 | 20 | 0 | 83 | 30 | 0 | 15 | 97 | 17 | 58 | 19 | 12 | 0 | 0 | 6 | 6591.7 | 883 | 236 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588 | 0 | 0 | 0 | 764.34 | 0 | 0 | 0 | 70 | 70 | 0 | 0 | 10 | 0 | 0 | 0 | 15 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 65 | 220 | 0 | 0 | 1085 | 35 | 5130.34 | 11722.04
20:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 539 | 31.6 | 35 | 85 | 48 | 160 | 30 | 35 | 67 | 0 | 0 | 0 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 90 | 23 | 20 | 0 | 0 | 60 | 16 | 0 | 0 | 12 | 0 | 8 | 0 | 50 | 25 | 0 | 40 | 68 | 32 | 430 | 0 | 0 | 33 | 0 | 65 | 179 | 0 | 0 | 0 | 1224 | 0 | 85 | 0 | 220 | 295 | 0 | 51 | 0 | 195 | 3 | 68 | 104 | 114 | 0 | 13 | 0 | 120 | 0 | 0 | 30 | 310 | 0 | 0 | 42 | 53 | 156 | 0 | 20 | 0 | 83 | 30 | 0 | 15 | 99 | 17 | 58 | 19 | 12 | 0 | 0 | 6 | 6396.6 | 887 | 236 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 764.3 | 0 | 0 | 0 | 70 | 70 | 0 | 0 | 20 | 0 | 0 | 0 | 15 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 65 | 220 | 0 | 0 | 1085 | 35 | 5131.3 | 11527.9 | 95.06
21:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 553 | 33.4 | 35 | 85 | 16 | 160 | 30 | 17 | 66 | 0 | 0 | 0 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 70 | 23 | 20 | 0 | 0 | 63 | 16 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 67 | 32 | 430 | 0 | 0 | 33 | 0 | 66 | 179 | 0 | 0 | 0 | 1224 | 0 | 85 | 0 | 215 | 320 | 0 | 51 | 0 | 176 | 3 | 66 | 104 | 118 | 0 | 13 | 0 | 122 | 0 | 0 | 0 | 320 | 0 | 0 | 42 | 53 | 160 | 0 | 20 | 0 | 83 | 30 | 0 | 15 | 99 | 0 | 58 | 19 | 12 | 0 | 0 | 6 | 6240.4 | 891 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610 | 0 | 0 | 0 | 757 | 0 | 0 | 0 | 70 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 80 | 220 | 0 | 0 | 1072 | 0 | 5059 | 11299.4 | 95.06
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 525 | 15.7 | 35 | 85 | 0 | 0 | 30 | 17 | 67 | 0 | 0 | 0 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 34 | 18 | 20 | 0 | 0 | 0 | 16 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 68 | 31 | 430 | 0 | 0 | 33 | 0 | 64 | 179 | 0 | 0 | 0 | 1224 | 0 | 80 | 0 | 215 | 315 | 0 | 51 | 0 | 192 | 3 | 63 | 104 | 111 | 0 | 13 | 0 | 114 | 0 | 0 | 0 | 310 | 0 | 0 | 42 | 53 | 154 | 0 | 20 | 0 | 83 | 30 | 0 | 15 | 99 | 0 | 58 | 19 | 12 | 0 | 0 | 6 | 5790.7 | 897 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605 | 0 | 0 | 0 | 763 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 1055 | 0 | 5029 | 10819.7 | 95.06
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 502 | 15 | 21 | 72 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 18 | 20 | 0 | 0 | 0 | 16 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 34 | 36 | 430 | 0 | 0 | 33 | 0 | 34 | 179 | 0 | 0 | 0 | 1224 | 0 | 12 | 0 | 215 | 300 | 0 | 51 | 0 | 187 | 3 | 61 | 104 | 68 | 0 | 13 | 0 | 110 | 0 | 0 | 0 | 310 | 0 | 0 | 42 | 53 | 153 | 0 | 20 | 0 | 83 | 30 | 0 | 15 | 98 | 0 | 59 | 19 | 12 | 0 | 0 | 6 | 5435 | 897 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610 | 0 | 0 | 0 | 763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 1055 | 0 | 4878 | 10313 | 95.05
Total KWH | 0 | 354278 | 140640 | 0 | 0 | 0 | 0 | 0 | 7801200 | 0 | 11718530 | 254880 | 296640 | 885600 | 432960 | 994604 | 244564 | 265685 | 653760 | 0 | 0 | 0 | 0 | 0 | 271132 | 7661931 | 0 | 0 | 204636 | 741600 | 418200 | 496080 | 0 | 0 | 304855 | 195709 | 173760 | 0 | 274560 | 81173 | 32400 | 123355 | 217920 | 126720 | 20004 | 960000 | 567055 | 403200 | 11796363.64 | 170618 | 0 | 298560 | 72939.6 | 568727 | 4188377 | 0 | 0 | 0 | 25025452 | 31725 | 647345 | 0 | 5313000 | 7307100 | 0 | 953677 | 264000 | 3469000 | 214992 | 555840 | 2352013 | 907680 | 0 | 353960 | 147060 | 2624640 | 116030 | 412955 | 116848 | 7629000 | 0 | 0 | 981000 | 1325160 | 3631909 | 63540 | 362784 | 0 | 1494720 | 660000 | 0 | 369000 | 234797.46 | 132840 | 957600 | 331200 | 279360 | 12600 | 264030 | 64800 | 124020873.7 | 21582545 | 5918976 | 0 | 61440 | 32384 | 0 | 0 | 0 | 0 | 0 | 0 | 529920 | 12996400 | 0 | 0 | 0 | 15500727 | 0 | 0 | 0 | 349344 | 390528 | 0 | 5696 | 10379 | 53774 | 331488 | 666030 | 30738 | 0 | 351008 | 3991545 | 0 | 0 | 0 | 0 | 0 | 9039418 | 0 | 28920 | 0 | 1274618 | 197716 | 164806 | 380697 | 0 | 0 | 0 | 28494.36 | 899280 | 3454 | 65280 | 6044000 | 1721000 | 5271120 | 0 | 0 | 22516363.64 | 118800 | 110556889 | 234577762.7

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 31-01-2026
Power Supply Scenario
| Day Peak Generation |  |  | 10202.18 | MW | 12:00 Hr. | Energy Generated |  |  | 234.5778 |  | MKWHr.
| Day Peak Demand |  |  | 10274.18 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.75 |  | MKWHr.
| Evening Peak Generation |  |  | 11900.14 | MW | 19:00 Hr. | Energy Demand |  |  | 235.3278 |  | MKWHr.
| Evening Peak Demand |  |  | 11980.14 | MW | 19:00 Hr. | Maximum Temperature |  |  | 27.7 |  | °C
| Minimum Generation of the Day |  |  | 7599 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 753.63 |  | MMCFD
| Maximum Generation of the Day |  |  | 11900.14 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.8448 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 28.0959 | 0 | 5.5363 | 0 | 0 | 0.20464 | 0 | 0 | 33.8369 | Gas | 95.825 | Gas | 340545445.1876
| Chattogram Zone |  |  | 4.5916 | 36.8218 | 2.9338 | 0 | 0.96 | 0.051729 | 0 | 0.27456 | 45.6335 | Coal | 79.6532 | Coal | 512479274.6204
| Cumilla Zone |  |  | 20.2277 | 0 | 2.4908 | 0 | 0 | 0.41296 | 2.6246 | 0 | 25.7561 | HFO | 14.1442 | HFO | 239681353.652
| Mymensingh Zone |  |  | 0.27936 | 0 | 1.4864 | 0 | 0 | 0.27663 | 0 | 0 | 2.0424 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 16.6884 | 0 | 0 | 0 | 0 | 0.06354 | 0 | 0 | 16.7519 | Hydro | 0.96 | Hydro | 96000
| Khulna Zone |  |  | 5.919 | 12.9964 | 0.093824 | 0 | 0 | 0.52992 | 21.5825 | 0 | 41.1217 | Solar | 4.0129 | Solar | 63595447.062
| Barishal Zone |  |  | 6.9921 | 28.5604 | 0.18408 | 0 | 0 | 0.003454 | 0 | 0 | 35.74 | Import | 39.7079 | Import | 210634208.21
| Rajshahi Zone |  |  | 13.031 | 0 | 0.84046 | 0 | 0 | 1.3774 | 15.5007 | 0 | 30.7496 | Wind | 0.27456 | Wind | 4038777.6
| Rangpur Zone |  |  | 0 | 1.2746 | 0.57841 | 0 | 0 | 1.0926 | 0 | 0 | 2.9456
| Total |  |  | 95.825 | 79.6532 | 14.1442 | 0 | 0.96 | 4.0129 | 39.7079 | 0.27456 | 234.5778
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 340545445.1876 |  | Hydro | 96000
|  |  |  | Coal | 512479274.6204 |  | Solar | 63595447.062
|  |  |  | HFO | 239681353.652 |  | Import | 210634208.21
|  |  |  | HSD | 0 |  | Wind | 4038777.6
[5 empty] | Total: | 137,10,70,506 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5825 | Peak Hr Flow | 883.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 35927673.99 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 15.5007 | Peak Hr Flow | 762.44 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1476 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.6246 | Peak Hr Flow | 126.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2089 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 39.7079 | Peak Hr Flow | 1771.44 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 22 |  | 4340
|  |  |  | Chattogram |  | 0 |  | 1193
|  |  |  | Cumilla |  | 0 |  | 970
|  |  |  | Mymensingh |  | 55 |  | 1003
|  |  |  | Sylhet |  | 0 |  | 414
|  |  |  | Khulna |  | 0 |  | 1305
|  |  |  | Barishal |  | 0 |  | 323
|  |  |  | Rajshahi |  | 0 |  | 1117
|  |  |  | Rangpur |  | 0 |  | 789
|  |  |  | Total |  | 77 |  | 11454
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Patenga 50MW PP (Baraka) |  |  | 50
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 50
|  |  |  | Total Unavailable Capacity |  |  |  | 350
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:02 | Chandpur 132/33kV S/S 402T (T-01) LT is restored.
| 08:02 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- STG (False SMS)
| 08:05 | 12:58 | Chandpur 132/33kV S/S 422T(T-5) HT Scheduled S/D Due to Maintenance (CPBS-2) | [7 empty] | 16.0MW load
interrup.
| 08:05 | 12:58 | Chandpur 132/33kV S/S 422T(T-5) LT Scheduled S/D Due to Maintenance (CPBS-2) | [7 empty] | 16.0MW load
interrup.
| 08:05 | 12:58 | Chandpur 132/33kV S/S 33 kV T-2 section Scheduled S/D Due to Maintenance (CPBS-2) | [7 empty] | 8.0MW load
interrup.
| 08:05 |  | Chandpur 132/33kV S/S 412T (T-2) HT Scheduled S/D Due to Maintenance (CPBS-2) | [7 empty] | 8.0MW load
interrup.
| 08:05 | 12:58 | Chandpur 132/33kV S/S 33 kV T-5 section Scheduled S/D Due to Maintenance (CPBS-2) | [7 empty] | 16.0MW load
interrup.
| 08:05 | 12:58 | Chandpur 132/33kV S/S 412T (T-2) LT Scheduled S/D Due to Maintenance (CPBS-2) | [7 empty] | 8.0MW load
interrup.
| 08:09 | 14:07 | Khulshi 132/33kV S/S 415T (T2) HT Scheduled S/D Due to Annual maintenance
| 08:18 |  | Gallamari- Khulna (S) 132kV Ckt-1 Scheduled S/D from Gollamari 132/33kV end Due to None
and from Khulna(S) 230/132kV end Due to OPGW Work
| 08:22 | 20:57 | Aminbazar-Airport(Old) 230kV Ckt-1 Scheduled S/D from Agargaon 230/132kV end Due to
Annual maintenance
| 08:22 | 11:23 | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) LT Scheduled S/D Due to 33kV Bus Maintenance. | [7 empty] | 32.0MW load
interrup.
| 08:22 | 11:22 | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) HT Scheduled S/D Due to 33kV Bus Maintenance. | [7 empty] | 32.0MW load
interrup.
| 08:23 | 11:24 | Chuadanga 132/33kV S/S 132kV Tr. T3 LT Scheduled S/D Due to 33kV Bus Maintenance. | [7 empty] | 32.0MW load
interrup.
| 08:23 | 11:24 | Chuadanga 132/33kV S/S 132kV Tr. T3 HT Scheduled S/D Due to 33kV Bus Maintenance. | [7 empty] | 32.0MW load
interrup.
| 08:26 | 14:06 | Bakulia-Sikalbaha 132 kV Ckt-1 Scheduled S/D from Bakulia 132/33kV end Due to Annual
Maintenance.
| 08:26 | 17:19 | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-2 Scheduled S/D Due to Annual Maintenance
| 08:31 | 15:03 | Chandraghona 132/33kV S/S TR-02(416T) LT Scheduled S/D Due to Annual maintenance
| 08:32 | 13:59 | Chandraghona 132/33kV S/S TR-02(416T) HT Scheduled S/D Due to Annual maintenance
| 08:38 | 17:03 | Brahmanbaria-Narsinghdi 132 kV Ckt-1 Scheduled S/D from Brahmanbaria 132/33kV end.
| 08:45 | 16:53 | Sirajganj 132/33kV S/S T4-(445) HT Project Work S/D Due to 33 kv Bay extension work | [7 empty] | 14.0MW load
interrup.
| 08:45 | 16:53 | Sirajganj 132/33kV S/S T4-(445) LT Project Work S/D Due to 33 kv Bay extension work | [7 empty] | 14.0MW load
interrup.
| 08:46 | 17:05 | Cumilla(N)-Cumilla(S) 132 kV Ckt-3 Scheduled S/D from Cumilla(S) 132/33kV end Due to
Annual Maintenance
| 08:47 | 19:33 | Fenchuganj 230/132/33kV S/S AT-02 LT Scheduled S/D Due to Tan delta test
| 08:47 | 19:33 | Fenchuganj 230/132/33kV S/S AT-02 LT Scheduled S/D Due to Tan delta test
| 08:47 | 19:33 | Fenchuganj 230/132/33kV S/S AT-02 LT Scheduled S/D Due to Tan Dalta Test
| 08:47 | 19:32 | Fenchuganj 230/132/33kV S/S AT-02 HT Scheduled S/D Due to Tan Delta Test
| 08:48 | 19:32 | Fenchuganj 230/132/33kV S/S AT-02 HT Scheduled S/D Due to Tan delta test
| 08:54 | 13:00 | Ashuganj-Brahmanbaria 132kV Ckt-1 Project Work S/D from Brahmanbaria 132/33kV end.
| 08:54 | 12:02 | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT Scheduled S/D | [7 empty] | 10.0MW load
interrup.
| 08:55 | 12:01 | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT Scheduled S/D Due to None
| 09:05 | 16:23 | Sylhet-Sylhet (South) 132KV Ckt-2 Scheduled S/D from Sylhet 132/33kV end Due to Dead Line
checking purpose, shutdown taken by AE, Sylhet S/S
|  | 09:07 | Baroirhat 132/33kV S/S TR-2, 416T HT is restored.
|  | 09:07 | Baroirhat 132/33kV S/S TR-2, 416T LT is restored.
| 09:14 | 17:03 | Kodda 132/33kV S/S Tr-5 (446T) LT Scheduled S/D Due to Work by PBS | [7 empty] | 70.0MW load
interrup.
| 09:15 | 17:03 | Kodda 132/33kV S/S Tr-5 (446T) HT Scheduled S/D Due to Work by pbs | [7 empty] | 70.0MW load
interrup.
| 09:52 |  | Hathazari 230/132/33kV S/S T-02 LT Forced S/D Due to PDB Demand | [7 empty] | 10.0MW load
interrup.
| 09:52 |  | Hathazari 230/132/33kV S/S T-02 HT Forced S/D Due to PDB Demand
| 10:00 | 13:30 | Sherpur 132/33kV S/S Transformer- 04 LT Scheduled S/D Due to PBS Roumary 33kv CB Bus Side
Maintenance Work
| 10:02 | 16:07 | Muradnagar 132/33kV S/S 132KV Transformar-01 LT Project Work S/D Due to CNEEC 33KV CB
Change.
| 10:02 | 16:06 | Muradnagar 132/33kV S/S 132KV Transformar-01 HT Project Work S/D Due to For CNEEC 33KV CB
Change.
| 10:20 | 13:30 | Sherpur 132/33kV S/S Transformer- 04 HT Scheduled S/D
| 10:24 | 16:53 | Sreepur 230/132/33kV S/S 230 kV Bus-1 Scheduled S/D Due to Annual Maintenance
| 10:38 | 12:06 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-1 Forced S/D Due to 230 kV BUS-1 Annual
Maintenance
| 10:40 | 13:29 | Jamalpur United (20MW)-Jamalpur 132kV Ckt-2 Scheduled S/D from Jamalpur 132/33kV end Due
to OPGW Preform work(Tower no 06).
| 11:04 |  | Kabirpur -Tongi 132kV Ckt-1 Forced S/D from Kabirpur 132/33kV end Due to 230/132 KV T-3
Transformer is on Shutdown at Tongi Grid S/S End
|  | 11:05 | Coxsbazar 132/33kV S/S Main Bus is restored.
| 11:05 |  | Kabirpur -Tongi 132kV Ckt-2 Forced S/D from Kabirpur 132/33kV end Due to 230/132 KV T-3
Transformer is on Shutdown at Tongi Grid S/S End
| 11:09 | 19:47 | Tongi 230/132/33kV S/S T-03 HT Scheduled S/D Due to Annual maintenance work
| 11:09 | 19:47 | Tongi 230/132/33kV S/S T-03 LT Scheduled S/D Due to Annual maintenance work
| 11:10 | 19:49 | Tongi 230/132/33kV S/S 230 kV Bus-1 Scheduled S/D Due to Loop changing work
| 11:18 | 13:35 | Kodda 132/33kV S/S Tr-3 (426T) HT Scheduled S/D Due to Wrk by pbs | [7 empty] | 20.0MW load
interrup.
| 11:18 | 13:35 | Kodda 132/33kV S/S Tr-3 (426T) LT Scheduled S/D Due to Work by pbs | [7 empty] | 20.0MW load
interrup.
| 11:18 | 13:36 | Kodda 132/33kV S/S Tr-4 (436T) LT Scheduled S/D Due to Wrk by pbs | [7 empty] | 20.0MW load
interrup.
| 11:18 | 13:36 | Kodda 132/33kV S/S Tr-4 (436T) HT Scheduled S/D Due to Wrk by pbs | [7 empty] | 20.0MW load
interrup.
| 11:47 |  | Gallamari- Khulna (S) 132kV Ckt-2 Scheduled S/D from Gollamari 132/33kV end Due to OPGW
Change. and from Khulna(S) 230/132kV end Due to OPGW Work
|  | 11:48 | Netrakona 132/33kV S/S Main Bus is restored.
| 12:00 |  | Day peak generation 10198 MW
| 12:08 | 13:23 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-2 Forced S/D Due to 230 kV BUS-1 Annual
Maintenance
| 13:03 | 19:08 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 Project Work S/D from Purbasadipur 132/33kV end
Due to DFDR test
|  | 13:35 | Kodda 132/33kV S/S Tr-3 (426T) HT is restored.
|  | 13:35 | Kodda 132/33kV S/S Tr-3 (426T) HT is restored.
|  | 13:41 | Coxsbazar 132/33kV S/S 415T-T2 HT is restored.
| 14:39 | 17:10 | Bhandaria 132/33kV S/S Transformer-2 HT Forced S/D Due to PBS Red hot maintenance | [7 empty] | 20.0MW load
interrup.
| 14:40 | 17:11 | Bhandaria 132/33kV S/S Transformer-2 LT Forced S/D Due to PBS red hot maintenance | [7 empty] | 20.0MW load
interrup.
| 15:06 | 17:20 | Dohazari-Sikalbaha 132 kV Ckt-2 Scheduled S/D from Dohazari 132/33kV end Due to Due to
Disks change
| 15:13 | 17:29 | Sreepur 230/132/33kV S/S 132 kV BUS-2 Scheduled S/D Due to Annual Maintenance
| 15:16 | 16:17 | Joydebpur 132/33kV S/S GT-2 HT Scheduled S/D Due to OLTC Oil Centrifuged
| 15:19 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- ST
|  | 15:38 | Purbasadipur 132/33kV S/S T-3 Transformer (423T) HT is restored.
| 15:42 | 16:39 | Barishal 230/132kV S/S ATR-1 LT Scheduled S/D
| 15:42 | 16:41 | Barishal 230/132kV S/S ATR-1 HT Scheduled S/D Due to Maintenance on Auxiliary txr
|  | 15:59 | Purbasadipur 132/33kV S/S T-3 Transformer (423T) LT is restored.
| 16:28 | 16:55 | Purbasadipur 132/33kV S/S T-4 Transformer LT Project Work S/D
| 16:30 | 16:53 | Purbasadipur 132/33kV S/S T-4 Transformer HT Project Work S/D
|  | 16:41 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-1 is restored.
|  | 16:43 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-2 is restored.
|  | 16:45 | Jashore 132/33kV S/S JH-1(L2) is restored.
|  | 16:45 | Jashore 132/33kV S/S JH-2(L1) is restored.
|  | 17:15 | Meghnaghat-Shyampur 230kV Ckt-2 is restored.
|  | 17:15 | Meghnaghat-Shyampur 230kV Ckt-2 is restored.
| 19:00 |  | Evening Peak Generation: 11899 MW
|  | 20:22 | Kallyanpur 132/33kV S/S GT-2 (132kV) HT is restored.
| 05:00 |  | Minimum generation 8063 MW
| 07:57 |  | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to Redhot maintenance of TR-1(B)
section
| 07:57 |  | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to Redhot maintenance of TR-1(B)
section
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 31-01-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 305 | 7801200 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 244564 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7661931 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 32.7 | 254880 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 80 | 432960 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 265685 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 271132 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22 | 418200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 496080 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 33 | 140640 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 160 | 994604 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 85 | 885600 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 50 | 354278 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 68 | 653760 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 204636 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 296640 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 548 | 11718530 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 90 | 741600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6667.111 | 1963.7 | 33836920
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 72939.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 31725 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 32 | 298560 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 960000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 179 | 4188377 | Plant availability less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 66 | 568727 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 8 | 32400 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 81173 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 217920 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 28 | 403200 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 50 | 173760 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20004 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 195709 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 35 | 123355 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 59 | 567055 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 126720 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 62 | 304855 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 75 | 170618 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 25025452 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 8 | 274560 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 430 | 11796363.64 | ps availability is less
Chattogram Area Total |  |  |  |  | 4898.863 | 2438 | 45633473.24
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 198 | 3469000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 280 | 7307100 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 220 | 5313000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 3 | 214992 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 264000 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 953677 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 85 | 647345 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 23 | 116848 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 103 | 2352013 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 103 | 907680 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 126 | 2624640 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 34 | 116030 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 353960 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 58 | 147060 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 69 | 555840 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 412955 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1366 | 25756140
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 9 | 279360 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 331200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 58 | 957600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 264030 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 3 | 64800 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 132840 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 106 | 2042430
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 63540 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 981000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 53 | 1325160 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 156 | 3631909 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 660000 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1494720 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 97 | 234797.46 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 369000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 20 | 362784 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7629000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | -
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 811 | 16751910.46
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 883 | 21582545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 34 | 61440 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 15 | 32384 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 236 | 5918976 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 529920 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 610 | 12996400 | U#1 Under Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1778 | 41121665
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 32 | 65280 | Fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 65 | 1721000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 1085 | 22516363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5271120 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 118800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6044000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3454 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1744 | 35740017.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 331488 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Machine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 10379 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 168 | 3991545 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9039418 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 15 | 30738 | machine problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 34 | 53774 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 5696 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 390528 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 70 | 349344 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 28920 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 762.44 | 15500727 | U#1 Under AOH
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 351008 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 666030 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1533.44 | 30749595
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 55 | 1274618 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 380697 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 28494.36 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 197716 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 164806 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 899280 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 160 | 2945611.36
Eastern Grid Total |  |  |  |  | 17398.245 | 6684.7 | 124020873.7
Western Grid Total |  |  |  |  | 10984.003 | 5215.44 | 110556889
National Grid Total |  |  |  |  | 28382.248 | 11900.14 | 234577762.7
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 31-01-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7842.63 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3534.2 | MW
i) Dhaka area |  |  | 4317.93 |  | MW | i) Khulna area |  |  |  | 1305 | MW
ii) Chattogram area |  |  | 1192.7 |  | MW | ii) Barishal area |  |  |  | 323 | MW
iii) Cumilla area |  |  | 970 |  | MW | iii) Rajshahi area |  |  |  | 1117.2 | MW
iv) Mymensingh area |  |  | 948 |  | MW | iv) Rangpur area |  |  |  | 789 | MW
v) Sylhet area |  |  | 414 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11376.83 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 10 | 21:00 | 67 | Hasnabad | 79 | 12:00 | 133 | Netrakona | 126 | 06:00
2 | AKSML | 119 | 16:00 | 68 | Hathazari | 75 | 18:00 | 134 | New | 60 | 12:00
3 | Aftabnagar | 30 | 14:00 | 69 | Hatirjheel | 28 | 14:00 | 135 | Niamatpur | 91 | 19:00
4 | Agargaon | 78 | 13:00 | 70 | Ishurdi | 50 | 18:30 | 136 | Noapara | 40 | 18:30
5 | Agrabad | 48 | 18:00 | 71 | Jaldhaka | 60 | 18:30 | 137 | PHP | 9 | 11:00
6 | Amnura | 34 | 09:00 | 72 | Jamalpur | 89 | 22:00 | 138 | Pabna | 78 | 19:00
7 | Ashuganj | 62 | 18:00 | 73 | Jashore | 105 | 13:00 | 139 | Palashbari | 104 | 18:00
8 | BSRM | 205 | 19:30 | 74 | Jhenaidah | 96 | 08:00 | 140 | Panchagarh | 46 | 18:30
9 | Bagerhat | 63 | 18:30 | 75 | Joydebpur | 102 | 19:30 | 141 | Patiya | 7 | 18:30
10 | Bajitpur | 68 | 13:00 | 76 | Joypurhat | 49 | 09:00 | 142 | Patuakhali | 37.3 | 21:00
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 17 | 14:00 | 143 | Payra | 30 | 18:00
12 | Bakulia | 68 | 19:00 | 78 | KSRM | 16 | 01:00 | 144 | Postogola | 43 | 13:00
13 | Banani | 36 | 13:00 | 79 | Kabirpur | 218 | 18:30 | 145 | Purbachal | 25 | 13:00
14 | Bangabhaban | 5 | 12:00 | 80 | Kachua | 62 | 13:00 | 146 | Purbasadipur | 111 | 19:00
15 | Barapukuria | 61 | 18:30 | 81 | Kallyanpur | 99 | 10:00 | 147 | Rahanpur | 27 | 13:00
16 | Barguna | 14 | 18:30 | 82 | Kalurghat | 30 | 16:00 | 148 | Rahim | 49 | 12:00
17 | Barishal | 84 | 13:00 | 83 | Kamrangirchar | 64 | 19:30 | 149 | Rajbari | 60 | 18:30
18 | Barishal-230 | 93 | 10:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 123 | 18:00
19 | Baroaulia | 63 | 11:00 | 85 | Kasba | 25 | 13:00 | 151 | Rajshahi | 71 | 13:00
20 | Baroirhat | 40 | 18:00 | 86 | Kazla | 94 | 13:00 | 152 | Rajshahi-230 | 73 | 13:00
21 | Bashundhara | 161 | 13:00 | 87 | Keranigonj | 65 | 13:00 | 153 | Ramganj | 68 | 13:00
22 | BashundharaCement | 6 | 00:00 | 88 | Khagrachori | 28 | 18:30 | 154 | Rampur | 40 | 14:00
23 | Beanibazar | 48 | 18:00 | 89 | Khulna | 58 | 13:00 | 155 | Rangamati | 13 | 18:00
24 | Benapole | 66 | 08:00 | 90 | Khulshi | 124 | 20:00 | 156 | Rangpur | 108 | 13:00
25 | Bhaluka | 128 | 18:00 | 91 | Kishoreganj | 106 | 18:00 | 157 | Ruppur | 1.6 | 15:00
26 | Bhandaria | 39 | 18:30 | 92 | Kodda | 246 | 18:30 | 158 | SSM | 0 | 00:00
27 | Bhangura | 24 | 13:00 | 93 | Kulaura | 29 | 18:00 | 159 | Saidpur | 95 | 09:00
28 | Bheramara(GK) | 42 | 18:30 | 94 | Kurigram | 64 | 08:00 | 160 | Satkhira | 95 | 18:30
29 | Bhulta | 206 | 23:00 | 95 | Kushtia | 124 | 18:30 | 161 | Satmasjid | 87 | 14:00
30 | Bog-Sherpur | 54 | 18:30 | 96 | Laksam | 13 | 17:00 | 162 | Savar | 182 | 12:00
31 | Bogura | 127 | 19:00 | 97 | Lakshmipur | 24 | 18:30 | 163 | SevenRings | 12.9 | 02:00
32 | Borhanuddin | 64 | 19:30 | 98 | Lalbag | 61 | 13:00 | 164 | ShahCement | 30 | 00:00
33 | Brahmanbaria | 94 | 18:00 | 99 | Lalmonirhat | 50 | 08:00 | 165 | Shahjadpur | 48 | 12:00
34 | Cantonment | 68 | 13:00 | 100 | MI_Cement | 18 | 23:00 | 166 | Shahjibazar | 97 | 18:30
35 | Chandina | 11 | 21:00 | 101 | Madanganj | 35 | 21:00 | 167 | Shahmirpur | 44 | 18:00
36 | Chandpur | 56 | 14:00 | 102 | Madaripur | 72 | 18:30 | 168 | Shariatpur | 56 | 21:00
37 | Chandraghona | 29 | 18:00 | 103 | Madartek | 60 | 13:00 | 169 | Sherpur | 120 | 23:00
38 | Chapai | 60 | 13:00 | 104 | Madunaghat | 42 | 12:00 | 170 | Shikalbaha | 19 | 09:00
39 | Charsaidpur | 42 | 11:00 | 105 | Magura | 63 | 18:30 | 171 | Shitalakhya | 68.1 | 13:00
40 | Chauddagram | 53 | 18:00 | 106 | Mahasthangarh | 50 | 08:00 | 172 | Sholosohor | 34 | 12:00
41 | Chhatak | 24 | 18:00 | 107 | Maijdee | 32 | 18:30 | 173 | Shyampur | 152 | 12:00
42 | Chowmuhani | 109 | 13:00 | 108 | Manikganj | 94 | 20:00 | 174 | Siddhirganj | 111 | 12:00
43 | Chuadanga | 79 | 18:00 | 109 | Maniknagar | 42 | 13:00 | 175 | Sirajganj | 84 | 18:30
44 | Coxsbazar | 120 | 14:00 | 110 | Matarbari | 41 | 18:00 | 176 | Sonargaon | 136 | 21:00
45 | Cumilla(N) | 89 | 13:00 | 111 | Matuail | 58 | 12:00 | 177 | Sreemongol | 56 | 18:00
46 | Cumilla(S) | 135 | 13:00 | 112 | Metrorail_Motijheel | 26 | 19:30 | 178 | Sreepur | 96 | 18:30
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 0 | 00:00 | 179 | Srinagar | 32.5 | 13:00
48 | Daudkandi | 91 | 19:00 | 114 | Millgate | 78 | 12:00 | 180 | Sunamganj | 42 | 18:30
49 | DhakaUniversity | 60 | 13:00 | 115 | Mirpur | 114 | 13:00 | 181 | Sylhet | 35 | 13:00
50 | Dhamrai | 112 | 18:00 | 116 | Mirsorai | 26 | 02:00 | 182 | Sylhet-132 | 80 | 18:00
51 | Dhanmondi | 79 | 13:00 | 117 | Mirzapur | 40 | 18:30 | 183 | TK | 17 | 18:00
52 | Dohazari | 74 | 18:30 | 118 | Mithapukur | 50 | 18:30 | 184 | Tangail | 138 | 08:00
53 | Faridpur | 115 | 18:30 | 119 | Modern | N/A | N/A | 185 | Taraganj | 20 | 09:00
54 | Fatullah | 82 | 19:00 | 120 | Mogbazar | 62.6 | 13:00 | 186 | Tasnim | 25 | 00:00
55 | Fenchuganj | 23 | 13:00 | 121 | Mongla | 30 | 18:30 | 187 | Thakurgaon | 79 | 18:30
56 | Feni | 81 | 13:00 | 122 | Motijheel | 37 | 13:00 | 188 | Tongi | 141 | 13:00
57 | GPH | 80 | 03:00 | 123 | Muktagacha | 32 | 19:00 | 189 | Ullahpara | 26 | 18:00
58 | Ghatail | 72 | 08:00 | 124 | Munshiganj | 71 | 13:00 | 190 | Ullon | 48 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 26 | 18:00 | 191 | Uttara | 60 | 13:00
60 | Ghorashal-230 | 97 | 18:00 | 126 | Mymensingh | 171 | 13:00 | 192 | UttaraNew | 26 | 13:00
61 | Goalpara | 33 | 13:00 | 127 | Naogaon | 113 | 09:00 | 193 | Zigatola | 60 | 13:00
62 | Gollamari | 70 | 13:00 | 128 | Narail | 44.5 | 18:30
63 | Gopalganj | 79 | 18:30 | 129 | Narinda | 53 | 13:00
64 | Gulshan | 68 | 13:00 | 130 | Narshingdi | 146 | 19:30
65 | Halishahar | 64 | 18:00 | 131 | Natore | 117 | 13:00
66 | HaripurSBU | 115 | 23:00 | 132 | Nawabganj | 33.8 | 18:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 31-01-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 9116 | 0 |  | 9116
1:00 | 8526 | 0 |  | 8526
2:00 | 8167 | 0 |  | 8167
3:00 | 7867 | 0 |  | 7867
4:00 | 7631 | 0 |  | 7631
5:00 | 7599 | 0 |  | 7599
6:00 | 8016 | 0 |  | 8016
7:00 | 8728.43 | 42 |  | 8772.32
8:00 | 9522.83 | 29 |  | 9552.83
9:00 | 9638.04 | 20 |  | 9659.04
10:00 | 9593.41 | 39 |  | 9634.41
11:00 | 9901.69 | 41 |  | 9944.69
12:00 | 10202.18 | 69 |  | 10274.18
13:00 | 10968.26 | 72 |  | 11043.26
14:00 | 10492.48 | 49 |  | 10543.48
15:00 | 10179.92 | 51 |  | 10232.92
16:00 | 9857.46 | 53 |  | 9912.46
17:00 | 9886.31 | 54 |  | 9942.31
18:00 | 11373.33 | 55 |  | 11430.33
19:00 | 11900.14 | 77 |  | 11980.14
19:30 | 11722.04 | 75 |  | 11800.04
20:00 | 11527.9 | 60 |  | 11590.9
21:00 | 11299.4 | 39 |  | 11340.4
22:00 | 10819.7 | 0 |  | 10819.7
23:00 | 10313 | 0 |  | 10313
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 31-01-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4631 | 4485 | 9116 | DAILY GENERATION CURVE
00:30 | 4555.5 | 4265.5 | 8821
01:00 | 4480 | 4046 | 8526 | 31-01-2026
01:30 | 4475.5 | 3871 | 8346.5
02:00 | 4471 | 3696 | 8167
02:30 | 4408 | 3609 | 8017
03:00 | 4345 | 3522 | 7867
03:30 | 4246.5 | 3502.5 | 7749
04:00 | 4148 | 3483 | 7631
04:30 | 4114 | 3501 | 7615
05:00 | 4080 | 3519 | 7599
05:30 | 4183.5 | 3624 | 7807.5
06:00 | 4287 | 3729 | 8016
06:30 | 4446.635 | 3925.58 | 8372.215
07:00 | 4606.27 | 4122.16 | 8728.43
07:30 | 4787.785 | 4337.845 | 9125.63
08:00 | 4969.3 | 4553.53 | 9522.83
08:30 | 4946.585 | 4633.85 | 9580.435
09:00 | 4923.87 | 4714.17 | 9638.04
09:30 | 4832.16 | 4783.565 | 9615.725
10:00 | 4740.45 | 4852.96 | 9593.41
10:30 | 4799.735 | 4947.815 | 9747.55
11:00 | 4859.02 | 5042.67 | 9901.69
11:30 | 4960.485 | 5091.45 | 10051.935
12:00 | 5061.95 | 5140.23 | 10202.18
12:30 | 5399.18 | 5186.04 | 10585.22
13:00 | 5736.41 | 5231.85 | 10968.26
13:30 | 5617.2 | 5113.17 | 10730.37
14:00 | 5497.99 | 4994.49 | 10492.48
14:30 | 5464.765 | 4871.435 | 10336.2
15:00 | 5431.54 | 4748.38 | 10179.92
15:30 | 5339.145 | 4679.545 | 10018.69
16:00 | 5246.75 | 4610.71 | 9857.46
16:30 | 5332.515 | 4539.37 | 9871.885
17:00 | 5418.28 | 4468.03 | 9886.31
17:30 | 5911.89 | 4717.93 | 10629.82
18:00 | 6405.5 | 4967.83 | 11373.33
18:30 | 6545.1 | 5091.635 | 11636.735
19:00 | 6684.7 | 5215.44 | 11900.14
19:30 | 6591.7 | 5130.34 | 11722.04
20:00 | 6396.6 | 5131.3 | 11527.9
20:30 | 6318.5 | 5095.15 | 11413.65 |  | Executive Engineer
21:00 | 6240.4 | 5059 | 11299.4 |  | Network Operation Division
21:30 | 6015.55 | 5044 | 11059.55
22:00 | 5790.7 | 5029 | 10819.7
22:30 | 5612.85 | 4953.5 | 10566.35
23:00 | 5435 | 4878 | 10313

## En-Curve
QF-LDC-12
Date | 31-01-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2759 | 1383 | 896 | 0 | 100 | 762 | 40 | 3103 | 0 | 0 | 53 | 0 | 0 | 20 | 0 | DAILY ENERGY CURVE
00:30 | 2724 | 1288.5 | 896.5 | 0 | 95 | 722 | 40 | 3005 | 0 | 0 | 26.5 | 0 | 0 | 23.5 | 0 | 31-01-2026
01:00 | 2689 | 1194 | 897 | 0 | 90 | 682 | 40 | 2907 | 0 | 0 | 0 | 0 | 0 | 27 | 0
01:30 | 2692 | 1202 | 897 | 0 | 89 | 603.5 | 40 | 2786.5 | 0 | 0 | 0 | 0 | 0 | 36.5 | 0 | Energy Generated | 234.5778 |  | MKWHr
02:00 | 2695 | 1210 | 897 | 0 | 88 | 525 | 40 | 2666 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | Energy not Served | 0.75 |  | MKWHr
02:30 | 2693.5 | 1192.5 | 897 | 0 | 87 | 476.5 | 40 | 2583.5 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | Total Energy Requirement | 235.3278 |  | MKWHr
03:00 | 2692 | 1175 | 897 | 0 | 86 | 428 | 40 | 2501 | 0 | 0 | 0 | 0 | 0 | 48 | 0
03:30 | 2670 | 1166.5 | 897 | 0 | 84 | 431.5 | 40 | 2425.5 | 0 | 0 | 0 | 0 | 0 | 34.5 | 0
04:00 | 2648 | 1158 | 897 | 0 | 82 | 435 | 40 | 2350 | 0 | 0 | 0 | 0 | 0 | 21 | 0
04:30 | 2638.5 | 1151.5 | 896.5 | 0 | 82 | 431.5 | 40 | 2348 | 0 | 0 | 0 | 0 | 0 | 27 | 0
05:00 | 2629 | 1145 | 896 | 0 | 82 | 428 | 40 | 2346 | 0 | 0 | 0 | 0 | 0 | 33 | 0
05:30 | 2672 | 1223 | 896.5 | 0 | 87 | 429 | 40 | 2443.5 | 0 | 0 | 0 | 0 | 0 | 16.5 | 0
06:00 | 2715 | 1301 | 897 | 0 | 92 | 430 | 40 | 2541 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:30 | 2723 | 1353 | 897 | 0 | 88 | 505.5 | 40 | 2761 | 4.715 | 0 | 0 | 0 | 0 | 0 | 21
07:00 | 2731 | 1405 | 897 | 0 | 84 | 581 | 40 | 2981 | 9.43 | 0 | 0 | 0 | 0 | 0 | 42
07:30 | 2733 | 1393 | 897 | 0 | 94 | 668.5 | 40 | 3196 | 56.63 | 8.5 | 39 | 0 | 0 | 0 | 35.5
08:00 | 2735 | 1381 | 897 | 0 | 104 | 756 | 40 | 3411 | 103.83 | 17 | 78 | 0 | 0 | 0 | 29
08:30 | 2653 | 1333.5 | 896.5 | 0 | 104 | 757.89 | 40 | 3439 | 216.545 | 17 | 123 | 0 | 0 | 0 | 24.5
09:00 | 2571 | 1286 | 896 | 0 | 104 | 759.78 | 40 | 3467 | 329.26 | 17 | 168 | 0 | 0 | 0 | 20
09:30 | 2513.5 | 1290.25 | 896 | 0 | 112 | 741.565 | 40 | 3471 | 412.41 | 17 | 122 | 0 | 0 | 0 | 29.5
10:00 | 2456 | 1294.5 | 896 | 0 | 120 | 723.35 | 40 | 3475 | 495.56 | 17 | 76 | 0 | 0 | 0 | 39
10:30 | 2531.5 | 1367.5 | 896.5 | 0 | 120 | 721.055 | 40 | 3441 | 545.495 | 8.5 | 76 | 0 | 0 | 0 | 40
11:00 | 2607 | 1440.5 | 897 | 0 | 120 | 718.76 | 40 | 3407 | 595.43 | 0 | 76 | 0 | 0 | 0 | 41
11:30 | 2610 | 1467.25 | 897 | 0 | 126 | 719.04 | 40 | 3456.5 | 610.145 | 0 | 126 | 0 | 0 | 0 | 55
12:00 | 2613 | 1494 | 897 | 0 | 132 | 719.32 | 40 | 3506 | 624.86 | 0 | 176 | 0 | 0 | 0 | 69
12:30 | 2607.5 | 1499 | 897 | 0 | 133 | 739.595 | 40 | 3563.5 | 606.975 | 45.5 | 453.15 | 0 | 0 | 0 | 70.5
13:00 | 2602 | 1504 | 897 | 0 | 134 | 759.87 | 40 | 3621 | 589.09 | 91 | 730.3 | 0 | 0 | 0 | 72
13:30 | 2541.5 | 1436.5 | 897 | 0 | 134 | 762.135 | 40 | 3572 | 562.285 | 103 | 681.95 | 0 | 0 | 0 | 60.5
14:00 | 2481 | 1369 | 897 | 0 | 134 | 764.4 | 40 | 3523 | 535.48 | 115 | 633.6 | 0 | 0 | 0 | 49
14:30 | 2448.5 | 1326.5 | 897 | 0 | 133 | 736.74 | 40 | 3535 | 468.96 | 127 | 621.5 | 0 | 0 | 2 | 50
15:00 | 2416 | 1284 | 897 | 0 | 132 | 709.08 | 40 | 3547 | 402.44 | 139 | 609.4 | 0 | 0 | 4 | 51
15:30 | 2422 | 1276 | 897 | 0 | 131 | 691.29 | 40 | 3555.5 | 321.45 | 155 | 524.95 | 0 | 0 | 4.5 | 52
16:00 | 2428 | 1268 | 897 | 0 | 130 | 673.5 | 40 | 3564 | 240.46 | 171 | 440.5 | 0 | 0 | 5 | 53
16:30 | 2499 | 1273 | 889 | 0 | 121 | 673.35 | 40 | 3542 | 149.785 | 175.5 | 503.25 | 0 | 0 | 6 | 53.5
17:00 | 2570 | 1278 | 881 | 0 | 112 | 673.2 | 40 | 3520 | 59.11 | 180 | 566 | 0 | 0 | 7 | 54
17:30 | 2657.5 | 1329.5 | 879.5 | 0 | 119 | 708.015 | 40 | 3537 | 29.555 | 276.5 | 1045.75 | 0 | 0 | 7.5 | 54.5
18:00 | 2745 | 1381 | 878 | 0 | 126 | 742.83 | 40 | 3554 | 0 | 373 | 1525.5 | 0 | 0 | 8 | 55
18:30 | 2748.5 | 1428.5 | 880.5 | 0 | 126 | 752.635 | 40 | 3632.5 | 0 | 377.5 | 1642.6 | 0 | 0 | 8 | 66
19:00 | 2752 | 1476 | 883 | 0 | 126 | 762.44 | 40 | 3711 | 0 | 382 | 1759.7 | 0 | 0 | 8 | 77
19:30 | 2838 | 1543 | 883 | 0 | 120 | 764.34 | 40 | 3689 | 0 | 371 | 1463.7 | 0 | 0 | 10 | 75
20:00 | 2793 | 1467 | 887 | 0 | 120 | 764.3 | 40 | 3681 | 0 | 321 | 1442.6 | 0 | 0 | 12 | 60
20:30 | 2807 | 1481 | 889 | 0 | 121 | 760.65 | 40 | 3689.5 | 0 | 242.5 | 1373 | 0 | 0 | 10 | 49.5
21:00 | 2821 | 1495 | 891 | 0 | 122 | 757 | 40 | 3698 | 0 | 164 | 1303.4 | 0 | 0 | 8 | 39
21:30 | 2840 | 1470 | 894 | 0 | 118 | 760 | 40 | 3687 | 0 | 99 | 1140.55 | 0 | 0 | 11 | 19.5
22:00 | 2859 | 1445 | 897 | 0 | 114 | 763 | 40 | 3676 | 0 | 34 | 977.7 | 0 | 0 | 14 | 0
22:30 | 2848 | 1435.5 | 897 | 0 | 112 | 763 | 40 | 3678.5 | 0 | 25.5 | 748.85 | 0 | 0 | 18 | 0
23:00 | 2837 | 1426 | 897 | 0 | 110 | 763 | 40 | 3681 | 0 | 17 | 520 | 0 | 0 | 22 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 31-01-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 422 | 04:00 | 398 | 11:00 | Madunaghat | 416 | 05:00 | 407 | 12:00
Amtali | 424 | 03:00 | 412 | 12:00 | Meghnaghat | 425 | 04:00 | 405 | 11:00
Ashuganj | 409 | 2:00 | 389 | 12:00 | Payra | 425 | 03:00 | 415 | 12:00
Bhulta | 404 | 03:00 | 381 | 12:00 | Rahanpur | 421 | 03:00 | 405 | 09:00
Bibiana | 423 | 02:00 | 407 | 11:00 | Rampal | 420 | 05:00 | 398 | 12:00
BIPTC | 401 | 04:00 | 389 | 11:00
Bogura | 419 | 04:00 | 399 | 13:00
Gopalganj | 423 | 04:00 | 402 | 12:00
Kaliakoir | 416 | 03:00 | 395 | 11:00
Korerhat | 424 | 03:00 | 409 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 244 | 04:00 | 227 | 12:00 | Jhenaidah | 245 | 04:00 | 229 | 12:00
AKSML | 238 | 05:00 | 231 | 11:00 | Kachua | 241 | 06:00 | 233 | 15:00
Aminbazar | 242 | 03:00 | 228 | 11:00 | Kaliakoir | 244 | 03:00 | 228 | 12:00
Ashuganj | 236 | 01:00 | 226 | 11:00 | Keranigonj | 242 | 03:00 | 225 | 12:00
Ashuganj-400 | 236 | 01:00 | 226 | 11:00 | Khulna(S) | 246 | 04:00 | 227 | 12:00
Baghabari | 242 | 03:00 | 232 | 12:00 | Korerhat | 241 | 03:00 | 232 | 11:00
Barapukuria | 231 | 03:00 | 217 | 09:00 | Madunaghat | 239 | 18:30 | 231 | 11:00
Barapukuria-230 | 231 | 03:00 | 217 | 09:00 | Madunaghat-400 | 238 | 04:00 | 232 | 12:00
Barishal | 241 | 04:00 | 231 | 12:00 | Maniknagar | 241 | 02:00 | 226 | 11:00
Bheramara | 242 | 03:00 | 228 | 12:00 | Meghnaghat | 243 | 01:00 | 231 | 12:00
Bhulta | 242 | 03:00 | 228 | 12:00 | Meghnaghat-400 | 241 | 04:00 | 228 | 12:00
Bibiana | 243 | 03:00 | 234 | 11:00 | Mirsorai | 241 | 04:00 | 232 | 11:00
BIPTC | 246 | 04:00 | 230 | 12:00 | Rajshahi | 242 | 04:00 | 227 | 12:00
Bogura | 245 | 04:00 | 232 | 08:00 | Rampal | 244 | 05:00 | 226 | 12:00
Bogura-400 | 244 | 04:00 | 232 | 08:00 | Rampur | N/A | N/A | N/A | N/A
Borhanuddin | 240 | 4:00 | 235 | 13:00 | Rampura | 242 | 03:00 | 226 | 12:00
BSRM | 241 | 04:00 | 231 | 11:00 | Shikalbaha | 238 | 19:00 | 230 | 11:00
Chowmuhani | 241 | 15:00 | 232 | 10:00 | Shyampur | 242 | 04:00 | 225 | 12:00
Cumilla(N) | 236 | 01:00 | 228 | 11:00 | Siddhirganj | 242 | 03:00 | 228 | 11:00
Faridpur | 240 | 03:00 | 228 | 12:00 | Sirajgonj | 247 | 04:00 | 236 | 12:00
Fenchuganj | 246 | 03:00 | 236 | 15:00 | Sreepur | 237 | 04:00 | 218 | 12:00
Feni | 242 | 04:00 | 231 | 11:00 | Tongi | 241 | 04:00 | 227 | 12:00
Ghorashal | 240 | 00:00 | 230 | 13:00
Ghorashal-230 | 242 | 05:00 | 225 | 12:00
Gopalganj | 238 | 03:00 | 227 | 12:00
GPH | 238 | 11:00 | 233 | 05:00
Haripur | 242 | 04:00 | 227 | 12:00
Hasnabad | 240 | 01:00 | 227 | 11:00
Hathazari | 237 | 04:00 | 229 | 16:00
Ishurdi | 246 | 03:00 | 232 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 03:00 | 124 | 11:00 | Maijdee | 135 | 03:00 | 130 | 11:00
Agargaon | 137 | 04:00 | 129 | 11:00 | Manikganj | 134 | 15:00 | 124 | 10:00
Agrabad | 139 | 19:00 | 133 | 11:00 | Maniknagar | 140 | 03:00 | 130 | 12:00
AKS | 136 | 03:00 | 132 | 11:00 | Matarbari | 135 | 06:00 | 122 | 16:00
Aminbazar | 139 | 00:00 | 129 | 11:00 | Matuail | 138 | 03:00 | 130 | 12:00
Amnura | 139 | 04:00 | 131 | 13:00 | Metrorail_Motijheel | 140 | 03:00 | 130 | 12:00
Ashuganj | 139 | 04:00 | 134 | 09:00 | Metrorail_Uttara | 135 | 03:00 | 121 | 12:00
Bagerhat | 136 | 04:00 | 121 | 12:00 | Millgate | 135 | 04:00 | 121 | 12:00
Bajitpur | 135 | 02:00 | 124 | 14:00 | Mirpur | 140 | 05:00 | 128 | 12:00
Bakerganj | 138.8 | 19:00 | 135 | 12:00 | Mirzapur | 135 | 05:00 | 126 | 12:00
Bakulia | 140 | 06:00 | 134 | 10:00 | Mithapukur | 136 | 04:00 | 124 | 09:00
Banani | 134 | 02:00 | 124 | 12:00 | MI_Cement | 137.6 | 04:00 | 123 | 12:00
Bangabhaban | 139 | 01:00 | 130 | 12:00 | Modern | N/A | N/A | N/A | N/A
Barapukuria | 134 | 03:00 | 125 | 09:00 | Mogbazar | 135 | 04:00 | 125 | 12:00
Barguna | 139 | 18:00 | 135 | 12:00 | Mongla | 135 | 03:00 | 120 | 12:00
Barishal | 140 | 03:00 | 134 | 12:00 | Motijheel | 139 | 01:00 | 130 | 12:00
Barishal-230 | 140 | 01:00 | 134 | 12:00 | Muktagacha | 132 | 17:00 | 120 | 07:00
Baroaulia | 140 | 18:00 | 134 | 10:00 | Munshiganj | 138 | 03:00 | 129 | 11:00
Baroirhat | 137 | 18:00 | 130 | 11:00 | Muradnagar | 139 | 04:00 | 130 | 11:00
Bashundhara | 134 | 03:00 | 124 | 12:00 | Mymensingh | 129 | 13:00 | 115 | 14:00
BashundharaCement | 137 | 00:00 | 131 | 13:00 | Naogaon | 141 | 03:00 | 125 | 08:00
Beanibazar | 134 | 04:00 | 128 | 12:00 | Narail | 142 | 04:00 | 129 | 18:30
Benapole | 134 | 17:00 | 113 | 12:00 | Narinda | 140 | 03:00 | 130 | 12:00
Bhaluka | 135 | 01:00 | 120 | 13:00 | Narshingdi | 135 | 00:00 | 119 | 12:00
Bhandaria | 138 | 03:00 | 132 | 12:00 | Natore | 138 | 01:00 | 131 | 12:00
Bhangura | 140 | 03:00 | 133 | 12:00 | Nawabganj | 138 | 05:00 | 125 | 12:00
Bheramara | 141 | 03:00 | 134 | 13:00 | Netrakona | 124 | 03:00 | 106 | 14:00
Bheramara(GK) | 141 | 04:00 | 135 | 11:00 | New | 134 | 05:00 | 123 | 12:00
Bhulta | 130 | 00:00 | 124 | 11:00 | Niamatpur | 140 | 04:00 | 134 | 08:00
Bog-Sherpur | 139 | 03:00 | 130 | 08:00 | Noapara | 135 | 05:00 | 119 | 12:00
Bogura | 138 | 04:00 | 131 | 08:00 | Pabna | 139 | 00:00 | 133 | 12:00
Bogura-230 | 139 | 03:00 | 131 | 08:00 | Palashbari | 134 | 04:00 | 122 | 08:00
Brahmanbaria | 132 | 03:00 | 123 | 12:00 | Panchagarh | 137 | 19:00 | 127 | 09:00
Cantonment | 139 | 03:00 | 128 | 12:00 | Patiya | 139 | 06:00 | 134 | 11:00
Chandina | 141 | 05:00 | 133 | 11:00 | Patuakhali | 139 | 03:00 | 134 | 11:00
Chandpur | 140 | 18:30 | 134 | 11:00 | Payra | 140 | 04:00 | 136 | 12:00
Chandraghona | 139 | 04:00 | 136 | 10:00 | PHP | 136 | 03:00 | 130 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 139 | 05:00 | 133 | 08:00 | Postogola | 138 | 02:00 | 125 | 12:00
Charsaidpur | 138 | 05:00 | 129 | 12:00 | Purbachal | 135 | 03:00 | 124 | 12:00
Chauddagram | 137 | 03:00 | 131 | 11:00 | Purbasadipur | 134 | 04:00 | 126 | 09:00
Chhatak | 132 | 00:00 | 127 | 11:00 | Rahanpur | 141 | 06:00 | 135 | 12:00
Chowmuhani | 135 | 04:00 | 130 | 11:00 | Rahanpur-400 | 142 | 03:00 | 135 | 13:00
Chuadanga | 141 | 02:00 | 129 | 18:00 | Rahim | 138 | 03:00 | 130 | 12:00
Coxsbazar | 132 | 13:00 | 121 | 16:00 | Rajbari | 139 | 03:00 | 131 | 13:00
Cumilla(N) | 138 | 00:00 | 133 | 12:00 | Rajendrapur | 135 | 04:00 | 120 | 13:00
Cumilla(S) | 137 | 00:00 | 123 | 10:00 | Rajshahi | 140 | 02:00 | 131 | 12:00
Daganbhuiyan | 136 | 03:00 | 130 | 11:00 | Rajshahi-230 | 140 | 03:00 | 130 | 13:00
Daudkandi | 138 | 02:00 | 128 | 12:00 | Ramganj | 137 | 18:30 | 129 | 11:00
DhakaUniversity | 134 | 02:00 | 124 | 12:00 | Rampur | 138 | 18:00 | 134 | 10:00
Dhamrai | 137 | 00:00 | 129 | 12:00 | Rampura | 134 | 03:00 | 124 | 12:00
Dhanmondi | 139.5 | 05:00 | 132.6 | 11:00 | Rangamati | 139 | 05:00 | 134 | 11:00
Dohazari | 139 | 06:00 | 127 | 16:00 | Rangpur | 135 | 03:00 | 125 | 08:00
Faridpur | 139 | 04:00 | 132 | 12:00 | Ruppur | 141 | 05:00 | 135 | 12:00
Fatullah | 140 | 04:00 | 124 | 12:00 | Saidpur | 135 | 04:00 | 124 | 12:00
Fenchuganj | 139 | 05:00 | 132 | 11:00 | Satkhira | 135 | 04:00 | 121 | 12:00
Feni | 135 | 18:00 | 129 | 11:00 | Satmasjid | 139 | 05:00 | 127 | 12:00
Feni-230 | 136 | 04:00 | 130 | 11:00 | Savar | 139 | 03:00 | 127 | 12:00
Ghatail | 130 | 17:00 | 119 | 07:00 | SevenRings | 135 | 04:00 | 126 | 13:00
Ghorashal | 133 | 01:00 | 127 | 11:00 | ShahCement | 138 | 05:00 | 129 | 12:00
Goalpara | 138 | 03:00 | 122 | 12:00 | Shahjadpur | 142 | 00:00 | 135 | 10:00
Gollamari | 137 | 03:00 | 128 | 08:00 | Shahjibazar | 133 | 04:00 | 125 | 12:00
Gopalganj | 140 | 03:00 | 133 | 08:00 | Shahmirpur | 140 | 18:30 | 135 | 11:00
Gopalganj-400 | 144 | 03:00 | 137 | 12:00 | Shariatpur | 143 | 04:00 | 135 | 12:00
Gulshan | 133 | 01:00 | 124 | 12:00 | Sherpur | 128 | 17:00 | 107 | 01:00
Halishahar | 140 | 18:30 | 134 | 11:00 | Shikalbaha | 129 | 18:00 | 124 | 11:00
Haripur | 139 | 04:00 | 130 | 12:00 | Shikalbaha-230 | 141 | 18:30 | 136 | 11:00
HaripurSBU | 138 | 04:00 | 132 | 11:00 | Shitalakhya | 137.6 | 04:00 | 123 | 12:00
Hasnabad | 136 | 00:00 | 126 | 11:00 | Sholosohor | 139 | 04:00 | 135 | 11:00
Hathazari | 139 | 04:00 | 135 | 11:00 | Shyampur | 137 | 03:00 | 128 | 12:00
Hatirjheel | 135 | 04:00 | 124 | 12:00 | Shyampur-230 | 140 | 04:00 | 130 | 12:00
Ishurdi | 144 | 04:00 | 136 | 12:00 | Siddhirganj | 137 | 00:00 | 130 | 12:00
Jaldhaka | 131 | 04:00 | 122 | 09:00 | Sirajganj | 137 | 02:00 | 130 | 12:00
Jamalpur | 128 | 17:00 | 113 | 06:00 | Sonargaon | 134 | 06:00 | 132 | 13:00
Jashore | 136 | 17:00 | 114 | 12:00 | Sreemongol | 134 | 01:00 | 127 | 12:00
Jhenaidah | 140 | 00:00 | 128 | 12:00 | Sreepur | 136 | 04:00 | 124 | 12:00
Jhenaidah-230 | 143 | 03:00 | 133 | 18:30 | Srinagar | 137 | 04:00 | 125 | 12:00
Joydebpur | 132 | 03:00 | 123 | 12:00 | SSM | 142 | 18:00 | 138 | 12:00
Joypurhat | 135 | 03:00 | 124 | 08:00 | Sunamganj | 132 | 04:00 | 125 | 12:00
Juldah | 140 | 19:00 | 133 | 11:00 | Sylhet | 134 | 03:00 | 128 | 12:00
Kabirpur | 138 | 02:00 | 125 | 09:00 | Sylhet-132 | 132 | 00:00 | 129 | 12:00
Kachua | 138 | 04:00 | 133 | 11:00 | Tangail | 131 | 17:00 | 122 | 18:30
Kaliakoir | 141 | 04:00 | 132 | 12:00 | Taraganj | 133 | 20:00 | 123 | 09:00
Kallyanpur | 139 | 00:00 | 129 | 12:00 | Tasnim | 138 | 04:00 | 129 | 12:00
Kalurghat | 139 | 05:00 | 135 | 11:00 | Thakurgaon | 137 | 04:00 | 126 | 09:00
Kamrangirchar | 137 | 04:00 | 124 | 12:00 | TK | 138 | 00:00 | 135 | 12:00
Kaptai | 140 | 1:00 | 136 | 10:00 | Tongi | 134 | 02:00 | 125 | 12:00
Kasba | 139 | 04:00 | 130 | 12:00 | Ullahpara | 140 | 03:00 | 132 | 08:00
Kazla | 140 | 04:00 | 129 | 13:00 | Ullon | 133 | 01:00 | 124 | 12:00
Keranigonj | 138 | 05:00 | 125 | 12:00 | Uttara | 135 | 04:00 | 121 | 12:00
Khagrachori | 139 | 05:00 | 134 | 11:00 | UttaraNew | 135 | 03:00 | 121 | 12:00
Khulna | 135 | 17:00 | 122 | 12:00 | Zigatola | 138 | 05:00 | 125 | 12:00
Khulna(S) | 138 | 04:00 | 124 | 12:00
Khulshi | 137 | 04:00 | 133 | 11:00
Kishoreganj | 133 | 04:00 | 122 | 14:00
Kodda | 137 | 02:00 | 128 | 11:00
KSRM | 139 | 19:00 | 133 | 11:00
Kulaura | 139 | 05:00 | 132 | 12:00
Kurigram | 130 | 19:00 | 118 | 09:00
Kushtia | 140 | 02:00 | 131 | 13:00
Laksam | 139 | 01:00 | 133 | 11:00
Lakshmipur | 136 | 05:00 | 129 | 12:00
Lalbag | 137 | 06:00 | 124 | 12:00
Lalmonirhat | 130 | 03:00 | 119 | 09:00
Madanganj | 137 | 00:00 | 131 | 13:00
Madaripur | 141 | 03:00 | 137 | 09:00
Madartek | 134 | 05:00 | 123 | 12:00
Madunaghat | 140 | 18:30 | 135 | 11:00
Magura | 140 | 04:00 | 130 | 18:30
Mahasthangarh | 138 | 05:00 | 127 | 08:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division