## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 05-02-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-02-2026 | during | 05-02-2026 | during | 05-02-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 343 | 291 | 412 | 412 | 350 | 350 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 335 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 15.9 | 53.97 | 53.97 | 53.97 | 53.97 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 15 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 12 | 12 | 33 | 33 | 23 | 23 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 70 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 34 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 49 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 0 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 516 | 475 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 70 | 160 | 160 | 52 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1245 | 1437.9 | 5357.35 | 5329.35 | 2586.02 | 2666.02
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 15 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 174 | 173 | 150 | 150 | 150 | 150 | Plant availability less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 34 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 8 | 8 | 8 | 8 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 34 | 34 | 34 | 34 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 34 | 42 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.3 | 0 | 3.52 | 0 | 3.52 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 35 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 34 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1148 | 1149 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 2 | 5 | 28 | 5 | 28 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 670 | 670 | 675 | 675 | 670 | 670 | ps availability is less
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2085.3 | 2144 | 3395.38 | 3402.86 | 2874.02 | 2899.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 200 | 189 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 355 | 310 | 353.35 | 353.35 | 317 | 317 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 380 | 380 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 40 | 0 | 46.7 | 46.7 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 5 | 0 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 32 | 32 | 24 | 24 | Machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 102 | 104 | 163 | 163 | 110 | 110 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 45 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 100 | 102 | 84 | 82 | 120 | 120 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 13 | 24.5 | 24.5 | 13 | 13 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 32 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 32 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1286 | 1226 | 2422.75 | 2360.75 | 1891.2 | 1831.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-02-2026 | during | 05-02-2026 | during | 05-02-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 106 | 143 | 157.5 | 157.5 | 35 | 35 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 19 | 20 | 20 | 20 | 20 | Fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 59 | 60 | 60 | 60 | 60 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 35.71 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 22 | 22 | 6 | 6 | Fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 35 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 221.71 | 227 | 358.1 | 314 | 182.1 | 156
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 42 | 42 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 53 | 53 | 0 | 0 | 53 | 53 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 160 | 152 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 0 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 83 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 77 | 75 | 100 | 100 | 0 | 0 | Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 15 | 15 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 20 | 21 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 804 | 747 | 784 | 784 | 682 | 683
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 898 | 898 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 250 | 410 | 410 | 250 | 250 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 63.16 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 386 | 608 | 617.1 | 617.1 | 617.1 | 617.1 | U1 under maintenance
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1597.16 | 1756 | 2964.1 | 2889.1 | 2049.2 | 1974.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 130 | 130 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 564 | 990 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 35 | 35 | Fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 209 | 274 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.21 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1123.21 | 1614 | 2003.32 | 2002.32 | 1888.32 | 1887.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 47.1 | 0 | 47 | 0 | 47 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Machine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 176 | 166 | 214 | 214 | 214 | 214 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 399 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 24 | 24 | 24 | 24 | Machine problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.2 | 0 | 5 | 0 | 5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 423.65 | 758.11 | 748 | 748 | 748 | 748 | U#1 Under AOH
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 50.64 | 0 | 56 | 0 | 56 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 96 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1211.59 | 1323.11 | 2389.99 | 2181.99 | 1908.61 | 1700.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.5 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 28 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 152 | 0 | 159 | 0 | 159 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 185.5 | 69 | 456.2 | 262 | 422.2 | 228
System Total |  |  |  |  | 28823.2 | 28382.8 | 9759.47 | 10544.01 | 20131.19 | 19526.37 | 14483.67 | 14025.85
Forecast Scenario (05-02-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9000 |  | 0 |  | 9000
|  |  |  | 1:00 | 8500 |  | 0 |  | 8500
|  |  |  | 2:00 | 8300 |  | 0 |  | 8300
|  |  |  | 3:00 | 8000 |  | 0 |  | 8000
|  |  |  | 4:00 | 7800 |  | 0 |  | 7800
|  |  |  | 5:00 | 7900 |  | 0 |  | 7900
|  |  |  | 6:00 | 8100 |  | 0 |  | 8100
|  |  |  | 7:00 | 8800 |  | 0 |  | 8800
|  |  |  | 8:00 | 9900 |  | 0 |  | 9900
|  |  |  | 9:00 | 10600 |  | 0 |  | 10600
|  |  |  | 10:00 | 10600 |  | 0 |  | 10600
|  |  |  | 11:00 | 10900 |  | 0 |  | 10900
|  |  |  | 12:00 | 11200 |  | 0 |  | 11200
|  |  |  | 13:00 | 11300 |  | 0 |  | 11300
|  |  |  | 14:00 | 10900 |  | 0 |  | 10900
|  |  |  | 15:00 | 11000 |  | 0 |  | 11000
|  |  |  | 16:00 | 10600 |  | 0 |  | 10600
|  |  |  | 17:00 | 10500 |  | 0 |  | 10500
|  |  |  | 18:00 | 11250 |  | 0 |  | 11250
|  |  |  | 18:30 | 11300 |  | 0 |  | 11300
|  |  |  | 19:00 | 11370 |  | 0 |  | 11370
|  |  |  | 19:30 | 10960 |  | 0 |  | 10960
|  |  |  | 20:00 | 10790 |  | 0 |  | 10790
|  |  |  | 21:00 | 10220 |  | 0 |  | 10220
|  |  |  | 22:00 | 9830 |  | 0 |  | 9830
|  |  |  | 23:00 | 9400 |  | 0 |  | 9400
Probable Maximum Temperature: |  |  | 27.80°C
Probable Maximum Demand at Day Peak: |  |  | 11200.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11370.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11370.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 236.76 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:05 hrs on 05-02-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 04-02-2026 | [28 empty] | Date: | 04-02-2026 | [28 empty] | Date: | 04-02-2026 | [28 empty] | Date: | 04-02-2026 | [28 empty] | Date: | 04-02-2026 | [17 empty] | Date: | 04-02-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [17 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 11.5 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 670 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 943 | 0 | 0 | 0 | 220 | 300 | 0 | 51 | 0 | 200 | 0 | 0 | 105 | 0 | 0 | 19 | 0 | 88 | 0 | 0 | 0 | 310 | 0 | 0 | 42 | 53 | 156 | 0 | 21 | 0 | 83 | 30 | 0 | 15 | 77 | 0 | 45 | 19 | 49 | 0 | 0 | 0 | 4916.5 | 898 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 130 | 220 | 0 | 0 | 700 | 0 | 3962 | 8878.5 | 94.8
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 10 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 575 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 220 | 300 | 0 | 51 | 0 | 219 | 0 | 0 | 105 | 0 | 0 | 19 | 0 | 84 | 0 | 0 | 0 | 305 | 0 | 0 | 42 | 53 | 151 | 0 | 17 | 0 | 83 | 20 | 0 | 15 | 77 | 0 | 45 | 0 | 51 | 0 | 0 | 0 | 4667 | 898 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 605.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 130 | 220 | 0 | 0 | 530 | 0 | 3564.3 | 8231.3 | 94.8
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 10 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 575 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 850 | 0 | 0 | 0 | 220 | 305 | 0 | 5 | 0 | 200 | 0 | 0 | 50 | 0 | 0 | 19 | 0 | 86 | 0 | 0 | 0 | 305 | 0 | 0 | 42 | 53 | 144 | 0 | 17 | 0 | 11 | 20 | 0 | 15 | 77 | 0 | 35 | 0 | 66 | 0 | 0 | 0 | 4479 | 898 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 421.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 100 | 220 | 0 | 0 | 530 | 0 | 3366.54 | 7845.54 | 94.8
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 10 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 575 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 820 | 0 | 0 | 0 | 220 | 295 | 0 | 5 | 0 | 200 | 0 | 0 | 51 | 0 | 0 | 13 | 0 | 82 | 0 | 0 | 0 | 300 | 0 | 0 | 41 | 53 | 134 | 0 | 0 | 0 | 11 | 20 | 0 | 15 | 77 | 0 | 24 | 0 | 63 | 0 | 0 | 0 | 4230 | 898 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 420.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 100 | 180 | 0 | 0 | 525 | 0 | 3313.42 | 7543.42 | 94.79
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 10 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 575 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 850 | 0 | 0 | 0 | 220 | 305 | 0 | 5 | 0 | 200 | 0 | 0 | 51 | 0 | 0 | 13 | 0 | 76 | 0 | 0 | 0 | 300 | 0 | 0 | 41 | 53 | 136 | 0 | 0 | 0 | 11 | 20 | 0 | 15 | 77 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 4271 | 898 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 422.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3276.66 | 7547.66 | 94.79
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 10 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 585 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 220 | 295 | 0 | 5 | 0 | 200 | 0 | 0 | 51 | 0 | 0 | 13 | 0 | 78 | 0 | 0 | 0 | 305 | 0 | 0 | 41 | 53 | 138 | 0 | 0 | 0 | 11 | 20 | 0 | 15 | 77 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 4229 | 898 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 422.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3265.44 | 7494.44 | 94.79
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 10 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 605 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 220 | 315 | 0 | 5 | 0 | 140 | 0 | 0 | 51 | 0 | 0 | 13 | 0 | 82 | 0 | 0 | 0 | 305 | 0 | 0 | 42 | 53 | 138 | 0 | 0 | 0 | 0 | 20 | 0 | 15 | 77 | 0 | 8 | 0 | 112 | 0 | 0 | 0 | 4161 | 898 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 421.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3219.6 | 7380.6 | 94.78
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 10 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 40 | 0 | 0 | 608 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 776 | 1 | 0 | 0 | 220 | 335 | 0 | 5 | 0 | 200 | 0 | 0 | 51 | 0 | 0 | 13 | 0 | 74 | 0 | 3 | 0 | 310 | 0 | 0 | 31 | 53 | 143 | 0 | 0 | 0 | 0 | 20 | 0 | 15 | 77 | 0 | 11 | 0 | 112 | 0 | 0.42 | 0 | 4317.62 | 898 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.33 | 382 | 0 | 0 | 0 | 422.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0.27 | 130 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0.01 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3323.42 | 7641.04 | 94.78
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 5 | 17 | 10 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74 | 40 | 0 | 32 | 650 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 858 | 3 | 0 | 0 | 345 | 345 | 0 | 11 | 0 | 206 | 0 | 0 | 106 | 0 | 0 | 18 | 0 | 78 | 0 | 12 | 0 | 320 | 0 | 0 | 42 | 53 | 156 | 1 | 0 | 0 | 22 | 30 | 0 | 15 | 77 | 0 | 57 | 19 | 111 | 0 | 10.28 | 0 | 5000.02 | 898 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 392 | 0 | 0 | 0 | 423.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.15 | 24 | 0 | 0 | 10.22 | 181 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.38 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 29 | 0.06 | 0 | 147 | 130 | 220 | 0 | 0 | 500 | 0 | 3640.92 | 8640.94 | 94.78
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 17 | 34 | 12 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.93 | 40 | 0 | 33 | 670 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 869 | 13 | 0 | 0 | 370 | 340 | 0 | 51 | 0 | 205 | 0 | 0 | 105 | 0 | 0 | 18 | 0 | 82 | 0 | 25 | 0 | 320 | 0 | 0 | 42 | 53 | 157 | 3 | 17 | 0 | 83 | 30 | 0 | 15 | 77 | 0 | 57 | 19 | 111 | 1 | 11.85 | 5 | 5228.78 | 898 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 385 | 0 | 0 | 0 | 423.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.82 | 40 | 0 | 0 | 24.28 | 181 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.32 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 2.5 | 72 | 0.25 | 0 | 203 | 130 | 220 | 0 | 0 | 515 | 0 | 3823.21 | 9051.99 | 94.78
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 13 | 52 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.85 | 40 | 0 | 33 | 670 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 950 | 16 | 0 | 8 | 325 | 315 | 0 | 51 | 5 | 198 | 37 | 0 | 105 | 0 | 0 | 7 | 0 | 90 | 0 | 29 | 0 | 315 | 0 | 0 | 42 | 53 | 154 | 7 | 17 | 0 | 83 | 30 | 0 | 15 | 77 | 0 | 58 | 19 | 111 | 2 | 32.01 | 6 | 5300.86 | 898 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 375 | 0 | 0 | 0 | 423.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.25 | 44 | 0 | 0 | 34.94 | 173 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 3.03 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 4 | 112 | 0.43 | 0 | 180 | 130 | 220 | 0 | 0 | 560 | 0 | 3862.97 | 9163.83 | 94.78
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 15 | 52 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.91 | 40 | 0 | 32 | 670 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 960 | 20 | 0 | 8 | 315 | 320 | 0 | 51 | 5 | 201 | 40 | 0 | 103 | 0 | 0 | 13 | 0 | 92 | 0 | 44 | 0 | 305 | 0 | 0 | 42 | 53 | 155 | 7 | 17 | 0 | 83 | 30 | 0 | 15 | 77 | 0 | 58 | 19 | 108 | 2 | 41.04 | 6 | 5343.95 | 898 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 375 | 0 | 0 | 0 | 423.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.86 | 88 | 0 | 0 | 47.24 | 166 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 4.03 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 5 | 138 | 0.33 | 0 | 181 | 130 | 220 | 0 | 0 | 560 | 0 | 3966.3 | 9310.25 | 94.77
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 52 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 40 | 0 | 34 | 670 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 1148 | 15 | 0 | 8 | 380 | 355 | 0 | 51 | 5 | 200 | 40 | 0 | 102 | 0 | 0 | 13 | 0 | 100 | 0 | 32 | 0 | 320 | 0 | 0 | 42 | 53 | 160 | 7 | 17 | 0 | 83 | 30 | 0 | 15 | 77 | 0 | 59 | 19 | 106 | 2 | 35.71 | 0 | 5642.01 | 898 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.16 | 386 | 0 | 0 | 0 | 423.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.1 | 96 | 0 | 0 | 50.64 | 176 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.2 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 5.5 | 152 | 0.21 | 0 | 209 | 130 | 220 | 0 | 0 | 564 | 0 | 4117.46 | 9759.47 | 94.76
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 22 | 52 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.99 | 40 | 0 | 33 | 670 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 1224 | 8 | 0 | 0 | 340 | 350 | 0 | 51 | 0 | 214 | 0 | 0 | 100 | 0 | 0 | 13 | 0 | 114 | 0 | 66 | 0 | 320 | 0 | 0 | 42 | 53 | 159 | 9 | 17 | 0 | 83 | 30 | 0 | 15 | 77 | 0 | 59 | 19 | 106 | 2 | 40.86 | 0 | 5847.85 | 898 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.16 | 538 | 0 | 0 | 0 | 545.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.6 | 98 | 0 | 0 | 49.3 | 191 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.12 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 5.4 | 145 | 0.36 | 0 | 307 | 130 | 220 | 0 | 0 | 668 | 0 | 4588.06 | 10435.91 | 94.76
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 510 | 6 | 5 | 2 | 0 | 0 | 0 | 4 | 31 | 0 | 0 | 0 | 0 | 0 | 10 | 335 | 0 | 0 | 24 | 52 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.09 | 40 | 3 | 25 | 670 | 0 | 0 | 1 | 0 | 6 | 174 | 0 | 0 | 0 | 1191 | 8 | 2 | 0 | 355 | 305 | 0 | 51 | 0 | 220 | 0 | 0 | 102 | 8 | 0 | 7 | 0 | 110 | 0 | 23 | 0 | 315 | 0 | 0 | 42 | 53 | 155 | 4 | 17 | 0 | 83 | 30 | 0 | 15 | 77 | 0 | 58 | 19 | 106 | 2 | 37.07 | 0 | 5667.16 | 898 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.68 | 611 | 0 | 0 | 0 | 615.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.61 | 86 | 0 | 0 | 43.48 | 183 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 1.46 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 4.4 | 128 | 0.32 | 0 | 262 | 128 | 180 | 0 | 0 | 766 | 0 | 4633.2 | 10300.36 | 94.76
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 459 | 0 | 17 | 17 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 17 | 52 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1.6 | 40 | 0 | 29 | 670 | 0 | 0 | 18 | 0 | 0 | 174 | 0 | 0 | 0 | 922 | 8 | 20 | 0 | 393 | 300 | 0 | 51 | 0 | 184 | 0 | 21 | 100 | 0 | 0 | 13 | 0 | 108 | 0 | 25 | 0 | 300 | 0 | 0 | 42 | 53 | 131 | 7 | 17 | 0 | 83 | 0 | 0 | 15 | 75 | 0 | 58 | 19 | 106 | 1 | 23.83 | 0 | 5257.43 | 898 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 520 | 0 | 0 | 0 | 617.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.73 | 69 | 0 | 0 | 32.93 | 157 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 2.77 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 3.6 | 94 | 0.34 | 0 | 196 | 128 | 180 | 0 | 0 | 690 | 0 | 4253.86 | 9511.29 | 94.75
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 503 | 0 | 17 | 17 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 10 | 52 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 40 | 0 | 30 | 670 | 0 | 0 | 18 | 0 | 0 | 174 | 0 | 0 | 0 | 917 | 4 | 20 | 0 | 380 | 335 | 0 | 51 | 0 | 200 | 0 | 0 | 100 | 0 | 0 | 11 | 0 | 96 | 0 | 16 | 0 | 310 | 0 | 0 | 42 | 53 | 137 | 4 | 17 | 0 | 31 | 0 | 0 | 15 | 75 | 0 | 45 | 19 | 106 | 1 | 11.39 | 0 | 5218.14 | 898 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.86 | 411 | 0 | 0 | 0 | 528.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.86 | 40 | 0 | 0 | 19.13 | 167 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 1.71 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 2 | 48 | 0.11 | 0 | 169 | 100 | 180 | 0 | 0 | 650 | 0 | 3886.08 | 9104.22 | 94.75
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 540 | 0 | 17 | 17 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 3 | 52 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 40 | 0 | 39 | 670 | 0 | 0 | 18 | 0 | 0 | 174 | 0 | 0 | 0 | 1030 | 1 | 20 | 0 | 355 | 360 | 0 | 51 | 0 | 209 | 0 | 0 | 102 | 0 | 0 | 11 | 0 | 96 | 0 | 4 | 0 | 320 | 0 | 0 | 42 | 53 | 146 | 1 | 17 | 0 | 31 | 0 | 0 | 15 | 75 | 0 | 49 | 19 | 136 | 0 | 3.1 | 0 | 5428.44 | 897 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 421 | 0 | 0 | 0 | 621.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.76 | 10 | 0 | 0 | 4.65 | 176 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0.37 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 8 | 0.6 | 13 | 0.06 | 0 | 220 | 100 | 180 | 0 | 0 | 722 | 0 | 4038.7 | 9467.14 | 94.75
18:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 486 | 17 | 17 | 48 | 15 | 15 | 15 | 17 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 90 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 7 | 39 | 670 | 0 | 0 | 19 | 0 | 20 | 173 | 0 | 0 | 0 | 1150 | 0 | 20 | 0 | 350 | 320 | 0 | 51 | 0 | 192 | 0 | 14 | 103 | 13 | 0 | 13 | 0 | 108 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 53 | 142 | 0 | 17 | 0 | 83 | 0 | 0 | 15 | 75 | 0 | 58 | 19 | 136 | 0 | 0 | 2 | 5749 | 897 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 506 | 0 | 0 | 0 | 770.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 35 | 0 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 276 | 100 | 180 | 0 | 0 | 860 | 0 | 4430.72 | 10179.72 | 94.74
19:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 475 | 15.9 | 0 | 70 | 15 | 15 | 0 | 17 | 49 | 0 | 0 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 70 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 34 | 42 | 670 | 0 | 0 | 0 | 0 | 34 | 173 | 0 | 0 | 0 | 1149 | 0 | 0 | 0 | 380 | 310 | 0 | 51 | 0 | 189 | 0 | 32 | 104 | 45 | 0 | 13 | 0 | 102 | 0 | 0 | 0 | 310 | 0 | 0 | 42 | 53 | 152 | 0 | 17 | 0 | 83 | 0 | 0 | 15 | 75 | 0 | 59 | 19 | 143 | 0 | 0 | 6 | 5781.9 | 898 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608 | 0 | 0 | 0 | 758.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 130 | 220 | 0 | 0 | 990 | 0 | 4762.11 | 10544.01 | 94.74
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 500 | 15.9 | 0 | 34 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 52 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 17 | 42 | 670 | 0 | 0 | 0 | 0 | 17 | 173 | 0 | 0 | 0 | 1164 | 0 | 0 | 0 | 390 | 325 | 0 | 51 | 0 | 195 | 0 | 32 | 104 | 33 | 0 | 13 | 0 | 102 | 0 | 0 | 0 | 310 | 0 | 0 | 42 | 53 | 154 | 0 | 17 | 0 | 83 | 0 | 0 | 15 | 75 | 0 | 45 | 19 | 147 | 0 | 0 | 0 | 5660.9 | 898 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 609 | 0 | 0 | 0 | 760.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 130 | 220 | 0 | 0 | 1015 | 0 | 4807.77 | 10468.67 | 94.74
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 502 | 15.6 | 0 | 46 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 35 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 17 | 42 | 670 | 0 | 0 | 0 | 0 | 17 | 173 | 0 | 0 | 0 | 1163 | 0 | 0 | 0 | 393 | 330 | 0 | 51 | 0 | 196 | 0 | 32 | 104 | 17 | 0 | 13 | 0 | 104 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 53 | 154 | 0 | 17 | 0 | 83 | 0 | 0 | 15 | 75 | 0 | 45 | 19 | 147 | 0 | 0 | 0 | 5653.6 | 898 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 0 | 0 | 0 | 761.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 130 | 220 | 0 | 0 | 1016 | 0 | 4772.18 | 10425.78 | 94.74
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 524 | 17 | 0 | 34 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 35 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 15 | 39 | 670 | 0 | 0 | 0 | 0 | 16 | 173 | 0 | 0 | 0 | 1178 | 0 | 0 | 0 | 355 | 350 | 0 | 51 | 0 | 205 | 0 | 33 | 104 | 17 | 0 | 13 | 0 | 108 | 0 | 0 | 0 | 320 | 0 | 0 | 42 | 53 | 161 | 0 | 17 | 0 | 83 | 0 | 0 | 15 | 72 | 0 | 45 | 19 | 147 | 0 | 0 | 0 | 5697 | 898 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 614 | 0 | 0 | 0 | 759.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 130 | 220 | 0 | 0 | 1020 | 0 | 4794.42 | 10491.42 | 94.73
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 670 | 0 | 0 | 0 | 0 | 16 | 173 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 345 | 325 | 0 | 51 | 0 | 193 | 0 | 32 | 105 | 16 | 0 | 13 | 0 | 106 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 53 | 158 | 0 | 17 | 0 | 83 | 0 | 0 | 15 | 72 | 0 | 45 | 19 | 149 | 0 | 0 | 0 | 5477 | 898 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 0 | 0 | 0 | 765.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 130 | 220 | 0 | 0 | 1022 | 0 | 4759.56 | 10236.56 | 94.73
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 31 | 670 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1108 | 0 | 0 | 0 | 355 | 315 | 0 | 51 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 100 | 0 | 0 | 0 | 305 | 0 | 0 | 41 | 53 | 151 | 0 | 17 | 0 | 83 | 0 | 0 | 15 | 72 | 0 | 32 | 0 | 144 | 0 | 0 | 0 | 5124 | 898 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 592 | 0 | 0 | 0 | 761.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 130 | 220 | 0 | 0 | 1015 | 0 | 4687.83 | 9811.83 | 94.73
Total KWH | 0 | 48960 | 0 | 0 | 0 | 0 | 0 | 0 | 7826400 | 0 | 11939950 | 80640 | 83880 | 287856 | 17280 | 25593 | 65294 | 105948 | 162720 | 0 | 0 | 0 | 0 | 0 | 84930 | 7421267 | 0 | 0 | 124808 | 736800 | 292200 | 448200 | 0 | 0 | 0 | 0 | 0 | 0 | 13920 | 0 | 0 | 0 | 0 | 0 | 17398 | 936000 | 121272 | 709440 | 15643636.36 | 0 | 0 | 83040 | 0 | 154727 | 4050268 | 0 | 0 | 0 | 23743634 | 93960 | 117091 | 16727 | 7589500 | 8153800 | 0 | 977488 | 18720 | 4887000 | 111672 | 186240 | 2007756 | 158400 | 0 | 349380 | 0 | 2242560 | 0 | 302136 | 0 | 7542000 | 0 | 0 | 970000 | 1322640 | 3573572.73 | 51248 | 308880 | 0 | 1305600 | 352032 | 0 | 322000 | 1823530 | 0 | 1034400 | 283200 | 2520000 | 11700 | 256910 | 30240 | 124146444.09 | 21709091 | 5802624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 427680 | 11018160 | 0 | 0 | 0 | 13665629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250128 | 598250 | 0 | 0 | 307504 | 3976909 | 0 | 0 | 0 | 0 | 0 | 9223418 | 0 | 23760 | 0 | 0 | 78837 | 174100 | 164198 | 0 | 0 | 11000 | 34050.48 | 931680 | 2616 | 0 | 5062000 | 2851000 | 5268060 | 0 | 0 | 17429818.18 | 0 | 99010512.66 | 223156956.75

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 04-02-2026
Power Supply Scenario
| Day Peak Generation |  |  | 9759.47 | MW | 12:00 Hr. | Energy Generated |  |  | 223.157 |  | MKWHr.
| Day Peak Demand |  |  | 9759.47 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 10544.01 | MW | 19:00 Hr. | Energy Demand |  |  | 223.157 |  | MKWHr.
| Evening Peak Demand |  |  | 10544.01 | MW | 19:00 Hr. | Maximum Temperature |  |  | 27.9 |  | °C
| Minimum Generation of the Day |  |  | 7380.6 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 787.61 |  | MMCFD
| Maximum Generation of the Day |  |  | 10544.01 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.1953 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 27.928 | 0 | 1.6999 | 0 | 0 | 0.12481 | 0 | 0 | 29.7527 | Gas | 103.962 | Gas | 369362054.6916
| Chattogram Zone |  |  | 4.7597 | 39.3873 | 0.35904 | 0 | 0.936 | 0.11136 | 0 | 0.01392 | 45.5673 | Coal | 72.8972 | Coal | 465877902.3952
| Cumilla Zone |  |  | 24.112 | 0 | 0.46173 | 0 | 0 | 0.30214 | 2.2426 | 0 | 27.1185 | HFO | 4.1115 | HFO | 69631078.78
| Mymensingh Zone |  |  | 2.52 | 0 | 1.3478 | 0 | 0 | 0.26861 | 0 | 0 | 4.1364 | HSD | 0.011 | HSD | 488730
| Sylhet Zone |  |  | 17.5203 | 0 | 0 | 0 | 0 | 0.051248 | 0 | 0 | 17.5715 | Hydro | 0.936 | Hydro | 93600
| Khulna Zone |  |  | 5.8026 | 11.0182 | 0 | 0 | 0 | 0.42768 | 21.7091 | 0 | 38.9576 | Solar | 3.6079 | Solar | 58188292.416
| Barishal Zone |  |  | 8.1191 | 22.4918 | 0 | 0 | 0 | 0.002616 | 0 | 0 | 30.6135 | Import | 37.6173 | Import | 195523639.03
| Rajshahi Zone |  |  | 13.2003 | 0 | 0 | 0 | 0 | 1.1796 | 13.6656 | 0 | 28.0456 | Wind | 0.01392 | Wind | 204763.2
| Rangpur Zone |  |  | 0 | 0 | 0.24304 | 0.011 | 0 | 1.1398 | 0 | 0 | 1.3939
| Total |  |  | 103.962 | 72.8972 | 4.1115 | 0.011 | 0.936 | 3.6079 | 37.6173 | 0.01392 | 223.157
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 369362054.6916 |  | Hydro | 93600
|  |  |  | Coal | 465877902.3952 |  | Solar | 58188292.416
|  |  |  | HFO | 69631078.78 |  | Import | 195523639.03
|  |  |  | HSD | 488730 |  | Wind | 204763.2
[5 empty] | Total: | 115,93,70,060 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7091 | Peak Hr Flow | 898.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 21993637.22 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 13.6656 | Peak Hr Flow | 758.11 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1307 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.2426 | Peak Hr Flow | 102.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1622 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 37.6173 | Peak Hr Flow | 1758.11 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3524
|  |  |  | Chattogram |  | 0 |  | 1108
|  |  |  | Cumilla |  | 0 |  | 943
|  |  |  | Mymensingh |  | 0 |  | 971
|  |  |  | Sylhet |  | 0 |  | 392
|  |  |  | Khulna |  | 0 |  | 1202
|  |  |  | Barishal |  | 0 |  | 304
|  |  |  | Rajshahi |  | 0 |  | 1068
|  |  |  | Rangpur |  | 0 |  | 754
|  |  |  | Total |  | 0 |  | 10266
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:20 | 08:45 | Gopalganj 400/132kV S/S 400kV Rooppur Scheduled S/D
| 08:21 |  | Aminbazar 400/230/132kV S/S Gopalganj-2 Scheduled S/D Due to Deadline Checking & Disc
Cleaning
| 08:22 | 17:24 | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-2 Scheduled S/D
| 08:42 |  | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) Forced S/D Due to Instructions by ALDC
Bogura. Due to low voltage.
| 09:13 | 18:13 | Lalmonirhat-Rangpur 132 kV Ckt-2 Scheduled S/D from Kurigram 132/33kV end Due to Annual
Maintenance of 132kv Line
| 09:20 | 18:12 | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat Scheduled S/D Due to Anual Maintanance
| 12:00 |  | Day Peak Generation: 9756 MW.
| 13:55 | 15:18 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Scheduled S/D Due to Keranihut 33KV | [7 empty] | 39.0MW load
|  |  | feeder redhot maintenance | [7 empty] | interrup.
| 13:55 | 15:18 | Dohazari 132/33kV S/S Power Transformer -T-2 HT Scheduled S/D Due to Keranihut 33KV | [7 empty] | 39.0MW load
|  |  | feeder redhot maintenance | [7 empty] | interrup.
|  | 17:41 | Aminbazar-Airport(Old) 230kV Ckt-2 is restored.
| 19:00 |  | Evening Peak Generation: 10543 MW.
| 05:00 |  | Minimum Generation: 7796 MW.
| 07:10 |  | Noapara 132/33kV S/S T-1 LT Scheduled S/D
| 07:12 |  | Noapara 132/33kV S/S T-1 HT Scheduled S/D
| 07:30 |  | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Scheduled S/D from Fenchuganj
230/132/33kV end Due to For Sylhet-South substation end maintenance work.
| 07:31 |  | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-2 Scheduled S/D Due to Re-conducting
work
| 07:31 |  | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-1 Scheduled S/D Due to Re-conducting
work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 04-02-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 291 | 7826400 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 65294 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7421267 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 15.9 | 80640 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 15 | 17280 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 105948 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 84930 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 12 | 292200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 448200 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 15 | 25593 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 70 | 287856 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 48960 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 49 | 162720 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 124808 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 83880 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 475 | 11939950 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 70 | 736800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6667.111 | 1437.9 | 29752726
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 93960 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 83040 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 936000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 173 | 4050268 | Plant availability less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 154727 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 42 | 709440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 17398 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 34 | 121272 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1149 | 23743634 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 2 | 13920 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 670 | 15643636.36 | ps availability is less
Chattogram Area Total |  |  |  |  | 4898.863 | 2144 | 45567295.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 189 | 4887000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 310 | 8153800 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 380 | 7589500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 111672 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 18720 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 16727 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 977488 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 117091 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 104 | 2007756 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 45 | 158400 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 102 | 2242560 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 349380 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 32 | 186240 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 302136 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1226 | 27118470
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 143 | 2520000 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11700 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 283200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 1034400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 256910 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 30240 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 227 | 4136450
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 51248 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 970000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 53 | 1322640 | GT3,4 are not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3573572.73 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 352032 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1305600 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 75 | 1823530 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 322000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 308880 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7542000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | -
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 747 | 17571502.73
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 898 | 21709091 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 250 | 5802624 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 427680 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 608 | 11018160 | U#1 Under Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1756 | 38957555
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 2851000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 990 | 17429818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5268060 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 274 | 5062000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2616 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1614 | 30613494.18
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 250128 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Machine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 166 | 3976909 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 399 | 9223418 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 23760 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 758.11 | 13665629 | U#1 Under AOH
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 307504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 598250 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1323.11 | 28045598
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 11000 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 164198 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 34050.48 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 78837 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 174100 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 931680 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 69 | 1393865.48
Eastern Grid Total |  |  |  |  | 17398.245 | 5781.9 | 124146444.09
Western Grid Total |  |  |  |  | 10984.555 | 4762.11 | 99010512.66
National Grid Total |  |  |  |  | 28382.8 | 10544.01 | 223156956.75
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 04-02-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6938.13 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3327.4 | MW
i) Dhaka area |  |  | 3524.13 |  | MW | i) Khulna area |  |  |  | 1201.6 | MW
ii) Chattogram area |  |  | 1108 |  | MW | ii) Barishal area |  |  |  | 303.5 | MW
iii) Cumilla area |  |  | 943 |  | MW | iii) Rajshahi area |  |  |  | 1067.8 | MW
iv) Mymensingh area |  |  | 971 |  | MW | iv) Rangpur area |  |  |  | 754.5 | MW
v) Sylhet area |  |  | 392 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10265.53 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 4 | 00:00 | 67 | Hasnabad | 71 | 14:00 | 133 | Netrakona | 150 | 08:00
2 | AKSML | 21.4 | 06:00 | 68 | Hathazari | 65 | 13:00 | 134 | New | 43.2 | 21:00
3 | Aftabnagar | 26 | 13:00 | 69 | Hatirjheel | 25 | 18:00 | 135 | Niamatpur | 98 | 12:00
4 | Agargaon | 68 | 14:00 | 70 | Ishurdi | 48 | 20:00 | 136 | Noapara | 30 | 18:30
5 | Agrabad | 40 | 18:00 | 71 | Jaldhaka | 58 | 18:30 | 137 | PHP | 8 | 03:00
6 | Amnura | 34 | 10:00 | 72 | Jamalpur | 114 | 08:00 | 138 | Pabna | 66 | 18:30
7 | Ashuganj | 62 | 14:00 | 73 | Jashore | 112 | 13:00 | 139 | Palashbari | 100 | 18:00
8 | BSRM | 204 | 18:00 | 74 | Jhenaidah | 80 | 08:00 | 140 | Panchagarh | 42 | 18:30
9 | Bagerhat | 60 | 18:30 | 75 | Joydebpur | 85 | 21:00 | 141 | Patiya | 6 | 18:00
10 | Bajitpur | 57 | 18:00 | 76 | Joypurhat | 50 | 10:00 | 142 | Patuakhali | 36.5 | 14:00
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 10 | 00:00 | 143 | Payra | 26 | 19:00
12 | Bakulia | 57 | 18:30 | 78 | KSRM | 16 | 21:00 | 144 | Postogola | 35 | 23:00
13 | Banani | 31.6 | 18:00 | 79 | Kabirpur | 130 | 00:00 | 145 | Purbachal | 20 | 12:00
14 | Bangabhaban | 3 | 00:00 | 80 | Kachua | 61 | 18:00 | 146 | Purbasadipur | 122 | 13:00
15 | Barapukuria | 60 | 09:00 | 81 | Kallyanpur | 78 | 14:00 | 147 | Rahanpur | 27 | 12:00
16 | Barguna | 14 | 19:00 | 82 | Kalurghat | 24 | 12:00 | 148 | Rahim | 19 | 23:00
17 | Barishal | 77 | 13:00 | 83 | Kamrangirchar | 46 | 21:00 | 149 | Rajbari | 54 | 18:30
18 | Barishal-230 | 64 | 18:30 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 100 | 13:00
19 | Baroaulia | 44 | 18:30 | 85 | Kasba | 26 | 13:00 | 151 | Rajshahi | 89 | 13:00
20 | Baroirhat | 40 | 13:00 | 86 | Kazla | 79 | 14:00 | 152 | Rajshahi-230 | 60 | 13:00
21 | Bashundhara | 147 | 13:00 | 87 | Keranigonj | 54 | 13:00 | 153 | Ramganj | 74 | 13:00
22 | BashundharaCement | 8 | 00:00 | 88 | Khagrachori | 26 | 18:30 | 154 | Rampur | 26 | 12:00
23 | Beanibazar | 46 | 18:30 | 89 | Khulna | 49 | 13:00 | 155 | Rangamati | 12 | 18:00
24 | Benapole | 52 | 08:00 | 90 | Khulshi | 138 | 12:00 | 156 | Rangpur | 108 | 18:00
25 | Bhaluka | 112 | 13:00 | 91 | Kishoreganj | 98 | 19:30 | 157 | Ruppur | 2.8 | 15:00
26 | Bhandaria | 36 | 21:00 | 92 | Kodda | 196 | 21:00 | 158 | SSM | 1 | 23:00
27 | Bhangura | 24 | 13:00 | 93 | Kulaura | 28 | 18:00 | 159 | Saidpur | 90 | 12:00
28 | Bheramara(GK) | 40 | 13:00 | 94 | Kurigram | 60 | 12:00 | 160 | Satkhira | 91 | 08:00
29 | Bhulta | 188 | 23:00 | 95 | Kushtia | 98 | 18:00 | 161 | Satmasjid | 69 | 14:00
30 | Bog-Sherpur | 52 | 18:30 | 96 | Laksam | 13 | 04:00 | 162 | Savar | 124 | 21:00
31 | Bogura | 120 | 21:00 | 97 | Lakshmipur | 24 | 18:30 | 163 | SevenRings | 19.62 | 12:00
32 | Borhanuddin | 64 | 20:00 | 98 | Lalbag | 49 | 23:00 | 164 | ShahCement | 15 | 23:00
33 | Brahmanbaria | 94 | 14:00 | 99 | Lalmonirhat | 45 | 18:00 | 165 | Shahjadpur | 57 | 12:00
34 | Cantonment | 64 | 13:00 | 100 | MI_Cement | 16.2 | 00:00 | 166 | Shahjibazar | 93 | 18:00
35 | Chandina | 17 | 14:00 | 101 | Madanganj | 31 | 22:00 | 167 | Shahmirpur | 31 | 19:00
36 | Chandpur | 52 | 18:00 | 102 | Madaripur | 71 | 14:00 | 168 | Shariatpur | 57 | 14:00
37 | Chandraghona | 27 | 18:00 | 103 | Madartek | 58 | 13:00 | 169 | Sherpur | 140 | 18:00
38 | Chapai | 57 | 13:00 | 104 | Madunaghat | 27 | 18:00 | 170 | Shikalbaha | 20.5 | 01:00
39 | Charsaidpur | 43 | 01:00 | 105 | Magura | 44 | 18:30 | 171 | Shitalakhya | 43.9 | 14:00
40 | Chauddagram | 52 | 14:00 | 106 | Mahasthangarh | 50 | 08:00 | 172 | Sholosohor | 30 | 21:00
41 | Chhatak | 25 | 19:30 | 107 | Maijdee | 32 | 18:30 | 173 | Shyampur | 128 | 13:00
42 | Chowmuhani | 99 | 14:00 | 108 | Manikganj | 82 | 22:00 | 174 | Siddhirganj | 87 | 13:00
43 | Chuadanga | 75 | 13:00 | 109 | Maniknagar | 41 | 13:00 | 175 | Sirajganj | 84 | 19:00
44 | Coxsbazar | 102 | 12:00 | 110 | Matarbari | 37 | 18:00 | 176 | Sonargaon | 122 | 22:00
45 | Cumilla(N) | 96 | 18:00 | 111 | Matuail | 38 | 13:00 | 177 | Sreemongol | 54 | 18:30
46 | Cumilla(S) | 114 | 13:00 | 112 | Metrorail_Motijheel | 18 | 15:00 | 178 | Sreepur | 77 | 21:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 0 | 00:00 | 179 | Srinagar | 31.2 | 14:00
48 | Daudkandi | 88 | 01:00 | 114 | Millgate | 52 | 15:00 | 180 | Sunamganj | 41 | 18:30
49 | DhakaUniversity | 34 | 13:00 | 115 | Mirpur | 105.5 | 20:00 | 181 | Sylhet | 36 | 18:00
50 | Dhamrai | 80 | 00:00 | 116 | Mirsorai | 30 | 11:00 | 182 | Sylhet-132 | 71 | 13:00
51 | Dhanmondi | 61 | 13:00 | 117 | Mirzapur | 36 | 08:00 | 183 | TK | 14 | 18:30
52 | Dohazari | 75 | 18:00 | 118 | Mithapukur | 50 | 08:00 | 184 | Tangail | 139 | 08:00
53 | Faridpur | 109 | 19:00 | 119 | Modern | N/A | N/A | 185 | Taraganj | 17 | 09:00
54 | Fatullah | 67 | 23:00 | 120 | Mogbazar | 53.8 | 14:00 | 186 | Tasnim | 20 | 11:00
55 | Fenchuganj | 23 | 18:00 | 121 | Mongla | 28 | 19:30 | 187 | Thakurgaon | 73 | 10:00
56 | Feni | 84 | 13:00 | 122 | Motijheel | 30 | 13:00 | 188 | Tongi | 85 | 13:00
57 | GPH | 27 | 18:00 | 123 | Muktagacha | 33 | 13:00 | 189 | Ullahpara | 26 | 13:00
58 | Ghatail | 68 | 08:00 | 124 | Munshiganj | 65 | 21:00 | 190 | Ullon | 48 | 14:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 25 | 13:00 | 191 | Uttara | 54 | 13:00
60 | Ghorashal-230 | 84 | 17:00 | 126 | Mymensingh | 164 | 18:00 | 192 | UttaraNew | 24 | 13:00
61 | Goalpara | 30 | 13:00 | 127 | Naogaon | 120 | 13:00 | 193 | Zigatola | 54 | 13:00
62 | Gollamari | 74 | 13:00 | 128 | Narail | 40 | 18:30
63 | Gopalganj | 76 | 18:30 | 129 | Narinda | 32 | 13:00
64 | Gulshan | 58 | 14:00 | 130 | Narshingdi | 142 | 19:00
65 | Halishahar | 52 | 18:30 | 131 | Natore | 111 | 13:00
66 | HaripurSBU | 95 | 22:00 | 132 | Nawabganj | 33.8 | 14:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 04-02-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 8878.5 | 0 |  | 8878.5
1:00 | 8231.3 | 0 |  | 8231.3
2:00 | 7845.54 | 0 |  | 7845.54
3:00 | 7543.42 | 0 |  | 7543.42
4:00 | 7547.66 | 0 |  | 7547.66
5:00 | 7494.44 | 0 |  | 7494.44
6:00 | 7380.6 | 0 |  | 7380.6
7:00 | 7641.04 | 0 |  | 7641.04
8:00 | 8640.94 | 0 |  | 8640.94
9:00 | 9051.99 | 0 |  | 9051.99
10:00 | 9163.83 | 0 |  | 9163.83
11:00 | 9310.25 | 0 |  | 9310.25
12:00 | 9759.47 | 0 |  | 9759.47
13:00 | 10435.91 | 0 |  | 10435.91
14:00 | 10300.36 | 0 |  | 10300.36
15:00 | 9511.29 | 0 |  | 9511.29
16:00 | 9104.22 | 0 |  | 9104.22
17:00 | 9467.14 | 0 |  | 9467.14
18:00 | 10179.72 | 0 |  | 10179.72
19:00 | 10544.01 | 0 |  | 10544.01
19:30 | 10468.67 | 0 |  | 10468.67
20:00 | 10425.78 | 0 |  | 10425.78
21:00 | 10491.42 | 0 |  | 10491.42
22:00 | 10236.56 | 0 |  | 10236.56
23:00 | 9811.83 | 0 |  | 9811.83
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 04-02-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4916.5 | 3962 | 8878.5 | DAILY GENERATION CURVE
00:30 | 4791.75 | 3763.15 | 8554.9
01:00 | 4667 | 3564.3 | 8231.3 | 04-02-2026
01:30 | 4573 | 3465.42 | 8038.42
02:00 | 4479 | 3366.54 | 7845.54
02:30 | 4354.5 | 3339.98 | 7694.48
03:00 | 4230 | 3313.42 | 7543.42
03:30 | 4250.5 | 3295.04 | 7545.54
04:00 | 4271 | 3276.66 | 7547.66
04:30 | 4250 | 3271.05 | 7521.05
05:00 | 4229 | 3265.44 | 7494.44
05:30 | 4195 | 3242.52 | 7437.52
06:00 | 4161 | 3219.6 | 7380.6
06:30 | 4239.31 | 3271.51 | 7510.82
07:00 | 4317.62 | 3323.42 | 7641.04
07:30 | 4658.82 | 3482.17 | 8140.99
08:00 | 5000.02 | 3640.92 | 8640.94
08:30 | 5114.4 | 3732.065 | 8846.465
09:00 | 5228.78 | 3823.21 | 9051.99
09:30 | 5264.82 | 3843.09 | 9107.91
10:00 | 5300.86 | 3862.97 | 9163.83
10:30 | 5322.405 | 3914.635 | 9237.04
11:00 | 5343.95 | 3966.3 | 9310.25
11:30 | 5492.98 | 4041.88 | 9534.86
12:00 | 5642.01 | 4117.46 | 9759.47
12:30 | 5744.93 | 4352.76 | 10097.69
13:00 | 5847.85 | 4588.06 | 10435.91
13:30 | 5757.505 | 4610.63 | 10368.135
14:00 | 5667.16 | 4633.2 | 10300.36
14:30 | 5462.295 | 4443.53 | 9905.825
15:00 | 5257.43 | 4253.86 | 9511.29
15:30 | 5237.785 | 4069.97 | 9307.755
16:00 | 5218.14 | 3886.08 | 9104.22
16:30 | 5323.29 | 3962.39 | 9285.68
17:00 | 5428.44 | 4038.7 | 9467.14
17:30 | 5588.72 | 4234.71 | 9823.43
18:00 | 5749 | 4430.72 | 10179.72
18:30 | 5765.45 | 4596.415 | 10361.865
19:00 | 5781.9 | 4762.11 | 10544.01
19:30 | 5660.9 | 4807.77 | 10468.67
20:00 | 5653.6 | 4772.18 | 10425.78
20:30 | 5675.3 | 4783.3 | 10458.6 |  | Executive Engineer
21:00 | 5697 | 4794.42 | 10491.42 |  | Network Operation Division
21:30 | 5587 | 4776.99 | 10363.99
22:00 | 5477 | 4759.56 | 10236.56
22:30 | 5300.5 | 4723.695 | 10024.195
23:00 | 5124 | 4687.83 | 9811.83

## En-Curve
QF-LDC-12
Date | 04-02-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2691 | 1425.5 | 898 | 0 | 88 | 755 | 40 | 2917 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2676 | 1416.25 | 898 | 0 | 86 | 680.15 | 40 | 2704 | 0 | 0 | 54.5 | 0 | 0 | 0 | 0 | 04-02-2026
01:00 | 2661 | 1407 | 898 | 0 | 84 | 605.3 | 40 | 2491 | 0 | 0 | 45 | 0 | 0 | 0 | 0
01:30 | 2621 | 1344.5 | 898 | 0 | 85 | 513.42 | 40 | 2496.5 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | Energy Generated | 223.157 |  | MKWHr
02:00 | 2581 | 1282 | 898 | 0 | 86 | 421.54 | 40 | 2502 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2541.5 | 1199.5 | 898 | 0 | 84 | 420.98 | 40 | 2481 | 0 | 0 | 29.5 | 0 | 0 | 0 | 0 | Total Energy Requirement | 223.157 |  | MKWHr
03:00 | 2502 | 1117 | 898 | 0 | 82 | 420.42 | 40 | 2460 | 0 | 0 | 24 | 0 | 0 | 0 | 0
03:30 | 2515.5 | 1127 | 898 | 0 | 79 | 421.54 | 40 | 2452.5 | 0 | 0 | 12 | 0 | 0 | 0 | 0
04:00 | 2529 | 1137 | 898 | 0 | 76 | 422.66 | 40 | 2445 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2520 | 1120.5 | 898 | 0 | 77 | 422.55 | 40 | 2443 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:00 | 2511 | 1104 | 898 | 0 | 78 | 422.44 | 40 | 2441 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 2496 | 1097 | 898 | 0 | 80 | 422.02 | 32.5 | 2408 | 0 | 0 | 4 | 0 | 0 | 0 | 0
06:00 | 2481 | 1090 | 898 | 0 | 82 | 421.6 | 25 | 2375 | 0 | 0 | 8 | 0 | 0 | 0 | 0
06:30 | 2565.5 | 1110 | 898 | 0 | 78 | 422.07 | 32.5 | 2390.5 | 4.75 | 0 | 9.5 | 0 | 0 | 0 | 0
07:00 | 2650 | 1130 | 898 | 0 | 74 | 422.54 | 40 | 2406 | 9.5 | 0 | 11 | 0 | 0 | 0 | 0
07:30 | 2885 | 1227 | 898 | 0 | 76 | 422.825 | 40 | 2476.5 | 63.665 | 8.5 | 43.5 | 0 | 0 | 0 | 0
08:00 | 3120 | 1324 | 898 | 0 | 78 | 423.11 | 40 | 2547 | 117.83 | 17 | 76 | 0 | 0 | 0 | 0
08:30 | 3129.5 | 1380 | 898 | 0 | 80 | 423.075 | 40 | 2594.5 | 197.39 | 25.5 | 78.5 | 0 | 0 | 0 | 0
09:00 | 3139 | 1436 | 898 | 0 | 82 | 423.04 | 40 | 2642 | 276.95 | 34 | 81 | 0 | 0 | 0 | 0
09:30 | 3078 | 1431.5 | 898 | 0 | 86 | 423.18 | 40 | 2688.5 | 337.73 | 43 | 82 | 0 | 0 | 0 | 0
10:00 | 3017 | 1427 | 898 | 0 | 90 | 423.32 | 40 | 2735 | 398.51 | 52 | 83 | 0 | 0 | 0 | 0
10:30 | 3020.5 | 1426 | 898 | 0 | 91 | 423.58 | 40 | 2740.5 | 462.46 | 52 | 83 | 0 | 0 | 0 | 0
11:00 | 3024 | 1425 | 898 | 0 | 92 | 423.84 | 40 | 2746 | 526.41 | 52 | 83 | 0 | 0 | 0 | 0
11:30 | 3105.5 | 1443 | 898 | 0 | 96 | 423.745 | 40 | 2861.5 | 534.615 | 52 | 80.5 | 0 | 0 | 0 | 0
12:00 | 3187 | 1461 | 898 | 0 | 100 | 423.65 | 40 | 2977 | 542.82 | 52 | 78 | 0 | 0 | 0 | 0
12:30 | 3180.5 | 1505.5 | 898 | 0 | 107 | 484.385 | 40 | 3192 | 560.305 | 52 | 78 | 0 | 0 | 0 | 0
13:00 | 3174 | 1550 | 898 | 0 | 114 | 545.12 | 40 | 3407 | 577.79 | 52 | 78 | 0 | 0 | 0 | 0
13:30 | 3111.5 | 1463.5 | 898 | 0 | 112 | 580.185 | 40 | 3453.5 | 540.95 | 52 | 116.5 | 0 | 0 | 0 | 0
14:00 | 3049 | 1377 | 898 | 0 | 110 | 615.25 | 40 | 3500 | 504.11 | 52 | 155 | 0 | 0 | 0 | 0
14:30 | 2997.5 | 1337 | 898 | 0 | 109 | 616.37 | 40 | 3249 | 437.955 | 52 | 168.5 | 0 | 0 | 0.5 | 0
15:00 | 2946 | 1297 | 898 | 0 | 108 | 617.49 | 40 | 2998 | 371.8 | 52 | 182 | 0 | 0 | 1 | 0
15:30 | 2974 | 1300.5 | 898 | 0 | 102 | 572.95 | 40 | 2907.5 | 293.805 | 52 | 166.5 | 0 | 0 | 0.5 | 0
16:00 | 3002 | 1304 | 898 | 0 | 96 | 528.41 | 40 | 2817 | 215.81 | 52 | 151 | 0 | 0 | 0 | 0
16:30 | 3054.5 | 1336.5 | 897.5 | 0 | 96 | 574.835 | 40 | 2940 | 137.345 | 52 | 153 | 4 | 0 | 0 | 0
17:00 | 3107 | 1369 | 897 | 0 | 96 | 621.26 | 40 | 3063 | 58.88 | 52 | 155 | 8 | 0 | 0 | 0
17:30 | 3035.5 | 1364.5 | 897 | 0 | 102 | 695.99 | 40 | 3262.5 | 29.44 | 95.5 | 293 | 8 | 0 | 0 | 0
18:00 | 2964 | 1360 | 897 | 0 | 108 | 770.72 | 40 | 3462 | 0 | 139 | 431 | 8 | 0 | 0 | 0
18:30 | 3009.5 | 1378.5 | 897.5 | 0 | 105 | 764.415 | 40 | 3576.5 | 0 | 129 | 456.45 | 4 | 0 | 1 | 0
19:00 | 3055 | 1397 | 898 | 0 | 102 | 758.11 | 40 | 3691 | 0 | 119 | 481.9 | 0 | 0 | 2 | 0
19:30 | 3123 | 1424 | 898 | 0 | 102 | 760.77 | 40 | 3736 | 0 | 52 | 331.9 | 0 | 0 | 1 | 0
20:00 | 3130 | 1431 | 898 | 0 | 104 | 761.18 | 40 | 3731 | 0 | 35 | 294.6 | 0 | 0 | 1 | 0
20:30 | 3138.5 | 1446.5 | 898 | 0 | 106 | 760.3 | 40 | 3747 | 0 | 35 | 286.8 | 0 | 0 | 0.5 | 0
21:00 | 3147 | 1462 | 898 | 0 | 108 | 759.42 | 40 | 3763 | 0 | 35 | 279 | 0 | 0 | 0 | 0
21:30 | 3116 | 1441 | 898 | 0 | 107 | 762.49 | 40 | 3753.5 | 0 | 26 | 220 | 0 | 0 | 0 | 0
22:00 | 3085 | 1420 | 898 | 0 | 106 | 765.56 | 40 | 3744 | 0 | 17 | 161 | 0 | 0 | 0 | 0
22:30 | 3024.5 | 1404.5 | 898 | 0 | 103 | 763.695 | 40 | 3682 | 0 | 8.5 | 96.5 | 0 | 0 | 3.5 | 0
23:00 | 2964 | 1389 | 898 | 0 | 100 | 761.83 | 40 | 3620 | 0 | 0 | 32 | 0 | 0 | 7 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 04-02-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 422 | 03:00 | 403 | 13:00 | Madunaghat | 415 | 07:00 | 404 | 14:00
Amtali | 425 | 03:00 | 416 | 5:00 | Meghnaghat | 426 | 05:00 | 411 | 14:00
Ashuganj | 412 | 5:00 | 394 | 13:00 | Payra | 425 | 01:00 | 418 | 13:00
Bhulta | 405 | 05:00 | 385 | 13:00 | Rahanpur | 420 | 03:00 | 406 | 08:00
Bibiana | 421 | 01:00 | 409 | 13:00 | Rampal | 420 | 05:00 | 402 | 13:00
BIPTC | 407 | 05:00 | 394 | 12:00
Bogura | 418 | 03:00 | 400 | 08:00
Gopalganj | 423 | 03:00 | 407 | 13:00
Kaliakoir | 420 | 05:00 | 408 | 01:00
Korerhat | 424 | 05:00 | 409 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 245 | 03:00 | 231 | 13:00 | Jhenaidah | 243 | 05:00 | 228 | 13:00
AKSML | 241 | 05:00 | 232 | 13:00 | Kachua | 242 | 03:00 | 232 | 13:00
Aminbazar | 245 | 03:00 | 236 | 13:00 | Kaliakoir | 244 | 02:00 | 231 | 13:00
Ashuganj | 238 | 01:00 | 230 | 13:00 | Keranigonj | 243 | 03:00 | 230 | 13:00
Ashuganj-400 | 238 | 5:00 | 228 | 13:00 | Khulna(S) | 246 | 03:00 | 232 | 13:00
Baghabari | 242 | 03:00 | 235 | 12:00 | Korerhat | 242 | 05:00 | 232 | 13:00
Barapukuria | 234 | 04:00 | 215 | 08:00 | Madunaghat | 236 | 08:00 | 230 | 13:00
Barapukuria-230 | 234 | 4:00 | 216 | 13:00 | Madunaghat-400 | 238 | 06:00 | 232 | 13:00
Barishal | 240 | 05:00 | 233 | 13:00 | Maniknagar | 242 | 02:00 | 230 | 13:00
Bheramara | 240 | 04:00 | 227 | 13:00 | Meghnaghat | 247 | 05:00 | 236 | 14:00
Bhulta | 244 | 05:00 | 230 | 13:00 | Meghnaghat-400 | 243 | 05:00 | 231 | 13:00
Bibiana | 242 | 01:00 | 235 | 13:00 | Mirsorai | 240 | 03:00 | 232 | 13:00
BIPTC | 243 | 04:00 | 228 | 13:00 | Rajshahi | 242 | 04:00 | 226 | 13:00
Bogura | 244 | 03:00 | 233 | 08:00 | Rampal | 243 | 03:00 | 229 | 13:00
Bogura-400 | 243 | 03:00 | 232 | 09:00 | Rampur | N/A | N/A | N/A | N/A
Borhanuddin | 241 | 06:00 | 237 | 00:00 | Rampura | 243 | 04:00 | 230 | 13:00
BSRM | 240 | 03:00 | 231 | 13:00 | Shikalbaha | 235 | 01:00 | 228 | 13:00
Chowmuhani | N/A | N/A | N/A | N/A | Shyampur | 242 | 03:00 | 230 | 13:00
Cumilla(N) | 240 | 04:00 | 230 | 13:00 | Siddhirganj | 244 | 05:00 | 231 | 13:00
Faridpur | 240 | 05:00 | 231 | 13:00 | Sirajgonj | 247 | 04:00 | 238 | 13:00
Fenchuganj | 243 | 07:00 | 239 | 13:00 | Sreepur | 236 | 04:00 | 225 | 13:00
Feni | 242 | 03:00 | 232 | 13:00 | Tongi | 239 | 04:00 | 232 | 13:00
Ghorashal | 242 | 04:00 | 230 | 00:00
Ghorashal-230 | 242 | 02:00 | 227 | 13:00
Gopalganj | 238 | 05:00 | 228 | 13:00
GPH | 239 | 02:00 | 231 | 13:00
Haripur | 243 | 04:00 | 231 | 13:00
Hasnabad | 242 | 01:00 | 231 | 13:00
Hathazari | 235 | 07:00 | 229 | 13:00
Ishurdi | 244 | 04:00 | 232 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 01:00 | 126 | 13:00 | Mahasthangarh | 137 | 03:00 | 127 | 13:00
Agargaon | 138 | 02:00 | 131 | 13:00 | Maijdee | 136 | 03:00 | 129 | 13:00
Agrabad | 137 | 01:00 | 132 | 13:00 | Manikganj | 130 | 00:00 | 124 | 13:00
AKS | 136 | 04:00 | 131 | 13:00 | Maniknagar | 141 | 05:00 | 133 | 13:00
Aminbazar | 141 | 03:00 | 135 | 12:00 | Matarbari | 130 | 02:00 | 122 | 18:30
Amnura | 139 | 03:00 | 131 | 13:00 | Matuail | 140 | 06:00 | 133 | 13:00
Ashuganj | 138 | 06:00 | 134 | 08:00 | Metrorail_Motijheel | 141 | 05:00 | 130 | 22:00
Bagerhat | 135 | 04:00 | 126 | 13:00 | Metrorail_Uttara | 135 | 03:00 | 128 | 22:00
Bajitpur | 133 | 02:00 | 125 | 13:00 | Millgate | 135 | 02:00 | 126 | 13:00
Bakerganj | 139 | 01:00 | 136 | 18:30 | Mirpur | 141 | 04:00 | 132 | 13:00
Bakulia | 137 | 06:00 | 133 | 13:00 | Mirzapur | 136 | 03:00 | 128 | 13:00
Banani | 135 | 03:00 | 126 | 13:00 | Mithapukur | 136 | 04:00 | 124 | 09:00
Bangabhaban | 140 | 01:00 | 132 | 13:00 | MI_Cement | 138 | 02:00 | 129 | 13:00
Barapukuria | 136 | 03:00 | 124 | 08:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 140 | 07:00 | 136 | 13:00 | Mogbazar | 135 | 00:00 | 127 | 13:00
Barishal | 140 | 02:00 | 135 | 13:00 | Mongla | 135 | 05:00 | 125 | 13:00
Barishal-230 | 141 | 05:00 | 135 | 13:00 | Motijheel | 140 | 01:00 | 132 | 13:00
Baroaulia | 139 | 09:00 | 134 | 12:00 | Muktagacha | 132 | 18:30 | 123 | 08:00
Baroirhat | 138 | 03:00 | 132 | 13:00 | Munshiganj | 138 | 01:00 | 133 | 12:00
Bashundhara | 135 | 05:00 | 126 | 13:00 | Muradnagar | 139 | 04:00 | 131 | 13:00
BashundharaCement | 136 | 00:00 | 130 | 21:00 | Mymensingh | 132 | 11:00 | 116 | 13:00
Beanibazar | 133 | 01:00 | 129 | 13:00 | Naogaon | 134 | 03:00 | 124 | 13:00
Benapole | 137 | 02:00 | 123 | 13:00 | Narail | 139 | 03:00 | 127 | 13:00
Bhaluka | 131 | 04:00 | 125 | 09:00 | Narinda | 141 | 5:00 | 133 | 13:00
Bhandaria | 139 | 04:00 | 134 | 13:00 | Narshingdi | 139 | 02:00 | 124 | 17:00
Bhangura | 139 | 03:00 | 133 | 13:00 | Natore | 139 | 05:00 | 131 | 13:00
Bheramara | 139 | 02:00 | 134 | 13:00 | Nawabganj | 138 | 03:00 | 129 | 13:00
Bheramara(GK) | 140 | 04:00 | 135 | 13:00 | Netrakona | 124 | 03:00 | 113 | 13:00
Bhulta | 132 | 03:00 | 126 | 13:00 | New | 135 | 02:00 | 127 | 13:00
Bog-Sherpur | 139 | 03:00 | 131 | 08:00 | Niamatpur | 139 | 03:00 | 133 | 07:00
Bogura | 137 | 01:00 | 130 | 08:00 | Noapara | 137 | 00:00 | 126 | 13:00
Bogura-230 | 139 | 04:00 | 131 | 08:00 | Pabna | 138 | 02:00 | 134 | 09:00
Brahmanbaria | 132 | 01:00 | 126 | 13:00 | Palashbari | 134 | 03:00 | 122 | 08:00
Cantonment | 139 | 02:00 | 131 | 13:00 | Panchagarh | 139 | 02:00 | 125 | 08:00
Chandina | 140 | 02:00 | 133 | 13:00 | Patiya | 138 | 05:00 | 132 | 13:00
Chandpur | 138 | 10:00 | 133 | 13:00 | Patuakhali | 139 | 01:00 | 135 | 23:00
Chandraghona | 140 | 06:00 | 135 | 13:00 | Payra | 140 | 03:00 | 130 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 140 | 02:00 | 134 | 08:00 | PHP | 138 | 05:00 | 132 | 13:00
Charsaidpur | 139 | 02:00 | 132 | 13:00 | Postogola | 139 | 03:00 | 131 | 13:00
Chauddagram | 137 | 01:00 | 131 | 13:00 | Purbachal | 135 | 01:00 | 128 | 14:00
Chhatak | 133 | 06:00 | 128 | 13:00 | Purbasadipur | 132 | 02:00 | 120 | 08:00
Chowmuhani | 134 | 03:00 | 129 | 13:00 | Rahanpur | 141 | 03:00 | 136 | 08:00
Chuadanga | 139 | 02:00 | 127 | 13:00 | Rahanpur-400 | 141 | 02:00 | 136 | 08:00
Coxsbazar | 130 | 04:00 | 123 | 12:00 | Rahim | 139 | 03:00 | 132 | 13:00
Cumilla(N) | 140 | 04:00 | 134 | 13:00 | Rajbari | 139 | 03:00 | 132 | 13:00
Cumilla(S) | 139 | 02:00 | 124 | 13:00 | Rajendrapur | 133 | 03:00 | 125 | 13:00
Daganbhuiyan | 137 | 03:00 | 131 | 13:00 | Rajshahi | 139 | 02:00 | 131 | 13:00
Daudkandi | 137 | 04:00 | 130 | 13:00 | Rajshahi-230 | 140 | 03:00 | 130 | 13:00
DhakaUniversity | 135 | 05:00 | 127 | 13:00 | Ramganj | 136 | 06:00 | 129 | 13:00
Dhamrai | 138 | 03:00 | 133 | 12:00 | Rampur | 138 | 06:00 | 132 | 13:00
Dhanmondi | 140.7 | 05:00 | 133.5 | 13:00 | Rampura | 135 | 05:00 | 127 | 13:00
Dohazari | 135 | 04:00 | 129 | 13:00 | Rangamati | 139 | 06:00 | 134 | 13:00
Faridpur | 139 | 03:00 | 133 | 13:00 | Rangpur | 136 | 03:00 | 124 | 13:00
Fatullah | 142 | 04:00 | 130 | 13:00 | Ruppur | 141 | 04:00 | 136 | 08:00
Fenchuganj | 138 | 04:00 | 135 | 13:00 | Saidpur | 134 | 01:00 | 121 | 08:00
Feni | 135 | 02:00 | 130 | 13:00 | Satkhira | 137 | 03:00 | 125 | 13:00
Feni-230 | 136 | 02:00 | 130 | 13:00 | Satmasjid | 139 | 03:00 | 131 | 13:00
Ghatail | 132 | 19:00 | 122 | 08:00 | Savar | 140 | 05:00 | 131 | 13:00
Ghorashal | 140 | 22:00 | 127 | 12:00 | SevenRings | 140 | 18:30 | 127 | 12:00
Goalpara | 139 | 05:00 | 129 | 13:00 | ShahCement | 139 | 02:00 | 132 | 13:00
Gollamari | 138 | 04:00 | 129 | 13:00 | Shahjadpur | 142 | 02:00 | 136 | 12:00
Gopalganj | 141 | 02:00 | 133 | 21:00 | Shahjibazar | 133 | 01:00 | 128 | 13:00
Gopalganj-400 | 144 | 03:00 | 137 | 13:00 | Shahmirpur | 139 | 02:00 | 134 | 13:00
Gulshan | 134 | 04:00 | 126 | 13:00 | Shariatpur | 143 | 04:00 | 135 | 13:00
Halishahar | 138 | 01:00 | 133 | 13:00 | Sherpur | 125 | 18:30 | 110 | 04:00
Haripur | 140 | 05:00 | 133 | 13:00 | Shikalbaha | 128 | 03:00 | 123 | 13:00
HaripurSBU | 139 | 05:00 | 133 | 13:00 | Shikalbaha-230 | 138 | 01:00 | 134 | 13:00
Hasnabad | 139 | 04:00 | 131 | 13:00 | Shitalakhya | 138 | 02:00 | 129 | 13:00
Hathazari | 139 | 04:00 | 135 | 19:30 | Sholosohor | 139 | 02:00 | 134 | 13:00
Hatirjheel | 135 | 03:00 | 127 | 13:00 | Shyampur | 141 | 04:00 | 134 | 14:00
Ishurdi | 142 | 02:00 | 137 | 13:00 | Shyampur-230 | 141 | 02:00 | 133 | 13:00
Jaldhaka | 132 | 03:00 | 119 | 13:00 | Siddhirganj | 140 | 02:00 | 133 | 13:00
Jamalpur | 130 | 18:30 | 114 | 08:00 | Sirajganj | 138 | 03:00 | 128 | 17:00
Jashore | 138 | 04:00 | 125 | 13:00 | Sonargaon | 136 | 02:00 | 131 | 13:00
Jhenaidah | 140 | 00:00 | 129 | 13:00 | Sreemongol | 134 | 01:00 | 129 | 14:00
Jhenaidah-230 | 141 | 04:00 | 131 | 13:00 | Sreepur | 135 | 03:00 | 128 | 13:00
Joydebpur | 137 | 18:00 | 123 | 10:00 | Srinagar | 138 | 02:00 | 129 | 13:00
Joypurhat | 134 | 04:00 | 123 | 08:00 | SSM | 142 | 00:00 | 138 | 14:00
Juldah | 138 | 01:00 | 133 | 13:00 | Sunamganj | 130 | 02:00 | 126 | 07:00
Kabirpur | 140 | 18:30 | 127 | 14:00 | Sylhet | 134 | 02:00 | 130 | 13:00
Kachua | 138 | 03:00 | 133 | 13:00 | Sylhet-132 | 133 | 00:00 | 131 | 13:00
Kaliakoir | 141 | 02:00 | 133 | 13:00 | Tangail | 133 | 19:00 | 124 | 07:00
Kaliganj | N/A | N/A | N/A | N/A | Taraganj | 133 | 03:00 | 118 | 08:00
Kallyanpur | 141 | 01:00 | 135 | 12:00 | Tasnim | 139 | 05:00 | 131 | 13:00
Kalurghat | 139 | 01:00 | 134 | 13:00 | Thakurgaon | 138 | 02:00 | 124 | 08:00
Kamrangirchar | 138 | 01:00 | 129 | 13:00 | TK | 138 | 00:00 | 135 | 13:00
Kaptai | N/A | N/A | N/A | N/A | Tongi | 135 | 04:00 | 130 | 13:00
Kasba | 138 | 02:00 | 131 | 13:00 | Ullahpara | 139 | 04:00 | 131 | 17:00
Kazla | 141 | 06:00 | 133 | 14:00 | Ullon | 135 | 03:00 | 126 | 13:00
Keranigonj | 138 | 03:00 | 129 | 13:00 | Uttara | 135 | 03:00 | 126 | 13:00
Khagrachori | 138 | 03:00 | 134 | 12:00 | UttaraNew | 135 | 03:00 | 126 | 13:00
Khulna | 137 | 02:00 | 128 | 13:00 | Zigatola | 138 | 02:00 | 129 | 13:00
Khulna(S) | 138 | 02:00 | 129 | 13:00
Khulshi | 137 | 05:00 | 132 | 12:00
Kishoreganj | 132 | 02:00 | 123 | 13:00
Kodda | 138 | 18:00 | 128 | 13:00
KSRM | 138 | 02:00 | 133 | 13:00
Kulaura | 138 | 06:00 | 134 | 17:00
Kurigram | 133 | 03:00 | 119 | 08:00
Kushtia | 139 | 02:00 | 132 | 13:00
Laksam | 137 | 01:00 | 134 | 12:00
Lakshmipur | 135 | 03:00 | 130 | 13:00
Lalbag | 138 | 05:00 | 130 | 22:00
Lalmonirhat | 130 | 02:00 | 118 | 08:00
Madanganj | 136 | 00:00 | 132 | 14:00
Madaripur | 141 | 01:00 | 137 | 13:00
Madartek | 134 | 05:00 | 126 | 13:00
Madunaghat | 139 | 04:00 | 134 | 13:00
Magura | 139 | 03:00 | 127 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division