## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 07-02-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-02-2026 | during | 07-02-2026 | during | 07-02-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 346 | 315 | 412 | 412 | 350 | 350 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 4 | 30 | 55 | 55 | 15 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 12 | 33.4 | 53.97 | 53.97 | 53.97 | 53.97 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 4 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 10 | 33 | 33 | 23 | 23 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 40 | 95 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 78 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 17 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 48 | 86 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 2 | 35 | 55 | 55 | 17 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 495 | 535 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 600 | 600 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 35 | 160 | 160 | 52 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1429 | 1696.4 | 5263.65 | 5231.65 | 3055.02 | 3211.02
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 50 | 0 | 0 | 80 | 80 | Unit #1 Under Maintenance, Unit#2 Machine Problem
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 5 | 25 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 14 | 50 | 105 | 105 | 95 | 95 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 8 | 8 | 8 | 8 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 34 | 34 | 34 | 34 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 27 | 42 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.76 | 0 | 3.27 | 0 | 3.27 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 30 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 35 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 11 | 51 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1105 | 1139 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 22 | 14 | 20 | 25 | 20 | 25 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 610 | 320 | 680 | 680 | 670 | 670 | ps availability is less
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1873.76 | 1761 | 3266.13 | 3254.86 | 2739.77 | 2746.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 204 | 193 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 340 | 310 | 353.35 | 353.35 | 317 | 317 | FGMO
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 40 | 40 | Trying to Sync ST
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 393 | 291 | 393 | 393 | 393 | 393 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 50 | 50 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 21 | 70 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 32 | 32 | 24 | 24 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 104 | 105 | 163 | 163 | 110 | 110 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 18 | 100 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 108 | 108 | 84 | 82 | 84 | 82 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 7 | 13 | 24.5 | 24.5 | 13 | 13 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 16 | 57 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 73 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1335 | 1298 | 2422.75 | 2360.75 | 1905.2 | 1843.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-02-2026 | during | 07-02-2026 | during | 07-02-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 117 | 139 | 157.5 | 157.5 | 35 | 35 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.3 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 19 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 59 | 60 | 60 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 41.83 | 0 | 41.7 | 0 | 41.7 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 35 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 245.13 | 223 | 357.8 | 314 | 181.8 | 156
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 0 | 0 | 0 | 0 | plant availability zero
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 53 | 53 | 53 | 53 | 53 | 53 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 162 | 149 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 80 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 99 | 100 | 100 | 0 | 0 | Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 15 | 13 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 20 | 21 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 739 | 798 | 795 | 795 | 640 | 641
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 898 | 898 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 358 | 367 | 410 | 410 | 250 | 250 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 90 | 0 | 86 | 0 | 86 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 542 | 515 | 617.1 | 617.1 | 617.1 | 617.1 | U#1 Under Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1888 | 1780 | 2975.1 | 2889.1 | 2060.2 | 1974.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 130 | 130 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 965 | 1025 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 35 | 150 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 230 | 274 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.58 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1505.58 | 1649 | 2003.32 | 2002.32 | 1888.32 | 2002.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 54.43 | 0 | 50 | 0 | 50 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Machine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 189 | 175 | 214 | 214 | 214 | 214 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 409 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 17 | 22 | 22 | 24 | 24 | Machine problem and fuel shortage
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 8.7 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.18 | 0 | 5.45 | 0 | 5.45 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 733 | 764.12 | 748 | 748 | 748 | 748 | U#1 Under AOH
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 59.47 | 0 | 56 | 0 | 56 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 109 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1572.78 | 1365.12 | 2431.44 | 2219.99 | 1912.06 | 1700.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 49 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.1 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 165 | 0 | 170.52 | 0 | 170.52 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 271.1 | 99 | 467.72 | 262 | 433.72 | 228
System Total |  |  |  |  | 28823.2 | 28382.8 | 10859.35 | 10669.52 | 19982.91 | 19329.67 | 14816.09 | 14502.85
Forecast Scenario (07-02-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9310 |  | 0 |  | 9310
|  |  |  | 1:00 | 8720 |  | 0 |  | 8720
|  |  |  | 2:00 | 8360 |  | 0 |  | 8360
|  |  |  | 3:00 | 8060 |  | 0 |  | 8060
|  |  |  | 4:00 | 7830 |  | 0 |  | 7830
|  |  |  | 5:00 | 7790 |  | 0 |  | 7790
|  |  |  | 6:00 | 8210 |  | 0 |  | 8210
|  |  |  | 7:00 | 8970 |  | 0 |  | 8970
|  |  |  | 8:00 | 9750 |  | 0 |  | 9750
|  |  |  | 9:00 | 9850 |  | 0 |  | 9850
|  |  |  | 10:00 | 9830 |  | 0 |  | 9830
|  |  |  | 11:00 | 10140 |  | 0 |  | 10140
|  |  |  | 12:00 | 10470 |  | 0 |  | 10470
|  |  |  | 13:00 | 11240 |  | 0 |  | 11240
|  |  |  | 14:00 | 10740 |  | 0 |  | 10740
|  |  |  | 15:00 | 10430 |  | 0 |  | 10430
|  |  |  | 16:00 | 10110 |  | 0 |  | 10110
|  |  |  | 17:00 | 10140 |  | 0 |  | 10140
|  |  |  | 18:00 | 11630 |  | 0 |  | 11630
|  |  |  | 18:30 | 11800 |  | 0 |  | 11800
|  |  |  | 19:00 | 12180 |  | 0 |  | 12180
|  |  |  | 19:30 | 12000 |  | 0 |  | 12000
|  |  |  | 20:00 | 11790 |  | 0 |  | 11790
|  |  |  | 21:00 | 11540 |  | 0 |  | 11540
|  |  |  | 22:00 | 11020 |  | 0 |  | 11020
|  |  |  | 23:00 | 10510 |  | 0 |  | 10510
Probable Maximum Temperature: |  |  | 27.90°C
Probable Maximum Demand at Day Peak: |  |  | 10470.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12180.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12180.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 238.62 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:48 hrs on 07-02-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 06-02-2026 | [28 empty] | Date: | 06-02-2026 | [28 empty] | Date: | 06-02-2026 | [28 empty] | Date: | 06-02-2026 | [28 empty] | Date: | 06-02-2026 | [17 empty] | Date: | 06-02-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [17 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 29 | 660 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 393 | 290 | 0 | 51 | 0 | 194 | 0 | 0 | 108 | 0 | 0 | 20 | 0 | 104 | 0 | 0 | 0 | 305 | 0 | 0 | 41 | 53 | 156 | 0 | 21 | 0 | 83 | 30 | 0 | 15 | 0 | 0 | 24 | 0 | 128 | 0 | 0 | 0 | 5258 | 898 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 542 | 0 | 0 | 0 | 770 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 130 | 220 | 0 | 0 | 950 | 0 | 4592 | 9850 | 94.64
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 29 | 680 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 963 | 0 | 0 | 0 | 393 | 305 | 0 | 51 | 0 | 198 | 0 | 0 | 108 | 0 | 0 | 13 | 0 | 100 | 0 | 0 | 0 | 310 | 0 | 0 | 42 | 53 | 139 | 0 | 17 | 0 | 83 | 30 | 0 | 15 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 5061 | 898 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 130 | 220 | 0 | 0 | 850 | 0 | 4146 | 9207 | 94.64
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 29 | 680 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 954 | 0 | 0 | 0 | 393 | 295 | 0 | 51 | 0 | 197 | 0 | 0 | 109 | 0 | 0 | 13 | 0 | 96 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 53 | 140 | 0 | 17 | 0 | 83 | 30 | 0 | 15 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 5046 | 898 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 130 | 220 | 0 | 0 | 620 | 0 | 3789 | 8835 | 94.64
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 29 | 680 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 750 | 0 | 0 | 0 | 393 | 305 | 0 | 51 | 0 | 201 | 0 | 0 | 108 | 0 | 0 | 13 | 0 | 94 | 0 | 0 | 0 | 310 | 0 | 0 | 42 | 53 | 138 | 0 | 17 | 0 | 11 | 20 | 0 | 15 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 4821 | 898 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 130 | 180 | 0 | 0 | 552 | 0 | 3579 | 8400 | 94.63
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 680 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 672 | 0 | 0 | 0 | 330 | 290 | 0 | 51 | 0 | 197 | 0 | 0 | 109 | 0 | 0 | 13 | 0 | 88 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 53 | 139 | 0 | 17 | 0 | 11 | 20 | 0 | 15 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 4606 | 898 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 100 | 180 | 0 | 0 | 552 | 0 | 3551 | 8157 | 94.63
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 680 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0 | 0 | 657 | 0 | 0 | 0 | 330 | 285 | 0 | 51 | 0 | 193 | 0 | 0 | 109 | 0 | 0 | 13 | 0 | 80 | 0 | 0 | 0 | 305 | 0 | 0 | 41 | 53 | 135 | 0 | 17 | 0 | 11 | 20 | 0 | 15 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 4577 | 898 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 100 | 180 | 0 | 0 | 540 | 0 | 3509 | 8086 | 94.63
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 680 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 683 | 0 | 0 | 0 | 393 | 330 | 0 | 51 | 0 | 199 | 0 | 0 | 110 | 0 | 0 | 7 | 0 | 86 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 53 | 145 | 0 | 17 | 0 | 80 | 30 | 0 | 15 | 0 | 0 | 10 | 0 | 133 | 0 | 0 | 0 | 4741 | 897 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 130 | 220 | 0 | 0 | 550 | 0 | 3661 | 8402 | 94.62
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 280 | 0 | 0 | 1 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0.11 | 40 | 0 | 35 | 680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 842 | 2 | 0 | 0 | 393 | 340 | 0 | 51 | 0 | 203 | 0 | 0 | 110 | 0 | 0 | 13 | 0 | 84 | 0 | 3 | 0 | 315 | 0 | 0 | 41 | 53 | 154 | 0 | 17 | 0 | 80 | 30 | 0 | 15 | 0 | 0 | 35 | 0 | 132 | 0 | 1.4 | 0 | 5026.51 | 898 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 381 | 0 | 0 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.37 | 2 | 0 | 0 | 1.41 | 160 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0.01 | 0 | 217 | 130 | 220 | 0 | 0 | 650 | 0 | 3841.42 | 8867.93 | 94.62
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 280 | 0 | 0 | 0 | 35 | 13.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0.98 | 40 | 0 | 29 | 680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 8 | 0 | 0 | 393 | 345 | 0 | 51 | 0 | 207 | 0 | 0 | 109 | 0 | 0 | 13 | 0 | 90 | 0 | 25 | 0 | 325 | 0 | 0 | 41 | 53 | 162 | 3 | 17 | 0 | 80 | 30 | 0 | 15 | 0 | 0 | 56 | 19 | 132 | 1 | 12.87 | 0 | 5198.35 | 898 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.19 | 477 | 0 | 0 | 0 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.62 | 28 | 0 | 0 | 15.11 | 171 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.29 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0.8 | 40 | 0.13 | 0 | 232 | 130 | 220 | 0 | 0 | 810 | 0 | 4429.14 | 9627.49 | 94.62
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 2.09 | 40 | 0 | 26 | 680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 14 | 0 | 0 | 393 | 340 | 0 | 51 | 0 | 203 | 0 | 0 | 107 | 0 | 0 | 13 | 0 | 100 | 0 | 46 | 0 | 325 | 0 | 0 | 41 | 53 | 163 | 7 | 17 | 0 | 83 | 30 | 0 | 15 | 0 | 0 | 56 | 19 | 130 | 1 | 25.77 | 3 | 5291.36 | 898 | 366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.79 | 560 | 0 | 0 | 0 | 573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.46 | 58 | 0 | 0 | 31.77 | 185 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.84 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 2.4 | 84 | 0.3 | 0 | 230 | 130 | 220 | 0 | 0 | 938 | 0 | 4787.56 | 10078.92 | 94.61
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 2.97 | 40 | 0 | 27 | 680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 18 | 0 | 0 | 393 | 320 | 0 | 45 | 0 | 194 | 0 | 0 | 108 | 0 | 0 | 13 | 0 | 102 | 0 | 61 | 0 | 310 | 0 | 0 | 42 | 53 | 159 | 9 | 17 | 0 | 83 | 30 | 0 | 15 | 0 | 0 | 58 | 19 | 130 | 2 | 36.23 | 2 | 5213.7 | 898 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 530 | 0 | 0 | 0 | 571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.83 | 82 | 0 | 0 | 46.04 | 179 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 3.92 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 3.8 | 123 | 0.46 | 0 | 230 | 130 | 180 | 0 | 0 | 900 | 0 | 4754.05 | 9967.75 | 94.61
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 13 | 0 | 15 | 0 | 0 | 14 | 0 | 0 | 0 | 465 | 0 | 0 | 300 | 0 | 0 | 31 | 35 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 3.53 | 40 | 0 | 27 | 630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1020 | 20 | 4 | 0 | 350 | 350 | 0 | 45 | 0 | 210 | 0 | 12 | 104 | 9 | 0 | 13 | 0 | 98 | 0 | 69 | 0 | 310 | 0 | 0 | 42 | 53 | 160 | 11 | 17 | 0 | 83 | 30 | 0 | 15 | 0 | 0 | 59 | 19 | 117 | 2 | 41.77 | 6 | 5234.8 | 898 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 480 | 0 | 0 | 0 | 573 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 50.78 | 99 | 0 | 0 | 56.79 | 181 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.26 | 0 | 0 | 0 | 29 | 34 | 0 | 0 | 0 | 4.9 | 152 | 0.55 | 0 | 229 | 130 | 180 | 0 | 0 | 890 | 0 | 4839.28 | 10074.08 | 94.61
12:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 12 | 2 | 17 | 0 | 40 | 4 | 4 | 48 | 0 | 0 | 0 | 495 | 0 | 0 | 335 | 0 | 0 | 32 | 35 | 20 | 22 | 0 | 0 | 0 | 16 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 3.76 | 40 | 11 | 27 | 610 | 0 | 0 | 5 | 0 | 14 | 0 | 0 | 0 | 0 | 1105 | 20 | 21 | 0 | 393 | 340 | 0 | 51 | 0 | 204 | 0 | 16 | 104 | 18 | 0 | 7 | 0 | 108 | 0 | 73 | 0 | 325 | 0 | 0 | 42 | 53 | 162 | 12 | 17 | 0 | 83 | 30 | 0 | 15 | 0 | 0 | 59 | 19 | 117 | 2.3 | 41.83 | 6 | 5621.89 | 898 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 542 | 0 | 0 | 0 | 733 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7 | 0 | 0 | 54.43 | 109 | 0 | 0 | 59.47 | 189 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.18 | 0 | 0 | 35 | 32 | 34 | 0 | 0 | 0 | 5.1 | 165 | 0.58 | 0 | 230 | 130 | 180 | 0 | 0 | 965 | 0 | 5237.46 | 10859.35 | 94.6
13:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 16.2 | 17 | 33 | 0 | 95 | 15 | 17 | 62 | 0 | 0 | 0 | 520 | 0 | 17 | 335 | 0 | 0 | 32 | 52 | 11 | 7 | 0 | 0 | 0 | 16 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 3.5 | 40 | 29 | 40 | 610 | 0 | 0 | 18 | 0 | 32 | 0 | 0 | 0 | 0 | 1224 | 20 | 43 | 0 | 387 | 310 | 0 | 51 | 0 | 192 | 0 | 28 | 103 | 47 | 0 | 11 | 0 | 130 | 0 | 70 | 0 | 320 | 0 | 0 | 42 | 53 | 160 | 11 | 17 | 0 | 83 | 30 | 0 | 15 | 0 | 0 | 59 | 19 | 111 | 2 | 43.19 | 6 | 6003.89 | 898 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 605 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 20 | 14 | 0 | 8.7 | 0 | 0 | 51.53 | 106 | 0 | 0 | 59.37 | 185 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 5.18 | 0 | 0 | 35 | 34 | 34 | 0 | 0 | 0 | 5.6 | 168 | 0.57 | 0 | 289 | 130 | 220 | 0 | 0 | 1040 | 0 | 5447.95 | 11451.84 | 94.6
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 425 | 0 | 0 | 280 | 0 | 0 | 29 | 35 | 11 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 3.08 | 40 | 0 | 34 | 580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 18 | 0 | 0 | 300 | 315 | 0 | 51 | 0 | 200 | 0 | 0 | 51 | 0 | 0 | 13 | 0 | 112 | 0 | 61 | 0 | 305 | 0 | 0 | 42 | 53 | 142 | 10 | 17 | 0 | 41 | 30 | 0 | 15 | 0 | 0 | 45 | 8 | 114 | 2 | 39.2 | 0 | 4881.28 | 898 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 487 | 0 | 0 | 0 | 664 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7 | 0 | 0 | 45.3 | 99 | 0 | 0 | 49.88 | 160 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 4.3 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 4.5 | 150 | 0.48 | 0 | 201 | 100 | 180 | 0 | 0 | 1000 | 0 | 4838.16 | 9719.44 | 94.6
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 280 | 0 | 0 | 22 | 17 | 12 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 2.29 | 40 | 0 | 30 | 474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 958 | 15 | 0 | 0 | 300 | 320 | 0 | 51 | 0 | 203 | 0 | 0 | 50 | 0 | 0 | 13 | 0 | 100 | 0 | 47 | 0 | 315 | 0 | 0 | 42 | 53 | 141 | 7 | 17 | 0 | 42 | 30 | 0 | 15 | 0 | 0 | 24 | 8 | 126 | 1 | 33.36 | 0 | 4548.65 | 898 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 380 | 0 | 0 | 0 | 667 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7 | 0 | 0 | 35.12 | 76 | 0 | 0 | 38.99 | 167 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 3.3 | 112 | 0.37 | 0 | 181 | 100 | 180 | 0 | 0 | 900 | 0 | 4543.48 | 9092.13 | 94.59
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 12 | 7 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 0 | 0 | 0 | 0 | 0 | 1.29 | 40 | 0 | 33 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 957 | 9 | 0 | 0 | 320 | 330 | 0 | 51 | 0 | 210 | 0 | 0 | 50 | 0 | 0 | 13 | 0 | 102 | 0 | 25 | 0 | 320 | 0 | 0 | 42 | 53 | 150 | 4 | 17 | 0 | 42 | 30 | 0 | 15 | 15 | 0 | 24 | 8 | 130 | 1 | 22.31 | 0 | 4482.6 | 898 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 386 | 0 | 0 | 0 | 664 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7 | 0 | 0 | 21.02 | 48 | 0 | 0 | 22.83 | 172 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 1.7 | 60 | 0.31 | 0 | 184 | 100 | 220 | 0 | 0 | 900 | 0 | 4466.56 | 8949.16 | 94.59
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 280 | 0 | 0 | 4 | 17 | 12 | 7 | 0 | 0 | 0 | 0 | 0 | 50 | 23 | 0 | 1 | 0 | 0 | 0 | 0.3 | 40 | 0 | 35 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 979 | 3 | 0 | 0 | 320 | 360 | 0 | 51 | 0 | 215 | 0 | 0 | 50 | 0 | 0 | 13 | 0 | 106 | 0 | 8 | 0 | 325 | 0 | 0 | 42 | 53 | 158 | 1 | 17 | 0 | 42 | 30 | 0 | 13 | 65 | 0 | 56 | 8 | 146 | 0 | 12.57 | 0 | 4667.87 | 898 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 390 | 0 | 0 | 0 | 664.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.59 | 13 | 0 | 0 | 5.48 | 175 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.4 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.5 | 16 | 0.07 | 0 | 190 | 100 | 220 | 0 | 0 | 900 | 0 | 4368.21 | 9036.08 | 94.59
18:00 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 12 | 17 | 54 | 0 | 95 | 25 | 35 | 82 | 0 | 0 | 0 | 440 | 0 | 30 | 333 | 0 | 0 | 0 | 52 | 10 | 7 | 0 | 0 | 0 | 30 | 0 | 20 | 13 | 34 | 8 | 0 | 0 | 0 | 0 | 40 | 25 | 42 | 320 | 0 | 0 | 5 | 0 | 34 | 0 | 0 | 0 | 0 | 1063 | 0 | 31 | 0 | 315 | 310 | 0 | 51 | 0 | 201 | 0 | 16 | 105 | 43 | 0 | 13 | 0 | 116 | 0 | 0 | 24 | 310 | 0 | 0 | 42 | 53 | 146 | 0 | 17 | 0 | 70 | 30 | 0 | 13 | 100 | 0 | 59 | 19 | 139 | 0 | 0 | 3 | 5428 | 898 | 342 | 0 | 14 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 761.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 40 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 100 | 220 | 0 | 0 | 930 | 0 | 4496.45 | 9924.45 | 94.58
19:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 33.4 | 35 | 78 | 0 | 95 | 30 | 35 | 86 | 0 | 0 | 0 | 535 | 0 | 35 | 335 | 0 | 0 | 0 | 35 | 10 | 22 | 0 | 0 | 0 | 30 | 0 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 51 | 42 | 320 | 0 | 0 | 25 | 0 | 50 | 0 | 0 | 0 | 0 | 1139 | 0 | 70 | 0 | 291 | 310 | 0 | 51 | 0 | 193 | 0 | 57 | 105 | 100 | 0 | 13 | 0 | 108 | 0 | 0 | 0 | 315 | 0 | 0 | 42 | 53 | 149 | 0 | 17 | 0 | 80 | 30 | 0 | 13 | 99 | 0 | 59 | 19 | 139 | 0 | 0 | 6 | 5776.4 | 898 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 515 | 0 | 0 | 0 | 764.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 0 | 0 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 130 | 220 | 0 | 0 | 1025 | 0 | 4893.12 | 10669.52 | 94.58
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 30 | 0 | 51 | 0 | 45 | 30 | 35 | 53 | 0 | 0 | 0 | 560 | 0 | 35 | 335 | 0 | 0 | 0 | 17 | 10 | 22 | 0 | 0 | 0 | 0 | 0 | 75 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 42 | 320 | 0 | 0 | 25 | 0 | 49 | 0 | 0 | 0 | 0 | 1162 | 0 | 10 | 0 | 316 | 335 | 0 | 51 | 0 | 202 | 0 | 34 | 105 | 51 | 0 | 13 | 0 | 114 | 0 | 0 | 0 | 320 | 0 | 0 | 42 | 53 | 159 | 0 | 17 | 0 | 83 | 30 | 0 | 13 | 100 | 0 | 59 | 19 | 142 | 0 | 0 | 6 | 5612 | 898 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 130 | 220 | 0 | 0 | 1085 | 0 | 4919 | 10531
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 31.6 | 0 | 55 | 0 | 0 | 30 | 35 | 52 | 0 | 0 | 0 | 545 | 0 | 35 | 335 | 0 | 0 | 0 | 17 | 10 | 22 | 0 | 0 | 0 | 0 | 0 | 120 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 48 | 42 | 320 | 0 | 0 | 26 | 0 | 48 | 0 | 0 | 0 | 0 | 1163 | 0 | 8 | 0 | 312 | 330 | 51 | 51 | 0 | 199 | 0 | 34 | 106 | 51 | 0 | 13 | 0 | 112 | 0 | 0 | 0 | 310 | 0 | 0 | 42 | 53 | 154 | 0 | 17 | 0 | 83 | 30 | 0 | 13 | 100 | 0 | 58 | 19 | 142 | 0 | 0 | 0 | 5600.6 | 898 | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 0 | 0 | 0 | 755.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 130 | 220 | 0 | 0 | 1085 | 0 | 4952.75 | 10553.35 | 94.58
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 10 | 22 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 17 | 42 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1162 | 0 | 0 | 0 | 310 | 330 | 250 | 51 | 0 | 195 | 0 | 31 | 106 | 48 | 0 | 13 | 0 | 118 | 0 | 0 | 0 | 310 | 0 | 0 | 42 | 53 | 154 | 0 | 17 | 0 | 83 | 30 | 0 | 13 | 100 | 0 | 58 | 19 | 143 | 0 | 0 | 0 | 5474 | 898 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 609 | 0 | 0 | 0 | 757.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 130 | 220 | 0 | 0 | 1085 | 0 | 4960.91 | 10434.91 | 94.57
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1163 | 0 | 0 | 0 | 220 | 260 | 250 | 51 | 0 | 122 | 0 | 32 | 108 | 0 | 0 | 13 | 0 | 116 | 0 | 0 | 0 | 325 | 0 | 0 | 42 | 53 | 159 | 0 | 17 | 0 | 83 | 30 | 0 | 13 | 100 | 0 | 58 | 19 | 140 | 0 | 0 | 0 | 5172.5 | 898 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617 | 0 | 0 | 0 | 756.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 130 | 220 | 0 | 0 | 1085 | 0 | 4950.48 | 10122.98 | 94.57
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 11 | 14 | 0 | 0 | 0 | 0 | 0 | 130 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 0 | 0 | 0 | 25 | 245 | 255 | 51 | 0 | 118 | 0 | 0 | 108 | 0 | 0 | 13 | 0 | 114 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 53 | 144 | 0 | 17 | 0 | 83 | 30 | 0 | 13 | 100 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 4765 | 898 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 609 | 0 | 0 | 0 | 759.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 130 | 220 | 0 | 0 | 1000 | 0 | 4796.62 | 9561.62 | 94.56
Total KWH | 0 | 104640 | 0 | 0 | 0 | 0 | 0 | 0 | 8121600 | 0 | 3341405 | 126360 | 97920 | 335520 | 0 | 343495 | 120254 | 151610 | 370080 | 0 | 0 | 0 | 8783550 | 0 | 135731 | 7525394 | 0 | 0 | 172781 | 421200 | 323400 | 423000 | 0 | 0 | 0 | 92836 | 0 | 700000 | 595200 | 44381 | 11664 | 0 | 0 | 0 | 23762 | 964000 | 236689 | 839040 | 12909090.91 | 0 | 0 | 101760 | 0 | 248399 | 1017241 | 0 | 0 | 0 | 23814543 | 137160 | 239200 | 0 | 7804000 | 7887500 | 946000 | 1234839 | 0 | 4752000 | 0 | 293760 | 2336371 | 377280 | 0 | 326460 | 0 | 2452800 | 0 | 494291 | 31711 | 7631000 | 0 | 0 | 985000 | 1331520 | 3607445.45 | 74470 | 406704 | 0 | 1513920 | 687072 | 0 | 345000 | 726500 | 0 | 894000 | 249600 | 3062400 | 14100 | 297280 | 43200 | 123679129.36 | 21702545 | 8648928 | 0 | 12960 | 11136 | 0 | 0 | 0 | 0 | 0 | 0 | 591120 | 11418140 | 0 | 0 | 0 | 14967829 | 0 | 0 | 0 | 25440 | 26784 | 0 | 49296 | 0 | 0 | 353092 | 737930 | 30825 | 0 | 385504 | 4173455 | 0 | 0 | 0 | 0 | 0 | 9395709 | 0 | 29640 | 0 | 0 | 179140 | 199802 | 226752 | 0 | 0 | 0 | 31479.24 | 1071360 | 3735 | 0 | 5324000 | 2905000 | 5342520 | 0 | 0 | 21617454.55 | 0 | 109461575.79 | 233140705.15

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 06-02-2026
Power Supply Scenario
| Day Peak Generation |  |  | 10859.35 | MW | 12:00 Hr. | Energy Generated |  |  | 233.1407 |  | MKWHr.
| Day Peak Demand |  |  | 10859.35 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 10669.52 | MW | 19:00 Hr. | Energy Demand |  |  | 233.1407 |  | MKWHr.
| Evening Peak Demand |  |  | 10669.52 | MW | 19:00 Hr. | Maximum Temperature |  |  | 26.7 |  | °C
| Minimum Generation of the Day |  |  | 8086 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 785.72 |  | MMCFD
| Maximum Generation of the Day |  |  | 11451.84 | MW | 13:00 Hr. | Production Cost per KWHr |  |  | 5.3322 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 28.5183 | 0 | 2.2068 | 0 | 0 | 0.17278 | 0 | 0 | 30.8979 | Gas | 107.124 | Gas | 381367834.574
| Chattogram Zone |  |  | 2.5563 | 36.7236 | 0.73573 | 0 | 0.964 | 0.16092 | 0 | 0.5952 | 41.7358 | Coal | 75.0832 | Coal | 480615292.9113
| Cumilla Zone |  |  | 25.2872 | 0 | 0.94195 | 0 | 0 | 0.49429 | 2.4528 | 0 | 29.1762 | HFO | 5.6336 | HFO | 92937914.81
| Mymensingh Zone |  |  | 3.0624 | 0 | 1.1868 | 0 | 0 | 0.31138 | 0 | 0 | 4.5606 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 17.2342 | 0 | 0 | 0 | 0 | 0.07447 | 0 | 0 | 17.3086 | Hydro | 0.964 | Hydro | 96400
| Khulna Zone |  |  | 8.6489 | 11.4181 | 0.024096 | 0 | 0 | 0.59112 | 21.7025 | 0 | 42.3848 | Solar | 4.6175 | Solar | 73370813.008
| Barishal Zone |  |  | 8.2475 | 26.9415 | 0 | 0 | 0 | 0.003735 | 0 | 0 | 35.1927 | Import | 39.1232 | Import | 206009137.77
| Rajshahi Zone |  |  | 13.5692 | 0 | 0.13234 | 0 | 0 | 1.5062 | 14.9678 | 0 | 30.1755 | Wind | 0.5952 | Wind | 8755392
| Rangpur Zone |  |  | 0 | 0 | 0.40589 | 0 | 0 | 1.3026 | 0 | 0 | 1.7085
| Total |  |  | 107.124 | 75.0832 | 5.6336 | 0 | 0.964 | 4.6175 | 39.1232 | 0.5952 | 233.1407
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 381367834.574 |  | Hydro | 96400
|  |  |  | Coal | 480615292.9113 |  | Solar | 73370813.008
|  |  |  | HFO | 92937914.81 |  | Import | 206009137.77
|  |  |  | HSD | 0 |  | Wind | 8755392
[5 empty] | Total: | 124,31,52,785 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7025 | Peak Hr Flow | 898.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 33391346.72 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 14.9678 | Peak Hr Flow | 764.12 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1592 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.4528 | Peak Hr Flow | 108.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1987 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 39.1232 | Peak Hr Flow | 1770.12 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3689
|  |  |  | Chattogram |  | 0 |  | 1133
|  |  |  | Cumilla |  | 0 |  | 913
|  |  |  | Mymensingh |  | 0 |  | 971
|  |  |  | Sylhet |  | 0 |  | 391
|  |  |  | Khulna |  | 0 |  | 1194
|  |  |  | Barishal |  | 0 |  | 294
|  |  |  | Rajshahi |  | 0 |  | 1030
|  |  |  | Rangpur |  | 0 |  | 765
|  |  |  | Total |  | 0 |  | 10380
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:20 | 11:48 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to Shutdown taken by PDB for
Maintenance work.
| 08:20 | 11:38 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to Shutdown taken by PDB for
Maintenance work.
| 08:28 | 14:02 | Khulna(C )-Noapara 132kV Ckt-1 Scheduled S/D from Khulna (C) end Due to South-1, DS
Clamp Change.
| 08:28 | 14:03 | Khulna(C )-Noapara 132kV Ckt-2 Scheduled S/D from Khulna (C) end Due to South-1, DS
Clamp Change.
| 08:30 | 13:59 | Khulna (C) S/S TR-1 425T LT Scheduled S/D Due to South-1, DS Clamp Change.
| 08:30 | 13:58 | Khulna (C) S/S TR-1 425T HT Scheduled S/D Due to South-1, DS Clamp Change.
| 08:37 | 12:05 | Barishal 230/132kV S/S T-4 LT Scheduled S/D Due to 33 kV Bus DS maintenance
| 08:39 | 12:02 | Barishal 230/132kV S/S T-4 HT Scheduled S/D Due to 33 kV Bus DS maintenance
| 08:42 | 13:52 | Khulna (C) S/S Bus Coupler Scheduled S/D Due to South-1, DS clamp change .
| 08:43 | 09:56 | Purbasadipur 132/33kV S/S T-4 Transformer HT Scheduled S/D | [7 empty] | 35.0MW load
interrup.
| 08:43 | 09:56 | Purbasadipur 132/33kV S/S T-4 Transformer LT Scheduled S/D | [7 empty] | 35.0MW load
interrup.
| 08:43 | 09:56 | Purbasadipur 132/33kV S/S T-4 Transformer LT Scheduled S/D | [7 empty] | 35.0MW load
interrup.
| 08:45 | 14:05 | Khulna (C) S/S North-WestCkt-1 Scheduled S/D Due to South-1, DS Clamp Change.
| 08:45 | 14:06 | Khulna (C) S/S North- West Ckt-2 Scheduled S/D Due to South-1, DS Clamp Change.
| 08:57 | 13:34 | Khulna(C )-Khulna (S) 132kV Ckt-1 Scheduled S/D from Khulna (C) end Due to South-1, DS
Clamp Change. and from Khulna(S) 230/132kVend.
| 09:07 | 13:35 | Khulna(C )-Khulna (S) 132kV Ckt-2 Scheduled S/D from Khulna (C) end Due to South-1, DS
Clamp Change.
| 09:11 | 10:34 | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to TR-1 (B) Underground Cable
Termination Kit maintenance.
| 09:11 | 10:36 | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to TR-1 (B) Underground Cable
Termination Kit maintenance
| 09:46 | 10:32 | Kalurghat 132/33kV S/S TRFO-02(516T) HT Forced S/D Due to Transporting T-1 under T-2 LT | [7 empty] | 10.0MW load
|  |  | cable | [7 empty] | interrup.
| 10:49 |  | Mirsorai 230/33kV S/S TR-2, 728T LT Project Work S/D Due to bus coupling
| 11:14 |  | Mirsorai 230/33kV S/S TR-2, 728T HT Project Work S/D Due to Bus Coupling
| 11:48 |  | Mirsorai 230/33kV S/S 150 MW Power Station -01 Project Work S/D Due to bus coupling
| 16:00 | 16:29 | Kabirpur - Manikganj 132kV Ckt-1 Tripped from Manikganj 132/33kV end showing Zone-1 | [7 empty] | 46.0MW load
|  |  | relays Due to General Trip Kabirpur end | [7 empty] | interrup. Manikganj
132/33kV end
|  | 17:19 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-2 is restored.
| 19:46 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 22:24 |  | Ashuganj 420 MW CCPP (East) ST was forced shutdown due to gas shortage and Ashuganj
(South) CCPP test purpose
| 23:08 |  | Ashuganj 420 MW CCPP (East) GT was forced shutdown due to gas shortage and Ashuganj
(South) CCPP test purpose
| 04:11 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 05:00 |  | Minimum Generation: 7571 MW.
| 05:43 | 07:10 | Rampura-Ullon-2 132kV Ckt-2 Tripped from Rampura 230/132kV end showing Distance
Protection 21/2 Z1 AN relays Due to Triped by Distance Relay
| 07:14 |  | Motijheel-Bangabhaban 132 kV ckt-1 tripped as a monkey fell on the transformer in
Bangabhaban showing intertrip in Motijheel end. Bangabhaban's load was shifted to New
Romna (DPDC 33/11 kV ss) source immedietly
| 07:44 |  | Niamatpur 132/33kV S/S Transformer-2 (417T) HT Forced S/D Due to PBS T-2, 33kV Busbar | [7 empty] | 43.0MW load
|  |  | Maintenance | [7 empty] | interrup.
| 07:44 |  | Niamatpur 132/33kV S/S Transformer-2 (417T) LT Forced S/D Due to PBS T-2, 33kV Busbar | [7 empty] | 43.0MW load
|  |  | Maintenance | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 06-02-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 315 | 8121600 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 120254 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7525394 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 33.4 | 126360 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 151610 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 135731 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 10 | 323400 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 423000 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 95 | 343495 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 78 | 335520 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 104640 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 86 | 370080 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 172781 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 97920 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 535 | 8783550 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 3341405 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 35 | 421200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6667.111 | 1696.4 | 30897940
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 50 | 700000 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 137160 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 25 | 101760 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 964000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 1017241 | Under Maintenance
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 50 | 248399 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 11664 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 44381 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 42 | 839040 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 23762 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 30 | 92836 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 51 | 236689 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1139 | 23814543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 14 | 595200 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 320 | 12909090.91 | ps availability is less
Chattogram Area Total |  |  |  |  | 4898.863 | 1761 | 41735765.91
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 193 | 4752000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 310 | 7887500 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 946000 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 291 | 7804000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1234839 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 70 | 239200 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 31711 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 105 | 2336371 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 377280 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 108 | 2452800 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 326460 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 57 | 293760 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 494291 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1298 | 29176212
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 139 | 3062400 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 249600 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 894000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 297280 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 43200 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 223 | 4560580
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 74470 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 985000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 53 | 1331520 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 149 | 3607445.45 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 687072 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1513920 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 99 | 726500 | Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 13 | 345000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 406704 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7631000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2325 | 798 | 17308631.45
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 898 | 21702545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 12960 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 11136 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 367 | 8648928 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 591120 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 515 | 11418140 | U1 under maintenance
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1780 | 42384829
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 2905000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 1025 | 21617454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5342520 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 274 | 5324000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3735 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1649 | 35192709.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 353092 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Machine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 175 | 4173455 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 409 | 9395709 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 17 | 30825 | Machine problem and fuel shortage
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 49296 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 26784 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 25440 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 29640 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 764.12 | 14967829 | U#1 Under AOH
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 385504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 737930 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1365.12 | 30175504
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 226752 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 31479.24 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 179140 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 199802 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1071360 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 99 | 1708533.24
Eastern Grid Total |  |  |  |  | 17398.245 | 5776.4 | 123679129.36
Western Grid Total |  |  |  |  | 10984.555 | 4893.12 | 109461575.79
National Grid Total |  |  |  |  | 28382.8 | 10669.52 | 233140705.15
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 06-02-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7097.61 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3283.9 | MW
i) Dhaka area |  |  | 3689.31 |  | MW | i) Khulna area |  |  |  | 1194 | MW
ii) Chattogram area |  |  | 1133.3 |  | MW | ii) Barishal area |  |  |  | 294.5 | MW
iii) Cumilla area |  |  | 913 |  | MW | iii) Rajshahi area |  |  |  | 1030.4 | MW
iv) Mymensingh area |  |  | 971 |  | MW | iv) Rangpur area |  |  |  | 765 | MW
v) Sylhet area |  |  | 391 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10381.51 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 77 | 14:00 | 133 | Netrakona | 150 | 13:00
2 | AKSML | 24 | 05:00 | 68 | Hathazari | 61 | 13:00 | 134 | New | 51 | 12:00
3 | Aftabnagar | 28 | 12:00 | 69 | Hatirjheel | 26 | 18:00 | 135 | Niamatpur | 95 | 09:00
4 | Agargaon | 75 | 13:00 | 70 | Ishurdi | 49 | 13:00 | 136 | Noapara | 30 | 18:30
5 | Agrabad | 40 | 12:00 | 71 | Jaldhaka | 59 | 18:30 | 137 | PHP | 8 | 10:00
6 | Amnura | 33 | 08:00 | 72 | Jamalpur | 114 | 08:00 | 138 | Pabna | 60 | 18:30
7 | Ashuganj | 64 | 12:00 | 73 | Jashore | 114 | 13:00 | 139 | Palashbari | 112 | 08:00
8 | BSRM | 205 | 17:00 | 74 | Jhenaidah | 81 | 18:30 | 140 | Panchagarh | 42 | 18:30
9 | Bagerhat | 60 | 18:30 | 75 | Joydebpur | 94 | 12:00 | 141 | Patiya | 6.6 | 20:00
10 | Bajitpur | 57 | 07:00 | 76 | Joypurhat | 50 | 09:00 | 142 | Patuakhali | 37 | 21:00
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 12.5 | 10:00 | 143 | Payra | 26 | 18:30
12 | Bakulia | 60 | 19:00 | 78 | KSRM | 12 | 19:00 | 144 | Postogola | 38 | 13:00
13 | Banani | 31.2 | 13:00 | 79 | Kabirpur | 171 | 18:30 | 145 | Purbachal | 22 | 13:00
14 | Bangabhaban | 4 | 12:00 | 80 | Kachua | 59 | 18:00 | 146 | Purbasadipur | 131 | 13:00
15 | Barapukuria | 65 | 08:00 | 81 | Kallyanpur | 90 | 12:00 | 147 | Rahanpur | 28 | 12:00
16 | Barguna | 14 | 18:30 | 82 | Kalurghat | 26 | 12:00 | 148 | Rahim | 22 | 01:00
17 | Barishal | 79 | 11:00 | 83 | Kamrangirchar | 54 | 12:00 | 149 | Rajbari | 55 | 18:30
18 | Barishal-230 | 64 | 13:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 105 | 11:00
19 | Baroaulia | 54 | 18:00 | 85 | Kasba | 29 | 13:00 | 151 | Rajshahi | 84 | 13:00
20 | Baroirhat | 41 | 12:00 | 86 | Kazla | 93 | 13:00 | 152 | Rajshahi-230 | 61 | 13:00
21 | Bashundhara | 167 | 13:00 | 87 | Keranigonj | 64 | 13:00 | 153 | Ramganj | 86 | 13:00
22 | BashundharaCement | 12 | 00:00 | 88 | Khagrachori | 26 | 18:00 | 154 | Rampur | 28 | 13:00
23 | Beanibazar | 50 | 13:00 | 89 | Khulna | 46 | 13:00 | 155 | Rangamati | 12 | 10:00
24 | Benapole | 52 | 09:00 | 90 | Khulshi | 148 | 19:30 | 156 | Rangpur | 114 | 13:00
25 | Bhaluka | 120 | 09:00 | 91 | Kishoreganj | 109 | 13:00 | 157 | Ruppur | 2.4 | 10:00
26 | Bhandaria | 35 | 21:00 | 92 | Kodda | 222 | 12:00 | 158 | SSM | 5 | 00:00
27 | Bhangura | 27 | 13:00 | 93 | Kulaura | 29 | 13:00 | 159 | Saidpur | 94 | 12:00
28 | Bheramara(GK) | 41 | 18:30 | 94 | Kurigram | 62 | 08:00 | 160 | Satkhira | 93 | 08:00
29 | Bhulta | 181 | 02:00 | 95 | Kushtia | 108 | 13:00 | 161 | Satmasjid | 77 | 13:00
30 | Bog-Sherpur | 54 | 08:00 | 96 | Laksam | 15 | 13:00 | 162 | Savar | 160 | 12:00
31 | Bogura | 116 | 18:30 | 97 | Lakshmipur | 21 | 00:00 | 163 | SevenRings | 16.01 | 20:00
32 | Borhanuddin | 63 | 21:00 | 98 | Lalbag | 56 | 00:00 | 164 | ShahCement | 34 | 09:00
33 | Brahmanbaria | 96 | 13:00 | 99 | Lalmonirhat | 48 | 19:00 | 165 | Shahjadpur | 40 | 07:00
34 | Cantonment | 76 | 13:00 | 100 | MI_Cement | 16.6 | 00:00 | 166 | Shahjibazar | 88 | 18:00
35 | Chandina | 18 | 13:00 | 101 | Madanganj | 34 | 13:00 | 167 | Shahmirpur | 30 | 18:00
36 | Chandpur | 58 | 13:00 | 102 | Madaripur | 75 | 13:00 | 168 | Shariatpur | 61 | 13:00
37 | Chandraghona | 28 | 18:00 | 103 | Madartek | 62 | 13:00 | 169 | Sherpur | 144 | 18:00
38 | Chapai | 59 | 11:00 | 104 | Madunaghat | 40 | 12:00 | 170 | Shikalbaha | 24 | 00:00
39 | Charsaidpur | 41 | 18:00 | 105 | Magura | 47 | 18:30 | 171 | Shitalakhya | 48.5 | 13:00
40 | Chauddagram | 57 | 13:00 | 106 | Mahasthangarh | 54 | 08:00 | 172 | Sholosohor | 32 | 12:00
41 | Chhatak | 26 | 13:00 | 107 | Maijdee | 31 | 19:00 | 173 | Shyampur | 146 | 00:00
42 | Chowmuhani | 105 | 18:00 | 108 | Manikganj | 83 | 11:00 | 174 | Siddhirganj | 114 | 12:00
43 | Chuadanga | 73 | 12:00 | 109 | Maniknagar | 43 | 13:00 | 175 | Sirajganj | 72 | 08:00
44 | Coxsbazar | 118 | 13:00 | 110 | Matarbari | 40 | 18:30 | 176 | Sonargaon | 128 | 01:00
45 | Cumilla(N) | 98 | 09:00 | 111 | Matuail | 49 | 12:00 | 177 | Sreemongol | 56 | 12:00
46 | Cumilla(S) | 132 | 13:00 | 112 | Metrorail_Motijheel | 20 | 20:00 | 178 | Sreepur | 88 | 19:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 0 | 00:00 | 179 | Srinagar | 35.8 | 13:00
48 | Daudkandi | 97 | 13:00 | 114 | Millgate | 68 | 12:00 | 180 | Sunamganj | 40 | 12:00
49 | DhakaUniversity | 38 | 12:00 | 115 | Mirpur | 114 | 13:00 | 181 | Sylhet | 42 | 13:00
50 | Dhamrai | 82 | 12:00 | 116 | Mirsorai | 45 | 16:00 | 182 | Sylhet-132 | 71 | 13:00
51 | Dhanmondi | 72 | 13:00 | 117 | Mirzapur | 46 | 18:00 | 183 | TK | 16.5 | 19:30
52 | Dohazari | 71 | 18:00 | 118 | Mithapukur | 54 | 08:00 | 184 | Tangail | 144 | 07:00
53 | Faridpur | 100 | 18:30 | 119 | Modern | N/A | N/A | 185 | Taraganj | 19 | 09:00
54 | Fatullah | 77 | 10:00 | 120 | Mogbazar | 55.7 | 13:00 | 186 | Tasnim | 24 | 02:00
55 | Fenchuganj | 23 | 12:00 | 121 | Mongla | 35 | 00:00 | 187 | Thakurgaon | 77 | 13:00
56 | Feni | 85 | 13:00 | 122 | Motijheel | 31 | 13:00 | 188 | Tongi | 117 | 12:00
57 | GPH | 86 | 23:00 | 123 | Muktagacha | 37 | 13:00 | 189 | Ullahpara | 26 | 18:30
58 | Ghatail | 74 | 08:00 | 124 | Munshiganj | 75 | 13:00 | 190 | Ullon | 55 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 25 | 19:30 | 191 | Uttara | 55 | 12:00
60 | Ghorashal-230 | 82 | 00:00 | 126 | Mymensingh | 172 | 12:00 | 192 | UttaraNew | 28 | 13:00
61 | Goalpara | 30 | 13:00 | 127 | Naogaon | 114 | 09:00 | 193 | Zigatola | 60 | 13:00
62 | Gollamari | 80 | 13:00 | 128 | Narail | 42 | 19:00
63 | Gopalganj | 76 | 18:30 | 129 | Narinda | 37 | 13:00
64 | Gulshan | 64 | 13:00 | 130 | Narshingdi | 139 | 20:00
65 | Halishahar | 57 | 18:30 | 131 | Natore | 106 | 13:00
66 | HaripurSBU | 115 | 04:00 | 132 | Nawabganj | 34.8 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 06-02-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 9850 | 0 |  | 9850
1:00 | 9207 | 0 |  | 9207
2:00 | 8835 | 0 |  | 8835
3:00 | 8400 | 0 |  | 8400
4:00 | 8157 | 0 |  | 8157
5:00 | 8086 | 0 |  | 8086
6:00 | 8402 | 0 |  | 8402
7:00 | 8867.93 | 0 |  | 8867.93
8:00 | 9627.49 | 0 |  | 9627.49
9:00 | 10078.92 | 0 |  | 10078.92
10:00 | 9967.75 | 0 |  | 9967.75
11:00 | 10074.08 | 0 |  | 10074.08
12:00 | 10859.35 | 0 |  | 10859.35
13:00 | 11451.84 | 0 |  | 11451.84
14:00 | 9719.44 | 0 |  | 9719.44
15:00 | 9092.13 | 0 |  | 9092.13
16:00 | 8949.16 | 0 |  | 8949.16
17:00 | 9036.08 | 0 |  | 9036.08
18:00 | 9924.45 | 0 |  | 9924.45
19:00 | 10669.52 | 0 |  | 10669.52
19:30 | 10531 | 0 |  | 10531
20:00 | 10553.35 | 0 |  | 10553.35
21:00 | 10434.91 | 0 |  | 10434.91
22:00 | 10122.98 | 0 |  | 10122.98
23:00 | 9561.62 | 0 |  | 9561.62
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 06-02-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5258 | 4592 | 9850 | DAILY GENERATION CURVE
00:30 | 5159.5 | 4369 | 9528.5
01:00 | 5061 | 4146 | 9207 | 06-02-2026
01:30 | 5053.5 | 3967.5 | 9021
02:00 | 5046 | 3789 | 8835
02:30 | 4933.5 | 3684 | 8617.5
03:00 | 4821 | 3579 | 8400
03:30 | 4713.5 | 3565 | 8278.5
04:00 | 4606 | 3551 | 8157
04:30 | 4591.5 | 3530 | 8121.5
05:00 | 4577 | 3509 | 8086
05:30 | 4659 | 3585 | 8244
06:00 | 4741 | 3661 | 8402
06:30 | 4883.755 | 3751.21 | 8634.965
07:00 | 5026.51 | 3841.42 | 8867.93
07:30 | 5112.43 | 4135.28 | 9247.71
08:00 | 5198.35 | 4429.14 | 9627.49
08:30 | 5244.855 | 4608.35 | 9853.205
09:00 | 5291.36 | 4787.56 | 10078.92
09:30 | 5252.53 | 4770.805 | 10023.335
10:00 | 5213.7 | 4754.05 | 9967.75
10:30 | 5224.25 | 4796.665 | 10020.915
11:00 | 5234.8 | 4839.28 | 10074.08
11:30 | 5428.345 | 5038.37 | 10466.715
12:00 | 5621.89 | 5237.46 | 10859.35
12:30 | 5812.89 | 5342.705 | 11155.595
13:00 | 6003.89 | 5447.95 | 11451.84
13:30 | 5442.585 | 5143.055 | 10585.64
14:00 | 4881.28 | 4838.16 | 9719.44
14:30 | 4714.965 | 4690.82 | 9405.785
15:00 | 4548.65 | 4543.48 | 9092.13
15:30 | 4515.625 | 4505.02 | 9020.645
16:00 | 4482.6 | 4466.56 | 8949.16
16:30 | 4575.235 | 4417.385 | 8992.62
17:00 | 4667.87 | 4368.21 | 9036.08
17:30 | 5047.935 | 4432.33 | 9480.265
18:00 | 5428 | 4496.45 | 9924.45
18:30 | 5602.2 | 4694.785 | 10296.985
19:00 | 5776.4 | 4893.12 | 10669.52
19:30 | 5612 | 4919 | 10531
20:00 | 5600.6 | 4952.75 | 10553.35
20:30 | 5537.3 | 4956.83 | 10494.13 |  | Executive Engineer
21:00 | 5474 | 4960.91 | 10434.91 |  | Network Operation Division
21:30 | 5323.25 | 4955.695 | 10278.945
22:00 | 5172.5 | 4950.48 | 10122.98
22:30 | 4968.75 | 4873.55 | 9842.3
23:00 | 4765 | 4796.62 | 9561.62

## En-Curve
QF-LDC-12
Date | 06-02-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3120 | 1451 | 898 | 0 | 104 | 770 | 40 | 3424 | 0 | 0 | 24 | 0 | 0 | 19 | 0 | DAILY ENERGY CURVE
00:30 | 3104.5 | 1408.5 | 898 | 0 | 102 | 695.5 | 40 | 3243 | 0 | 0 | 12 | 0 | 0 | 25 | 0 | 06-02-2026
01:00 | 3089 | 1366 | 898 | 0 | 100 | 621 | 40 | 3062 | 0 | 0 | 0 | 0 | 0 | 31 | 0
01:30 | 3087 | 1366 | 898 | 0 | 98 | 569 | 40 | 2932 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | Energy Generated | 233.1407 |  | MKWHr
02:00 | 3085 | 1366 | 898 | 0 | 96 | 517 | 40 | 2802 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3083 | 1334 | 898 | 0 | 95 | 466 | 40 | 2667 | 0 | 0 | 0 | 0 | 0 | 34.5 | 0 | Total Energy Requirement | 233.1407 |  | MKWHr
03:00 | 3081 | 1302 | 898 | 0 | 94 | 415 | 40 | 2532 | 0 | 0 | 0 | 0 | 0 | 38 | 0
03:30 | 2993 | 1307 | 898 | 0 | 91 | 417 | 40 | 2493.5 | 0 | 0 | 0 | 0 | 0 | 39 | 0
04:00 | 2905 | 1312 | 898 | 0 | 88 | 419 | 40 | 2455 | 0 | 0 | 0 | 0 | 0 | 40 | 0
04:30 | 2862 | 1334 | 898 | 0 | 84 | 419.5 | 40 | 2438.5 | 0 | 0 | 0 | 0 | 0 | 45.5 | 0
05:00 | 2819 | 1356 | 898 | 0 | 80 | 420 | 40 | 2422 | 0 | 0 | 0 | 0 | 0 | 51 | 0
05:30 | 2882.5 | 1423.5 | 897.5 | 0 | 83 | 419.5 | 40 | 2444 | 0 | 0 | 5 | 0 | 0 | 49 | 0
06:00 | 2946 | 1491 | 897 | 0 | 86 | 419 | 40 | 2466 | 0 | 0 | 10 | 0 | 0 | 47 | 0
06:30 | 2952 | 1545 | 897.5 | 0 | 85 | 418.5 | 40 | 2618 | 9.965 | 0 | 22.5 | 0 | 0 | 46.5 | 0
07:00 | 2958 | 1599 | 898 | 0 | 84 | 418 | 40 | 2770 | 19.93 | 0 | 35 | 0 | 0 | 46 | 0
07:30 | 2997 | 1500.75 | 898 | 0 | 87 | 496.5 | 40 | 3014.5 | 100.46 | 17.5 | 55 | 0 | 0 | 41 | 0
08:00 | 3036 | 1402.5 | 898 | 0 | 90 | 575 | 40 | 3259 | 180.99 | 35 | 75 | 0 | 0 | 36 | 0
08:30 | 3065.5 | 1403.5 | 898 | 0 | 95 | 574 | 40 | 3363.5 | 275.205 | 35 | 76.5 | 0 | 0 | 27 | 0
09:00 | 3095 | 1404.5 | 898 | 0 | 100 | 573 | 40 | 3468 | 369.42 | 35 | 78 | 0 | 0 | 18 | 0
09:30 | 3045.5 | 1362.5 | 898 | 0 | 101 | 572 | 40 | 3424 | 447.835 | 35 | 78.5 | 0 | 0 | 19 | 0
10:00 | 2996 | 1320.5 | 898 | 0 | 102 | 571 | 40 | 3380 | 526.25 | 35 | 79 | 0 | 0 | 20 | 0
10:30 | 2980 | 1328.5 | 898 | 0 | 100 | 572 | 40 | 3314.5 | 593.415 | 39 | 132 | 0 | 0 | 23.5 | 0
11:00 | 2964 | 1336.5 | 898 | 0 | 98 | 573 | 40 | 3249 | 660.58 | 43 | 185 | 0 | 0 | 27 | 0
11:30 | 3017 | 1362.75 | 898 | 0 | 103 | 653 | 40 | 3350.5 | 683.115 | 51.85 | 283 | 0 | 0 | 24.5 | 0
12:00 | 3070 | 1389 | 898 | 0 | 108 | 733 | 40 | 3452 | 705.65 | 60.7 | 381 | 0 | 0 | 22 | 0
12:30 | 3008 | 1414.5 | 898 | 0 | 119 | 746.5 | 40 | 3610 | 703.295 | 69.2 | 526.6 | 0 | 0 | 20.5 | 0
13:00 | 2946 | 1440 | 898 | 0 | 130 | 760 | 40 | 3768 | 700.94 | 77.7 | 672.2 | 0 | 0 | 19 | 0
13:30 | 2807 | 1333 | 898 | 0 | 121 | 712 | 40 | 3548 | 660.84 | 60.7 | 386.6 | 0 | 0 | 18.5 | 0
14:00 | 2668 | 1226 | 898 | 0 | 112 | 664 | 40 | 3328 | 620.74 | 43.7 | 101 | 0 | 0 | 18 | 0
14:30 | 2697.5 | 1219.5 | 898 | 0 | 106 | 665.5 | 40 | 3110.5 | 546.585 | 34.7 | 66.5 | 0 | 0 | 21 | 0
15:00 | 2727 | 1213 | 898 | 0 | 100 | 667 | 40 | 2893 | 472.43 | 25.7 | 32 | 0 | 0 | 24 | 0
15:30 | 2776 | 1244 | 898 | 0 | 101 | 665.5 | 40 | 2850 | 366.445 | 25.7 | 32 | 0 | 0 | 22 | 0
16:00 | 2825 | 1275 | 898 | 0 | 102 | 664 | 40 | 2807 | 260.46 | 25.7 | 32 | 0 | 0 | 20 | 0
16:30 | 2923.5 | 1287.5 | 898 | 0 | 104 | 664.085 | 40 | 2813 | 171.185 | 21.85 | 48 | 0 | 0 | 21.5 | 0
17:00 | 3022 | 1300 | 898 | 0 | 106 | 664.17 | 40 | 2819 | 81.91 | 18 | 64 | 0 | 0 | 23 | 0
17:30 | 3011.5 | 1313 | 898 | 0 | 111 | 712.81 | 40 | 2863.5 | 40.955 | 102 | 369.5 | 0 | 0 | 18 | 0
18:00 | 3001 | 1326 | 898 | 0 | 116 | 761.45 | 40 | 2908 | 0 | 186 | 675 | 0 | 0 | 13 | 0
18:30 | 3028.5 | 1390 | 898 | 0 | 112 | 762.785 | 40 | 3090.5 | 0 | 127.5 | 834.2 | 0 | 0 | 13.5 | 0
19:00 | 3056 | 1454 | 898 | 0 | 108 | 764.12 | 40 | 3273 | 0 | 69 | 993.4 | 0 | 0 | 14 | 0
19:30 | 3192 | 1497 | 898 | 0 | 114 | 756 | 40 | 3425 | 0 | 17 | 582 | 0 | 0 | 10 | 0
20:00 | 3273 | 1467 | 898 | 0 | 112 | 755.75 | 40 | 3451 | 0 | 17 | 530.6 | 0 | 0 | 9 | 0
20:30 | 3378.5 | 1467 | 898 | 0 | 115 | 756.83 | 40 | 3452.5 | 0 | 8.5 | 369.8 | 0 | 0 | 8 | 0
21:00 | 3484 | 1467 | 898 | 0 | 118 | 757.91 | 40 | 3454 | 0 | 0 | 209 | 0 | 0 | 7 | 0
21:30 | 3365.5 | 1475.75 | 898 | 0 | 117 | 757.195 | 40 | 3458.5 | 0 | 0 | 159 | 0 | 0 | 8 | 0
22:00 | 3247 | 1484.5 | 898 | 0 | 116 | 756.48 | 40 | 3463 | 0 | 0 | 109 | 0 | 0 | 9 | 0
22:30 | 3105 | 1469.75 | 898 | 0 | 115 | 758.05 | 40 | 3390.5 | 0 | 0 | 54.5 | 0 | 0 | 11.5 | 0
23:00 | 2963 | 1455 | 898 | 0 | 114 | 759.62 | 40 | 3318 | 0 | 0 | 0 | 0 | 0 | 14 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 06-02-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 421 | 05:00 | 406 | 11:00 | Madunaghat | 415 | 05:00 | 407 | 00:00
Amtali | 425 | 05:00 | 416 | 12:00 | Meghnaghat | 425 | 04:00 | 411 | 10:00
Ashuganj | 409 | 4:00 | 395 | 12:00 | Payra | 425 | 04:00 | 405 | 08:00
Bhulta | 401 | 04:00 | 387 | 12:00 | Rahanpur | 425 | 04:00 | 407 | 08:00
Bibiana | 423 | 05:00 | 412 | 12:00 | Rampal | 419 | 05:00 | 406 | 12:00
BIPTC | 405 | 02:00 | 391 | 10:00
Bogura | 424 | 05:00 | 402 | 08:00
Gopalganj | 423 | 03:00 | 410 | 12:00
Kaliakoir | 418 | 05:00 | 401 | 12:00
Korerhat | 424 | 18:00 | 413 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 244 | 04:00 | 234 | 12:00 | Jhenaidah | 242 | 04:00 | 229 | 13:00
AKSML | 239 | 05:00 | 233 | 10:00 | Kachua | 243 | 18:00 | 237 | 10:00
Aminbazar | 244 | 05:00 | 235 | 10:00 | Kaliakoir | 243 | 05:00 | 234 | 10:00
Ashuganj | 239 | 03:00 | 230 | 12:00 | Keranigonj | 242 | 18:00 | 232 | 12:00
Ashuganj-400 | 239 | 03:00 | 230 | 12:00 | Khulna(S) | 247 | 04:00 | 235 | 12:00
Baghabari | 243 | 06:00 | 235 | 07:00 | Korerhat | 241 | 04:00 | 234 | 11:00
Barapukuria | 234 | 05:00 | 216 | 09:00 | Madunaghat | 239 | 18:00 | 233 | 11:00
Barapukuria-230 | 234 | 05:00 | 216 | 09:00 | Madunaghat-400 | 239 | 18:00 | 233 | 00:00
Barishal | 240 | 04:00 | 232 | 13:00 | Maniknagar | 240 | 04:00 | 231 | 12:00
Bheramara | 241 | 04:00 | 230 | 09:00 | Meghnaghat | 245 | 18:00 | 237 | 12:00
Bhulta | 241 | 04:00 | 232 | 12:00 | Meghnaghat-400 | 241 | 18:00 | 232 | 11:00
Bibiana | 247 | 04:00 | 237 | 12:00 | Mirsorai | 241 | 18:00 | 234 | 00:00
BIPTC | 245 | 04:00 | 231 | 09:00 | Rajshahi | 242 | 05:00 | 230 | 09:00
Bogura | 247 | 04:00 | 232 | 08:00 | Rampal | 242 | 04:00 | 233 | 12:00
Bogura-400 | 246 | 04:00 | 232 | 08:00 | Rampur | N/A | N/A | N/A | N/A
Borhanuddin | 240 | 05:00 | 235 | 13:00 | Rampura | 240 | 04:00 | 231 | 12:00
BSRM | 241 | 04:00 | 234 | 11:00 | Shikalbaha | 238 | 18:00 | 231 | 10:00
Chowmuhani | N/A | N/A | N/A | N/A | Shyampur | 241 | 18:00 | 231 | 12:00
Cumilla(N) | 240 | 18:00 | 232 | 12:00 | Siddhirganj | 240 | 23:00 | 234 | 09:00
Faridpur | 239 | 04:00 | 231 | 12:00 | Sirajgonj | 246 | 02:00 | 240 | 08:00
Fenchuganj | 246 | 18:00 | 241 | 00:00 | Sreepur | 236 | 04:00 | 226 | 09:00
Feni | 242 | 04:00 | 235 | 10:00 | Tongi | 239 | 18:30 | 230 | 11:00
Ghorashal | 240 | 00:00 | 235 | 03:00
Ghorashal-230 | 239 | 05:00 | 229 | 11:00
Gopalganj | 238 | 04:00 | 230 | 12:00
GPH | 240 | 18:00 | 233 | 11:00
Haripur | 241 | 04:00 | 233 | 12:00
Hasnabad | 241 | 18:00 | 232 | 12:00
Hathazari | 238 | 19:00 | 229 | 11:00
Ishurdi | 245 | 04:00 | 235 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 04:00 | 127 | 12:00 | Mahasthangarh | 137 | 04:00 | 126 | 08:00
Agargaon | 138 | 04:00 | 132 | 12:00 | Maijdee | 136 | 04:00 | 132 | 00:00
Agrabad | 138 | 03:00 | 133 | 11:00 | Manikganj | 130 | 04:00 | 124 | 12:00
AKS | 136 | 18:00 | 132 | 11:00 | Maniknagar | 139 | 03:00 | 133 | 12:00
Aminbazar | 141 | 18:00 | 135 | 00:00 | Matarbari | 132 | 04:00 | 125 | 19:30
Amnura | 140 | 03:00 | 133 | 08:00 | Matuail | 138 | 18:00 | 133 | 12:00
Ashuganj | 140 | 02:00 | 136 | 12:00 | Metrorail_Motijheel | 139 | 04:00 | 134 | 11:00
Bagerhat | 136 | 05:00 | 127 | 12:00 | Metrorail_Uttara | 132 | 03:00 | 126 | 12:00
Bajitpur | 135 | 02:00 | 129 | 09:00 | Millgate | 135 | 08:00 | 126 | 12:00
Bakerganj | 139 | 06:00 | 136 | 01:00 | Mirpur | 140 | 18:00 | 134 | 10:00
Bakulia | 139 | 05:00 | 134 | 11:00 | Mirzapur | 136 | 05:00 | 130 | 08:00
Banani | 133 | 03:00 | 126 | 12:00 | Mithapukur | 136 | 04:00 | 122 | 08:00
Bangabhaban | 139 | 03:00 | 133 | 12:00 | MI_Cement | 136 | 05:00 | 129 | 12:00
Barapukuria | 135 | 05:00 | 124 | 09:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 140 | 04:00 | 136 | 11:00 | Mogbazar | 135 | 03:00 | 128 | 12:00
Barishal | 140 | 03:00 | 136 | 12:00 | Mongla | 135 | 05:00 | 126 | 12:00
Barishal-230 | 141 | 03:00 | 135 | 12:00 | Motijheel | 139 | 03:00 | 133 | 12:00
Baroaulia | 140 | 18:00 | 134 | 16:00 | Muktagacha | 133 | 12:00 | 127 | 07:00
Baroirhat | 138 | 18:00 | 134 | 11:00 | Munshiganj | 137 | 18:00 | 131 | 00:00
Bashundhara | 134 | 05:00 | 126 | 13:00 | Muradnagar | 138 | 04:00 | 133 | 11:00
BashundharaCement | 138 | 18:00 | 132 | 00:00 | Mymensingh | 134 | 11:00 | 118 | 09:00
Beanibazar | 134 | 02:00 | 130 | 13:00 | Naogaon | 135 | 03:00 | 124 | 09:00
Benapole | 137 | 04:00 | 119 | 13:00 | Narail | 139 | 04:00 | 127 | 13:00
Bhaluka | 131 | 01:00 | 124 | 12:00 | Narinda | 139 | 03:00 | 133 | 12:00
Bhandaria | 139 | 05:00 | 134 | 12:00 | Narshingdi | 136 | 18:00 | 129 | 00:00
Bhangura | 140 | 03:00 | 134 | 08:00 | Natore | 139 | 06:00 | 132 | 08:00
Bheramara | 140 | 03:00 | 136 | 08:00 | Nawabganj | 136 | 05:00 | 129 | 12:00
Bheramara(GK) | 140 | 04:00 | 136 | 09:00 | Netrakona | 125 | 04:00 | 112 | 09:00
Bhulta | 132 | 18:00 | 125 | 00:00 | New | 134 | 06:00 | 127 | 11:00
Bog-Sherpur | 139 | 03:00 | 130 | 08:00 | Niamatpur | 141 | 05:00 | 135 | 09:00
Bogura | 139 | 05:00 | 130 | 08:00 | Noapara | 137 | 06:00 | 121 | 13:00
Bogura-230 | 140 | 04:00 | 130 | 08:00 | Pabna | 141 | 04:00 | 135 | 08:00
Brahmanbaria | 134 | 05:00 | 129 | 13:00 | Palashbari | 134 | 02:00 | 121 | 08:00
Cantonment | 138 | 04:00 | 131 | 12:00 | Panchagarh | 138 | 19:00 | 123 | 08:00
Chandina | 140 | 04:00 | 135 | 12:00 | Patiya | 139 | 05:00 | 134 | 11:00
Chandpur | 141 | 18:30 | 135 | 09:00 | Patuakhali | 138 | 00:00 | 136 | 07:00
Chandraghona | 140 | 03:00 | 136 | 12:00 | Payra | 140 | 04:00 | 137 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 140 | 06:00 | 134 | 08:00 | PHP | 138 | 06:00 | 133 | 12:00
Charsaidpur | 138 | 18:00 | 132 | 11:00 | Postogola | 137 | 18:00 | 130 | 12:00
Chauddagram | 138 | 04:00 | 133 | 11:00 | Purbachal | 134 | 04:00 | 126 | 12:00
Chhatak | 135 | 03:00 | 128 | 12:00 | Purbasadipur | 134 | 04:00 | 118 | 08:00
Chowmuhani | 135 | 18:00 | 131 | 00:00 | Rahanpur | 142 | 05:00 | 136 | 08:00
Chuadanga | 139 | 04:00 | 127 | 08:00 | Rahanpur-400 | 143 | 04:00 | 136 | 08:00
Coxsbazar | 130 | 03:00 | 124 | 13:00 | Rahim | 137 | 05:00 | 133 | 11:00
Cumilla(N) | 140 | 18:00 | 134 | 12:00 | Rajbari | 139 | 04:00 | 133 | 12:00
Cumilla(S) | 140 | 04:00 | 124 | 10:00 | Rajendrapur | 134 | 04:00 | 125 | 12:00
Daganbhuiyan | 137 | 18:00 | 132 | 11:00 | Rajshahi | 138 | 03:00 | 133 | 09:00
Daudkandi | 136 | 05:00 | 130 | 11:00 | Rajshahi-230 | 140 | 05:00 | 133 | 08:00
DhakaUniversity | 133 | 02:00 | 127 | 12:00 | Ramganj | 137 | 17:00 | 132 | 11:00
Dhamrai | 139 | 18:00 | 132 | 09:00 | Rampur | 138 | 05:00 | 134 | 10:00
Dhanmondi | 139 | 18:00 | 134 | 11:00 | Rampura | 133.1 | 06:00 | 127 | 12:00
Dohazari | 135 | 05:00 | 131 | 12:00 | Rangamati | 139 | 04:00 | 135 | 10:00
Faridpur | 138 | 04:00 | 135 | 00:00 | Rangpur | 135 | 03:00 | 125 | 08:00
Fatullah | 140 | 18:00 | 129 | 12:00 | Ruppur | 140 | 6:00 | 137 | 08:00
Fenchuganj | 139 | 01:00 | 136 | 00:00 | Saidpur | 134 | 06:00 | 121 | 08:00
Feni | 136 | 18:30 | 130 | 13:00 | Satkhira | 136 | 05:00 | 127 | 08:00
Feni-230 | 136 | 04:00 | 132 | 11:00 | Satmasjid | 138 | 04:00 | 132 | 11:00
Ghatail | 133 | 20:00 | 124 | 07:00 | Savar | 140 | 18:00 | 133 | 09:00
Ghorashal | 143 | 00:00 | 139 | 09:00 | SevenRings | 144 | 05:00 | 138 | 12:00
Goalpara | 139 | 04:00 | 128 | 13:00 | ShahCement | 138 | 18:00 | 132 | 11:00
Gollamari | 138 | 04:00 | 131 | 12:00 | Shahjadpur | 142 | 04:00 | 136 | 18:30
Gopalganj | 141 | 04:00 | 134 | 12:00 | Shahjibazar | 134 | 05:00 | 131 | 00:00
Gopalganj-400 | 145 | 04:00 | 139 | 09:00 | Shahmirpur | 138 | 06:00 | 136 | 00:00
Gulshan | 132 | 04:00 | 126 | 12:00 | Shariatpur | 143 | 04:00 | 136 | 13:00
Halishahar | 139 | 04:00 | 134 | 00:00 | Sherpur | 126 | 22:00 | 113 | 07:00
Haripur | 138 | 04:00 | 133 | 09:00 | Shikalbaha | 128 | 03:00 | 124 | 00:00
HaripurSBU | 138 | 04:00 | 134 | 00:00 | Shikalbaha-230 | 140 | 05:00 | 136 | 13:00
Hasnabad | 137 | 04:00 | 130 | 12:00 | Shitalakhya | 136 | 05:00 | 129 | 12:00
Hathazari | 140 | 18:30 | 136 | 00:00 | Sholosohor | 139 | 04:00 | 135 | 11:00
Hatirjheel | 133 | 04:00 | 127 | 12:00 | Shyampur | 139 | 19:00 | 132 | 11:00
Ishurdi | 143 | 04:00 | 138 | 08:00 | Shyampur-230 | 140 | 18:00 | 134 | 00:00
Jaldhaka | 132 | 14:00 | 117 | 08:00 | Siddhirganj | 138 | 18:00 | 133 | 12:00
Jamalpur | 130 | 22:00 | 118 | 07:00 | Sirajganj | 138 | 03:00 | 132 | 07:00
Jashore | 136 | 02:00 | 121 | 13:00 | Sonargaon | 136 | 19:00 | 131 | 12:00
Jhenaidah | 140 | 05:00 | 129 | 13:00 | Sreemongol | 136 | 03:00 | 132 | 12:00
Jhenaidah-230 | 141 | 05:00 | 130 | 13:00 | Sreepur | 136 | 04:00 | 127 | 09:00
Joydebpur | 142 | 06:00 | 136 | 12:00 | Srinagar | 136 | 04:00 | 130 | 12:00
Joypurhat | 135 | 04:00 | 122 | 08:00 | SSM | 142 | 18:30 | 140 | 00:00
Juldah | 137 | 16:00 | 135 | 00:00 | Sunamganj | 134 | 05:00 | 127 | 12:00
Kabirpur | 141 | 18:00 | 125 | 11:00 | Sylhet | 136 | 04:00 | 131 | 12:00
Kachua | 139 | 18:00 | 135 | 10:00 | Sylhet-132 | 136 | 03:00 | 132 | 12:00
Kaliakoir | 142 | 18:00 | 135 | 08:00 | Tangail | 132 | 04:00 | 125 | 07:00
Kaliganj | N/A | N/A | N/A | N/A | Taraganj | 133 | 06:00 | 119 | 08:00
Kallyanpur | 141 | 18:00 | 133 | 10:00 | Tasnim | 137 | 18:00 | 131 | 11:00
Kalurghat | 139 | 04:00 | 136 | 00:00 | Thakurgaon | 137 | 04:00 | 121 | 08:00
Kamrangirchar | 137 | 05:00 | 129 | 12:00 | TK | 140 | 18:00 | 136 | 00:00
Kaptai | 140 | 5:00 | 138 | 1:00 | Tongi | 134 | 04:00 | 127 | 11:00
Kasba | 138 | 04:00 | 132 | 11:00 | Ullahpara | 140 | 03:00 | 133 | 08:00
Kazla | 139 | 05:00 | 133 | 12:00 | Ullon | 134 | 04:00 | 127 | 12:00
Keranigonj | 136 | 04:00 | 130 | 12:00 | Uttara | 133 | 04:00 | 125 | 12:00
Khagrachori | 139 | 05:00 | 135 | 10:00 | UttaraNew | 132 | 03:00 | 126 | 12:00
Khulna | 138 | 04:00 | 129 | 13:00 | Zigatola | 136 | 04:00 | 130 | 12:00
Khulna(S) | 139 | 05:00 | 131 | 12:00
Khulshi | 137 | 05:00 | 133 | 11:00
Kishoreganj | 134 | 06:00 | 124 | 13:00
Kodda | 138 | 18:00 | 128 | 12:00
KSRM | 139 | 04:00 | 135 | 11:00
Kulaura | 138 | 06:00 | 135 | 11:00
Kurigram | 130 | 11:00 | 116 | 08:00
Kushtia | 139 | 04:00 | 134 | 08:00
Laksam | 140 | 18:00 | 135 | 09:00
Lakshmipur | 136 | 18:00 | 132 | 00:00
Lalbag | 135 | 03:00 | 131 | 00:00
Lalmonirhat | 130 | 05:00 | 118 | 08:00
Madanganj | 138 | 18:00 | 132 | 00:00
Madaripur | 142 | 04:00 | 137 | 13:00
Madartek | 133 | 04:00 | 127 | 10:00
Madunaghat | 139 | 18:00 | 136 | 00:00
Magura | 139 | 05:00 | 128 | 09:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division