## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 15-02-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-02-2026 | during | 15-02-2026 | during | 15-02-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 230 | 0 | 230 | 230 | 200 | 200 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 8 | 16 | 97.7 | 97.7 | 0 | 10 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 412 | 306 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 15 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 327 | 335 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 31 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 45 | 78 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23 | 20.5 | 33 | 33 | 23 | 23 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 95 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 43 | 70 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 51 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 81 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 34 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 18 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 560 | 545 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 52 | 160 | 160 | 160 | 160 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1772 | 1814.5 | 5362.22 | 5331.22 | 2839.05 | 2896.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | U#1 Under maintenance, U#2 Running
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 0 | 0 | 0 | 0 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 220 | 221 | 225 | 225 | 225 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 47 | 105 | 105 | 95 | 95 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 30 | 16 | 16 | 10 | 10 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 34 | 34 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 50 | 100 | 100 | 25 | 50 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 8 | 5 | 12 | 40 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 4 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.49 | 0 | 3.49 | 0 | 3.49 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 32 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 17 | 54.36 | 54.36 | 17 | 35 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 50 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 51 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 45 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 833 | 1157 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 6 | 8 | 3 | 30 | 3 | 30 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 265 | 417 | 675 | 675 | 675 | 675 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1387.49 | 2267 | 3454.35 | 3464.86 | 2933.99 | 2980.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 115 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 325 | 270 | 353.35 | 353.35 | 317 | 317 | FGMO
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 240 | 350 | 318.81 | 318.81 | 318.81 | 318.81 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 42 | 42 | 46.7 | 46.7 | 43 | 43 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 40 | 10 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 135 | 8 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 50 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 31 | 42 | 42 | 32 | 32 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 | 110 | 110 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 51 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 28 | 126 | 0 | 0 | 0 | 0 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 15 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 14 | 24.5 | 24.5 | 13 | 13 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 34 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 46 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 67 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 939 | 1213 | 2509.56 | 2444.56 | 2019.01 | 1954.01
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-02-2026 | during | 15-02-2026 | during | 15-02-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 155 | 111 | 157.5 | 157.5 | 35 | 35 | GT-4 U/M
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 19 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 56 | 58 | 60 | 60 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 44.28 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 282.28 | 211 | 358.1 | 314 | 182.1 | 138
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 30 | 30 | 30 | 0 | 0 | plant availability zero
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 23 | 23 | 53 | 53 | 53 | 53 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 162 | 154 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 83 | 86 | 86 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 99 | 100 | 100 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 20 | 25 | 25 | 20 | 21 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 391 | 340 | 385 | 385 | 292 | 292 | -
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1164 | 1089 | 1213.01 | 1213.01 | 1032 | 1033
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 901 | 712 | 0 | 0 | 0 | 0 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 8 | 44 | 44 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 40 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 398 | 340 | 410 | 410 | 370 | 370 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 90.58 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 525 | 563 | 617.1 | 617.1 | 617.1 | 617.1 | U#1 Under Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1914.58 | 1663 | 1981.1 | 1891.1 | 1184.2 | 1094.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 40 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 130 | 130 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 560 | 530 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 44 | 150 | 150 | 15 | 150 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 285 | 268 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.58 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2700.36 | 1195.58 | 1232 | 2003.32 | 2002.32 | 1868.32 | 2002.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 51.08 | 0 | 50 | 0 | 50 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 197 | 180 | 214 | 214 | 214 | 214 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 328 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 27 | 27 | 28 | 28 | Machine problem and fuel shortage
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 50 | 50 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 38 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.39 | 0 | 5.45 | 0 | 5.45 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1232.25 | 1460.27 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 59.4 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 115 | 0 | 100 | 0.01 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2074.12 | 2081.27 | 3107.32 | 2890.88 | 2576.94 | 2360.5
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 56 | 56 | 55 | 55 | 56 | 56 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 49 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.8 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 29 | 0 | 29 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 159 | 0 | 160 | 0 | 160 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 284.8 | 155 | 497.2 | 303 | 478.2 | 284
System Total |  |  |  |  | 28823.2 | 28385.703 | 11013.85 | 11725.77 | 20486.18 | 19854.95 | 15113.81 | 14742.58
Forecast Scenario (15-02-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8800 |  | 0 |  | 8800
|  |  |  | 1:00 | 8500 |  | 0 |  | 8500
|  |  |  | 2:00 | 7800 |  | 0 |  | 7800
|  |  |  | 3:00 | 7700 |  | 0 |  | 7700
|  |  |  | 4:00 | 7500 |  | 0 |  | 7500
|  |  |  | 5:00 | 7300 |  | 0 |  | 7300
|  |  |  | 6:00 | 7900 |  | 0 |  | 7900
|  |  |  | 7:00 | 8800 |  | 0 |  | 8800
|  |  |  | 8:00 | 9800 |  | 0 |  | 9800
|  |  |  | 9:00 | 10400 |  | 0 |  | 10400
|  |  |  | 10:00 | 10300 |  | 0 |  | 10300
|  |  |  | 11:00 | 10300 |  | 0 |  | 10300
|  |  |  | 12:00 | 10920 |  | 0 |  | 10920
|  |  |  | 13:00 | 11310 |  | 0 |  | 11310
|  |  |  | 14:00 | 10790 |  | 0 |  | 10790
|  |  |  | 15:00 | 10310 |  | 0 |  | 10310
|  |  |  | 16:00 | 9990 |  | 0 |  | 9990
|  |  |  | 17:00 | 9900 |  | 0 |  | 9900
|  |  |  | 18:00 | 10730 |  | 0 |  | 10730
|  |  |  | 18:30 | 11150 |  | 0 |  | 11150
|  |  |  | 19:00 | 11510 |  | 0 |  | 11510
|  |  |  | 19:30 | 11190 |  | 0 |  | 11190
|  |  |  | 20:00 | 11000 |  | 0 |  | 11000
|  |  |  | 21:00 | 10880 |  | 0 |  | 10880
|  |  |  | 22:00 | 10380 |  | 0 |  | 10380
|  |  |  | 23:00 | 9800 |  | 0 |  | 9800
Probable Maximum Temperature: |  |  | 28.00°C
Probable Maximum Demand at Day Peak: |  |  | 10920.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11510.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11510.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 232.62 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:19 hrs on 15-02-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 14-02-2026 | [28 empty] | Date: | 14-02-2026 | [28 empty] | Date: | 14-02-2026 | [28 empty] | Date: | 14-02-2026 | [28 empty] | Date: | 14-02-2026 | [17 empty] | Date: | 14-02-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 265 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 405 | 0 | 0 | 87 | 0 | 315 | 330 | 5 | 19 | 0 | 39 | 0 | 104 | 0 | 0 | 14 | 0 | 26 | 0 | 0 | 0 | 310 | 0 | 322 | 30 | 23 | 137 | 0 | 20 | 0 | 5 | 20 | 0 | 0 | 99 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 4303 | 794 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 824.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 130 | 180 | 0 | 0 | 450 | 0 | 3835.23 | 8138.23 | 94
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 265 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 316 | 0 | 0 | 8 | 0 | 335 | 330 | 5 | 5 | 0 | 39 | 0 | 105 | 0 | 0 | 14 | 0 | 30 | 0 | 0 | 0 | 305 | 0 | 319 | 30 | 23 | 139 | 0 | 17 | 0 | 5 | 20 | 0 | 0 | 100 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 3937 | 607 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 824.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 130 | 180 | 0 | 0 | 280 | 0 | 3525.87 | 7462.87 | 93.99
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 265 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 305 | 0 | 0 | 8 | 0 | 315 | 330 | 5 | 5 | 0 | 39 | 0 | 106 | 0 | 0 | 14 | 0 | 20 | 0 | 0 | 0 | 310 | 0 | 319 | 30 | 23 | 139 | 0 | 17 | 0 | 5 | 20 | 0 | 0 | 100 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 3890 | 418 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 824.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 130 | 180 | 0 | 0 | 278 | 0 | 3312.24 | 7202.24 | 93.99
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 265 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 305 | 0 | 0 | 8 | 0 | 340 | 330 | 5 | 5 | 0 | 39 | 0 | 0 | 0 | 0 | 14 | 0 | 16 | 0 | 0 | 0 | 305 | 0 | 319 | 30 | 23 | 139 | 0 | 17 | 0 | 5 | 20 | 0 | 0 | 100 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 3770 | 237 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 823.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 130 | 180 | 0 | 0 | 280 | 0 | 3145.62 | 6915.62 | 93.99
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 265 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 305 | 0 | 0 | 8 | 0 | 280 | 270 | 5 | 5 | 0 | 39 | 0 | 0 | 0 | 0 | 14 | 0 | 20 | 0 | 0 | 0 | 305 | 0 | 319 | 30 | 23 | 138 | 0 | 17 | 0 | 5 | 20 | 0 | 0 | 100 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 3645 | 237 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 825.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 100 | 180 | 0 | 0 | 280 | 0 | 3074.06 | 6719.06 | 93.98
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 265 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 305 | 0 | 0 | 8 | 0 | 300 | 270 | 5 | 5 | 0 | 39 | 0 | 0 | 0 | 0 | 14 | 0 | 22 | 0 | 0 | 0 | 310 | 0 | 319 | 30 | 23 | 138 | 0 | 17 | 0 | 5 | 20 | 0 | 0 | 100 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 3628 | 236 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 827.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 100 | 180 | 0 | 0 | 280 | 0 | 3105.24 | 6733.24 | 93.98
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 265 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 305 | 0 | 0 | 8 | 0 | 335 | 270 | 5 | 5 | 0 | 39 | 0 | 0 | 0 | 0 | 14 | 0 | 24 | 0 | 0 | 0 | 315 | 0 | 319 | 30 | 23 | 142 | 0 | 17 | 0 | 5 | 20 | 0 | 0 | 100 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 3731 | 429 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 0 | 0 | 827.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 100 | 220 | 0 | 0 | 280 | 0 | 3431.88 | 7162.88 | 93.98
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 0 | 0 | 335 | 0 | 0 | 1 | 0 | 7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0.17 | 40 | 0 | 24 | 265 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 412 | 1 | 0 | 70 | 0 | 350 | 355 | 27 | 6 | 0 | 39 | 0 | 0 | 0 | 0 | 14 | 0 | 22 | 0 | 3 | 0 | 325 | 0 | 319 | 30 | 23 | 159 | 0 | 17 | 0 | 72 | 30 | 0 | 0 | 100 | 0 | 18 | 3 | 165 | 0 | 1.28 | 0 | 4417.45 | 618 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 416 | 0 | 0 | 0 | 824.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.67 | 3 | 0 | 0 | 1.5 | 178 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.16 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0.02 | 0 | 228 | 130 | 220 | 0 | 0 | 285 | 0 | 3806.24 | 8223.69 | 93.97
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 413 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 335 | 0 | 0 | 11 | 35 | 7.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0.89 | 40 | 0 | 18 | 265 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 590 | 6 | 0 | 102 | 0 | 345 | 355 | 51 | 33 | 0 | 39 | 0 | 0 | 0 | 0 | 11 | 0 | 18 | 0 | 18 | 0 | 320 | 0 | 319 | 30 | 23 | 162 | 2 | 17 | 0 | 79 | 30 | 0 | 0 | 100 | 0 | 56 | 19 | 164 | 1 | 10.2 | 0 | 4865.59 | 768 | 411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 516 | 0 | 0 | 0 | 1181.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.63 | 30 | 0 | 0 | 18.18 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.6 | 0 | 56 | 0 | 7 | 0 | 0 | 0 | 0 | 1 | 40 | 0.14 | 0 | 282 | 130 | 220 | 0 | 0 | 380 | 0 | 4671.3 | 9536.89 | 93.97
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 415 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 335 | 0 | 0 | 20 | 52 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 1.91 | 40 | 0 | 7 | 265 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 580 | 12 | 0 | 160 | 0 | 315 | 355 | 51 | 49 | 0 | 42 | 0 | 0 | 0 | 0 | 11 | 0 | 22 | 0 | 37 | 0 | 325 | 0 | 322 | 30 | 23 | 161 | 4 | 17 | 0 | 81 | 30 | 0 | 0 | 100 | 0 | 56 | 19 | 162 | 1 | 21.66 | 4 | 5015.57 | 826 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 595 | 0 | 0 | 0 | 1327.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.45 | 62 | 0 | 0 | 35.29 | 192 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 3.21 | 0 | 56 | 17 | 17 | 30 | 0 | 0 | 0 | 2.7 | 86 | 0.3 | 0 | 273 | 130 | 180 | 0 | 0 | 460 | 0 | 5171.96 | 10187.53 | 93.97
10:00 | 0 | 2 | 0 | 0 | 0 | 130 | 0 | 6 | 416 | 0 | 0 | 0 | 0 | 10 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 0 | 0 | 335 | 0 | 0 | 27 | 52 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 2.74 | 40 | 0 | 8 | 265 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 583 | 17 | 0 | 165 | 0 | 335 | 320 | 51 | 49 | 0 | 42 | 0 | 0 | 0 | 0 | 11 | 0 | 32 | 0 | 53 | 0 | 305 | 0 | 322 | 30 | 23 | 149 | 7 | 17 | 0 | 82 | 30 | 0 | 0 | 100 | 0 | 56 | 19 | 160 | 2 | 34.05 | 6 | 5157.79 | 901 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 575 | 0 | 0 | 0 | 1222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.1 | 87 | 0 | 0 | 47.62 | 174 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 4.34 | 0 | 56 | 35 | 25 | 34 | 0 | 0 | 0 | 4.2 | 128 | 0.45 | 0 | 220 | 130 | 220 | 0 | 0 | 525 | 0 | 5214.71 | 10372.5 | 93.96
11:00 | 0 | 14 | 0 | 0 | 0 | 130 | 0 | 8 | 415 | 0 | 0 | 0 | 0 | 31 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545 | 0 | 0 | 330 | 0 | 0 | 31 | 52 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 3.28 | 40 | 0 | 8 | 265 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 639 | 19 | 0 | 165 | 0 | 335 | 320 | 51 | 48 | 0 | 42 | 0 | 0 | 0 | 0 | 11 | 0 | 28 | 0 | 62 | 0 | 310 | 0 | 391 | 30 | 23 | 148 | 8 | 17 | 0 | 82 | 30 | 0 | 0 | 100 | 0 | 56 | 19 | 157 | 2 | 39.9 | 6 | 5322.18 | 900 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 540 | 0 | 0 | 0 | 1182.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.84 | 106 | 0 | 0 | 57.55 | 177 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 5.24 | 0 | 56 | 0 | 30 | 34 | 0 | 0 | 0 | 5.2 | 150 | 0.53 | 0 | 219 | 130 | 220 | 0 | 0 | 540 | 0 | 5246.57 | 10568.75 | 93.96
12:00 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 8 | 412 | 0 | 0 | 0 | 0 | 43 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 327 | 0 | 0 | 34 | 52 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 3.49 | 40 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 833 | 20 | 0 | 135 | 0 | 325 | 240 | 51 | 40 | 0 | 42 | 0 | 0 | 0 | 0 | 11 | 0 | 28 | 0 | 67 | 0 | 320 | 0 | 391 | 30 | 23 | 162 | 9 | 17 | 0 | 82 | 30 | 0 | 0 | 100 | 0 | 56 | 19 | 155 | 2 | 44.28 | 6 | 5544.77 | 901 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.58 | 525 | 0 | 0 | 0 | 1232.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.08 | 115 | 0 | 0 | 59.4 | 197 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.39 | 0 | 56 | 0 | 30 | 34 | 0 | 0 | 0 | 5.8 | 159 | 0.58 | 0 | 285 | 130 | 220 | 0 | 0 | 560 | 0 | 5469.08 | 11013.85 | 93.96
13:00 | 0 | 29 | 0 | 0 | 0 | 230 | 0 | 9 | 412 | 0 | 0 | 0 | 0 | 56 | 45 | 0 | 0 | 11 | 44 | 0 | 0 | 0 | 550 | 0 | 0 | 330 | 0 | 0 | 33 | 52 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 3.2 | 40 | 9 | 16 | 265 | 0 | 0 | 0 | 0 | 12 | 221 | 0 | 0 | 0 | 885 | 19 | 0 | 76 | 0 | 275 | 320 | 51 | 10 | 0 | 42 | 22 | 0 | 21 | 0 | 11 | 0 | 134 | 0 | 66 | 0 | 315 | 0 | 364 | 30 | 23 | 160 | 9 | 17 | 0 | 82 | 30 | 0 | 0 | 98 | 0 | 59 | 19 | 155 | 2 | 43.34 | 6 | 5767.54 | 901 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 612 | 0 | 0 | 0 | 1395.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.47 | 110 | 0 | 0 | 58.57 | 192 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 5.61 | 0 | 56 | 35 | 30 | 33 | 0 | 0 | 0 | 5.6 | 158 | 0.57 | 0 | 307 | 126 | 220 | 0 | 0 | 602 | 0 | 5763.35 | 11530.89 | 93.95
14:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 7 | 410 | 0 | 0 | 17 | 0 | 58 | 15 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 550 | 0 | 0 | 300 | 0 | 0 | 28 | 52 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 2.84 | 40 | 15 | 14 | 265 | 0 | 0 | 0 | 0 | 10 | 220 | 0 | 0 | 0 | 1000 | 17 | 0 | 76 | 0 | 290 | 320 | 51 | 10 | 0 | 42 | 24 | 0 | 17 | 0 | 11 | 0 | 140 | 0 | 61 | 0 | 320 | 0 | 395 | 30 | 23 | 150 | 8 | 17 | 0 | 82 | 30 | 0 | 0 | 99 | 0 | 58 | 19 | 140 | 2 | 37.84 | 6 | 5576.68 | 900 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 581 | 0 | 0 | 0 | 1371.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.06 | 98 | 0 | 0 | 52.26 | 174 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 5.16 | 0 | 56 | 35 | 27 | 34 | 0 | 0 | 0 | 5 | 142 | 0.5 | 0 | 274 | 126 | 220 | 0 | 0 | 560 | 0 | 5539.55 | 11116.23 | 93.95
15:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 11 | 383 | 0 | 0 | 16 | 0 | 52 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 525 | 0 | 0 | 300 | 0 | 0 | 23 | 52 | 15 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 2.02 | 40 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1000 | 12 | 0 | 16 | 0 | 310 | 320 | 51 | 10 | 0 | 40 | 15 | 0 | 0 | 0 | 11 | 0 | 128 | 0 | 47 | 0 | 315 | 0 | 405 | 30 | 23 | 152 | 7 | 17 | 0 | 82 | 30 | 0 | 0 | 99 | 0 | 58 | 19 | 140 | 2 | 28.83 | 6 | 5366.85 | 901 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 580 | 0 | 0 | 0 | 1264.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.01 | 77 | 0 | 0 | 43.64 | 185 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 4.16 | 0 | 56 | 0 | 20 | 34 | 0 | 0 | 0 | 3.5 | 104 | 0.36 | 0 | 210 | 126 | 220 | 0 | 0 | 500 | 0 | 5139.42 | 10506.27 | 93.95
16:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 11 | 383 | 0 | 0 | 16.5 | 0 | 52 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 300 | 0 | 0 | 14 | 52 | 19 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 1.06 | 40 | 0 | 2 | 265 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1020 | 0 | 0 | 8 | 0 | 310 | 330 | 51 | 10 | 0 | 40 | 16 | 0 | 0 | 0 | 11 | 0 | 116 | 0 | 28 | 0 | 320 | 0 | 404 | 30 | 23 | 145 | 3 | 17 | 0 | 82 | 30 | 0 | 0 | 99 | 0 | 58 | 19 | 130 | 1 | 14.96 | 6 | 5345.52 | 901 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 525 | 0 | 0 | 0 | 1132.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.9 | 48 | 0 | 0 | 27.79 | 176 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 2.87 | 0 | 56 | 0 | 11 | 34 | 0 | 0 | 0 | 1.5 | 60 | 0.13 | 0 | 201 | 126 | 220 | 0 | 0 | 475 | 0 | 4795.09 | 10140.61 | 93.95
17:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 11 | 388 | 0 | 0 | 16.4 | 0 | 60 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 300 | 0 | 0 | 5 | 52 | 23.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0.3 | 40 | 0 | 3 | 265 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1020 | 2 | 0 | 8 | 0 | 320 | 345 | 51 | 10 | 0 | 40 | 17 | 0 | 0 | 0 | 14 | 0 | 118 | 0 | 8 | 0 | 320 | 0 | 413 | 30 | 23 | 145 | 1 | 8 | 0 | 82 | 30 | 0 | 0 | 99 | 0 | 58 | 19 | 130 | 0 | 4.93 | 6 | 5361.13 | 901 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.9 | 516 | 0 | 0 | 0 | 1224.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.94 | 14 | 0 | 0 | 6.68 | 174 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0.8 | 0 | 56 | 0 | 3 | 34 | 0 | 0 | 0 | 0.7 | 18 | 0.07 | 0 | 202 | 126 | 220 | 0 | 0 | 475 | 0 | 4736.95 | 10098.08 | 93.94
18:00 | 0 | 50 | 2 | 0 | 0 | 0 | 0 | 11 | 331 | 0 | 0 | 18.2 | 8 | 70 | 78 | 45 | 0 | 12 | 66 | 0 | 0 | 0 | 555 | 0 | 25 | 300 | 0 | 0 | 0 | 90 | 23.5 | 21 | 0 | 0 | 11 | 16 | 0 | 0 | 10 | 22 | 23 | 5 | 30 | 12 | 0 | 40 | 15 | 4 | 265 | 32 | 0 | 3 | 4 | 30 | 220 | 0 | 0 | 0 | 1145 | 0 | 18 | 8 | 0 | 300 | 350 | 51 | 10 | 0 | 40 | 21 | 0 | 11 | 0 | 14 | 0 | 130 | 2 | 0 | 27 | 315 | 0 | 390 | 30 | 23 | 145 | 0 | 20 | 0 | 82 | 30 | 0 | 0 | 99 | 5 | 58 | 19 | 120 | 0 | 0 | 6 | 5916.7 | 900 | 352 | 0 | 28 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 512 | 0 | 0 | 0 | 1372.1 | 0 | 0 | 0 | 35 | 7 | 0 | 0 | 3 | 2 | 0 | 0 | 16 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 55 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 196 | 126 | 220 | 0 | 0 | 485 | 17 | 4952.1 | 10868.8 | 93.94
19:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 16 | 306 | 0 | 0 | 31 | 18 | 70 | 78 | 95 | 0 | 35 | 81 | 0 | 0 | 0 | 545 | 0 | 35 | 335 | 0 | 0 | 0 | 52 | 20.5 | 21 | 0 | 0 | 51 | 32 | 4 | 0 | 8 | 51 | 30 | 17 | 50 | 12 | 0 | 40 | 50 | 8 | 417 | 45 | 0 | 19 | 8 | 47 | 221 | 0 | 0 | 0 | 1157 | 0 | 50 | 8 | 0 | 270 | 350 | 51 | 10 | 115 | 42 | 46 | 0 | 51 | 0 | 14 | 34 | 126 | 15 | 0 | 31 | 310 | 0 | 340 | 30 | 23 | 154 | 0 | 20 | 0 | 83 | 30 | 0 | 0 | 99 | 17 | 58 | 19 | 111 | 0 | 0 | 6 | 6594.5 | 712 | 340 | 0 | 8 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 563 | 0 | 0 | 0 | 1460.27 | 0 | 0 | 0 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 56 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 268 | 130 | 220 | 0 | 0 | 530 | 44 | 5131.27 | 11725.77 | 93.94
19:30 | 0 | 51 | 16 | 0 | 0 | 0 | 0 | 16 | 370 | 0 | 0 | 0 | 0 | 75 | 78 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 583 | 0 | 17 | 331 | 0 | 0 | 0 | 35 | 21.5 | 21 | 0 | 0 | 0 | 32 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 25 | 12 | 445 | 0 | 0 | 0 | 1 | 51 | 221 | 0 | 0 | 0 | 1164 | 0 | 12 | 8 | 0 | 320 | 350 | 51 | 10 | 127 | 20 | 52 | 0 | 17 | 0 | 14 | 0 | 126 | 0 | 0 | 0 | 330 | 0 | 340 | 30 | 23 | 150 | 0 | 20 | 0 | 83 | 30 | 0 | 0 | 99 | 0 | 58 | 19 | 110 | 0 | 0 | 6 | 6051.5 | 712 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 595 | 0 | 0 | 0 | 1460.63 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 56 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 288 | 130 | 220 | 0 | 0 | 542 | 0 | 5054.63 | 11106.13
20:00 | 0 | 51 | 16 | 0 | 0 | 0 | 0 | 16 | 347 | 0 | 0 | 0 | 0 | 82 | 78 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 520 | 0 | 0 | 333 | 0 | 0 | 0 | 35 | 21.5 | 21 | 0 | 0 | 0 | 32 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 22 | 550 | 0 | 0 | 0 | 0 | 50 | 221 | 0 | 0 | 0 | 1164 | 0 | 12 | 8 | 0 | 330 | 320 | 51 | 10 | 84 | 20 | 49 | 0 | 17 | 0 | 15 | 0 | 118 | 0 | 0 | 0 | 315 | 0 | 386 | 30 | 23 | 154 | 0 | 20 | 0 | 83 | 30 | 0 | 0 | 99 | 0 | 58 | 19 | 110 | 0 | 0 | 6 | 6006.5 | 712 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 0 | 0 | 0 | 1450.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 56 | 35 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 542 | 0 | 5086.64 | 11093.14 | 93.94
21:00 | 0 | 51 | 8 | 0 | 0 | 0 | 0 | 20 | 340 | 0 | 0 | 0 | 0 | 87 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 330 | 0 | 0 | 0 | 17 | 21.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 23 | 635 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1172 | 0 | 0 | 0 | 0 | 315 | 320 | 51 | 5 | 67 | 10 | 40 | 0 | 0 | 0 | 15 | 0 | 114 | 0 | 0 | 0 | 315 | 0 | 388 | 30 | 23 | 159 | 0 | 20 | 0 | 83 | 30 | 0 | 0 | 99 | 0 | 58 | 19 | 110 | 0 | 0 | 6 | 5833.5 | 712 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608 | 0 | 0 | 0 | 1455.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 542 | 0 | 5022.83 | 10856.33 | 93.93
22:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 24 | 340 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 7.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 26 | 635 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 0 | 300 | 280 | 51 | 5 | 68 | 10 | 0 | 0 | 0 | 0 | 15 | 0 | 110 | 0 | 0 | 0 | 310 | 0 | 384 | 30 | 23 | 158 | 0 | 20 | 0 | 83 | 30 | 0 | 0 | 99 | 0 | 58 | 19 | 102 | 0 | 0 | 6 | 5639.5 | 900 | 399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579 | 0 | 0 | 0 | 1424.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 130 | 220 | 0 | 0 | 500 | 0 | 5031.95 | 10671.45 | 93.93
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 325 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 14 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 23 | 578 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1104 | 0 | 0 | 0 | 0 | 305 | 280 | 51 | 5 | 30 | 10 | 0 | 50 | 0 | 0 | 15 | 0 | 112 | 0 | 0 | 0 | 305 | 0 | 392 | 30 | 23 | 156 | 0 | 20 | 0 | 83 | 30 | 0 | 0 | 98 | 0 | 16 | 0 | 70 | 0 | 0 | 0 | 5362 | 900 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 429 | 0 | 0 | 0 | 1214.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 130 | 220 | 0 | 0 | 500 | 0 | 4590.11 | 9952.11 | 93.93
Total KWH | 0 | 472320 | 61440 | 0 | 0 | 672500 | 0 | 220590.91 | 9104400 | 0 | 0 | 122040 | 43560 | 870048 | 550560 | 124451 | 0 | 94066 | 249120 | 0 | 0 | 0 | 11937534 | 0 | 67004 | 7408721 | 0 | 0 | 226031 | 724800 | 338400 | 516600 | 0 | 0 | 79036 | 77782 | 4800 | 0 | 314880 | 70790 | 37360 | 26651 | 71040 | 21120 | 21961 | 952000 | 129640 | 516000 | 8123636.36 | 45164 | 0 | 33600 | 14072.4 | 199890 | 5359676 | 0 | 0 | 0 | 17961816 | 125145 | 115418 | 1103999 | 0 | 7931600 | 7838000 | 982542 | 364320 | 399000 | 842256 | 269760 | 390683 | 174720 | 0 | 322240 | 20520 | 1697280 | 20362 | 448709 | 39776 | 7645000 | 0 | 8721000 | 715000 | 601680 | 3620618 | 61260 | 425328 | 0 | 1416960 | 656640 | 0 | 0 | 2391380 | 26640 | 939600 | 300000 | 3278400 | 14690 | 280750 | 87840 | 122134216.67 | 17528000 | 9280224 | 0 | 34560 | 35200 | 0 | 0 | 0 | 0 | 0 | 0 | 597600 | 11970910 | 0 | 0 | 0 | 27514499 | 0 | 0 | 0 | 71328 | 72384 | 0 | 4432 | 1789 | 7435 | 360964 | 770540 | 30857 | 0 | 413264 | 4280091 | 0 | 0 | 0 | 0 | 0 | 9323781 | 0 | 38220 | 0 | 1304727 | 261401 | 203345 | 487075 | 0 | 0 | 0 | 35321.16 | 1059120 | 3762 | 63264 | 5455000 | 3091000 | 5330290 | 0 | 0 | 11160727.27 | 72000 | 110863110.43 | 232997327.1

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 14-02-2026
Power Supply Scenario
| Day Peak Generation |  |  | 11013.85 | MW | 12:00 Hr. | Energy Generated |  |  | 232.9973 |  | MKWHr.
| Day Peak Demand |  |  | 11013.85 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11725.77 | MW | 19:00 Hr. | Energy Demand |  |  | 232.9973 |  | MKWHr.
| Evening Peak Demand |  |  | 11725.77 | MW | 19:00 Hr. | Maximum Temperature |  |  | 28.5 |  | °C
| Minimum Generation of the Day |  |  | 6719.06 | MW | 04:00 Hr. | Total Gas Supplied |  |  | 808.8 |  | MMCFD
| Maximum Generation of the Day |  |  | 11725.77 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.3281 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 30.1987 | 0 | 3.3794 | 0 | 0 | 0.22603 | 0 | 0 | 33.8042 | Gas | 117.0265 | Gas | 407535144.7785
| Chattogram Zone |  |  | 5.8757 | 26.0855 | 0.81095 | 0 | 0.952 | 0.14711 | 0 | 0.31488 | 34.1861 | Coal | 55.9768 | Coal | 362344256.4974
| Cumilla Zone |  |  | 20.1746 | 0 | 0.64056 | 0 | 0 | 0.44871 | 1.6973 | 0 | 22.9612 | HFO | 7.3267 | HFO | 127418918.968
| Mymensingh Zone |  |  | 3.2784 | 0 | 1.3541 | 0 | 0 | 0.29544 | 0 | 0 | 4.9279 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.1936 | 0 | 0 | 0 | 0 | 0.06126 | 0 | 0 | 26.2549 | Hydro | 0.952 | Hydro | 95200
| Khulna Zone |  |  | 9.2802 | 11.9709 | 0.06976 | 0 | 0 | 0.5976 | 17.528 | 0 | 39.4465 | Solar | 4.6607 | Solar | 74136134.222
| Barishal Zone |  |  | 8.4213 | 16.6157 | 0.13526 | 0 | 0 | 0.003762 | 0 | 0 | 25.176 | Import | 46.7398 | Import | 265262750.62
| Rajshahi Zone |  |  | 13.6039 | 0 | 0.18823 | 0 | 0 | 1.583 | 27.5145 | 0 | 42.8896 | Wind | 0.31488 | Wind | 4631884.8
| Rangpur Zone |  |  | 0 | 1.3047 | 0.74848 | 0 | 0 | 1.2978 | 0 | 0 | 3.351
| Total |  |  | 117.0265 | 55.9768 | 7.3267 | 0 | 0.952 | 4.6607 | 46.7398 | 0.31488 | 232.9973
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 407535144.7785 |  | Hydro | 95200
|  |  |  | Coal | 362344256.4974 |  | Solar | 74136134.222
|  |  |  | HFO | 127418918.968 |  | Import | 265262750.62
|  |  |  | HSD | 0 |  | Wind | 4631884.8
[5 empty] | Total: | 124,14,24,289 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 17.528 | Peak Hr Flow | 712.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 27280003.1 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.5145 | Peak Hr Flow | 1460.27 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1435 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.6973 | Peak Hr Flow | 126.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2063 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 46.7398 | Peak Hr Flow | 2298.27 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4107
|  |  |  | Chattogram |  | 0 |  | 1120
|  |  |  | Cumilla |  | 0 |  | 1016
|  |  |  | Mymensingh |  | 0 |  | 1036
|  |  |  | Sylhet |  | 0 |  | 416
|  |  |  | Khulna |  | 0 |  | 1279
|  |  |  | Barishal |  | 0 |  | 321
|  |  |  | Rajshahi |  | 0 |  | 1135
|  |  |  | Rangpur |  | 0 |  | 788
|  |  |  | Total |  | 0 |  | 11218
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:51 | 15:12 | Halishahar 132/33kV S/S 415T(TR-2) HT Scheduled S/D Due to Annual maintenance
| 09:29 |  | Ghorasal Repowered CCPP Unit-4 Synchronized
| 10:33 |  | SS Power Bashkhali Unit-2 was synchronized
| 10:33 |  | SS Power Synchronized
|  | 11:03 | Khulna (C) S/S TR-1 425T HT is restored.
|  | 11:04 | Khulna (C) S/S TR-1 425T LT is restored.
| 11:14 | 13:35 | Khulna (C) S/S Tr-2 415 T HT Scheduled S/D Due to Red hot maintenance
| 11:14 | 13:35 | Khulna (C) S/S Tr-2 415 T LT Scheduled S/D Due to Red hot maintenance
| 11:48 | 12:04 | Halishahar 132/33kV S/S 405T(TR-1) LT Tripped showing F51 relay relays Due to Due to 33 | [7 empty] | 32.0MW load
|  |  | kv feeder fault. | [7 empty] | interrup.
| 12:00 |  | Day peak generation 11010 MW
| 12:04 | 12:09 | Cumilla(S) 132/33kV S/S TR-3 HT Scheduled S/D Due to None
| 12:09 | 12:10 | Cumilla(S) 132/33kV S/S TR-3 LT Scheduled S/D
| 12:17 | 12:18 | Cumilla(S) 132/33kV S/S TR-1 HT Scheduled S/D Due to None
| 12:17 | 12:18 | Cumilla(S) 132/33kV S/S TR-1 LT Scheduled S/D Due to None
| 12:25 | 12:26 | Cumilla(S) 132/33kV S/S TR-2 HT Scheduled S/D
| 12:25 | 12:27 | Cumilla(S) 132/33kV S/S TR-2 LT Scheduled S/D Due to None
| 12:27 |  | Cumilla (S) all transformers are shifted to Tripura side bus
| 13:38 |  | Ghorasal Repowered CCPP Unit-4 Shutdown
|  | 13:46 | Chauddagram-Feni 132 kV Ckt-2 is restored.
| 14:11 | 15:30 | Khulna (C) S/S TR-1 425T LT Scheduled S/D Due to incoming bus loop tighting
| 14:11 | 15:29 | Khulna (C) S/S TR-1 425T HT Scheduled S/D Due to incoming bus loop tighting
| 15:00 | 15:05 | Ghatail 132/33kV S/S T-1 LT Scheduled S/D Due to SPS Installation
| 15:30 | 15:35 | Ghatail 132/33kV S/S T-2 LT Scheduled S/D Due to SPS Installation
| 18:06 |  | Matarbari 2*600 MW (CPGCBL) Synchronized with remarks:- U-1
| 18:39 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- GT
| 19:00 |  | Evening Peak Generation: 11725 MW.
| 22:06 |  | Chandpur CCPP GT was sync.
|  | 23:50 | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) is restored.
| 01:15 |  | Ashuganj 225 MW CCPP ST was sync.
| 01:15 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- ST
| 05:00 |  | Minimum Generation is 7691 MW.
| 07:37 |  | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) Forced S/D Due to Aldc Instruction.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 14-02-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 672500 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 16 | 220590.91 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 306 | 9104400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7408721 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 31 | 122040 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 78 | 550560 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 94066 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 67004 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20.5 | 338400 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 516600 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 61440 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 95 | 124451 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 70 | 870048 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 51 | 472320 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 81 | 249120 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 226031 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 18 | 43560 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 545 | 11937534 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 52 | 724800 | -
Dhaka Area Total |  |  |  |  | 6668.974 | 1814.5 | 33804185.91
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | U#1 Under maintenance, U#2 Running
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 14072.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 125145 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 33600 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 952000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 221 | 5359676 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 47 | 199890 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 30 | 37360 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 70790 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 71040 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 8 | 516000 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 4 | 4800 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21961 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 32 | 77782 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 17 | 26651 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 50 | 129640 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 21120 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 51 | 79036 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 45 | 45164 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1157 | 17961816 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 8 | 314880 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 417 | 8123636.36 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 2267 | 34186059.76
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 115 | 399000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 270 | 7931600 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 350 | 7838000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage as per NLDC instructions.
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 42 | 842256 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 10 | 364320 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 1103999 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 982542 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 50 | 115418 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 31 | 39776 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 390683 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 174720 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 126 | 1697280 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 15 | 20362 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 322240 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 20520 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 46 | 269760 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 448709 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1213 | 22961185
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 111 | 3278400 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14690 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 300000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 58 | 939600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 280750 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 87840 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 26640 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 211 | 4927920
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 61260 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 715000 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 23 | 601680 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 154 | 3620618 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 656640 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1416960 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 99 | 2391380 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 20 | 425328 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7645000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 340 | 8721000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1089 | 26254866
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 712 | 17528000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 8 | 34560 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 40 | 35200 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 340 | 9280224 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 597600 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 563 | 11970910 | U#1 Under Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1663 | 39446494
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 40 | 63264 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 3091000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 530 | 11160727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5330290 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 44 | 72000 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 268 | 5455000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3762 | -
Barishal Area Total |  |  |  |  | 2700.36 | 1232 | 25176043.27
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 360964 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 1789 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 180 | 4280091 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 328 | 9323781 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 30857 | Machine problem and fuel shortage
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 7435 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 4432 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 38 | 72384 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 50 | 71328 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 38220 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1460.27 | 27514499 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 413264 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 770540 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2081.27 | 42889584
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 56 | 1304727 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 487075 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 35321.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 261401 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 203345 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1059120 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 155 | 3350989.16
Eastern Grid Total |  |  |  |  | 17400.108 | 6594.5 | 122134216.67
Western Grid Total |  |  |  |  | 10985.595 | 5131.27 | 110863110.43
National Grid Total |  |  |  |  | 28385.703 | 11725.77 | 232997327.1
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 14-02-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7694.55 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3523.6 | MW
i) Dhaka area |  |  | 4107.05 |  | MW | i) Khulna area |  |  |  | 1279 | MW
ii) Chattogram area |  |  | 1119.5 |  | MW | ii) Barishal area |  |  |  | 321.2 | MW
iii) Cumilla area |  |  | 1016 |  | MW | iii) Rajshahi area |  |  |  | 1135.4 | MW
iv) Mymensingh area |  |  | 1036 |  | MW | iv) Rangpur area |  |  |  | 788 | MW
v) Sylhet area |  |  | 416 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11218.15 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 77 | 13:00 | 133 | Nawabganj | 32.6 | 13:00
2 | AKSML | 15 | 18:00 | 68 | Hathazari | 61 | 13:00 | 134 | Netrakona | 150 | 08:00
3 | Aftabnagar | 26 | 13:00 | 69 | Hatirjheel | 27 | 13:00 | 135 | New | 55.8 | 12:00
4 | Agargaon | 75 | 13:00 | 70 | Ishurdi | 56 | 18:30 | 136 | Niamatpur | 98 | 09:00
5 | Agrabad | 38 | 18:00 | 71 | Jaldhaka | 65 | 09:00 | 137 | Noapara | 37 | 18:30
6 | Amnura | 34 | 09:00 | 72 | Jamalpur | 103 | 08:00 | 138 | PHP | 9 | 19:30
7 | Ashuganj | 66 | 13:00 | 73 | Jashore | 117 | 13:00 | 139 | Pabna | 68 | 18:30
8 | BSRM | 196 | 01:00 | 74 | Jhenaidah | 85 | 14:00 | 140 | Palashbari | 110 | 08:00
9 | Bagerhat | 64 | 18:30 | 75 | Joydebpur | 111 | 18:30 | 141 | Panchagarh | 43 | 18:30
10 | Bajitpur | 68 | 18:30 | 76 | Joypurhat | 55 | 09:00 | 142 | Patiya | 6 | 00:00
11 | Bakerganj | 9.5 | 18:30 | 77 | Juldah | 13 | 16:00 | 143 | Patuakhali | 44.5 | 18:30
12 | Bakulia | 64 | 13:00 | 78 | KSRM | 11 | 18:30 | 144 | Payra | 22 | 18:30
13 | Banani | 33.8 | 13:00 | 79 | Kabirpur | 206 | 18:30 | 145 | Postogola | 39 | 13:00
14 | Bangabhaban | 5 | 10:00 | 80 | Kachua | 62 | 19:30 | 146 | Purbachal | 21 | 13:00
15 | Barapukuria | 65 | 09:00 | 81 | Kaliganj | N/A | N/A | 147 | Purbasadipur | 115 | 13:00
16 | Barguna | 14 | 18:00 | 82 | Kallyanpur | 84 | 13:00 | 148 | Rahanpur | 29 | 08:00
17 | Barishal | 76 | 13:00 | 83 | Kalurghat | 30 | 12:00 | 149 | Rahim | 26 | 18:00
18 | Barishal-230 | 66 | 18:30 | 84 | Kamrangirchar | 67 | 13:00 | 150 | Rajbari | 58 | 18:30
19 | Baroaulia | 52 | 11:00 | 85 | Kaptai | N/A | N/A | 151 | Rajendrapur | 110 | 13:00
20 | Baroirhat | 41 | 18:30 | 86 | Kasba | 26 | 13:00 | 152 | Rajshahi | 78 | 13:00
21 | Bashundhara | 155 | 13:00 | 87 | Kazla | 94 | 13:00 | 153 | Rajshahi-230 | 70 | 13:00
22 | BashundharaCement | 1 | 09:00 | 88 | Keranigonj | 69 | 13:00 | 154 | Ramganj | 70 | 13:00
23 | Beanibazar | 48 | 18:30 | 89 | Khagrachori | 26 | 18:00 | 155 | Rampur | 27 | 17:00
24 | Benapole | 54 | 08:00 | 90 | Khulna | 38 | 13:00 | 156 | Rangamati | 13 | 18:00
25 | Bhaluka | 128 | 12:00 | 91 | Khulshi | 155 | 14:00 | 157 | Rangpur | 105 | 18:30
26 | Bhandaria | 37 | 21:00 | 92 | Kishoreganj | 101 | 18:30 | 158 | Ruppur | 1.8 | 15:00
27 | Bhangura | 27 | 13:00 | 93 | Kodda | 248 | 16:00 | 159 | SSM | 0 | 00:00
28 | Bheramara(GK) | 42 | 18:30 | 94 | Kulaura | 28 | 18:00 | 160 | Saidpur | 98 | 10:00
29 | Bhulta | 179 | 19:30 | 95 | Kurigram | 62 | 09:00 | 161 | Satkhira | 104 | 08:00
30 | Bog-Sherpur | 60 | 09:00 | 96 | Kushtia | 107 | 18:30 | 162 | Satmasjid | 77 | 13:00
31 | Bogura | 123 | 18:30 | 97 | Laksam | 24 | 18:00 | 163 | Savar | 170 | 15:00
32 | Borhanuddin | 67 | 21:00 | 98 | Lakshmipur | 25 | 18:30 | 164 | SevenRings | 17.21 | 18:30
33 | Brahmanbaria | 90 | 18:00 | 99 | Lalbag | 58 | 13:00 | 165 | ShahCement | 16 | 12:00
34 | Cantonment | 71 | 13:00 | 100 | Lalmonirhat | 48 | 19:00 | 166 | Shahjadpur | 52 | 12:00
35 | Chandina | 14 | 18:30 | 101 | MI_Cement | 14 | 19:30 | 167 | Shahjibazar | 96 | 18:30
36 | Chandpur | 52 | 19:00 | 102 | Madanganj | 32 | 13:00 | 168 | Shahmirpur | 41 | 18:30
37 | Chandraghona | 27 | 18:30 | 103 | Madaripur | 74 | 14:00 | 169 | Shariatpur | 57 | 21:00
38 | Chapai | 57 | 13:00 | 104 | Madartek | 56 | 14:00 | 170 | Sherpur | 144 | 18:00
39 | Charsaidpur | 33 | 21:00 | 105 | Madunaghat | 40 | 18:30 | 171 | Shikalbaha | 18 | 13:00
40 | Chauddagram | 54 | 13:00 | 106 | Magura | 51 | 18:30 | 172 | Shitalakhya | 64.2 | 12:00
41 | Chhatak | 28 | 18:30 | 107 | Mahasthangarh | 62 | 08:00 | 173 | Sholosohor | 33 | 15:00
42 | Chowmuhani | 96 | 18:00 | 108 | Maijdee | 34 | 18:30 | 174 | Shyampur | 130 | 12:00
43 | Chuadanga | 82 | 13:00 | 109 | Manikganj | 92 | 12:00 | 175 | Siddhirganj | 107 | 12:00
44 | Coxsbazar | 113 | 18:00 | 110 | Maniknagar | 40 | 13:00 | 176 | Sirajganj | 86 | 19:00
45 | Cumilla(N) | 89 | 00:00 | 111 | Matarbari | 40 | 18:00 | 177 | Sonargaon | 112 | 19:30
46 | Cumilla(S) | 140 | 14:00 | 112 | Matuail | 55 | 12:00 | 178 | Sreemongol | 54 | 18:00
47 | Daganbhuiyan | 22 | 18:30 | 113 | Metrorail_Motijheel | 20 | 10:00 | 179 | Sreepur | 103 | 19:00
48 | Daudkandi | 106 | 19:00 | 114 | Metrorail_Uttara | 8 | 14:00 | 180 | Srinagar | 31.8 | 13:00
49 | DhakaUniversity | 50 | 13:00 | 115 | Millgate | 68 | 12:00 | 181 | Sunamganj | 42 | 18:00
50 | Dhamrai | 100 | 16:00 | 116 | Mirpur | 111 | 13:00 | 182 | Sylhet | 41 | 18:00
51 | Dhanmondi | 74 | 13:00 | 117 | Mirsorai | 9 | 10:00 | 183 | Sylhet-132 | 69 | 18:30
52 | Dohazari | 76 | 13:00 | 118 | Mirzapur | 44 | 08:00 | 184 | TK | 17 | 18:00
53 | Faridpur | 111 | 18:00 | 119 | Mithapukur | 52 | 08:00 | 185 | Tangail | 150 | 08:00
54 | Fatullah | 89 | 15:00 | 120 | Modern | N/A | N/A | 186 | Taraganj | 20 | 09:00
55 | Fenchuganj | 23 | 14:00 | 121 | Mogbazar | 59.1 | 13:00 | 187 | Tasnim | 12 | 13:00
56 | Feni | 73 | 14:00 | 122 | Mongla | 38 | 15:00 | 188 | Thakurgaon | 81 | 18:30
57 | GPH | 1 | 00:00 | 123 | Motijheel | 32 | 13:00 | 189 | Tongi | 124 | 11:00
58 | Ghatail | 92 | 08:00 | 124 | Muktagacha | 35 | 13:00 | 190 | Ullahpara | 29 | 18:30
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 72 | 13:00 | 191 | Ullon | 48 | 13:00
60 | Ghorashal-230 | 87 | 20:00 | 126 | Muradnagar | 26 | 18:30 | 192 | Uttara | 45 | 18:00
61 | Goalpara | 30 | 13:00 | 127 | Mymensingh | 179 | 18:00 | 193 | UttaraNew | 32 | 13:00
62 | Gollamari | 86 | 13:00 | 128 | Naogaon | 116 | 13:00 | 194 | Zigatola | 56 | 13:00
63 | Gopalganj | 79 | 18:30 | 129 | Narail | 47 | 19:00
64 | Gulshan | 66 | 13:00 | 130 | Narinda | 42 | 13:00
65 | Halishahar | 61 | 14:00 | 131 | Narshingdi | 142 | 19:00
66 | HaripurSBU | 117 | 11:00 | 132 | Natore | 116 | 18:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 14-02-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 8138.23 | 0 |  | 8138.23
1:00 | 7462.87 | 0 |  | 7462.87
2:00 | 7202.24 | 0 |  | 7202.24
3:00 | 6915.62 | 0 |  | 6915.62
4:00 | 6719.06 | 0 |  | 6719.06
5:00 | 6733.24 | 0 |  | 6733.24
6:00 | 7162.88 | 0 |  | 7162.88
7:00 | 8223.69 | 0 |  | 8223.69
8:00 | 9536.89 | 0 |  | 9536.89
9:00 | 10187.53 | 0 |  | 10187.53
10:00 | 10372.5 | 0 |  | 10372.5
11:00 | 10568.75 | 0 |  | 10568.75
12:00 | 11013.85 | 0 |  | 11013.85
13:00 | 11530.89 | 0 |  | 11530.89
14:00 | 11116.23 | 0 |  | 11116.23
15:00 | 10506.27 | 0 |  | 10506.27
16:00 | 10140.61 | 0 |  | 10140.61
17:00 | 10098.08 | 0 |  | 10098.08
18:00 | 10868.8 | 0 |  | 10868.8
19:00 | 11725.77 | 0 |  | 11725.77
19:30 | 11106.13 | 0 |  | 11106.13
20:00 | 11093.14 | 0 |  | 11093.14
21:00 | 10856.33 | 0 |  | 10856.33
22:00 | 10671.45 | 0 |  | 10671.45
23:00 | 9952.11 | 0 |  | 9952.11
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 14-02-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4303 | 3835.23 | 8138.23 | DAILY GENERATION CURVE
00:30 | 4120 | 3680.55 | 7800.55
01:00 | 3937 | 3525.87 | 7462.87 | 14-02-2026
01:30 | 3913.5 | 3419.055 | 7332.555
02:00 | 3890 | 3312.24 | 7202.24
02:30 | 3830 | 3228.93 | 7058.93
03:00 | 3770 | 3145.62 | 6915.62
03:30 | 3707.5 | 3109.84 | 6817.34
04:00 | 3645 | 3074.06 | 6719.06
04:30 | 3636.5 | 3089.65 | 6726.15
05:00 | 3628 | 3105.24 | 6733.24
05:30 | 3679.5 | 3268.56 | 6948.06
06:00 | 3731 | 3431.88 | 7162.88
06:30 | 4074.225 | 3619.06 | 7693.285
07:00 | 4417.45 | 3806.24 | 8223.69
07:30 | 4641.52 | 4238.77 | 8880.29
08:00 | 4865.59 | 4671.3 | 9536.89
08:30 | 4940.58 | 4921.63 | 9862.21
09:00 | 5015.57 | 5171.96 | 10187.53
09:30 | 5086.68 | 5193.335 | 10280.015
10:00 | 5157.79 | 5214.71 | 10372.5
10:30 | 5239.985 | 5230.64 | 10470.625
11:00 | 5322.18 | 5246.57 | 10568.75
11:30 | 5433.475 | 5357.825 | 10791.3
12:00 | 5544.77 | 5469.08 | 11013.85
12:30 | 5656.155 | 5616.215 | 11272.37
13:00 | 5767.54 | 5763.35 | 11530.89
13:30 | 5672.11 | 5651.45 | 11323.56
14:00 | 5576.68 | 5539.55 | 11116.23
14:30 | 5471.765 | 5339.485 | 10811.25
15:00 | 5366.85 | 5139.42 | 10506.27
15:30 | 5356.185 | 4967.255 | 10323.44
16:00 | 5345.52 | 4795.09 | 10140.61
16:30 | 5353.325 | 4766.02 | 10119.345
17:00 | 5361.13 | 4736.95 | 10098.08
17:30 | 5638.915 | 4844.525 | 10483.44
18:00 | 5916.7 | 4952.1 | 10868.8
18:30 | 6255.6 | 5041.685 | 11297.285
19:00 | 6594.5 | 5131.27 | 11725.77
19:30 | 6051.5 | 5054.63 | 11106.13
20:00 | 6006.5 | 5086.64 | 11093.14
20:30 | 5920 | 5054.735 | 10974.735 |  | Executive Engineer
21:00 | 5833.5 | 5022.83 | 10856.33 |  | Network Operation Division
21:30 | 5736.5 | 5027.39 | 10763.89
22:00 | 5639.5 | 5031.95 | 10671.45
22:30 | 5500.75 | 4811.03 | 10311.78
23:00 | 5362 | 4590.11 | 9952.11

## En-Curve
QF-LDC-12
Date | 14-02-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3404 | 1334 | 794 | 0 | 26 | 824.23 | 40 | 1715 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | DAILY ENERGY CURVE
00:30 | 3364.5 | 1247.5 | 700.5 | 0 | 28 | 824.55 | 40 | 1591.5 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 14-02-2026
01:00 | 3325 | 1161 | 607 | 0 | 30 | 824.87 | 40 | 1468 | 0 | 0 | 0 | 0 | 0 | 7 | 0
01:30 | 3297.5 | 1160.5 | 512.5 | 0 | 25 | 824.555 | 40 | 1462 | 0 | 0 | 0 | 0 | 0 | 10.5 | 0 | Energy Generated | 232.9973 |  | MKWHr
02:00 | 3270 | 1160 | 418 | 0 | 20 | 824.24 | 40 | 1456 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3238.5 | 1138.5 | 327.5 | 0 | 18 | 823.93 | 40 | 1455 | 0 | 0 | 0 | 0 | 0 | 17.5 | 0 | Total Energy Requirement | 232.9973 |  | MKWHr
03:00 | 3207 | 1117 | 237 | 0 | 16 | 823.62 | 40 | 1454 | 0 | 0 | 0 | 0 | 0 | 21 | 0
03:30 | 3119 | 1104 | 237 | 0 | 18 | 824.34 | 40 | 1448 | 0 | 0 | 0 | 0 | 0 | 27 | 0
04:00 | 3031 | 1091 | 237 | 0 | 20 | 825.06 | 40 | 1442 | 0 | 0 | 0 | 0 | 0 | 33 | 0
04:30 | 3048.5 | 1075.5 | 236.5 | 0 | 21 | 826.15 | 40 | 1449.5 | 0 | 0 | 0 | 0 | 0 | 29 | 0
05:00 | 3066 | 1060 | 236 | 0 | 22 | 827.24 | 40 | 1457 | 0 | 0 | 0 | 0 | 0 | 25 | 0
05:30 | 3123.5 | 1111.5 | 332.5 | 0 | 23 | 827.56 | 40 | 1465.5 | 0 | 0 | 0 | 0 | 0 | 24.5 | 0
06:00 | 3181 | 1163 | 429 | 0 | 24 | 827.88 | 40 | 1474 | 0 | 0 | 0 | 0 | 0 | 24 | 0
06:30 | 3354 | 1318.5 | 523.5 | 0 | 23 | 826.385 | 40 | 1567 | 11.4 | 0 | 10.5 | 0 | 0 | 19 | 0
07:00 | 3527 | 1474 | 618 | 0 | 22 | 824.89 | 40 | 1660 | 22.8 | 0 | 21 | 0 | 0 | 14 | 0
07:30 | 3516.5 | 1541.25 | 693 | 0 | 20 | 1003.32 | 40 | 1874.5 | 106.22 | 22 | 48 | 0 | 0 | 15.5 | 0
08:00 | 3506 | 1608.5 | 768 | 0 | 18 | 1181.75 | 40 | 2089 | 189.64 | 44 | 75 | 0 | 0 | 17 | 0
08:30 | 3490 | 1630.75 | 797 | 0 | 20 | 1254.38 | 40 | 2159 | 288.08 | 70.5 | 100.5 | 0 | 0 | 12 | 0
09:00 | 3474 | 1653 | 826 | 0 | 22 | 1327.01 | 40 | 2229 | 386.52 | 97 | 126 | 0 | 0 | 7 | 0
09:30 | 3480.5 | 1650.5 | 863.5 | 0 | 27 | 1274.505 | 40 | 2226.5 | 470.51 | 98 | 143 | 0 | 0 | 6 | 0
10:00 | 3487 | 1648 | 901 | 0 | 32 | 1222 | 40 | 2224 | 554.5 | 99 | 160 | 0 | 0 | 5 | 0
10:30 | 3541.5 | 1653 | 900.5 | 0 | 30 | 1202.105 | 40 | 2241.5 | 603.52 | 98.5 | 153 | 0 | 0 | 7 | 0
11:00 | 3596 | 1658 | 900 | 0 | 28 | 1182.21 | 40 | 2259 | 652.54 | 98 | 146 | 0 | 0 | 9 | 0
11:30 | 3630 | 1654 | 900.5 | 0 | 28 | 1207.23 | 40 | 2391.5 | 674.57 | 106 | 152 | 0 | 0 | 7.5 | 0
12:00 | 3664 | 1650 | 901 | 0 | 28 | 1232.25 | 40 | 2524 | 696.6 | 114 | 158 | 0 | 0 | 6 | 0
12:30 | 3643 | 1605.5 | 901 | 0 | 81 | 1313.89 | 40 | 2625.5 | 690.98 | 120 | 242.5 | 0 | 0 | 9 | 0
13:00 | 3622 | 1561 | 901 | 0 | 134 | 1395.53 | 40 | 2727 | 685.36 | 126 | 327 | 0 | 0 | 12 | 0
13:30 | 3488 | 1544.5 | 900.5 | 0 | 137 | 1383.55 | 40 | 2731.5 | 647.51 | 113.5 | 318.5 | 0 | 0 | 19 | 0
14:00 | 3354 | 1528 | 900 | 0 | 140 | 1371.57 | 40 | 2736 | 609.66 | 101 | 310 | 0 | 0 | 26 | 0
14:30 | 3340.5 | 1486.5 | 900.5 | 0 | 134 | 1318.16 | 40 | 2673.5 | 539.09 | 101 | 255 | 0 | 0 | 23 | 0
15:00 | 3327 | 1445 | 901 | 0 | 128 | 1264.75 | 40 | 2611 | 468.52 | 101 | 200 | 0 | 0 | 20 | 0
15:30 | 3334 | 1460.5 | 901 | 0 | 122 | 1198.825 | 40 | 2576.5 | 369.365 | 101 | 200.75 | 0 | 0 | 19.5 | 0
16:00 | 3341 | 1476 | 901 | 0 | 116 | 1132.9 | 40 | 2542 | 270.21 | 101 | 201.5 | 0 | 0 | 19 | 0
16:30 | 3362 | 1475.75 | 901 | 0 | 117 | 1178.88 | 40 | 2538 | 176.765 | 108.5 | 205.95 | 0 | 0 | 15.5 | 0
17:00 | 3383 | 1475.5 | 901 | 0 | 118 | 1224.86 | 40 | 2534 | 83.32 | 116 | 210.4 | 0 | 0 | 12 | 0
17:30 | 3306 | 1477.5 | 900.5 | 0 | 124 | 1298.48 | 40 | 2596 | 41.66 | 237.5 | 450.8 | 0 | 0 | 11 | 0
18:00 | 3229 | 1479.5 | 900 | 0 | 130 | 1372.1 | 40 | 2658 | 0 | 359 | 691.2 | 0 | 0 | 10 | 0
18:30 | 3239.5 | 1480 | 806 | 0 | 128 | 1416.185 | 40 | 2824.5 | 0 | 375 | 979.1 | 0 | 0 | 9 | 0
19:00 | 3250 | 1480.5 | 712 | 0 | 126 | 1460.27 | 40 | 2991 | 0 | 391 | 1267 | 0 | 0 | 8 | 0
19:30 | 3450 | 1539.5 | 712 | 0 | 126 | 1460.63 | 40 | 3090 | 0 | 180 | 500 | 0 | 0 | 8 | 0
20:00 | 3443 | 1476.5 | 712 | 0 | 118 | 1450.64 | 40 | 3225 | 0 | 180 | 442 | 0 | 0 | 6 | 0
20:30 | 3424 | 1490 | 712 | 0 | 116 | 1453.235 | 40 | 3272.5 | 0 | 135.5 | 326 | 0 | 0 | 5.5 | 0
21:00 | 3405 | 1503.5 | 712 | 0 | 114 | 1455.83 | 40 | 3320 | 0 | 91 | 210 | 0 | 0 | 5 | 0
21:30 | 3374.5 | 1494.5 | 806 | 0 | 112 | 1440.39 | 40 | 3239.5 | 0 | 62.5 | 190 | 0 | 0 | 4.5 | 0
22:00 | 3344 | 1485.5 | 900 | 0 | 110 | 1424.95 | 40 | 3159 | 0 | 34 | 170 | 0 | 0 | 4 | 0
22:30 | 3325.5 | 1464.25 | 900 | 0 | 111 | 1319.53 | 40 | 2997 | 0 | 17 | 133 | 0 | 0 | 4.5 | 0
23:00 | 3307 | 1443 | 900 | 0 | 112 | 1214.11 | 40 | 2835 | 0 | 0 | 96 | 0 | 0 | 5 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 14-02-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 427 | 04:00 | 409 | 08:00 | Madunaghat | 420 | 04:00 | 408 | 13:00
Amtali | 429 | 04:00 | 415 | 12:00 | Meghnaghat | 428 | 04:00 | 409 | 12:00
Ashuganj | 417 | 4:00 | 401 | 9:00 | Payra | 429 | 04:00 | 415 | 12:00
Bhulta | 414 | 04:00 | 395 | 12:00 | Rahanpur | 423 | 04:00 | 408 | 08:00
Bibiana | 425 | 02:00 | 413 | 12:00 | Rampal | 422 | 04:00 | 404 | 12:00
BIPTC | 408 | 04:00 | 389 | 10:00
Bogura | 421 | 04:00 | 402 | 13:00
Gopalganj | 427 | 04:00 | 407 | 12:00
Kaliakoir | 421 | 04:00 | 398 | 12:00
Korerhat | 428 | 04:00 | 411 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 244 | 04:00 | 228 | 12:00 | Jhenaidah | 245 | 04:00 | 225 | 13:00
AKSML | 242 | 02:00 | 232 | 12:00 | Kachua | 246 | 03:00 | 233 | 12:00
Aminbazar | 242 | 04:00 | 233 | 08:00 | Kaliakoir | 244 | 03:00 | 229 | 12:00
Ashuganj | 242 | 03:00 | 232 | 12:00 | Keranigonj | 243 | 04:00 | 226 | 12:00
Ashuganj-400 | 240 | 4:00 | 232 | 10:00 | Khulna(S) | 248 | 03:00 | 230 | 12:00
Baghabari | 244 | 03:00 | 231 | 10:00 | Korerhat | 244 | 04:00 | 232 | 12:00
Barapukuria | 230 | 04:00 | 212 | 08:00 | Madunaghat | 239 | 03:00 | 232 | 12:00
Barapukuria-230 | 230 | 4:00 | 213 | 9:00 | Madunaghat-400 | 241 | 04:00 | 233 | 12:00
Barishal | 241 | 03:00 | 231 | 12:00 | Maniknagar | 240 | 01:00 | 228 | 12:00
Bheramara | 244 | 04:00 | 226 | 12:00 | Meghnaghat | 248 | 05:00 | 234 | 12:00
Bhulta | 243 | 04:00 | 229 | 12:00 | Meghnaghat-400 | 242 | 04:00 | 229 | 12:00
Bibiana | 247 | 04:00 | 237 | 12:00 | Mirsorai | 243 | 05:00 | 233 | 12:00
BIPTC | 245 | 03:00 | 227 | 12:00 | Rajshahi | 242 | 04:00 | 224 | 13:00
Bogura | 240 | 04:00 | 227 | 08:00 | Rampal | 243 | 02:00 | 230 | 12:00
Bogura-400 | 239 | 04:00 | 226 | 08:00 | Rampur | N/A | N/A | N/A | N/A
Borhanuddin | 239 | 06:00 | 235 | 12:00 | Rampura | 242 | 04:00 | 227 | 13:00
BSRM | 243 | 05:00 | 233 | 12:00 | Shikalbaha | 239 | 04:00 | 232 | 11:00
Chowmuhani | N/A | N/A | N/A | N/A | Shyampur | 242 | 04:00 | 227 | 12:00
Cumilla(N) | 238 | 00:00 | 231 | 12:00 | Siddhirganj | 241 | 01:00 | 229 | 12:00
Faridpur | 240 | 03:00 | 228 | 12:00 | Sirajgonj | 247 | 04:00 | 237 | 13:00
Fenchuganj | 247 | 04:00 | 240 | 12:00 | Sreepur | 238 | 04:00 | 227 | 08:00
Feni | 244 | 04:00 | 233 | 12:00 | Tongi | 238 | 00:00 | 228 | 11:00
Ghorashal | 240 | 00:00 | 235 | 08:00
Ghorashal-230 | 243 | 04:00 | 228 | 12:00
Gopalganj | 239 | 04:00 | 227 | 12:00
GPH | 241 | 04:00 | 234 | 08:00
Haripur | 243 | 04:00 | 229 | 12:00
Hasnabad | 240 | 00:00 | 226 | 12:00
Hathazari | 238 | 00:00 | 231 | 13:00
Ishurdi | 246 | 04:00 | 230 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 05:00 | 125 | 12:00 | Mahasthangarh | 135 | 02:00 | 123 | 08:00
Agargaon | 139 | 04:00 | 129 | 12:00 | Maijdee | 137 | 04:00 | 130 | 12:00
Agrabad | 139 | 03:00 | 133 | 12:00 | Manikganj | 133 | 05:00 | 123 | 12:00
AKS | 135 | 00:00 | 131 | 13:00 | Maniknagar | 137 | 03:00 | 128 | 12:00
Aminbazar | 138 | 04:00 | 131 | 16:00 | Matarbari | 131 | 02:00 | 124 | 19:30
Amnura | 140 | 02:00 | 130 | 12:00 | Matuail | 138 | 01:00 | 131.5 | 12:00
Ashuganj | 140 | 00:00 | 137 | 08:00 | Metrorail_Motijheel | 137 | 03:00 | 128 | 12:00
Bagerhat | 138 | 04:00 | 123 | 13:00 | Metrorail_Uttara | 135 | 03:00 | 124 | 12:00
Bajitpur | 136 | 02:00 | 127 | 13:00 | Millgate | 136 | 04:00 | 124 | 12:00
Bakerganj | 140 | 03:00 | 135 | 12:00 | Mirpur | 136 | 00:00 | 127 | 12:00
Bakulia | 138 | 03:00 | 134 | 10:00 | Mirzapur | 136 | 04:00 | 127 | 08:00
Banani | 134 | 02:00 | 125 | 12:00 | Mithapukur | 134 | 04:00 | 120 | 08:00
Bangabhaban | 135 | 01:00 | 128 | 12:00 | MI_Cement | 138 | 04:00 | 125 | 12:00
Barapukuria | 134 | 02:00 | 121 | 08:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 140 | 01:00 | 135 | 12:00 | Mogbazar | 137 | 02:00 | 126 | 12:00
Barishal | 141 | 02:00 | 133 | 12:00 | Mongla | 137 | 04:00 | 124 | 12:00
Barishal-230 | 142 | 04:00 | 133 | 12:00 | Motijheel | 135 | 01:00 | 128 | 12:00
Baroaulia | 139 | 01:00 | 133 | 14:00 | Muktagacha | 132 | 20:00 | 123 | 08:00
Baroirhat | 138 | 00:00 | 133 | 12:00 | Munshiganj | 137 | 03:00 | 130 | 12:00
Bashundhara | 135 | 04:00 | 125 | 12:00 | Muradnagar | 140 | 04:00 | 131 | 12:00
BashundharaCement | 139 | 04:00 | 132 | 12:00 | Mymensingh | 132 | 22:00 | 117 | 08:00
Beanibazar | 136 | 04:00 | 130 | 12:00 | Naogaon | 135 | 04:00 | 121 | 08:00
Benapole | 137 | 03:00 | 121 | 13:00 | Narail | 141 | 04:00 | 125 | 13:00
Bhaluka | 134 | 04:00 | 123 | 08:00 | Narinda | 137 | 3:00 | 128 | 12:00
Bhandaria | 137 | 03:00 | 131 | 11:00 | Narshingdi | 135 | 03:00 | 128 | 12:00
Bhangura | 138 | 00:00 | 131 | 13:00 | Natore | 137 | 00:00 | 128 | 13:00
Bheramara | 141 | 04:00 | 134 | 12:00 | Nawabganj | 137 | 03:00 | 126 | 12:00
Bheramara(GK) | 141 | 03:00 | 133 | 13:00 | Netrakona | 127 | 03:00 | 111 | 08:00
Bhulta | 130 | 00:00 | 127 | 11:00 | New | 134 | 00:00 | 125 | 12:00
Bog-Sherpur | 138 | 04:00 | 127 | 08:00 | Niamatpur | 141 | 02:00 | 134 | 13:00
Bogura | 137 | 03:00 | 128 | 09:00 | Noapara | 138 | 04:00 | 125 | 12:00
Bogura-230 | 137 | 03:00 | 127 | 08:00 | Pabna | 141 | 04:00 | 132 | 12:00
Brahmanbaria | 135 | 02:00 | 130 | 12:00 | Palashbari | 132 | 00:00 | 119 | 08:00
Cantonment | 138 | 03:00 | 128 | 12:00 | Panchagarh | 136 | 00:00 | 123 | 08:00
Chandina | 141 | 03:00 | 133 | 12:00 | Patiya | 139 | 02:00 | 133 | 12:00
Chandpur | 139 | 04:00 | 132 | 10:00 | Patuakhali | 140 | 19:00 | 135 | 11:00
Chandraghona | 140 | 01:00 | 135 | 12:00 | Payra | 141 | 05:00 | 137 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 137 | 00:00 | 133 | 13:00 | PHP | 139 | 04:00 | 132 | 12:00
Charsaidpur | 139 | 03:00 | 130 | 12:00 | Postogola | 138 | 02:00 | 127 | 12:00
Chauddagram | 138 | 02:00 | 131 | 12:00 | Purbachal | 135 | 03:00 | 125 | 12:00
Chhatak | 134 | 01:00 | 129 | 13:00 | Purbasadipur | 132 | 03:00 | 120 | 08:00
Chowmuhani | 134 | 02:00 | 129 | 12:00 | Rahanpur | 142 | 23:00 | 136 | 07:00
Chuadanga | 140 | 03:00 | 122 | 13:00 | Rahanpur-400 | 142 | 03:00 | 136 | 08:00
Coxsbazar | 129 | 00:00 | 125 | 21:00 | Rahim | 137 | 00:00 | 131 | 12:00
Cumilla(N) | 139 | 00:00 | 133 | 12:00 | Rajbari | 138 | 02:00 | 131 | 12:00
Cumilla(S) | 139 | 19:00 | 122 | 13:00 | Rajendrapur | 136 | 03:00 | 125 | 09:00
Daganbhuiyan | 137 | 03:00 | 132 | 09:00 | Rajshahi | 140 | 01:00 | 128 | 13:00
Daudkandi | 138 | 05:00 | 129 | 12:00 | Rajshahi-230 | 140 | 04:00 | 129 | 12:00
DhakaUniversity | 134 | 02:00 | 126 | 12:00 | Ramganj | 136 | 01:00 | 128 | 12:00
Dhamrai | 138 | 01:00 | 129 | 08:00 | Rampur | 139 | 03:00 | 133 | 12:00
Dhanmondi | 140 | 03:00 | 132 | 12:00 | Rampura | 134 | 03:00 | 125 | 12:00
Dohazari | 136 | 04:00 | 131 | 11:00 | Rangamati | 140 | 04:00 | 134 | 12:00
Faridpur | 139 | 04:00 | 132 | 12:00 | Rangpur | 133 | 02:00 | 120 | 08:00
Fatullah | 139 | 03:00 | 125 | 12:00 | Ruppur | 141 | 04:00 | 133 | 13:00
Fenchuganj | 140 | 05:00 | 135 | 13:00 | Saidpur | 132 | 03:00 | 118 | 08:00
Feni | 136 | 19:00 | 130 | 12:00 | Satkhira | 136 | 03:00 | 122 | 13:00
Feni-230 | 137 | 03:00 | 131 | 12:00 | Satmasjid | 139 | 04:00 | 128 | 12:00
Ghatail | 132 | 03:00 | 120 | 07:00 | Savar | 135 | 00:00 | 125 | 12:00
Ghorashal | 144 | 00:00 | 141 | 08:00 | SevenRings | 147 | 04:00 | 140 | 12:00
Goalpara | 140 | 03:00 | 127 | 12:00 | ShahCement | 139 | 03:00 | 130 | 12:00
Gollamari | 139 | 04:00 | 127 | 13:00 | Shahjadpur | 143 | 04:00 | 136 | 07:00
Gopalganj | 140 | 02:00 | 131 | 12:00 | Shahjibazar | 136 | 04:00 | 131 | 12:00
Gopalganj-400 | 143 | 03:00 | 135 | 12:00 | Shahmirpur | 140 | 03:00 | 134 | 12:00
Gulshan | 133 | 04:00 | 125 | 12:00 | Shariatpur | 142 | 04:00 | 133 | 12:00
Halishahar | 140 | 04:00 | 134 | 11:00 | Sherpur | 125 | 05:00 | 113 | 08:00
Haripur | 139 | 04:00 | 131 | 12:00 | Shikalbaha | 129 | 05:00 | 122 | 13:00
HaripurSBU | 139 | 04:00 | 132 | 12:00 | Shikalbaha-230 | 140 | 01:00 | 135 | 11:00
Hasnabad | 138 | 03:00 | 127 | 12:00 | Shitalakhya | 138 | 04:00 | 125 | 12:00
Hathazari | 140 | 00:00 | 135 | 13:00 | Sholosohor | 140 | 19:00 | 135 | 10:00
Hatirjheel | 135 | 04:00 | 126 | 12:00 | Shyampur | 139 | 04:00 | 130 | 12:00
Ishurdi | 143 | 04:00 | 135 | 12:00 | Shyampur-230 | 141 | 04:00 | 131 | 12:00
Jaldhaka | 130 | 02:00 | 117 | 08:00 | Siddhirganj | 139 | 02:00 | 131 | 12:00
Jamalpur | 128 | 05:00 | 118 | 08:00 | Sirajganj | 140 | 04:00 | 128 | 08:00
Jashore | 138 | 02:00 | 123 | 12:00 | Sonargaon | 138 | 01:00 | 130 | 12:00
Jhenaidah | 140 | 00:00 | 127 | 13:00 | Sreemongol | 136 | 01:00 | 132 | 12:00
Jhenaidah-230 | 142 | 04:00 | 128 | 13:00 | Sreepur | 137 | 03:00 | 128 | 09:00
Joydebpur | 140 | 23:00 | 125 | 12:00 | Srinagar | 137 | 03:00 | 126 | 12:00
Joypurhat | 132 | 01:00 | 118 | 08:00 | SSM | 140 | 00:00 | 140 | 00:00
Juldah | 139 | 19:00 | 133 | 12:00 | Sunamganj | 133 | 02:00 | 126 | 11:00
Kabirpur | 138 | 03:00 | 123 | 12:00 | Sylhet | 136 | 04:00 | 131 | 12:00
Kachua | 140 | 02:00 | 133 | 10:00 | Sylhet-132 | 135 | 01:00 | 131 | 13:00
Kaliakoir | 141 | 02:00 | 132 | 08:00 | Tangail | 131 | 00:00 | 123 | 07:00
Kaliganj | N/A | N/A | N/A | N/A | Taraganj | 132 | 02:00 | 120 | 08:00
Kallyanpur | 137 | 03:00 | 128 | 12:00 | Tasnim | 139 | 03:00 | 130 | 12:00
Kalurghat | 140 | 02:00 | 136 | 10:00 | Thakurgaon | 134 | 04:00 | 121 | 08:00
Kamrangirchar | 136 | 00:00 | 125 | 12:00 | TK | 140 | 03:00 | 135 | 12:00
Kaptai | N/A | N/A | N/A | N/A | Tongi | 135 | 04:00 | 126 | 11:00
Kasba | 139 | 04:00 | 130 | 12:00 | Ullahpara | 138 | 00:00 | 130 | 12:00
Kazla | 138 | 06:00 | 127 | 13:00 | Ullon | 134 | 05:00 | 125 | 12:00
Keranigonj | 138 | 04:00 | 126 | 12:00 | Uttara | 136 | 04:00 | 125 | 12:00
Khagrachori | 140 | 03:00 | 133 | 13:00 | UttaraNew | 135 | 03:00 | 124 | 12:00
Khulna | 138 | 05:00 | 126 | 12:00 | Zigatola | 138 | 05:00 | 126 | 13:00
Khulna(S) | 139 | 03:00 | 127 | 13:00
Khulshi | 137 | 04:00 | 131 | 12:00
Kishoreganj | 133 | 00:00 | 127 | 09:00
Kodda | 136 | 19:30 | 124 | 09:00
KSRM | 139 | 00:00 | 134 | 12:00
Kulaura | 139 | 02:00 | 135 | 12:00
Kurigram | 131 | 18:30 | 120 | 08:00
Kushtia | 139 | 00:00 | 132 | 12:00
Laksam | 137 | 00:00 | 131 | 11:00
Lakshmipur | 136 | 02:00 | 130 | 12:00
Lalbag | 137 | 06:00 | 125 | 13:00
Lalmonirhat | 130 | 23:00 | 116 | 08:00
Madanganj | 139 | 04:00 | 132 | 12:00
Madaripur | 140 | 04:00 | 136 | 15:00
Madartek | 134 | 05:00 | 125 | 12:00
Madunaghat | 140 | 04:00 | 135 | 12:00
Magura | 140 | 03:00 | 125 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division