## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 17-02-2026 | [28 empty] | Date: | 17-02-2026 | [28 empty] | Date: | 17-02-2026 | [28 empty] | Date: | 17-02-2026 | [28 empty] | Date: | 17-02-2026 | [17 empty] | Date: | 17-02-2026
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [17 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 32 | 875 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 872 | 0 | 0 | 0 | 0 | 275 | 139 | 51 | 0 | 189 | 0 | 0 | 104 | 0 | 0 | 20 | 0 | 88 | 0 | 0 | 0 | 305 | 0 | 314 | 30 | 23 | 133 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 99 | 0 | 59 | 19 | 0 | 0 | 0 | 0 | 5416 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 779 | 0 | 0 | 0 | 1120.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 130 | 220 | 0 | 0 | 800 | 0 | 4680.65 | 10096.65 | 93.76
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 32 | 720 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 810 | 0 | 0 | 0 | 0 | 275 | 200 | 51 | 0 | 188 | 0 | 0 | 105 | 0 | 0 | 14 | 0 | 88 | 0 | 0 | 0 | 305 | 0 | 316 | 30 | 23 | 133 | 0 | 17 | 0 | 83 | 20 | 0 | 0 | 100 | 0 | 59 | 19 | 0 | 0 | 0 | 0 | 5155 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753 | 0 | 0 | 0 | 923.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 130 | 220 | 0 | 0 | 560 | 0 | 4252.5 | 9407.5 | 93.76
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 827 | 0 | 0 | 0 | 0 | 295 | 200 | 5 | 0 | 195 | 0 | 0 | 51 | 0 | 0 | 14 | 0 | 82 | 0 | 0 | 0 | 310 | 0 | 323 | 30 | 23 | 134 | 0 | 0 | 0 | 5 | 20 | 0 | 0 | 100 | 0 | 59 | 19 | 0 | 0 | 0 | 0 | 4977 | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 833.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 4009.16 | 8986.16 | 93.75
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 466 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 630 | 0 | 0 | 0 | 0 | 295 | 200 | 5 | 0 | 200 | 0 | 0 | 50 | 0 | 0 | 14 | 0 | 82 | 0 | 0 | 0 | 305 | 0 | 336 | 20 | 16 | 136 | 0 | 0 | 0 | 5 | 20 | 0 | 0 | 100 | 0 | 45 | 8 | 0 | 0 | 0 | 0 | 4623 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 827.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3962.61 | 8585.61 | 93.75
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 613 | 0 | 0 | 0 | 0 | 290 | 200 | 5 | 0 | 195 | 0 | 0 | 50 | 0 | 0 | 14 | 0 | 84 | 0 | 0 | 0 | 310 | 0 | 330 | 20 | 16 | 136 | 0 | 0 | 0 | 5 | 7 | 0 | 0 | 100 | 0 | 45 | 8 | 0 | 0 | 0 | 0 | 4532 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 762 | 0 | 0 | 0 | 830.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3897.86 | 8429.86 | 93.74
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 616 | 0 | 0 | 0 | 0 | 285 | 200 | 5 | 0 | 196 | 0 | 0 | 50 | 0 | 0 | 14 | 0 | 86 | 0 | 0 | 0 | 300 | 0 | 320 | 20 | 16 | 135 | 0 | 0 | 0 | 5 | 7 | 0 | 0 | 100 | 0 | 45 | 8 | 0 | 0 | 0 | 0 | 4379 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757 | 0 | 0 | 0 | 830.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3962.35 | 8341.35 | 93.74
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 7 | 720 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 0 | 305 | 200 | 5 | 0 | 230 | 0 | 0 | 106 | 0 | 0 | 11 | 0 | 86 | 0 | 0 | 0 | 305 | 0 | 338 | 20 | 23 | 137 | 0 | 0 | 0 | 5 | 7 | 0 | 0 | 100 | 0 | 58 | 19 | 0 | 0 | 0 | 0 | 4719 | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 769 | 0 | 0 | 0 | 831.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 100 | 180 | 0 | 0 | 540 | 0 | 3996.84 | 8715.84 | 93.73
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 311 | 0 | 0 | 1 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0.19 | 75 | 0 | 37 | 875 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 1015 | 2 | 0 | 0 | 0 | 270 | 200 | 31 | 0 | 228 | 0 | 0 | 106 | 0 | 0 | 11 | 0 | 92 | 0 | 4 | 0 | 310 | 0 | 351 | 30 | 23 | 137 | 0 | 17 | 0 | 76 | 30 | 0 | 0 | 100 | 0 | 58 | 19 | 0 | 0 | 1.69 | 0 | 5500.88 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.58 | 769 | 0 | 0 | 0 | 833.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.51 | 3 | 0 | 0 | 1.65 | 137 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0.18 | 0 | 55 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 6 | 0.02 | 0 | 221 | 100 | 180 | 0 | 0 | 645 | 0 | 4177.55 | 9678.43 | 93.73
08:00 | 0 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 32 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 0 | 0 | 324 | 0 | 0 | 8 | 52 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1.02 | 75 | 0 | 14 | 875 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 1105 | 7 | 0 | 0 | 0 | 270 | 200 | 51 | 0 | 230 | 0 | 0 | 106 | 0 | 0 | 11 | 0 | 98 | 0 | 22 | 0 | 300 | 0 | 357 | 30 | 23 | 136 | 2 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 58 | 19 | 0 | 1 | 13.67 | 4 | 5854.69 | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 826 | 0 | 0 | 0 | 988.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.22 | 23 | 0 | 0 | 13.51 | 140 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 54 | 35 | 7 | 34 | 0 | 0 | 0 | 1.1 | 39 | 0.13 | 0 | 219 | 130 | 220 | 0 | 0 | 896 | 0 | 4926.53 | 10781.22 | 93.72
09:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 50 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425 | 0 | 0 | 330 | 0 | 0 | 17 | 52 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 2.11 | 75 | 0 | 7 | 875 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 1105 | 13 | 0 | 0 | 0 | 270 | 200 | 51 | 0 | 226 | 0 | 0 | 106 | 0 | 0 | 11 | 0 | 104 | 0 | 40 | 0 | 315 | 0 | 322 | 30 | 23 | 153 | 6 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 58 | 19 | 0 | 1 | 26.03 | 6 | 5929.14 | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 871 | 0 | 0 | 0 | 1024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.49 | 49 | 0 | 0 | 29.6 | 140 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 2.72 | 0 | 54 | 35 | 15 | 34 | 0 | 0 | 0 | 3.1 | 88 | 0.28 | 0 | 220 | 130 | 220 | 0 | 0 | 1000 | 0 | 5253.19 | 11182.33 | 93.71
10:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 50 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 0 | 335 | 0 | 0 | 24 | 52 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 2.96 | 75 | 0 | 11 | 875 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1080 | 17 | 0 | 0 | 0 | 270 | 200 | 51 | 0 | 227 | 0 | 0 | 105 | 0 | 0 | 11 | 0 | 88 | 0 | 53 | 0 | 305 | 0 | 316 | 30 | 23 | 146 | 9 | 17 | 0 | 77 | 30 | 0 | 0 | 100 | 0 | 58 | 19 | 0 | 2 | 36.37 | 6 | 5899.33 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 847 | 0 | 0 | 0 | 1023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.18 | 76 | 0 | 0 | 45.31 | 140 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 4.11 | 0 | 54 | 0 | 23 | 34 | 0 | 0 | 0 | 4.5 | 131 | 0.42 | 0 | 216 | 130 | 180 | 0 | 0 | 990 | 0 | 5230.52 | 11129.85 | 93.7
11:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 0 | 50 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 330 | 0 | 0 | 28 | 52 | 7 | 21 | 0 | 0 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3.38 | 35 | 0 | 8 | 875 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1110 | 19 | 0 | 0 | 0 | 270 | 200 | 51 | 0 | 223 | 0 | 0 | 102 | 0 | 0 | 8 | 0 | 88 | 0 | 64 | 0 | 315 | 0 | 340 | 10 | 23 | 140 | 11 | 17 | 0 | 77 | 20 | 0 | 0 | 100 | 0 | 59 | 19 | 0 | 2 | 42.34 | 6 | 5851.72 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 864 | 0 | 0 | 0 | 1024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.76 | 91 | 0 | 0 | 55.21 | 158 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.21 | 0 | 56 | 0 | 30 | 34 | 0 | 0 | 0 | 5.5 | 163 | 0.53 | 0 | 222 | 100 | 180 | 0 | 0 | 992 | 0 | 5416.21 | 11267.93 | 93.69
12:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 50 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 0 | 0 | 327 | 0 | 0 | 30 | 52 | 21 | 22 | 0 | 0 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.56 | 35 | 0 | 10 | 875 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1110 | 20 | 0 | 0 | 0 | 270 | 230 | 51 | 0 | 220 | 0 | 0 | 99 | 0 | 0 | 8 | 0 | 94 | 0 | 68 | 0 | 315 | 0 | 352 | 16 | 23 | 144 | 12 | 17 | 0 | 80 | 30 | 0 | 0 | 99 | 0 | 59 | 19 | 0 | 2 | 44.51 | 6 | 6022.07 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 861 | 0 | 0 | 0 | 1232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.68 | 99 | 0 | 0 | 61.19 | 174 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.86 | 0 | 54 | 0 | 32 | 34 | 0 | 0 | 0 | 5.9 | 177 | 0.56 | 0 | 221 | 125 | 220 | 0 | 0 | 1000 | 0 | 5743.19 | 11765.26 | 93.68
13:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 50 | 48 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 540 | 0 | 0 | 325 | 0 | 0 | 29 | 52 | 21 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.47 | 35 | 0 | 8 | 875 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1140 | 19 | 0 | 0 | 0 | 270 | 230 | 51 | 0 | 219 | 0 | 0 | 99 | 0 | 0 | 14 | 0 | 96 | 0 | 65 | 0 | 325 | 0 | 319 | 16 | 23 | 160 | 11 | 17 | 0 | 80 | 30 | 0 | 0 | 99 | 0 | 58 | 19 | 0 | 2 | 44.66 | 6 | 6170.13 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 930 | 0 | 0 | 0 | 1312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.36 | 99 | 0 | 0 | 59.48 | 177 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.9 | 0 | 54 | 0 | 32 | 34 | 0 | 0 | 0 | 5.9 | 169 | 0.54 | 0 | 276 | 125 | 220 | 0 | 0 | 1030 | 0 | 5960.18 | 12130.31 | 93.67
14:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 50 | 48 | 0 | 0 | 17 | 14 | 0 | 0 | 0 | 530 | 0 | 0 | 322 | 0 | 0 | 27 | 52 | 21 | 21 | 0 | 0 | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.99 | 70 | 0 | 6 | 875 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1140 | 16 | 0 | 0 | 0 | 270 | 230 | 51 | 0 | 217 | 0 | 0 | 99 | 0 | 0 | 13 | 0 | 102 | 6 | 56 | 0 | 315 | 0 | 366 | 16 | 23 | 155 | 10 | 17 | 0 | 80 | 30 | 0 | 0 | 98 | 0 | 58 | 19 | 0 | 2 | 39.16 | 6 | 6206.15 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 910 | 0 | 0 | 0 | 1266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.04 | 89 | 0 | 0 | 50.87 | 182 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 54 | 0 | 29 | 34 | 0 | 0 | 0 | 5.1 | 154 | 0.44 | 0 | 218 | 125 | 220 | 0 | 0 | 920 | 0 | 5680.45 | 11886.6 | 93.66
15:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 50 | 48 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 525 | 0 | 0 | 300 | 0 | 0 | 23 | 52 | 21 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 2.24 | 70 | 0 | 6 | 875 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1105 | 12 | 0 | 0 | 0 | 270 | 230 | 51 | 0 | 219 | 0 | 0 | 98 | 0 | 0 | 13 | 0 | 104 | 52 | 41 | 0 | 310 | 0 | 320 | 42 | 23 | 140 | 8 | 16 | 0 | 80 | 30 | 0 | 0 | 98 | 0 | 58 | 19 | 0 | 1 | 30.72 | 6 | 6089.96 | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 900 | 0 | 0 | 0 | 1228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.88 | 67 | 0 | 0 | 38.52 | 183 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.7 | 0 | 54 | 0 | 22 | 0 | 0 | 0 | 0 | 3.8 | 120 | 0.32 | 0 | 174 | 125 | 180 | 0 | 0 | 930 | 0 | 5425.22 | 11515.18 | 93.65
16:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 50 | 48 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 525 | 0 | 0 | 280 | 0 | 0 | 13 | 52 | 21 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 1.29 | 70 | 0 | 6 | 875 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1055 | 7 | 0 | 0 | 0 | 270 | 230 | 51 | 0 | 201 | 0 | 0 | 98 | 0 | 0 | 13 | 0 | 102 | 52.2 | 25 | 0 | 315 | 0 | 323 | 42 | 23 | 137 | 4 | 19 | 0 | 82 | 30 | 0 | 0 | 99 | 0 | 58 | 19 | 0 | 1 | 17.95 | 6 | 5961.44 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 886 | 0 | 0 | 0 | 1164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.72 | 48 | 0 | 0 | 22.97 | 186 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.22 | 0 | 55 | 0 | 14 | 0 | 0 | 0 | 0 | 2.3 | 71 | 0.2 | 0 | 180 | 125 | 180 | 0 | 0 | 890 | 0 | 5188.41 | 11149.85 | 93.64
17:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 50 | 80 | 15 | 0 | 15 | 14 | 0 | 0 | 0 | 535 | 0 | 0 | 280 | 0 | 0 | 5 | 52 | 20 | 21 | 0 | 0 | 118 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0.39 | 70 | 0 | 14 | 875 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1060 | 2 | 1 | 0 | 0 | 305 | 230 | 51 | 0 | 203 | 0 | 0 | 99 | 0 | 0 | 13 | 0 | 94 | 52.2 | 8 | 0 | 315 | 0 | 326 | 42 | 23 | 141 | 1 | 13 | 0 | 85 | 30 | 0 | 0 | 99 | 0 | 58 | 19 | 0 | 0 | 4.61 | 6 | 6051.2 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 900 | 0 | 0 | 0 | 1157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.97 | 17 | 0 | 0 | 5.7 | 187 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.62 | 0 | 55 | 0 | 4 | 21 | 0 | 0 | 0 | 0.7 | 23 | 0.07 | 0 | 180 | 125 | 180 | 0 | 0 | 891 | 0 | 5075.06 | 11126.26 | 93.63
18:00 | 0 | 52 | 20 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 20 | 11 | 76 | 80 | 48 | 0 | 28 | 50 | 0 | 0 | 0 | 525 | 0 | 20 | 280 | 0 | 0 | 0 | 90 | 20 | 20 | 0 | 0 | 45 | 16 | 0 | 0 | 2 | 17 | 0 | 0 | 0 | 12 | 0 | 70 | 9 | 16 | 875 | 0 | 0 | 3 | 0 | 12 | 220 | 0 | 0 | 0 | 1160 | 0 | 21 | 0 | 0 | 295 | 250 | 51 | 0 | 199 | 0 | 14 | 98 | 6 | 0 | 13 | 0 | 124 | 52.2 | 0 | 0 | 310 | 0 | 340 | 42 | 23 | 137 | 0 | 11 | 0 | 86 | 30 | 0 | 0 | 98 | 7 | 59 | 19 | 0 | 0 | 0 | 6 | 6401.2 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 910 | 0 | 0 | 0 | 1271 | 0 | 0 | 0 | 10 | 2 | 0 | 13 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 35 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 229 | 125 | 180 | 0 | 0 | 902 | 6 | 5292 | 11693.2 | 93.62
19:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 29.7 | 35 | 78 | 62 | 80 | 0 | 35 | 66 | 0 | 0 | 0 | 535 | 0 | 35 | 327 | 0 | 0 | 0 | 90 | 20 | 20 | 0 | 0 | 0 | 16 | 0 | 0 | 2 | 17 | 0 | 0 | 0 | 0 | 0 | 70 | 40 | 21 | 875 | 0 | 0 | 18 | 0 | 44 | 226 | 0 | 0 | 0 | 1145 | 0 | 50 | 0 | 0 | 295 | 300 | 51 | 0 | 193 | 0 | 31 | 101 | 34 | 0 | 13 | 0 | 116 | 52.2 | 0 | 0 | 310 | 0 | 362 | 42 | 23 | 134 | 0 | 11 | 0 | 86 | 30 | 0 | 0 | 98 | 0 | 59 | 19 | 0 | 0 | 0 | 3 | 6693.9 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1022 | 0 | 0 | 0 | 1428 | 0 | 0 | 0 | 16 | 33 | 0 | 34 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 274 | 130 | 220 | 0 | 0 | 990 | 0 | 5801 | 12494.9 | 93.61
19:30 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 29.7 | 17 | 78 | 48 | 0 | 0 | 35 | 34 | 0 | 0 | 0 | 540 | 0 | 17 | 328 | 0 | 0 | 0 | 90 | 20 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 17 | 25 | 875 | 0 | 0 | 0 | 0 | 34 | 227 | 0 | 0 | 0 | 1160 | 0 | 24 | 0 | 0 | 295 | 330 | 51 | 0 | 196 | 0 | 32 | 101 | 33 | 0 | 13 | 0 | 114 | 52.2 | 0 | 0 | 310 | 0 | 368 | 42 | 23 | 132 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 98 | 0 | 59 | 19 | 0 | 0 | 0 | 4 | 6501.9 | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1026 | 0 | 0 | 0 | 1391 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 130 | 220 | 0 | 0 | 1020 | 0 | 5736 | 12237.9
20:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 21 | 0 | 78 | 48 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 535 | 0 | 0 | 328 | 0 | 0 | 0 | 70 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 27 | 875 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 1162 | 0 | 0 | 0 | 0 | 305 | 350 | 51 | 0 | 204 | 0 | 0 | 105 | 0 | 0 | 13 | 0 | 116 | 52.2 | 0 | 0 | 310 | 0 | 386 | 42 | 23 | 135 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 98 | 0 | 59 | 19 | 0 | 0 | 0 | 4 | 6324.2 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1026 | 0 | 0 | 0 | 1374 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 130 | 220 | 0 | 0 | 1036 | 0 | 5703 | 12027.2 | 93.6
21:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 78 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 328 | 0 | 0 | 0 | 70 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 30 | 875 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 0 | 305 | 355 | 51 | 0 | 202 | 0 | 0 | 105 | 0 | 0 | 13 | 0 | 114 | 52.2 | 0 | 0 | 315 | 0 | 392 | 41 | 23 | 142 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 98 | 0 | 59 | 19 | 0 | 0 | 0 | 6 | 6313.2 | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1026 | 0 | 0 | 0 | 1310 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 130 | 220 | 0 | 0 | 1050 | 0 | 5597 | 11910.2 | 93.59
22:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 78 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 535 | 0 | 0 | 317 | 0 | 0 | 0 | 35 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 25 | 875 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 1102 | 0 | 0 | 0 | 0 | 295 | 360 | 51 | 0 | 197 | 0 | 0 | 106 | 0 | 0 | 13 | 0 | 104 | 52.2 | 0 | 0 | 300 | 0 | 372 | 41 | 23 | 137 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 98 | 0 | 59 | 19 | 0 | 0 | 0 | 6 | 6084.2 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 972 | 0 | 0 | 0 | 1262 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 130 | 220 | 0 | 0 | 950 | 0 | 5335 | 11419.2 | 93.58
23:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 0 | 0 | 313 | 0 | 0 | 0 | 17 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 27 | 875 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 1102 | 0 | 0 | 0 | 0 | 295 | 365 | 51 | 0 | 197 | 0 | 0 | 106 | 0 | 0 | 13 | 0 | 106 | 0 | 0 | 0 | 305 | 0 | 372 | 41 | 23 | 136 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 98 | 0 | 59 | 18 | 0 | 0 | 0 | 6 | 5922 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 832 | 0 | 0 | 0 | 1096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 130 | 220 | 0 | 0 | 850 | 0 | 4844 | 10766 | 93.57
Total KWH | 0 | 636480 | 278400 | 0 | 0 | 0 | 0 | 0 | 8838000 | 0 | 0 | 66960 | 66600 | 1084896 | 784320 | 164095 | 0 | 178180 | 227520 | 0 | 0 | 0 | 11306285 | 0 | 82575 | 7418758 | 0 | 0 | 207946 | 938400 | 457800 | 471240 | 0 | 0 | 835527 | 37636 | 0 | 0 | 140160 | 27315 | 0 | 0 | 0 | 13440 | 23641 | 1640860 | 72764 | 376800 | 20130909.09 | 0 | 0 | 31200 | 0 | 98691 | 4991450 | 0 | 0 | 0 | 24027270 | 132975 | 120436 | 0 | 0 | 7220100 | 5964000 | 1043399 | 0 | 5138000 | 0 | 74880 | 2194293 | 72480 | 0 | 329700 | 0 | 2309760 | 432250 | 446618 | 0 | 7509000 | 0 | 8465000 | 732000 | 554040 | 3366573 | 74130 | 306648 | 0 | 1524480 | 609120 | 0 | 0 | 2379410 | 21960 | 1374000 | 405600 | 0 | 13700 | 301750 | 97920 | 138870340.09 | 21760000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 532800 | 20843660 | 0 | 0 | 0 | 26306182 | 0 | 0 | 0 | 39360 | 52416 | 0 | 153728 | 0 | 0 | 305432 | 671830 | 44681 | 0 | 380256 | 3912091 | 0 | 0 | 0 | 0 | 0 | 9445890 | 0 | 30300 | 0 | 1354909 | 166909 | 211039 | 365270 | 0 | 0 | 0 | 38279.76 | 1142640 | 3523 | 30432 | 4953000 | 2865000 | 5221480 | 0 | 0 | 20903272.73 | 22800 | 121757180.49 | 260627520.58

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 18-02-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-02-2026 | during | 18-02-2026 | during | 18-02-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 10 | Demand "0"MW due to gas restriction by Titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 331 | 317 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 327 | 327 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 29.7 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 48 | 62 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 20 | 4.4 | 4.4 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 20 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 80 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 50 | 78 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 52 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 66 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 410 | 410 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 440 | 535 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 90 | 160 | 160 | 52 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1371 | 1806.7 | 5743.62 | 5712.62 | 2515.05 | 2638.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | U#1 Under maintenance, U#2 Running
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 18 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 35 | 70 | 75 | 75 | 75 | 75 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 220 | 226 | 225 | 225 | 225 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 44 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 16 | 16 | 16 | 16 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 51 | 51 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 10 | 21 | 5 | 12 | 40 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.56 | 0 | 3.54 | 0 | 3.54 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 16 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 40 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 119 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1110 | 1145 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 2 | 0 | 11 | 0 | 11 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 875 | 875 | 875 | 875 | 875 | 875 | ps availability is less
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2392.56 | 2474 | 3726.4 | 3720.86 | 3229.04 | 3216.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 220 | 193 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 270 | 295 | 353.35 | 353.35 | 353.35 | 353.35 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 230 | 300 | 318.81 | 318.81 | 318.81 | 318.81 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0 | 0 | Gas shortage as per NLDC instructions.
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 50 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 42 | 42 | 42 | 42 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 99 | 101 | 163 | 163 | 110 | 110 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 34 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 94 | 116 | 84 | 82 | 118 | 118 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 8 | 13 | 24.5 | 24.5 | 13 | 13 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 31 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1040 | 1236.2 | 2761.56 | 2689.56 | 1879.36 | 1809.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-02-2026 | during | 18-02-2026 | during | 18-02-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 35 | 35 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 19 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 59 | 60 | 60 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 44.51 | 0 | 45.12 | 0 | 45.12 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 3 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 130.51 | 81 | 361.32 | 314 | 185.32 | 138
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 16 | 42 | 30 | 30 | 0 | 0 | plant availability zero
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 23 | 23 | 23 | 23 | 23 | 23 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 144 | 134 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 86 | 86 | 86 | 83 | 83 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 99 | 98 | 100 | 100 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 11 | 25 | 25 | 20 | 21 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 352 | 362 | 400 | 400 | 385 | 385 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1088 | 1096 | 1198 | 1198 | 1095 | 1096
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 900 | 900 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 44 | 44 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 80 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 861 | 1022 | 1070 | 1070 | 1070 | 1070 | Plant availability less
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1841 | 1922 | 3429 | 3344 | 2264.1 | 2179.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 125 | 130 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 1000 | 990 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 15 | 15 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 221 | 274 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.56 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2700.36 | 1566.56 | 1630 | 2003.32 | 2002.32 | 1868.32 | 1867.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 46.68 | 0 | 50 | 0 | 50 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 174 | 179 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 21 | 28 | 28 | 28 | 28 | Machine problem and fuel shortage
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 34 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 33 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 16 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.86 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1232 | 1428 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 61.19 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 99 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2032.73 | 2125 | 3105.47 | 2888.87 | 2577.09 | 2360.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 54 | 55 | 56 | 56 | 55 | 55 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 34 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.9 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 177 | 0 | 172 | 0 | 172 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 302.9 | 124 | 525.2 | 318 | 490.2 | 283
System Total |  |  |  |  | 28823.2 | 28385.703 | 11765.26 | 12494.9 | 22853.89 | 22188.23 | 16103.48 | 15587.82
Forecast Scenario (18-02-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 10330 |  | 0 |  | 10330
|  |  |  | 1:00 | 9630 |  | 0 |  | 9630
|  |  |  | 2:00 | 9180 |  | 0 |  | 9180
|  |  |  | 3:00 | 8780 |  | 0 |  | 8780
|  |  |  | 4:00 | 8630 |  | 0 |  | 8630
|  |  |  | 5:00 | 8540 |  | 0 |  | 8540
|  |  |  | 6:00 | 8910 |  | 0 |  | 8910
|  |  |  | 7:00 | 10000 |  | 0 |  | 10000
|  |  |  | 8:00 | 11070 |  | 0 |  | 11070
|  |  |  | 9:00 | 11450 |  | 0 |  | 11450
|  |  |  | 10:00 | 11390 |  | 0 |  | 11390
|  |  |  | 11:00 | 11540 |  | 0 |  | 11540
|  |  |  | 12:00 | 12020 |  | 0 |  | 12020
|  |  |  | 13:00 | 12400 |  | 0 |  | 12400
|  |  |  | 14:00 | 12160 |  | 0 |  | 12160
|  |  |  | 15:00 | 11780 |  | 0 |  | 11780
|  |  |  | 16:00 | 11410 |  | 0 |  | 11410
|  |  |  | 17:00 | 11380 |  | 0 |  | 11380
|  |  |  | 18:00 | 11970 |  | 0 |  | 11970
|  |  |  | 18:30 | 12350 |  | 0 |  | 12350
|  |  |  | 19:00 | 12780 |  | 0 |  | 12780
|  |  |  | 19:30 | 12520 |  | 0 |  | 12520
|  |  |  | 20:00 | 12300 |  | 0 |  | 12300
|  |  |  | 21:00 | 12180 |  | 0 |  | 12180
|  |  |  | 22:00 | 11610 |  | 0 |  | 11610
|  |  |  | 23:00 | 11000 |  | 0 |  | 11000
Probable Maximum Temperature: |  |  | 30.90°C
Probable Maximum Demand at Day Peak: |  |  | 12020.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12780.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12780.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 262.44 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:20 hrs on 18-02-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 17-02-2026
Power Supply Scenario
| Day Peak Generation |  |  | 11765.26 | MW | 12:00 Hr. | Energy Generated |  |  | 260.6275 |  | MKWHr.
| Day Peak Demand |  |  | 11824.26 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.254 |  | MKWHr.
| Evening Peak Generation |  |  | 12494.9 | MW | 19:00 Hr. | Energy Demand |  |  | 261.8815 |  | MKWHr.
| Evening Peak Demand |  |  | 12585.9 | MW | 19:00 Hr. | Maximum Temperature |  |  | 31.6 |  | °C
| Minimum Generation of the Day |  |  | 8341.35 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 743.73 |  | MMCFD
| Maximum Generation of the Day |  |  | 12494.9 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.6507 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 28.4921 | 0 | 4.5084 | 0 | 0 | 0.20795 | 0 | 0 | 33.2085 | Gas | 102.6406 | Gas | 355650122.91
| Chattogram Zone |  |  | 5.3682 | 44.1582 | 1.1166 | 0 | 1.6409 | 0.15662 | 0 | 0.14016 | 52.5806 | Coal | 92.213 | Coal | 601085091.0111
| Cumilla Zone |  |  | 21.8895 | 0 | 0.70005 | 0 | 0 | 0.44662 | 2.3098 | 0 | 25.3459 | HFO | 9.1001 | HFO | 161778520.53
| Mymensingh Zone |  |  | 0 | 0 | 1.8995 | 0 | 0 | 0.31545 | 0 | 0 | 2.2149 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 25.4463 | 0 | 0 | 0 | 0 | 0.07413 | 0 | 0 | 25.5204 | Hydro | 1.6409 | Hydro | 164086
| Khulna Zone |  |  | 0 | 20.8437 | 0 | 0 | 0 | 0.5328 | 21.76 | 0 | 43.1365 | Solar | 4.5169 | Solar | 72478752.862
| Barishal Zone |  |  | 8.0865 | 25.8563 | 0.053232 | 0 | 0 | 0.003523 | 0 | 0 | 33.9995 | Import | 50.3759 | Import | 279518459.96
| Rajshahi Zone |  |  | 13.358 | 0 | 0.29019 | 0 | 0 | 1.3878 | 26.3062 | 0 | 41.3422 | Wind | 0.14016 | Wind | 2061753.6
| Rangpur Zone |  |  | 0 | 1.3549 | 0.53218 | 0 | 0 | 1.392 | 0 | 0 | 3.279
| Total |  |  | 102.6406 | 92.213 | 9.1001 | 0 | 1.6409 | 4.5169 | 50.3759 | 0.14016 | 260.6275
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 355650122.91 |  | Hydro | 164086
|  |  |  | Coal | 601085091.0111 |  | Solar | 72478752.862
|  |  |  | HFO | 161778520.53 |  | Import | 279518459.96
|  |  |  | HSD | 0 |  | Wind | 2061753.6
[5 empty] | Total: | 147,27,36,786 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.76 | Peak Hr Flow | 900.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 29130002.1 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.3062 | Peak Hr Flow | 1428.00 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1972 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.3098 | Peak Hr Flow | 116.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2203 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.3759 | Peak Hr Flow | 2444.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4696
|  |  |  | Chattogram |  | 0 |  | 1202
|  |  |  | Cumilla |  | 0 |  | 1051
|  |  |  | Mymensingh |  | 87 |  | 1076
|  |  |  | Sylhet |  | 0 |  | 443
|  |  |  | Khulna |  | 0 |  | 1366
|  |  |  | Barishal |  | 0 |  | 329
|  |  |  | Rajshahi |  | 0 |  | 1176
|  |  |  | Rangpur |  | 0 |  | 828
|  |  |  | Total |  | 87 |  | 12167
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:25 | 10:43 | Chauddagram 132/33kV S/S 132 kv T-1 LT Scheduled S/D Due to Red hot maintenance at 33 kv | [7 empty] | 19.0MW load
|  |  | bus - 1. | [7 empty] | interrup.
| 08:25 | 10:43 | Chauddagram 132/33kV S/S 132 kv T-1 HT Scheduled S/D Due to Red hot maintenance at 33 kv | [7 empty] | 19.0MW load
|  |  | bus-1. | [7 empty] | interrup.
| 08:45 | 09:45 | Brahmanbaria 132/33kV S/S 401T HT Forced S/D | [7 empty] | 35.0MW load
interrup.
|  | 09:05 | Keranigonj 230/132/33kV S/S ATR-1 LT is restored.
|  | 09:05 | Keranigonj 230/132/33kV S/S ATR-1 HT is restored.
| 09:09 | 15:14 | Juldah-Shahmirpur 132kV Ckt-2 Scheduled S/D from Juldah 132/33kV end Due to Annual
Maintenance dead line chacking
| 09:27 |  | Ghorasal- Ishwardi 230 kV Ckt-2 Project Work S/D from Ghorashal 230kV end Due to
Shutdown requisition from STGE Project of Ghorashal Ishwardi ckt-02 for 1 Month due to
reconducting work. and from Ishurdi 230/132kV end Due to reconductoring work
| 09:31 |  | Bheramara P/S-Kustia 132 kV Ckt-2 Project Work S/D from Kushtia 132/33kV end. and from
Bheramara 230/132kV end Due to Works at Kushtia ss
| 09:35 |  | Jhenaidah-Kushtia 132kV Ckt-2 Project Work S/D from Kushtia 132/33kV end.
|  | 09:45 | Brahmanbaria 132/33kV S/S 401T LT is restored.
| 09:54 | 17:04 | Kalurghat 132/33kV S/S TRFO-01(506T) LT Scheduled S/D Due to Temperature Meter Checking
| 09:55 | 11:50 | Kabirpur 132/33kV S/S XFR, T-2 LT Scheduled S/D Due to 33 kV Chondoma feeder Red Hot | [7 empty] | 65.0MW load
|  |  | Maintanence | [7 empty] | interrup.
| 09:55 | 11:49 | Kabirpur 132/33kV S/S XFR, T-2 HT Scheduled S/D Due to RedHot Maintanence of 33kV Chandra | [7 empty] | 65.0MW load
|  |  | feeder | [7 empty] | interrup.
| 10:08 |  | Sirajganj 132/33kV S/S Solar Park 1 Scheduled S/D Due to Teleprotection commissioning.
S/D taken by BCRECL.
| 10:09 | 15:46 | Chauddagram-Feni 132 kV Ckt-2 Scheduled S/D from Chauddagram 132/33kV end Due to SPMD
work and from Feni 230/132kV end Due to Due to work at chauddagram substation
|  | 10:18 | Keranigonj 230/132/33kV S/S TR-1 HT is restored.
|  | 10:18 | Keranigonj 230/132/33kV S/S TR-1 LT is restored.
| 10:26 |  | Bhulta-Rampura 230 kV Ckt-4 Project Work S/D from Bhulta 400/230kV end. and from Rampura
230/132kV end Due to OPGW installation work by EEGBPS Project continued to 28.02.2026
| 12:20 |  | Rampal 400/230kV S/S Gopalganj Line-1 Reactor Forced S/D Due to Due to low voltage at
Aldc Ends.
|  | 17:21 | Niamatpur 132/33kV S/S Transformer-1(407T) HT is restored.
| 02:52 |  | Meghnaghat CCPP(Summit)-2 Shutdown with remarks:- ST
| 02:53 |  | Meghnaghat CCPP(Summit)-2 Shutdown with remarks:- GT
| 05:00 |  | Minimum Generation: 8392 MW.
| 07:25 |  | Rahanpur 400/132kV S/S Bus Reactor 400 KV Forced S/D Due to Voltage balanced
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 17-02-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0"MW due to gas restriction by Titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 317 | 8838000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 327 | 7418758 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 29.7 | 66960 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 62 | 784320 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 178180 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 82575 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 457800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 471240 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 278400 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 80 | 164095 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 78 | 1084896 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 636480 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 66 | 227520 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 207946 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 66600 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 535 | 11306285 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 90 | 938400 | Engine Problem
Dhaka Area Total |  |  |  |  | 6668.974 | 1806.7 | 33208455
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | U#1 Under maintenance, U#2 Running
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 132975 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 18 | 31200 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1640860 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 226 | 4991450 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 44 | 98691 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 27315 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 21 | 376800 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 23641 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 37636 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 40 | 72764 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 13440 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 835527 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1145 | 24027270 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 2 | 140160 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 875 | 20130909.09 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 2474 | 52580638.09
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 193 | 5138000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 295 | 7220100 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 300 | 5964000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage as per NLDC instructions.
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1043399 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 50 | 120436 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 101 | 2194293 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 72480 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 116 | 2309760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 432250 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 329700 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 31 | 74880 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 446618 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1236.2 | 25345916
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13700 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 405600 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 1374000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 301750 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 3 | 97920 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 21960 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 81 | 2214930
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 74130 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 732000 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 23 | 554040 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 134 | 3366573 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 609120 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1524480 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 98 | 2379410 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 11 | 306648 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7509000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 362 | 8465000 | -
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2325 | 1096 | 25520401
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 900 | 21760000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 532800 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1022 | 20843660 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1922 | 43136460
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 30432 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 2865000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 990 | 20903272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5221480 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 22800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 274 | 4953000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3523 | -
Barishal Area Total |  |  |  |  | 2700.36 | 1630 | 33999507.73
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 305432 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 179 | 3912091 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9445890 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 44681 | Machine problem and fuel shortage
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 34 | 153728 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 33 | 52416 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 16 | 39360 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 30300 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1428 | 26306182 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 380256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 671830 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2125 | 41342166
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 55 | 1354909 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 365270 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 38279.76 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 166909 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 211039 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1142640 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 124 | 3279046.76
Eastern Grid Total |  |  |  |  | 17400.108 | 6693.9 | 138870340.09
Western Grid Total |  |  |  |  | 10985.595 | 5801 | 121757180.49
National Grid Total |  |  |  |  | 28385.703 | 12494.9 | 260627520.58
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 17-02-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8381.48 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3698.5 | MW
i) Dhaka area |  |  | 4696.48 |  | MW | i) Khulna area |  |  |  | 1366 | MW
ii) Chattogram area |  |  | 1202 |  | MW | ii) Barishal area |  |  |  | 328.9 | MW
iii) Cumilla area |  |  | 1051 |  | MW | iii) Rajshahi area |  |  |  | 1175.6 | MW
iv) Mymensingh area |  |  | 989 |  | MW | iv) Rangpur area |  |  |  | 828 | MW
v) Sylhet area |  |  | 443 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12079.98 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 18 | 06:00 | 67 | Hasnabad | 91 | 10:00 | 133 | Nawabganj | 34.2 | 13:00
2 | AKSML | 12 | 18:30 | 68 | Hathazari | 60 | 13:00 | 134 | Netrakona | 153 | 18:00
3 | Aftabnagar | 30 | 13:00 | 69 | Hatirjheel | 34 | 14:00 | 135 | New | 64 | 11:00
4 | Agargaon | 85 | 13:00 | 70 | Ishurdi | 59 | 18:30 | 136 | Niamatpur | 95 | 09:00
5 | Agrabad | 52 | 18:00 | 71 | Jaldhaka | 62 | 09:00 | 137 | Noapara | 41 | 13:00
6 | Amnura | 36 | 13:00 | 72 | Jamalpur | 90 | 23:00 | 138 | PHP | 8 | 02:00
7 | Ashuganj | 77 | 14:00 | 73 | Jashore | 110 | 18:30 | 139 | Pabna | 72 | 18:30
8 | BSRM | 205 | 19:30 | 74 | Jhenaidah | 85 | 08:00 | 140 | Palashbari | 112 | 08:00
9 | Bagerhat | 68 | 18:30 | 75 | Joydebpur | 116 | 18:30 | 141 | Panchagarh | 45 | 19:00
10 | Bajitpur | 68 | 19:00 | 76 | Joypurhat | 49 | 09:00 | 142 | Patiya | 6.5 | 18:30
11 | Bakerganj | 9.7 | 21:00 | 77 | Juldah | 17 | 11:00 | 143 | Patuakhali | 39.5 | 21:00
12 | Bakulia | 71 | 18:30 | 78 | KSRM | 15 | 16:00 | 144 | Payra | 28 | 18:30
13 | Banani | 45.2 | 13:00 | 79 | Kabirpur | 222 | 19:00 | 145 | Postogola | 43 | 13:00
14 | Bangabhaban | 13 | 15:00 | 80 | Kachua | 65 | 18:30 | 146 | Purbachal | 24 | 18:00
15 | Barapukuria | 66 | 10:00 | 81 | Kaliganj | 17 | 18:30 | 147 | Purbasadipur | 124 | 08:00
16 | Barguna | 14 | 13:00 | 82 | Kallyanpur | 87 | 13:00 | 148 | Rahanpur | 29 | 08:00
17 | Barishal | 79 | 12:00 | 83 | Kalurghat | 32 | 15:00 | 149 | Rahim | 37 | 17:00
18 | Barishal-230 | 62 | 18:30 | 84 | Kamrangirchar | 79 | 13:00 | 150 | Rajbari | 60 | 18:30
19 | Baroaulia | 63 | 18:00 | 85 | Kaptai | N/A | N/A | 151 | Rajendrapur | 126 | 18:30
20 | Baroirhat | 42 | 18:30 | 86 | Kasba | 26 | 13:00 | 152 | Rajshahi | 93 | 13:00
21 | Bashundhara | 167 | 13:00 | 87 | Kazla | 98 | 13:00 | 153 | Rajshahi-230 | 54 | 13:00
22 | BashundharaCement | 8 | 22:00 | 88 | Keranigonj | 70 | 13:00 | 154 | Ramganj | 66 | 18:30
23 | Beanibazar | 50 | 18:30 | 89 | Khagrachori | 30 | 18:30 | 155 | Rampur | 28 | 15:00
24 | Benapole | 52 | 08:00 | 90 | Khulna | 42 | 13:00 | 156 | Rangamati | 17 | 18:30
25 | Bhaluka | 143 | 18:30 | 91 | Khulshi | 165 | 18:30 | 157 | Rangpur | 118 | 18:30
26 | Bhandaria | 45 | 22:00 | 92 | Kishoreganj | 108 | 18:30 | 158 | Ruppur | 3 | 15:00
27 | Bhangura | 29 | 14:00 | 93 | Kodda | 290 | 16:00 | 159 | SSM | 0 | 00:00
28 | Bheramara(GK) | 43 | 18:30 | 94 | Kulaura | 31 | 18:00 | 160 | Saidpur | 102 | 09:00
29 | Bhulta | 204 | 17:00 | 95 | Kurigram | 68 | 08:00 | 161 | Satkhira | 110 | 18:30
30 | Bog-Sherpur | 62 | 18:30 | 96 | Kushtia | 117 | 13:00 | 162 | Satmasjid | 84 | 13:00
31 | Bogura | 127 | 13:00 | 97 | Laksam | 23 | 18:30 | 163 | Savar | 200 | 15:00
32 | Borhanuddin | 68 | 20:00 | 98 | Lakshmipur | 27 | 18:30 | 164 | SevenRings | 18.18 | 19:00
33 | Brahmanbaria | 97 | 17:00 | 99 | Lalbag | 68 | 13:00 | 165 | ShahCement | 37 | 05:00
34 | Cantonment | 78 | 13:00 | 100 | Lalmonirhat | 50 | 08:00 | 166 | Shahjadpur | 61 | 19:00
35 | Chandina | 31 | 12:00 | 101 | MI_Cement | 17.8 | 13:00 | 167 | Shahjibazar | 108 | 18:30
36 | Chandpur | 52 | 18:30 | 102 | Madanganj | 31 | 18:00 | 168 | Shahmirpur | 42 | 18:00
37 | Chandraghona | 29 | 18:00 | 103 | Madaripur | 76 | 13:00 | 169 | Shariatpur | 58 | 21:00
38 | Chapai | 63 | 12:00 | 104 | Madartek | 59 | 13:00 | 170 | Sherpur | 116 | 00:00
39 | Charsaidpur | 41 | 13:00 | 105 | Madunaghat | 40 | 18:00 | 171 | Shikalbaha | 27 | 18:00
40 | Chauddagram | 58 | 13:00 | 106 | Magura | 52 | 18:30 | 172 | Shitalakhya | 70.7 | 12:00
41 | Chhatak | 28 | 18:00 | 107 | Mahasthangarh | 70 | 08:00 | 173 | Sholosohor | 37 | 15:00
42 | Chowmuhani | 102 | 14:00 | 108 | Maijdee | 36 | 18:30 | 174 | Shyampur | 152 | 10:00
43 | Chuadanga | 84 | 13:00 | 109 | Manikganj | 102 | 18:30 | 175 | Siddhirganj | 115 | 11:00
44 | Coxsbazar | 110 | 18:00 | 110 | Maniknagar | 44 | 13:00 | 176 | Sirajganj | 98 | 19:00
45 | Cumilla(N) | 98 | 15:00 | 111 | Matarbari | 41 | 18:30 | 177 | Sonargaon | 148 | 19:30
46 | Cumilla(S) | 123 | 18:00 | 112 | Matuail | 60 | 12:00 | 178 | Sreemongol | 56 | 19:00
47 | Daganbhuiyan | 25 | 18:30 | 113 | Metrorail_Motijheel | 36 | 18:30 | 179 | Sreepur | 104 | 18:30
48 | Daudkandi | 112 | 18:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Srinagar | 33.6 | 13:00
49 | DhakaUniversity | 70 | 12:00 | 115 | Millgate | 82 | 12:00 | 181 | Sunamganj | 45 | 18:00
50 | Dhamrai | 124 | 18:00 | 116 | Mirpur | 120 | 19:00 | 182 | Sylhet | 41 | 18:30
51 | Dhanmondi | 87.6 | 13:00 | 117 | Mirsorai | 12 | 19:00 | 183 | Sylhet-132 | 83 | 18:00
52 | Dohazari | 75 | 19:30 | 118 | Mirzapur | 46 | 21:00 | 184 | TK | 16 | 18:30
53 | Faridpur | 118 | 18:30 | 119 | Mithapukur | 56 | 08:00 | 185 | Tangail | 140 | 13:00
54 | Fatullah | 95 | 16:00 | 120 | Modern | N/A | N/A | 186 | Taraganj | 18 | 09:00
55 | Fenchuganj | 30 | 18:30 | 121 | Mogbazar | 71.3 | 13:00 | 187 | Tasnim | 23 | 16:00
56 | Feni | 76 | 18:00 | 122 | Mongla | 37 | 18:30 | 188 | Thakurgaon | 84 | 09:00
57 | GPH | 1 | 00:00 | 123 | Motijheel | 40 | 13:00 | 189 | Tongi | 131 | 15:00
58 | Ghatail | 66 | 22:00 | 124 | Muktagacha | 28 | 11:00 | 190 | Ullahpara | 32 | 18:30
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 74 | 13:00 | 191 | Ullon | 51 | 18:30
60 | Ghorashal-230 | 99 | 19:00 | 126 | Muradnagar | 28 | 18:30 | 192 | Uttara | 62 | 13:00
61 | Goalpara | 33 | 13:00 | 127 | Mymensingh | 166 | 08:00 | 193 | UttaraNew | 30 | 13:00
62 | Gollamari | 80 | 18:30 | 128 | Naogaon | 119 | 08:00 | 194 | Zigatola | 59 | 13:00
63 | Gopalganj | 84 | 19:00 | 129 | Narail | 49 | 18:30
64 | Gulshan | 86 | 13:00 | 130 | Narinda | 55 | 13:00
65 | Halishahar | 74.5 | 12:00 | 131 | Narshingdi | 153 | 19:30
66 | HaripurSBU | 113 | 15:00 | 132 | Natore | 118 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 17-02-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 10096.65 | 32 |  | 10130.09
1:00 | 9407.5 | 27 |  | 9435.5
2:00 | 8986.16 | 0 |  | 8986.16
3:00 | 8585.61 | 0 |  | 8585.61
4:00 | 8429.86 | 0 |  | 8429.86
5:00 | 8341.35 | 0 |  | 8341.35
6:00 | 8715.84 | 0 |  | 8715.84
7:00 | 9678.43 | 119 |  | 9802.79
8:00 | 10781.22 | 87 |  | 10872.22
9:00 | 11182.33 | 67 |  | 11252.33
10:00 | 11129.85 | 60 |  | 11192.85
11:00 | 11267.93 | 72 |  | 11342.93
12:00 | 11765.26 | 56 |  | 11824.26
13:00 | 12130.31 | 71 |  | 12204.51
14:00 | 11886.6 | 73 |  | 11962.6
15:00 | 11515.18 | 66 |  | 11584.18
16:00 | 11149.85 | 61 |  | 11213.85
17:00 | 11126.26 | 55 |  | 11183.26
18:00 | 11693.2 | 74 |  | 11770.2
19:00 | 12494.9 | 87 |  | 12585.9
19:30 | 12237.9 | 79 |  | 12320.9
20:00 | 12027.2 | 70 |  | 12100.2
21:00 | 11910.2 | 67 |  | 11980.2
22:00 | 11419.2 | 58 |  | 11480.2
23:00 | 10766 | 52 |  | 10820
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 17-02-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5416 | 4680.65 | 10096.65 | DAILY GENERATION CURVE
00:30 | 5285.5 | 4466.575 | 9752.075
01:00 | 5155 | 4252.5 | 9407.5 | 17-02-2026
01:30 | 5066 | 4130.83 | 9196.83
02:00 | 4977 | 4009.16 | 8986.16
02:30 | 4800 | 3985.885 | 8785.885
03:00 | 4623 | 3962.61 | 8585.61
03:30 | 4577.5 | 3930.235 | 8507.735
04:00 | 4532 | 3897.86 | 8429.86
04:30 | 4455.5 | 3930.105 | 8385.605
05:00 | 4379 | 3962.35 | 8341.35
05:30 | 4549 | 3979.595 | 8528.595
06:00 | 4719 | 3996.84 | 8715.84
06:30 | 5109.94 | 4087.195 | 9197.135
07:00 | 5500.88 | 4177.55 | 9678.43
07:30 | 5677.785 | 4552.04 | 10229.825
08:00 | 5854.69 | 4926.53 | 10781.22
08:30 | 5891.915 | 5089.86 | 10981.775
09:00 | 5929.14 | 5253.19 | 11182.33
09:30 | 5914.235 | 5241.855 | 11156.09
10:00 | 5899.33 | 5230.52 | 11129.85
10:30 | 5875.525 | 5323.365 | 11198.89
11:00 | 5851.72 | 5416.21 | 11267.93
11:30 | 5936.895 | 5579.7 | 11516.595
12:00 | 6022.07 | 5743.19 | 11765.26
12:30 | 6096.1 | 5851.685 | 11947.785
13:00 | 6170.13 | 5960.18 | 12130.31
13:30 | 6188.14 | 5820.315 | 12008.455
14:00 | 6206.15 | 5680.45 | 11886.6
14:30 | 6148.055 | 5552.835 | 11700.89
15:00 | 6089.96 | 5425.22 | 11515.18
15:30 | 6025.7 | 5306.815 | 11332.515
16:00 | 5961.44 | 5188.41 | 11149.85
16:30 | 6006.32 | 5131.735 | 11138.055
17:00 | 6051.2 | 5075.06 | 11126.26
17:30 | 6226.2 | 5183.53 | 11409.73
18:00 | 6401.2 | 5292 | 11693.2
18:30 | 6547.55 | 5546.5 | 12094.05
19:00 | 6693.9 | 5801 | 12494.9
19:30 | 6501.9 | 5736 | 12237.9
20:00 | 6324.2 | 5703 | 12027.2
20:30 | 6318.7 | 5650 | 11968.7 |  | Executive Engineer
21:00 | 6313.2 | 5597 | 11910.2 |  | Network Operation Division
21:30 | 6198.7 | 5466 | 11664.7
22:00 | 6084.2 | 5335 | 11419.2
22:30 | 6003.1 | 5089.5 | 11092.6
23:00 | 5922 | 4844 | 10766

## En-Curve
QF-LDC-12
Date | 17-02-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2819 | 1379 | 900 | 0 | 88 | 1120.65 | 75 | 3543 | 0 | 8 | 156 | 0 | 0 | 8 | 32 | DAILY ENERGY CURVE
00:30 | 2857.5 | 1376 | 900 | 0 | 88 | 1022.075 | 75 | 3304 | 0 | 4 | 117 | 0 | 0 | 8.5 | 29.5 | 17-02-2026
01:00 | 2896 | 1373 | 900 | 0 | 88 | 923.5 | 75 | 3065 | 0 | 0 | 78 | 0 | 0 | 9 | 27
01:30 | 2859.5 | 1275.5 | 899.5 | 0 | 85 | 878.33 | 75 | 3032.5 | 0 | 0 | 78 | 0 | 0 | 13.5 | 13.5 | Energy Generated | 260.6275 |  | MKWHr
02:00 | 2823 | 1178 | 899 | 0 | 82 | 833.16 | 75 | 3000 | 0 | 0 | 78 | 0 | 0 | 18 | 0 | Energy not Served | 1.254 |  | MKWHr
02:30 | 2750.5 | 1164.5 | 899.5 | 0 | 82 | 830.385 | 75 | 2902.5 | 0 | 0 | 65.5 | 0 | 0 | 16 | 0 | Total Energy Requirement | 261.8815 |  | MKWHr
03:00 | 2678 | 1151 | 900 | 0 | 82 | 827.61 | 75 | 2805 | 0 | 0 | 53 | 0 | 0 | 14 | 0
03:30 | 2628 | 1123 | 900 | 0 | 83 | 829.235 | 75 | 2797.5 | 0 | 0 | 53 | 0 | 0 | 19 | 0
04:00 | 2578 | 1095 | 900 | 0 | 84 | 830.86 | 75 | 2790 | 0 | 0 | 53 | 0 | 0 | 24 | 0
04:30 | 2605.5 | 1029.5 | 900 | 0 | 85 | 830.605 | 75 | 2789 | 0 | 0 | 53 | 0 | 0 | 18 | 0
05:00 | 2633 | 964 | 900 | 0 | 86 | 830.35 | 75 | 2788 | 0 | 0 | 53 | 0 | 0 | 12 | 0
05:30 | 2700 | 957 | 899.5 | 0 | 86 | 831.095 | 75 | 2902 | 0 | 0 | 65 | 0 | 0 | 13 | 0
06:00 | 2767 | 950 | 899 | 0 | 86 | 831.84 | 75 | 3016 | 0 | 0 | 77 | 0 | 0 | 14 | 0
06:30 | 2806.5 | 1091.5 | 899.5 | 0 | 89 | 832.675 | 75 | 3298 | 12.96 | 0 | 77 | 0 | 0 | 15 | 59.5
07:00 | 2846 | 1233 | 900 | 0 | 92 | 833.51 | 75 | 3580 | 25.92 | 0 | 77 | 0 | 0 | 16 | 119
07:30 | 2897 | 1272.5 | 899.5 | 0 | 95 | 911.04 | 75 | 3777.5 | 97.785 | 63 | 129.5 | 0 | 0 | 12 | 103
08:00 | 2948 | 1312 | 899 | 0 | 98 | 988.57 | 75 | 3975 | 169.65 | 126 | 182 | 0 | 0 | 8 | 87
08:30 | 2931.5 | 1316.5 | 899 | 0 | 101 | 1006.285 | 75 | 4050 | 265.49 | 138 | 192 | 0 | 0 | 7 | 77
09:00 | 2915 | 1321 | 899 | 0 | 104 | 1024 | 75 | 4125 | 361.33 | 150 | 202 | 0 | 0 | 6 | 67
09:30 | 2894.5 | 1288 | 899.5 | 0 | 96 | 1023.5 | 75 | 4093.5 | 446.09 | 150 | 184.5 | 0 | 0 | 5.5 | 63.5
10:00 | 2874 | 1255 | 900 | 0 | 88 | 1023 | 75 | 4062 | 530.85 | 150 | 167 | 0 | 0 | 5 | 60
10:30 | 2885.5 | 1239.5 | 900 | 0 | 88 | 1023.5 | 55 | 4090.5 | 586.39 | 150 | 177.5 | 0 | 0 | 3 | 66
11:00 | 2897 | 1224 | 900 | 0 | 88 | 1024 | 35 | 4119 | 641.93 | 150 | 188 | 0 | 0 | 1 | 72
11:30 | 2913.5 | 1276 | 900 | 0 | 91 | 1128 | 35 | 4120 | 665.095 | 150 | 237.5 | 0 | 0 | 0.5 | 64
12:00 | 2930 | 1328 | 900 | 0 | 94 | 1232 | 35 | 4121 | 688.26 | 150 | 287 | 0 | 0 | 0 | 56
12:30 | 2922 | 1382 | 900 | 0 | 95 | 1272 | 35 | 4213 | 675.285 | 150 | 303.5 | 0 | 0 | 0 | 63.5
13:00 | 2914 | 1436 | 900 | 0 | 96 | 1312 | 35 | 4305 | 662.31 | 150 | 320 | 0 | 0 | 0 | 71
13:30 | 2925.5 | 1432.5 | 900 | 0 | 99 | 1289 | 52.5 | 4211 | 626.455 | 150 | 322.5 | 0 | 0 | 0 | 72
14:00 | 2937 | 1429 | 900 | 0 | 102 | 1266 | 70 | 4117 | 590.6 | 150 | 325 | 0 | 0 | 0 | 73
14:30 | 2911.5 | 1385.5 | 900.5 | 0 | 103 | 1247 | 70 | 4077.5 | 522.39 | 150 | 332 | 0 | 0 | 1.5 | 69.5
15:00 | 2886 | 1342 | 901 | 0 | 104 | 1228 | 70 | 4038 | 454.18 | 150 | 339 | 0 | 0 | 3 | 66
15:30 | 2870.5 | 1345.5 | 900.5 | 0 | 103 | 1196 | 70 | 3989.5 | 365.915 | 150 | 338.6 | 0 | 0 | 3 | 63.5
16:00 | 2855 | 1349 | 900 | 0 | 102 | 1164 | 70 | 3941 | 277.65 | 150 | 338.2 | 0 | 0 | 3 | 61
16:30 | 2876.5 | 1368.5 | 900 | 0 | 98 | 1160.5 | 70 | 3951 | 181.855 | 175 | 353.7 | 0 | 0 | 3 | 58
17:00 | 2898 | 1388 | 900 | 0 | 94 | 1157 | 70 | 3961 | 86.06 | 200 | 369.2 | 0 | 0 | 3 | 55
17:30 | 2903.5 | 1378.5 | 900 | 0 | 109 | 1214 | 70 | 4046 | 43.03 | 245 | 498.2 | 0 | 0 | 2.5 | 64.5
18:00 | 2909 | 1369 | 900 | 0 | 124 | 1271 | 70 | 4131 | 0 | 290 | 627.2 | 0 | 0 | 2 | 74
18:30 | 2973 | 1395 | 900 | 0 | 120 | 1349.5 | 70 | 4246 | 0 | 295.5 | 743.05 | 0 | 0 | 2 | 80.5
19:00 | 3037 | 1421 | 900 | 0 | 116 | 1428 | 70 | 4361 | 0 | 301 | 858.9 | 0 | 0 | 2 | 87
19:30 | 3091 | 1435 | 901 | 0 | 114 | 1391 | 70 | 4410 | 0 | 271 | 553.9 | 0 | 0 | 1 | 79
20:00 | 3147 | 1436 | 900 | 0 | 116 | 1374 | 70 | 4431 | 0 | 251 | 301.2 | 0 | 0 | 1 | 70
20:30 | 3160 | 1451 | 899.5 | 0 | 115 | 1342 | 70 | 4437 | 0 | 235.5 | 257.7 | 0 | 0 | 1 | 68.5
21:00 | 3173 | 1466 | 899 | 0 | 114 | 1310 | 70 | 4443 | 0 | 220 | 214.2 | 0 | 0 | 1 | 67
21:30 | 3146.5 | 1446 | 899.5 | 0 | 109 | 1286 | 70 | 4307.5 | 0 | 185.5 | 214.2 | 0 | 0 | 0.5 | 62.5
22:00 | 3120 | 1426 | 900 | 0 | 104 | 1262 | 70 | 4172 | 0 | 151 | 214.2 | 0 | 0 | 0 | 58
22:30 | 3117.5 | 1414 | 900 | 0 | 105 | 1179 | 70 | 4027 | 0 | 92.5 | 187.6 | 0 | 0 | 0 | 55
23:00 | 3115 | 1402 | 900 | 0 | 106 | 1096 | 70 | 3882 | 0 | 34 | 161 | 0 | 0 | 0 | 52
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 17-02-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 415 | 03:00 | 384 | 12:00 | Madunaghat | 413 | 04:00 | 397 | 13:00
Amtali | 422 | 03:00 | 409 | 13:00 | Meghnaghat | 415 | 04:00 | 386 | 12:00
Ashuganj | N/A | N/A | N/A | N/A | Payra | 423 | 04:00 | 411 | 12:00
Bhulta | 419 | 03:00 | 380 | 12:00 | Rahanpur | 422 | 04:00 | 403 | 13:00
Bibiana | 419 | 01:00 | 403 | 12:00 | Rampal | 417 | 04:00 | 397 | 12:00
BIPTC | 401 | 02:00 | 390 | 12:00
Bogura | 420 | 04:00 | 396 | 19:00
Gopalganj | 419 | 04:00 | 396 | 12:00
Kaliakoir | 409 | 04:00 | 378 | 12:00
Korerhat | 419 | 03:00 | 399 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 243 | 04:00 | 222 | 12:00 | Jhenaidah | 242 | 04:00 | 223 | 12:00
AKSML | 236 | 01:00 | 228 | 11:00 | Kachua | 241 | 03:00 | 226 | 13:00
Aminbazar | 242 | 03:00 | 221 | 12:00 | Kaliakoir | 244 | 03:00 | 223 | 12:00
Ashuganj | 242 | 03:00 | 224 | 12:00 | Keranigonj | 242 | 03:00 | 221 | 12:00
Ashuganj-400 | N/A | N/A | N/A | N/A | Khulna(S) | 244 | 03:00 | 228 | 12:00
Baghabari | 236 | 00:00 | 225 | 12:00 | Korerhat | 239 | 03:00 | 222 | 12:00
Barapukuria | 225 | 05:00 | 208 | 07:00 | Madunaghat | 235 | 07:00 | 228 | 11:00
Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat-400 | 237 | 03:00 | 227 | 13:00
Barishal | 237 | 04:00 | 228 | 12:00 | Maniknagar | 244 | 03:00 | 223 | 12:00
Bheramara | 237 | 04:00 | 221 | 12:00 | Meghnaghat | 251 | 04:00 | 240 | 09:00
Bhulta | 244 | 03:00 | 221 | 12:00 | Meghnaghat-400 | 246 | 04:00 | 227 | 12:00
Bibiana | 246 | 05:00 | 232 | 12:00 | Mirsorai | 239 | 03:00 | 225 | 12:00
BIPTC | 241 | 04:00 | 222 | 12:00 | Rajshahi | 236 | 04:00 | 220 | 08:00
Bogura | 238 | 04:00 | 224 | 12:00 | Rampal | 241 | 03:00 | 227 | 12:00
Bogura-400 | 237 | 04:00 | 223 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Borhanuddin | 238 | 04:00 | 234 | 09:00 | Rampura | 244 | 04:00 | 222 | 12:00
BSRM | 238 | 03:00 | 225 | 12:00 | Shikalbaha | 234 | 01:00 | 226 | 12:00
Chowmuhani | N/A | N/A | N/A | N/A | Shyampur | 243 | 03:00 | 222 | 12:00
Cumilla(N) | 243 | 04:00 | 225 | 12:00 | Siddhirganj | 240 | 00:00 | 225 | 12:00
Faridpur | 236 | 03:00 | 222 | 12:00 | Sirajgonj | 243 | 04:00 | 231 | 12:00
Fenchuganj | 246 | 05:00 | 236 | 12:00 | Sreepur | 236 | 04:00 | 219 | 12:00
Feni | 241 | 03:00 | 226 | 12:00 | Tongi | 240 | 04:00 | 218 | 11:00
Ghorashal | 245 | 02:00 | 230 | 12:00
Ghorashal-230 | 242 | 04:00 | 219 | 12:00
Gopalganj | 239 | 22:00 | 222 | 12:00
GPH | 235 | 03:00 | 226 | 12:00
Haripur | 245 | 04:00 | 225 | 12:00
Hasnabad | 241 | 02:00 | 222 | 12:00
Hathazari | 232 | 23:00 | 223 | 12:00
Ishurdi | 241 | 04:00 | 224 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 03:00 | 124 | 12:00 | Magura | 140 | 04:00 | 126 | 12:00
Agargaon | 138 | 04:00 | 124 | 12:00 | Mahasthangarh | 134 | 04:00 | 121 | 08:00
Agrabad | 136 | 02:00 | 130 | 11:00 | Maijdee | 134 | 03:00 | 126 | 12:00
AKS | 135 | 01:00 | 127 | 12:00 | Manikganj | 130 | 01:00 | 116 | 12:00
Aminbazar | 139 | 03:00 | 123 | 12:00 | Maniknagar | 136 | 02:00 | 124 | 12:00
Amnura | 139 | 04:00 | 127 | 12:00 | Matarbari | 130 | 03:00 | 120 | 18:30
Ashuganj | 142 | 05:00 | 134 | 12:00 | Matuail | 140 | 04:00 | 128.4 | 12:00
Bagerhat | 136 | 05:00 | 121 | 18:30 | Metrorail_Motijheel | 136 | 01:00 | 124 | 12:00
Bajitpur | 136 | 01:00 | 125 | 12:00 | Metrorail_Uttara | 133 | 03:00 | 118 | 12:00
Bakerganj | 138.5 | 06:00 | 134 | 11:00 | Millgate | 133 | 03:00 | 117 | 12:00
Bakulia | 136 | 03:00 | 130 | 11:00 | Mirpur | 137 | 03:00 | 122 | 12:00
Banani | 138 | 04:00 | 124 | 12:00 | Mirzapur | 135 | 04:00 | 127 | 12:00
Bangabhaban | 138 | 04:00 | 123 | 13:00 | Mithapukur | 134 | 04:00 | 120 | 08:00
Barapukuria | 136 | 23:00 | 122 | 07:00 | MI_Cement | 137 | 04:00 | 120 | 12:00
Barguna | 139 | 03:00 | 133 | 13:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 139 | 03:00 | 131 | 12:00 | Mogbazar | 138 | 06:00 | 125 | 12:00
Barishal-230 | 139 | 04:00 | 131 | 13:00 | Mongla | 133 | 03:00 | 122 | 12:00
Baroaulia | 135 | 00:00 | 130 | 12:00 | Motijheel | 138 | 04:00 | 123 | 13:00
Baroirhat | 138 | 03:00 | 129 | 12:00 | Muktagacha | 125 | 02:00 | 114 | 14:00
Bashundhara | 138 | 03:00 | 123 | 12:00 | Munshiganj | 137 | 04:00 | 125 | 12:00
BashundharaCement | 135 | 00:00 | 129 | 13:00 | Muradnagar | 138 | 03:00 | 126 | 12:00
Beanibazar | 134 | 01:00 | 128 | 12:00 | Mymensingh | 128 | 01:00 | 112 | 12:00
Benapole | 136 | 03:00 | 117 | 13:00 | Naogaon | 134 | 03:00 | 120 | 08:00
Bhaluka | 129 | 00:00 | 118 | 12:00 | Narail | 140 | 03:00 | 125 | 12:00
Bhandaria | 136 | 05:00 | 126 | 12:00 | Narinda | 136 | 02:00 | 124 | 12:00
Bhangura | 136 | 01:00 | 128 | 09:00 | Narshingdi | 132 | 00:00 | 123 | 12:00
Bheramara | 137 | 04:00 | 126 | 12:00 | Natore | 135 | 05:00 | 125 | 12:00
Bheramara(GK) | 136 | 04:00 | 126 | 12:00 | Nawabganj | 136 | 04:00 | 124 | 12:00
Bhulta | 129 | 00:00 | 121 | 12:00 | Netrakona | 126 | 02:00 | 107 | 12:00
Bog-Sherpur | 136 | 04:00 | 124 | 12:00 | New | 134 | 04:00 | 120 | 12:00
Bogura | 136 | 04:00 | 123 | 08:00 | Niamatpur | 141 | 03:00 | 133 | 07:00
Bogura-230 | 136 | 04:00 | 126 | 08:00 | Noapara | 137 | 04:00 | 121 | 13:00
Brahmanbaria | 135 | 05:00 | 124 | 12:00 | Pabna | 138 | 04:00 | 127 | 12:00
Cantonment | 137 | 02:00 | 124 | 12:00 | Palashbari | 130 | 04:00 | 117 | 08:00
Chandina | 140 | 03:00 | 129 | 12:00 | Panchagarh | 137 | 04:00 | 124 | 12:00
Chandpur | 137 | 05:00 | 129 | 11:00 | Patiya | 136 | 02:00 | 129 | 12:00
Chandraghona | 139 | 04:00 | 131 | 12:00 | Patuakhali | 136 | 18:00 | 132 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 138 | 00:00 | 132 | 13:00 | Payra | 138 | 01:00 | 135 | 12:00
Charsaidpur | 138 | 03:00 | 127 | 12:00 | PHP | 137 | 03:00 | 127 | 13:00
Chauddagram | 137 | 02:00 | 126 | 12:00 | Postogola | 137 | 01:00 | 123 | 12:00
Chhatak | 133 | 01:00 | 127 | 12:00 | Purbachal | 138 | 03:00 | 123 | 12:00
Chowmuhani | 133 | 00:00 | 126 | 12:00 | Purbasadipur | 132 | 04:00 | 119 | 12:00
Chuadanga | 140 | 04:00 | 126 | 12:00 | Rahanpur | 141 | 01:00 | 134 | 13:00
Coxsbazar | 127 | 03:00 | 121 | 18:00 | Rahanpur-400 | 142 | 03:00 | 135 | 12:00
Cumilla(N) | 141 | 04:00 | 130 | 12:00 | Rahim | 139 | 06:00 | 128 | 12:00
Cumilla(S) | 138 | 02:00 | 125 | 08:00 | Rajbari | 136 | 02:00 | 128 | 12:00
Daganbhuiyan | 136 | 04:00 | 126 | 12:00 | Rajendrapur | 133 | 03:00 | 118 | 12:00
Daudkandi | 137 | 02:00 | 124 | 12:00 | Rajshahi | 137 | 01:00 | 126 | 12:00
DhakaUniversity | 138 | 03:00 | 124 | 12:00 | Rajshahi-230 | 136 | 04:00 | 127 | 08:00
Dhamrai | 137 | 06:00 | 130 | 16:00 | Ramganj | 134 | 01:00 | 127 | 11:00
Dhanmondi | 139.8 | 04:00 | 129 | 12:00 | Rampur | 136 | 02:00 | 128 | 12:00
Dohazari | 133 | 03:00 | 128 | 12:00 | Rampura | 138 | 04:00 | 122 | 12:00
Faridpur | 136 | 04:00 | 129 | 13:00 | Rangamati | 137 | 05:00 | 131 | 11:00
Fatullah | 140 | 03:00 | 121 | 12:00 | Rangpur | 134 | 00:00 | 120 | 08:00
Fenchuganj | 139 | 03:00 | 134 | 12:00 | Ruppur | 139 | 05:00 | 128 | 12:00
Feni | 133 | 03:00 | 126 | 13:00 | Saidpur | 133 | 22:00 | 120 | 09:00
Feni-230 | 136 | 03:00 | 127 | 12:00 | Satkhira | 136 | 04:00 | 121 | 08:00
Ghatail | 127 | 19:00 | 118 | 18:30 | Satmasjid | 138 | 05:00 | 124 | 13:00
Ghorashal | 147 | 05:00 | 134 | 12:00 | Savar | 138 | 04:00 | 120 | 12:00
Goalpara | 138 | 03:00 | 125 | 13:00 | SevenRings | 147 | 03:00 | 133 | 12:00
Gollamari | 137 | 03:00 | 126 | 12:00 | ShahCement | 139 | 16:00 | 127 | 12:00
Gopalganj | 138 | 01:00 | 128 | 12:00 | Shahjadpur | 142 | 04:00 | 131 | 12:00
Gopalganj-400 | 140 | 04:00 | 132 | 12:00 | Shahjibazar | 135 | 03:00 | 126 | 12:00
Gulshan | 137 | 05:00 | 123 | 12:00 | Shahmirpur | 137 | 02:00 | 130 | 11:00
Halishahar | 137 | 05:00 | 129 | 12:00 | Shariatpur | 139 | 04:00 | 130 | 13:00
Haripur | 139 | 03:00 | 128 | 12:00 | Sherpur | 120 | 02:00 | 110 | 17:00
HaripurSBU | 139 | 04:00 | 128 | 12:00 | Shikalbaha | 124 | 00:00 | 122 | 13:00
Hasnabad | 136 | 05:00 | 122 | 12:00 | Shikalbaha-230 | 137 | 01:00 | 130 | 12:00
Hathazari | 136 | 00:00 | 131 | 12:00 | Shitalakhya | 137 | 04:00 | 120 | 12:00
Hatirjheel | 138 | 03:00 | 124 | 12:00 | Sholosohor | 138 | 03:00 | 131 | 12:00
Ishurdi | 140 | 04:00 | 130 | 08:00 | Shyampur | 136 | 00:00 | 126 | 12:00
Jaldhaka | 130 | 05:00 | 117 | 08:00 | Shyampur-230 | 141 | 03:00 | 128 | 12:00
Jamalpur | 124 | 02:00 | 112 | 18:30 | Siddhirganj | 139 | 03:00 | 128 | 11:00
Jashore | 134 | 05:00 | 118 | 13:00 | Sirajganj | 136 | 03:00 | 124 | 09:00
Jhenaidah | 140 | 05:00 | 111 | 13:00 | Sonargaon | 135 | 03:00 | 126 | 12:00
Jhenaidah-230 | 141 | 04:00 | 128 | 12:00 | Sreemongol | 135 | 02:00 | 128 | 12:00
Joydebpur | 143 | 01:00 | 128 | 12:00 | Sreepur | 136 | 04:00 | 125 | 09:00
Joypurhat | 132 | 03:00 | 117 | 09:00 | Srinagar | 135 | 02:00 | 124 | 12:00
Juldah | 136 | 00:00 | 130 | 12:00 | SSM | 140 | 00:00 | 130 | 14:00
Kabirpur | 138 | 01:00 | 117 | 12:00 | Sunamganj | 132 | 01:00 | 126 | 18:00
Kachua | 138 | 04:00 | 129 | 12:00 | Sylhet | 135 | 04:00 | 129 | 13:00
Kaliakoir | 141 | 03:00 | 131 | 12:00 | Sylhet-132 | 133 | 01:00 | 129 | 12:00
Kaliganj | 136 | 16:00 | 129 | 12:00 | Tangail | 128 | 00:00 | 123 | 16:00
Kallyanpur | 137 | 03:00 | 123 | 12:00 | Taraganj | 132 | 04:00 | 121 | 08:00
Kalurghat | 138 | 03:00 | 133 | 09:00 | Tasnim | 138 | 04:00 | 126 | 12:00
Kamrangirchar | 136 | 02:00 | 120 | 12:00 | Thakurgaon | 136 | 04:00 | 122 | 12:00
Kaptai | N/A | N/A | N/A | N/A | TK | 139 | 03:00 | 131 | 12:00
Kasba | 138 | 03:00 | 127 | 12:00 | Tongi | 135 | 04:00 | 120 | 11:00
Kazla | 137 | 04:00 | 122 | 13:00 | Ullahpara | 137 | 03:00 | 126 | 12:00
Keranigonj | 137 | 04:00 | 124 | 12:00 | Ullon | 137 | 02:00 | 124 | 12:00
Khagrachori | 134 | 00:00 | 130 | 12:00 | Uttara | 133 | 03:00 | 117 | 12:00
Khulna | 137 | 04:00 | 124 | 13:00 | UttaraNew | 133 | 03:00 | 118 | 12:00
Khulna(S) | 138 | 03:00 | 126 | 12:00 | Zigatola | 137 | 05:00 | 123 | 13:00
Khulshi | 134 | 04:00 | 128 | 12:00
Kishoreganj | 134 | 03:00 | 123 | 12:00
Kodda | 137 | 18:00 | 129 | 12:00
Korerhat | 139 | 03:00 | 131 | 12:00
KSRM | 137 | 03:00 | 131 | 12:00
Kulaura | 139 | 04:00 | 132 | 12:00
Kurigram | 130 | 03:00 | 114 | 07:00
Kushtia | 135 | 05:00 | 117 | 12:00
Laksam | 137 | 03:00 | 128 | 12:00
Lakshmipur | 134 | 02:00 | 126 | 12:00
Lalbag | 135 | 03:00 | 121 | 12:00
Lalmonirhat | 132 | 00:00 | 117 | 08:00
Madanganj | 135 | 00:00 | 129 | 13:00
Madaripur | 137 | 05:00 | 131 | 12:00
Madartek | 138 | 05:00 | 124 | 12:00
Madunaghat | 138 | 19:30 | 133 | 10:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division