## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 19-02-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-02-2026 | during | 19-02-2026 | during | 19-02-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 100 | Demand "0"MW due to gas restriction by Titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 342 | 412 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 198 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 310 | 315 | 335 | 335 | 335 | 335
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 33.4 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 48 | 80 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 4 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 24 | 23 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 19 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 15 | 130 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 52 | 78 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 52 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 15 | 86 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 90 | 420 | 420 | 490 | 490 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 23 | 0 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 108 | 160 | 160 | 160 | 160
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 979 | 1754.4 | 5782.22 | 5751.22 | 3151.05 | 3256.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | U#1 Under maintenance, U#2 Running
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 31 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 75 | 70 | 70 | 70 | 70 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 223 | 225 | 225 | 225 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 46 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 24 | 32 | 32 | 32 | 32 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 51 | 51 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 24 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 30 | 5 | 12 | 40 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 109 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.49 | 0 | 3.56 | 0 | 3.56 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 16 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 33 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 24 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 20 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1160 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 875 | 875 | 875 | 875 | 875 | 875 | ps availability is less
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2319.49 | 2707 | 3736.42 | 3720.86 | 3239.06 | 3216.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 204 | 207 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 335 | 330 | 353.35 | 353.35 | 353.35 | 353.35 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 350 | 355 | 318.81 | 318.81 | 318.81 | 318.81
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 36 | 46.7 | 46.7 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 41 | 195 | 195 | 1 | 1 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 61 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 42 | 42 | 42 | 42 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 98 | 103 | 163 | 163 | 110 | 110 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 85 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 124 | 110 | 84 | 82 | 126 | 126 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 14 | 24.5 | 24.5 | 13 | 13 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 9 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 50 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1244 | 1452 | 2756.56 | 2689.56 | 1883.36 | 1818.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-02-2026 | during | 19-02-2026 | during | 19-02-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 16 | 157.5 | 157.5 | 35 | 35 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 19 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 78 | 60 | 80 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 45.86 | 0 | 45.12 | 0 | 45.12 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 16 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 148.86 | 135 | 361.22 | 334 | 185.22 | 138
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 41 | 42 | 42 | 0 | 0 | plant availability zero
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 23 | 23 | 23 | 23 | 23 | 23 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 28 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 86 | 86 | 86 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 98 | 97 | 100 | 100 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 17 | 25 | 25 | 20 | 21 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 285 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 392 | 361 | 400 | 400 | 385 | 385 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1129 | 993 | 1210 | 1210 | 1095 | 1096
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 900 | 890 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 44 | 44 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 320 | 320 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 87 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 947 | 1039 | 1120 | 1120 | 1070 | 1070 | Plant availability less
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1934 | 1929 | 3474 | 3394 | 2579.1 | 2499.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 125 | 130 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 1010 | 1013 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 150 | 150 | 15 | 15 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 278 | 239 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.56 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2700.36 | 1633.56 | 1653 | 2003.32 | 2002.32 | 1868.32 | 1867.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 48.56 | 0 | 50 | 0 | 50 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 171 | 188 | 214 | 214 | 214 | 214
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 28 | 28 | 28 | 28 | Machine problem and fuel shortage
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 50 | 50 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 33 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 45 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.52 | 0 | 5.45 | 0 | 5.45 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1377.13 | 1451.85 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 59.65 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 101 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2176.86 | 2159.85 | 3187.32 | 2970.87 | 2576.94 | 2360.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 54 | 53 | 55 | 55 | 55 | 55 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 49 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.3 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 176 | 0 | 177 | 0 | 177 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 305.3 | 152 | 529.2 | 317 | 495.2 | 283
System Total |  |  |  |  | 28823.2 | 28385.703 | 11870.07 | 12935.25 | 23040.26 | 22389.83 | 17073.25 | 16534.82
Forecast Scenario (19-02-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11000 |  | 0 |  | 11000
|  |  |  | 1:00 | 10340 |  | 0 |  | 10340
|  |  |  | 2:00 | 10080 |  | 0 |  | 10080
|  |  |  | 3:00 | 10500 |  | 0 |  | 10500
|  |  |  | 4:00 | 10540 |  | 0 |  | 10540
|  |  |  | 5:00 | 9710 |  | 0 |  | 9710
|  |  |  | 6:00 | 9050 |  | 0 |  | 9050
|  |  |  | 7:00 | 9050 |  | 0 |  | 9050
|  |  |  | 8:00 | 9670 |  | 0 |  | 9670
|  |  |  | 9:00 | 10450 |  | 0 |  | 10450
|  |  |  | 10:00 | 10980 |  | 0 |  | 10980
|  |  |  | 11:00 | 11650 |  | 0 |  | 11650
|  |  |  | 12:00 | 12230 |  | 0 |  | 12230
|  |  |  | 13:00 | 12400 |  | 0 |  | 12400
|  |  |  | 14:00 | 12380 |  | 0 |  | 12380
|  |  |  | 15:00 | 12190 |  | 0 |  | 12190
|  |  |  | 16:00 | 12240 |  | 0 |  | 12240
|  |  |  | 17:00 | 12280 |  | 0 |  | 12280
|  |  |  | 18:00 | 12270 |  | 0 |  | 12270
|  |  |  | 18:30 | 12700 |  | 0 |  | 12700
|  |  |  | 19:00 | 13000 |  | 0 |  | 13000
|  |  |  | 19:30 | 12710 |  | 0 |  | 12710
|  |  |  | 20:00 | 12630 |  | 0 |  | 12630
|  |  |  | 21:00 | 12350 |  | 0 |  | 12350
|  |  |  | 22:00 | 12000 |  | 0 |  | 12000
|  |  |  | 23:00 | 11700 |  | 0 |  | 11700
Probable Maximum Temperature: |  |  | 31.00°C
Probable Maximum Demand at Day Peak: |  |  | 12230.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13000.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13000.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 270.69 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:06 hrs on 19-02-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 18-02-2026 | [28 empty] | Date: | 18-02-2026 | [28 empty] | Date: | 18-02-2026 | [28 empty] | Date: | 18-02-2026 | [28 empty] | Date: | 18-02-2026 | [17 empty] | Date: | 18-02-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [17 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 35 | 875 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 908 | 0 | 0 | 0 | 0 | 280 | 365 | 51 | 0 | 189 | 0 | 0 | 106 | 0 | 0 | 14 | 0 | 102 | 0 | 0 | 0 | 295 | 0 | 362 | 41 | 23 | 135 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 100 | 0 | 59 | 18 | 0 | 0 | 0 | 6 | 5622 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 765 | 0 | 0 | 0 | 952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 130 | 220 | 0 | 0 | 790 | 0 | 4571 | 10193 | 93.56
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 35 | 720 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 285 | 370 | 51 | 0 | 191 | 0 | 0 | 107 | 0 | 0 | 14 | 0 | 98 | 0 | 0 | 0 | 290 | 0 | 362 | 41 | 23 | 135 | 0 | 17 | 0 | 5 | 30 | 0 | 0 | 100 | 0 | 59 | 18 | 0 | 0 | 0 | 6 | 5316 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764 | 0 | 0 | 0 | 833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 130 | 220 | 0 | 0 | 600 | 0 | 4264 | 9580 | 93.55
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 290 | 280 | 5 | 0 | 191 | 0 | 0 | 50 | 0 | 0 | 14 | 0 | 96 | 0 | 0 | 0 | 305 | 0 | 368 | 41 | 23 | 132 | 0 | 17 | 0 | 5 | 20 | 0 | 0 | 100 | 0 | 59 | 18 | 0 | 0 | 0 | 6 | 5035 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 766 | 0 | 0 | 0 | 835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 100 | 180 | 0 | 0 | 560 | 0 | 4159 | 9194 | 93.54
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 296 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 295 | 370 | 5 | 0 | 196 | 0 | 0 | 50 | 0 | 0 | 14 | 0 | 94 | 0 | 0 | 0 | 310 | 0 | 325 | 41 | 23 | 133 | 0 | 17 | 0 | 5 | 20 | 0 | 0 | 100 | 0 | 59 | 8 | 0 | 0 | 0 | 0 | 4927 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 0 | 0 | 0 | 835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 100 | 220 | 0 | 0 | 560 | 0 | 4141 | 9068 | 93.53
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 830 | 0 | 0 | 0 | 0 | 285 | 370 | 5 | 0 | 192 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 90 | 0 | 0 | 0 | 310 | 0 | 317 | 41 | 23 | 133 | 0 | 17 | 0 | 5 | 20 | 0 | 0 | 102 | 0 | 59 | 8 | 0 | 0 | 0 | 0 | 4535 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 0 | 0 | 0 | 834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 100 | 180 | 0 | 0 | 555 | 0 | 4080 | 8615 | 93.52
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 780 | 0 | 0 | 0 | 0 | 295 | 370 | 5 | 0 | 197 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 88 | 0 | 0 | 0 | 305 | 0 | 319 | 41 | 23 | 133 | 0 | 17 | 0 | 5 | 20 | 0 | 0 | 100 | 0 | 58 | 8 | 0 | 0 | 0 | 0 | 4446 | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 0 | 0 | 0 | 834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 100 | 180 | 0 | 0 | 557 | 0 | 3946 | 8392 | 93.51
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 902 | 0 | 0 | 0 | 0 | 295 | 370 | 5 | 0 | 195 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 86 | 0 | 0 | 0 | 315 | 0 | 319 | 41 | 23 | 143 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 100 | 0 | 58 | 19 | 0 | 0 | 0 | 0 | 4695 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 779 | 0 | 0 | 0 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 100 | 180 | 0 | 0 | 587 | 0 | 4223 | 8918 | 93.5
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 1 | 0 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 70 | 0 | 8 | 720 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 1125 | 1 | 0 | 0 | 0 | 325 | 370 | 5 | 0 | 211 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 94 | 0 | 4 | 0 | 305 | 0 | 360 | 41 | 23 | 142 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 100 | 0 | 59 | 19 | 0 | 0 | 1.92 | 0 | 5130.08 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 829 | 0 | 0 | 0 | 1065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.73 | 3 | 0 | 0 | 1.65 | 130 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.2 | 0 | 55 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 6 | 0.02 | 0 | 218 | 100 | 180 | 0 | 0 | 730 | 0 | 4637.7 | 9767.78 | 93.49
08:00 | 0 | 11 | 16 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 30 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 9 | 52 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 70 | 0 | 3 | 875 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 1160 | 7 | 0 | 0 | 0 | 325 | 370 | 33 | 0 | 195 | 0 | 0 | 106 | 0 | 0 | 11 | 0 | 108 | 0 | 24 | 0 | 305 | 0 | 357 | 41 | 23 | 153 | 3 | 17 | 0 | 86 | 30 | 0 | 0 | 100 | 0 | 59 | 19 | 0 | 1 | 14.35 | 3 | 5537.35 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 997 | 0 | 0 | 0 | 1263 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 12.4 | 26 | 0 | 0 | 15.04 | 173 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.44 | 0 | 55 | 35 | 9 | 17 | 0 | 0 | 0 | 1.4 | 48 | 0.13 | 0 | 276 | 130 | 220 | 0 | 0 | 920 | 0 | 5393.41 | 10930.76 | 93.48
09:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 52 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 18 | 52 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 70 | 0 | 2 | 875 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 1135 | 13 | 0 | 0 | 0 | 310 | 370 | 51 | 0 | 190 | 0 | 0 | 105 | 0 | 0 | 11 | 0 | 108 | 0 | 43 | 0 | 300 | 0 | 352 | 41 | 23 | 154 | 7 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 6 | 59 | 19 | 0 | 1 | 27.93 | 6 | 5627.93 | 784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 1004 | 0 | 0 | 0 | 1262.23 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 26.64 | 55 | 0 | 0 | 30.04 | 174 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 2.88 | 0 | 55 | 35 | 19 | 34 | 0 | 0 | 0 | 3.2 | 97 | 0.28 | 0 | 273 | 130 | 220 | 0 | 0 | 1020 | 0 | 5708.27 | 11336.2 | 93.48
10:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 52 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 25 | 52 | 24 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.81 | 70 | 0 | 2 | 875 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1090 | 17 | 0 | 0 | 0 | 325 | 360 | 51 | 0 | 195 | 0 | 0 | 102 | 0 | 0 | 11 | 0 | 112 | 0 | 57 | 0 | 290 | 0 | 370 | 42 | 23 | 154 | 9 | 17 | 0 | 81 | 30 | 0 | 0 | 100 | 17 | 59 | 19 | 0 | 2 | 38.35 | 6 | 5630.16 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 926 | 0 | 0 | 0 | 1265.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.94 | 81 | 0 | 0 | 45.92 | 161 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.22 | 0 | 55 | 0 | 27 | 34 | 0 | 0 | 0 | 4.3 | 136 | 0.43 | 0 | 216 | 130 | 220 | 0 | 0 | 950 | 0 | 5675.18 | 11305.34 | 93.48
11:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 52 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 29 | 52 | 13 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.32 | 75 | 0 | 2 | 875 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1100 | 19 | 0 | 0 | 0 | 330 | 355 | 51 | 0 | 204 | 0 | 0 | 99 | 0 | 0 | 14 | 0 | 114 | 0 | 66 | 0 | 290 | 0 | 392 | 42 | 23 | 155 | 11 | 17 | 0 | 83 | 30 | 0 | 0 | 98 | 17 | 59 | 19 | 0 | 2 | 44.46 | 6 | 5717.78 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 912 | 0 | 0 | 0 | 1278.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.45 | 98 | 0 | 0 | 55.55 | 167 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.13 | 0 | 54 | 0 | 31 | 34 | 0 | 0 | 0 | 5.5 | 167 | 0.52 | 0 | 219 | 125 | 220 | 0 | 0 | 940 | 0 | 5753.6 | 11471.38 | 93.47
12:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 52 | 48 | 15 | 0 | 4 | 15 | 0 | 0 | 0 | 23 | 0 | 0 | 310 | 0 | 0 | 30 | 52 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.49 | 40 | 0 | 2 | 875 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1160 | 20 | 0 | 0 | 0 | 335 | 350 | 51 | 0 | 204 | 0 | 0 | 98 | 0 | 0 | 14 | 0 | 124 | 0 | 68 | 0 | 285 | 0 | 392 | 42 | 23 | 157 | 11 | 8 | 0 | 83 | 30 | 0 | 0 | 98 | 17 | 59 | 19 | 0 | 2 | 45.86 | 6 | 5820.35 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 947 | 0 | 0 | 0 | 1377.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.56 | 101 | 0 | 0 | 59.65 | 171 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.52 | 0 | 54 | 0 | 35 | 34 | 0 | 0 | 0 | 6.3 | 176 | 0.56 | 0 | 278 | 125 | 220 | 0 | 0 | 1010 | 0 | 6049.72 | 11870.07 | 93.47
13:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 17 | 0 | 52 | 47 | 60 | 0 | 17 | 50 | 0 | 0 | 0 | 60 | 0 | 0 | 310 | 0 | 0 | 31 | 52 | 23 | 14 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.35 | 75 | 0 | 5 | 875 | 0 | 0 | 0 | 0 | 12 | 219 | 0 | 0 | 0 | 1165 | 0 | 0 | 0 | 0 | 330 | 350 | 51 | 0 | 198 | 0 | 12 | 97 | 33 | 0 | 14 | 0 | 114 | 0 | 65 | 0 | 285 | 0 | 358 | 42 | 23 | 157 | 11 | 17 | 0 | 85 | 30 | 0 | 0 | 98 | 0 | 59 | 19 | 19 | 2 | 45.3 | 6 | 6063.65 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 1030 | 0 | 0 | 0 | 1372.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.97 | 99 | 0 | 0 | 52.99 | 185 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 54 | 0 | 34 | 34 | 0 | 0 | 0 | 6.1 | 174 | 0.53 | 0 | 307 | 125 | 220 | 0 | 0 | 1040 | 0 | 6183.65 | 12247.3 | 93.47
14:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 15.2 | 0 | 52 | 47 | 15 | 0 | 17 | 17 | 0 | 0 | 0 | 122 | 0 | 0 | 310 | 0 | 0 | 28 | 52 | 23 | 14 | 0 | 0 | 0 | 0 | 95 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2.9 | 75 | 0 | 2 | 875 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 0 | 330 | 350 | 51 | 0 | 196 | 0 | 16 | 97 | 17 | 0 | 14 | 0 | 126 | 0 | 58 | 0 | 290 | 0 | 358 | 42 | 23 | 155 | 9 | 17 | 0 | 85 | 30 | 0 | 0 | 98 | 0 | 59 | 19 | 19 | 2 | 40.66 | 6 | 6022.76 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 1082 | 0 | 0 | 0 | 1378.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.63 | 91 | 0 | 0 | 51.55 | 186 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 5.19 | 0 | 54 | 0 | 30 | 0 | 0 | 0 | 0 | 5.5 | 160 | 0.47 | 0 | 275 | 125 | 220 | 0 | 0 | 1026 | 0 | 6111.63 | 12134.39 | 93.46
15:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 52 | 30 | 15 | 0 | 17 | 15 | 0 | 0 | 0 | 150 | 0 | 0 | 310 | 0 | 0 | 22 | 52 | 23 | 14 | 0 | 75 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.09 | 75 | 0 | 2 | 875 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 0 | 335 | 350 | 51 | 0 | 199 | 0 | 0 | 97 | 0 | 0 | 14 | 0 | 118 | 0 | 46 | 0 | 295 | 0 | 375 | 42 | 23 | 153 | 7 | 17 | 0 | 85 | 30 | 0 | 0 | 97 | 0 | 58 | 19 | 19 | 1 | 31.82 | 6 | 5996.91 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 1019 | 0 | 0 | 0 | 1320.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.22 | 71 | 0 | 0 | 39.95 | 183 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 4 | 0 | 54 | 0 | 24 | 0 | 0 | 0 | 0 | 3.1 | 121 | 0.33 | 0 | 277 | 125 | 220 | 0 | 0 | 1040 | 0 | 5901.41 | 11898.32 | 93.45
16:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 52 | 30 | 15 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 14 | 52 | 18 | 15 | 0 | 75 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.22 | 75 | 0 | 5 | 875 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1065 | 0 | 0 | 0 | 0 | 315 | 340 | 51 | 0 | 211 | 0 | 0 | 97 | 0 | 0 | 14 | 0 | 114 | 0 | 28 | 0 | 295 | 0 | 393 | 42 | 23 | 147 | 4 | 17 | 0 | 85 | 30 | 0 | 0 | 98 | 0 | 59 | 19 | 16 | 1 | 18.29 | 6 | 5759.51 | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 988 | 0 | 0 | 0 | 1230.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.53 | 41 | 0 | 0 | 24.11 | 178 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 2.31 | 0 | 54 | 0 | 16 | 0 | 0 | 0 | 0 | 2.5 | 70 | 0.18 | 0 | 241 | 125 | 180 | 0 | 0 | 1000 | 0 | 5490.88 | 11250.39 | 93.45
17:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 13 | 1 | 60 | 46 | 15 | 0 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 5 | 70 | 23 | 20 | 0 | 95 | 0 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41 | 75 | 2 | 14 | 875 | 0 | 0 | 0 | 0 | 5 | 217 | 0 | 0 | 0 | 1105 | 0 | 10 | 4 | 0 | 305 | 345 | 51 | 0 | 203 | 0 | 15 | 97 | 9 | 0 | 14 | 0 | 112 | 0 | 9 | 0 | 310 | 0 | 326 | 42 | 23 | 0 | 1 | 17 | 0 | 85 | 30 | 0 | 0 | 97 | 0 | 59 | 19 | 16 | 0 | 5.12 | 6 | 5699.53 | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 991 | 0 | 0 | 0 | 1315.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.83 | 14 | 0 | 0 | 6.87 | 182 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0.73 | 0 | 54 | 0 | 5 | 34 | 0 | 0 | 0 | 0.8 | 21 | 0.06 | 0 | 239 | 125 | 180 | 0 | 0 | 1000 | 0 | 5458.28 | 11157.81 | 93.44
18:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 30 | 32 | 78 | 80 | 100 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 20 | 310 | 142 | 0 | 0 | 90 | 23 | 20 | 0 | 95 | 10 | 16 | 108 | 0 | 0 | 15 | 22 | 0 | 12 | 12 | 0 | 75 | 16 | 14 | 875 | 0 | 0 | 3 | 0 | 16 | 219 | 0 | 0 | 0 | 1160 | 0 | 50 | 13 | 0 | 290 | 355 | 51 | 0 | 197 | 0 | 47 | 98 | 68 | 4 | 14 | 0 | 126 | 0 | 0 | 0 | 305 | 0 | 347 | 42 | 23 | 7 | 0 | 17 | 0 | 85 | 30 | 0 | 0 | 96 | 0 | 78 | 19 | 16 | 0 | 0 | 6 | 6464 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 1015 | 0 | 0 | 0 | 1462.16 | 0 | 0 | 0 | 15 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 54 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 238 | 125 | 180 | 0 | 0 | 1004 | 12 | 5633.26 | 12097.26 | 93.44
19:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 33.4 | 35 | 78 | 80 | 130 | 0 | 35 | 86 | 0 | 0 | 0 | 0 | 0 | 35 | 315 | 198 | 0 | 0 | 108 | 23 | 19 | 0 | 90 | 20 | 16 | 109 | 0 | 0 | 17 | 24 | 0 | 24 | 24 | 0 | 75 | 33 | 30 | 875 | 0 | 0 | 31 | 0 | 46 | 223 | 0 | 0 | 0 | 1160 | 0 | 61 | 41 | 0 | 330 | 355 | 51 | 0 | 207 | 36 | 50 | 103 | 85 | 9 | 14 | 0 | 110 | 0 | 0 | 0 | 310 | 0 | 361 | 41 | 23 | 28 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 97 | 16 | 78 | 19 | 16 | 0 | 0 | 6 | 7041.4 | 890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1039 | 0 | 0 | 0 | 1451.85 | 0 | 0 | 0 | 45 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 53 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 239 | 130 | 220 | 0 | 0 | 1013 | 35 | 5893.85 | 12935.25 | 93.43
19:30 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 33.4 | 35 | 78 | 80 | 145 | 0 | 35 | 88 | 0 | 0 | 0 | 0 | 0 | 35 | 315 | 200 | 0 | 0 | 108 | 23 | 19 | 0 | 90 | 40 | 16 | 109 | 0 | 0 | 17 | 24 | 0 | 24 | 24 | 0 | 75 | 45 | 25 | 875 | 0 | 0 | 32 | 0 | 46 | 225 | 0 | 0 | 0 | 1150 | 0 | 70 | 43 | 0 | 315 | 360 | 51 | 0 | 195 | 38 | 47 | 103 | 100 | 9 | 14 | 0 | 118 | 0 | 0 | 0 | 295 | 0 | 348 | 41 | 23 | 30 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 96 | 17 | 79 | 19 | 16 | 0 | 0 | 6 | 6954.4 | 890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1033 | 0 | 0 | 0 | 1453.26 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 53 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 236 | 130 | 220 | 0 | 0 | 1000 | 35 | 5812.26 | 12766.66 | 93.43
20:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 29.8 | 35 | 78 | 46 | 145 | 0 | 35 | 97 | 0 | 0 | 0 | 0 | 0 | 35 | 315 | 143 | 0 | 0 | 108 | 18 | 19 | 0 | 90 | 42 | 16 | 109 | 0 | 0 | 17 | 15 | 0 | 24 | 24 | 0 | 75 | 47 | 27 | 875 | 0 | 0 | 32 | 0 | 47 | 226 | 0 | 0 | 0 | 1130 | 0 | 70 | 43 | 0 | 305 | 360 | 51 | 0 | 188 | 39 | 49 | 102 | 96 | 9 | 14 | 0 | 118 | 0 | 0 | 0 | 295 | 0 | 297 | 41 | 23 | 32 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 97 | 17 | 98 | 19 | 16 | 0 | 0 | 6 | 6819.8 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1030 | 0 | 0 | 0 | 1447.96 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 53 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 253 | 130 | 220 | 0 | 0 | 997 | 35 | 5788.96 | 12608.76 | 93.43
21:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 30.2 | 35 | 95 | 46 | 0 | 0 | 35 | 98 | 0 | 0 | 0 | 0 | 0 | 35 | 310 | 142 | 0 | 0 | 90 | 18 | 20 | 0 | 83 | 0 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 58 | 27 | 875 | 0 | 0 | 32 | 0 | 66 | 226 | 0 | 0 | 0 | 1160 | 0 | 40 | 8 | 0 | 295 | 360 | 51 | 0 | 197 | 20 | 60 | 102 | 111 | 0 | 14 | 0 | 116 | 0 | 0 | 0 | 300 | 0 | 326 | 41 | 23 | 42 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 98 | 0 | 99 | 19 | 16 | 0 | 0 | 0 | 6481.2 | 890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 993 | 0 | 0 | 0 | 1460.08 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 55 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 130 | 220 | 0 | 0 | 1004 | 0 | 5690.08 | 12171.28 | 93.42
22:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 26.5 | 0 | 95 | 46 | 0 | 0 | 35 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 204 | 0 | 0 | 70 | 18 | 20 | 0 | 83 | 0 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 34 | 26 | 875 | 0 | 0 | 12 | 0 | 34 | 226 | 0 | 0 | 0 | 1150 | 0 | 0 | 0 | 0 | 310 | 320 | 51 | 0 | 207 | 0 | 67 | 102 | 113 | 0 | 14 | 0 | 116 | 0 | 0 | 0 | 305 | 0 | 327 | 41 | 23 | 105 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 98 | 0 | 99 | 19 | 16 | 0 | 0 | 0 | 6315.5 | 890 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1006 | 0 | 0 | 0 | 1448.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 130 | 220 | 0 | 0 | 1020 | 0 | 5630.75 | 11946.25 | 93.42
23:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 15 | 0 | 95 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 288 | 207 | 0 | 0 | 35 | 17 | 21 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 17 | 36 | 875 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 1135 | 0 | 0 | 0 | 0 | 280 | 320 | 51 | 0 | 190 | 0 | 57 | 104 | 51 | 0 | 17 | 0 | 106 | 0 | 0 | 0 | 300 | 0 | 304 | 41 | 23 | 155 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 98 | 0 | 59 | 19 | 16 | 0 | 0 | 1 | 5802 | 891 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 990 | 0 | 0 | 0 | 1453.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 130 | 220 | 0 | 0 | 1002 | 0 | 5546.48 | 11348.48 | 93.41
Total KWH | 0 | 607680 | 257760 | 0 | 0 | 0 | 0 | 0 | 7963200 | 0 | 0 | 194040 | 149760 | 1354176 | 768480 | 491531 | 0 | 302192 | 558720 | 0 | 0 | 0 | 1529284 | 0 | 145713 | 7125612 | 1251000 | 0 | 213364 | 1040400 | 459600 | 428760 | 0 | 780909.09 | 84055 | 52691 | 1072320 | 0 | 35520 | 37390 | 37680 | 0 | 50880 | 48960 | 22801 | 1673320 | 256764 | 272160 | 20123636.36 | 0 | 0 | 134880 | 0 | 304436 | 5306971 | 0 | 0 | 0 | 25265452 | 75870 | 276000 | 117091 | 0 | 7825100 | 8546000 | 991285 | 0 | 4915000 | 99432 | 401280 | 2140246 | 654720 | 24360 | 322420 | 0 | 2572800 | 0 | 471918 | 0 | 7240000 | 0 | 8651000 | 983000 | 591360 | 2933755 | 73480 | 391728 | 0 | 1598400 | 673728 | 0 | 0 | 2371930 | 105120 | 1556400 | 405600 | 184320 | 13450 | 315840 | 101280 | 138026010.45 | 21453818 | 106848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 563760 | 22385500 | 0 | 0 | 0 | 28865455 | 0 | 0 | 0 | 141600 | 214656 | 0 | 0 | 0 | 0 | 333348 | 704560 | 46419 | 0 | 389248 | 4150455 | 0 | 0 | 0 | 0 | 0 | 9276945 | 0 | 33840 | 0 | 1174255 | 259757 | 231506 | 439555 | 0 | 0 | 0 | 40750.68 | 1182240 | 3480 | 37056 | 5651000 | 2892000 | 5325090 | 0 | 0 | 21794909.09 | 81600 | 127779650.77 | 265805661.22

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 18-02-2026
Power Supply Scenario
| Day Peak Generation |  |  | 11870.07 | MW | 12:00 Hr. | Energy Generated |  |  | 265.8057 |  | MKWHr.
| Day Peak Demand |  |  | 11944.07 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.079 |  | MKWHr.
| Evening Peak Generation |  |  | 12935.25 | MW | 19:00 Hr. | Energy Demand |  |  | 266.8847 |  | MKWHr.
| Evening Peak Demand |  |  | 13001.25 | MW | 19:00 Hr. | Maximum Temperature |  |  | 33 |  | °C
| Minimum Generation of the Day |  |  | 8392 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 767.19 |  | MMCFD
| Maximum Generation of the Day |  |  | 12935.25 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.877 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 19.5384 | 0 | 5.8705 | 0 | 0 | 0.21336 | 0 | 0 | 25.6222 | Gas | 97.4446 | Gas | 343568714.6353
| Chattogram Zone |  |  | 5.5791 | 45.3891 | 2.0801 | 0 | 1.6733 | 0.098671 | 0 | 0.03552 | 54.8558 | Coal | 96.3948 | Coal | 628866460.413
| Cumilla Zone |  |  | 24.9566 | 0 | 1.3564 | 0 | 0 | 0.47192 | 2.5728 | 0 | 29.3577 | HFO | 12.6959 | HFO | 217053055.71
| Mymensingh Zone |  |  | 0.18432 | 0 | 2.1684 | 0 | 0 | 0.32929 | 0 | 0 | 2.682 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 25.4349 | 0 | 0 | 0 | 0 | 0.07348 | 0 | 0 | 25.5084 | Hydro | 1.6733 | Hydro | 167332
| Khulna Zone |  |  | 0.10685 | 22.3855 | 0 | 0 | 0 | 0.56376 | 21.4538 | 0 | 44.5099 | Solar | 4.6695 | Solar | 74838084.436
| Barishal Zone |  |  | 8.2171 | 27.4459 | 0.11866 | 0 | 0 | 0.00348 | 0 | 0 | 35.7851 | Import | 52.8921 | Import | 297119845.27
| Rajshahi Zone |  |  | 13.4274 | 0 | 0.40268 | 0 | 0 | 1.461 | 28.8655 | 0 | 44.1565 | Wind | 0.03552 | Wind | 522499.2
| Rangpur Zone |  |  | 0 | 1.1743 | 0.69931 | 0 | 0 | 1.4545 | 0 | 0 | 3.3281
| Total |  |  | 97.4446 | 96.3948 | 12.6959 | 0 | 1.6733 | 4.6695 | 52.8921 | 0.03552 | 265.8057
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 343568714.6353 |  | Hydro | 167332
|  |  |  | Coal | 628866460.413 |  | Solar | 74838084.436
|  |  |  | HFO | 217053055.71 |  | Import | 297119845.27
|  |  |  | HSD | 0 |  | Wind | 522499.2
[5 empty] | Total: | 156,21,35,991 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.4538 | Peak Hr Flow | 890.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 39483001.84 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 28.8655 | Peak Hr Flow | 1451.85 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1860 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.5728 | Peak Hr Flow | 110.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2522 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 52.8921 | Peak Hr Flow | 2451.85 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4768
|  |  |  | Chattogram |  | 0 |  | 1250
|  |  |  | Cumilla |  | 0 |  | 1100
|  |  |  | Mymensingh |  | 63 |  | 1124
|  |  |  | Sylhet |  | 0 |  | 456
|  |  |  | Khulna |  | 0 |  | 1432
|  |  |  | Barishal |  | 0 |  | 353
|  |  |  | Rajshahi |  | 0 |  | 1197
|  |  |  | Rangpur |  | 0 |  | 872
|  |  |  | Total |  | 63 |  | 12552
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:56 | 16:41 | Kallyanpur 132/33kV S/S GT-1 (132kV) HT Scheduled S/D Due to Oil Centrifuging Purpose
| 08:57 |  | Adani 400 kV line-1 shunt reactor was shut down
| 09:10 | 14:25 | Shahmirpur-Sikalbaha 132kV Ckt-2 Scheduled S/D from Shahmirpur 132/33kV end Due to Jumper
Maintenance Work
| 10:37 |  | Mirpur-Uttara 3PH 132kV Ckt-1 Project Work S/D from Mirpur 132/33kV end Due to G2G
Project Development Work
| 11:00 | 16:00 | Agrabad-Rampur 132kV Ckt-2 Scheduled S/D from Agrabad 132/33kV end Due to Annual
Maintenance.
| 11:00 | 16:01 | Rampur 230/132/33 S/S Agrabad-2 Scheduled S/D Due to relay testing
| 11:40 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- GT
| 12:00 |  | Day Peak Generation: 11866 MW.
| 12:30 |  | Rooppur Nuclear Power Plant 400/230 kV ATT-20 transformer was shut down
| 13:26 | 13:44 | Chandpur 132/33kV S/S 402T (T-01) HT Scheduled S/D Due to Kite Removal
| 13:34 | 13:58 | Bogura 132/33kV S/S Transformer-2 LT Tripped showing Over Current relays Due to Talora | [7 empty] | 19.0MW load
|  |  | -33 KV Nesco | [7 empty] | interrup.
| 14:04 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- GT
| 14:43 |  | Unique Meghnaghat Power Limited (UMPL) GT Synchronized with remarks:- None
| 15:42 |  | Meghnaghat CCPP(Summit)-2 Shutdown with remarks:- GT
| 22:42 |  | Unique Meghnaghat Power Limited (UMPL) ST Synchronized with remarks:- None
| 22:42 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- ST
| 01:26 | 01:47 | Cumilla(N)-Shahjibazar 230 kV Ckt-2 Tripped from Cumilla(N) 230/132/33kV end showing
Distance Relay relays.
| 02:10 |  | Cumilla(N)-Shahjibazar 230 kV Ckt-2 Tripped from Cumilla(N) 230/132/33kV end showing
Distance Relay relays.
| 02:19 |  | Bheramara 410 MW CCPP ST was sync.
| 04:00 |  | Sehri Peak Generation: 10703 MW.
| 04:05 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- GT
| 04:35 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- ST
| 06:00 |  | Minimum Generation: 8501 MW.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 18-02-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0"MW due to gas restriction by Titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 412 | 7963200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 198 | 1251000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 315 | 7125612 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 33.4 | 194040 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 80 | 768480 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 302192 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 145713 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 459600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 19 | 428760 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 257760 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 130 | 491531 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 78 | 1354176 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 607680 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 86 | 558720 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 213364 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 149760 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 90 | 780909.09 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 1529284 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 108 | 1040400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1754.4 | 25622181.09
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | U#1 Under maintenance, U#2 Running
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 75870 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 31 | 134880 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 75 | 1673320 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 223 | 5306971 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 46 | 304436 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 24 | 37680 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 37390 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 50880 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 30 | 272160 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 109 | 1072320 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22801 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 52691 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 33 | 256764 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 48960 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 20 | 84055 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1160 | 25265452 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 35520 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 875 | 20123636.36 | ps availability is less
Chattogram Area Total |  |  |  |  | 4898.863 | 2707 | 54855786.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 207 | 4915000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 330 | 7825100 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 355 | 8546000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage as per NLDC instructions.
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 36 | 99432 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 41 | 117091 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 991285 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 61 | 276000 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 103 | 2140246 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 85 | 654720 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 110 | 2572800 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 322420 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 24360 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 50 | 401280 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 471918 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1452 | 29357652
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 16 | 184320 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 405600 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 1556400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 315840 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 101280 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 16 | 105120 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 135 | 2682010
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 73480 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 983000 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 23 | 591360 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 28 | 2933755 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 673728 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1598400 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 97 | 2371930 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 391728 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7240000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 361 | 8651000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2325 | 993 | 25508381
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 890 | 21453818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 106848 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 563760 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1039 | 22385500 | Plant availability less
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1929 | 44509926
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 37056 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 2892000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 1013 | 21794909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5325090 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 81600 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 239 | 5651000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3480 | -
Barishal Area Total |  |  |  |  | 2700.36 | 1653 | 35785135.09
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 333348 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 188 | 4150455 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9276945 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 46419 | Machine problem and fuel shortage
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 33 | 214656 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 45 | 141600 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 33840 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1451.85 | 28865455 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 389248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 704560 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2159.85 | 44156526
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 53 | 1174255 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 439555 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 40750.68 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 259757 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 231506 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1182240 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 152 | 3328063.68
Eastern Grid Total |  |  |  |  | 17400.108 | 7041.4 | 138026010.45
Western Grid Total |  |  |  |  | 10985.595 | 5893.85 | 127779650.77
National Grid Total |  |  |  |  | 28385.703 | 12935.25 | 265805661.22
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 18-02-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8634.61 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3853.64 | MW
i) Dhaka area |  |  | 4767.81 |  | MW | i) Khulna area |  |  |  | 1432 | MW
ii) Chattogram area |  |  | 1249.8 |  | MW | ii) Barishal area |  |  |  | 353.04 | MW
iii) Cumilla area |  |  | 1100 |  | MW | iii) Rajshahi area |  |  |  | 1196.6 | MW
iv) Mymensingh area |  |  | 1061 |  | MW | iv) Rangpur area |  |  |  | 872 | MW
v) Sylhet area |  |  | 456 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12488.25 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 12 | 00:00 | 67 | Hasnabad | 96 | 19:00 | 133 | Nawabganj | 33.6 | 13:00
2 | AKSML | 12.4 | 16:00 | 68 | Hathazari | 60 | 18:00 | 134 | Netrakona | 153 | 18:00
3 | Aftabnagar | 32 | 13:00 | 69 | Hatirjheel | 35 | 13:00 | 135 | New | 66 | 15:00
4 | Agargaon | 89 | 13:00 | 70 | Ishurdi | 59 | 19:00 | 136 | Niamatpur | 93 | 08:00
5 | Agrabad | 56 | 15:00 | 71 | Jaldhaka | 67 | 19:00 | 137 | Noapara | 40 | 13:00
6 | Amnura | 35 | 08:00 | 72 | Jamalpur | 114 | 20:00 | 138 | PHP | 8 | 00:00
7 | Ashuganj | 81 | 12:00 | 73 | Jashore | 110 | 20:00 | 139 | Pabna | 77 | 13:00
8 | BSRM | 198 | 08:00 | 74 | Jhenaidah | 86 | 07:00 | 140 | Palashbari | 112 | 08:00
9 | Bagerhat | 72 | 18:30 | 75 | Joydebpur | 133 | 18:00 | 141 | Panchagarh | 47 | 19:00
10 | Bajitpur | 78 | 18:30 | 76 | Joypurhat | 54 | 08:00 | 142 | Patiya | 7 | 18:30
11 | Bakerganj | 11.32 | 19:30 | 77 | Juldah | 16.5 | 15:00 | 143 | Patuakhali | 43.5 | 19:30
12 | Bakulia | 75 | 19:00 | 78 | KSRM | 17 | 22:00 | 144 | Payra | 30 | 19:30
13 | Banani | 47 | 14:00 | 79 | Kabirpur | 235 | 18:30 | 145 | Postogola | 46 | 13:00
14 | Bangabhaban | 14 | 13:00 | 80 | Kachua | 68 | 19:00 | 146 | Purbachal | 24 | 13:00
15 | Barapukuria | 67 | 08:00 | 81 | Kaliganj | 19 | 08:00 | 147 | Purbasadipur | 125 | 13:00
16 | Barguna | 16 | 19:00 | 82 | Kallyanpur | 88 | 13:00 | 148 | Rahanpur | 28 | 08:00
17 | Barishal | 84 | 13:00 | 83 | Kalurghat | 32 | 10:00 | 149 | Rahim | 39 | 00:00
18 | Barishal-230 | 74 | 20:00 | 84 | Kamrangirchar | 84 | 13:00 | 150 | Rajbari | 61 | 19:00
19 | Baroaulia | 66 | 12:00 | 85 | Kaptai | N/A | N/A | 151 | Rajendrapur | 123 | 14:00
20 | Baroirhat | 58 | 14:00 | 86 | Kasba | 28 | 18:30 | 152 | Rajshahi | 104 | 13:00
21 | Bashundhara | 163 | 13:00 | 87 | Kazla | 102 | 13:00 | 153 | Rajshahi-230 | 58 | 13:00
22 | BashundharaCement | 8 | 20:00 | 88 | Keranigonj | 72 | 13:00 | 154 | Ramganj | 80 | 18:30
23 | Beanibazar | 54 | 18:30 | 89 | Khagrachori | 30 | 18:30 | 155 | Rampur | 30 | 14:00
24 | Benapole | 52 | 08:00 | 90 | Khulna | 43 | 13:00 | 156 | Rangamati | 15 | 18:30
25 | Bhaluka | 138 | 08:00 | 91 | Khulshi | 157 | 18:00 | 157 | Rangpur | 116 | 19:30
26 | Bhandaria | 48 | 18:30 | 92 | Kishoreganj | 112 | 20:00 | 158 | Ruppur | 3.2 | 15:00
27 | Bhangura | 29 | 08:00 | 93 | Kodda | 269 | 18:30 | 159 | SSM | 0 | 00:00
28 | Bheramara(GK) | 43 | 18:30 | 94 | Kulaura | 33 | 18:00 | 160 | Saidpur | 104 | 09:00
29 | Bhulta | 223 | 21:00 | 95 | Kurigram | 67 | 08:00 | 161 | Satkhira | 120 | 19:00
30 | Bog-Sherpur | 66 | 08:00 | 96 | Kushtia | 121 | 13:00 | 162 | Satmasjid | 81 | 19:30
31 | Bogura | 125 | 19:00 | 97 | Laksam | 26 | 14:00 | 163 | Savar | 194 | 12:00
32 | Borhanuddin | 74 | 20:00 | 98 | Lakshmipur | 27 | 18:00 | 164 | SevenRings | 18.01 | 20:00
33 | Brahmanbaria | 105 | 18:30 | 99 | Lalbag | 68 | 12:00 | 165 | ShahCement | 35 | 16:00
34 | Cantonment | 80 | 13:00 | 100 | Lalmonirhat | 56 | 18:30 | 166 | Shahjadpur | 55 | 19:00
35 | Chandina | 30 | 14:00 | 101 | MI_Cement | 17.7 | 12:00 | 167 | Shahjibazar | 112 | 18:30
36 | Chandpur | 56 | 18:00 | 102 | Madanganj | 36 | 18:30 | 168 | Shahmirpur | 38.5 | 18:00
37 | Chandraghona | 30 | 18:00 | 103 | Madaripur | 78 | 20:00 | 169 | Shariatpur | 63 | 20:00
38 | Chapai | 60 | 12:00 | 104 | Madartek | 68 | 21:00 | 170 | Sherpur | 134 | 21:00
39 | Charsaidpur | 44 | 11:00 | 105 | Madunaghat | 48 | 14:00 | 171 | Shikalbaha | 27 | 00:00
40 | Chauddagram | 61 | 14:00 | 106 | Magura | 57 | 18:30 | 172 | Shitalakhya | 75.2 | 16:00
41 | Chhatak | 28 | 18:00 | 107 | Mahasthangarh | 74 | 08:00 | 173 | Sholosohor | 38 | 17:00
42 | Chowmuhani | 101 | 20:00 | 108 | Maijdee | 36 | 19:00 | 174 | Shyampur | 166 | 13:00
43 | Chuadanga | 83 | 13:00 | 109 | Manikganj | 100 | 18:30 | 175 | Siddhirganj | 118 | 12:00
44 | Coxsbazar | 118 | 18:00 | 110 | Maniknagar | 48 | 22:00 | 176 | Sirajganj | 94 | 19:00
45 | Cumilla(N) | 89 | 18:30 | 111 | Matarbari | 45 | 18:30 | 177 | Sonargaon | 160 | 16:00
46 | Cumilla(S) | 127 | 14:00 | 112 | Matuail | 62 | 13:00 | 178 | Sreemongol | 61 | 18:30
47 | Daganbhuiyan | 26 | 18:30 | 113 | Metrorail_Motijheel | 28 | 18:30 | 179 | Sreepur | 106 | 18:30
48 | Daudkandi | 123 | 18:30 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Srinagar | 35.6 | 14:00
49 | DhakaUniversity | 80 | 13:00 | 115 | Millgate | 82 | 12:00 | 181 | Sunamganj | 46 | 18:00
50 | Dhamrai | 128 | 18:30 | 116 | Mirpur | 126 | 14:00 | 182 | Sylhet | 45 | 13:00
51 | Dhanmondi | 95 | 13:00 | 117 | Mirsorai | 11 | 15:00 | 183 | Sylhet-132 | 87 | 14:00
52 | Dohazari | 75 | 18:00 | 118 | Mirzapur | 41 | 12:00 | 184 | TK | 19 | 18:00
53 | Faridpur | 122 | 18:30 | 119 | Mithapukur | 56 | 08:00 | 185 | Tangail | 150 | 12:00
54 | Fatullah | 89 | 12:00 | 120 | Modern | N/A | N/A | 186 | Taraganj | 19 | 09:00
55 | Fenchuganj | 26 | 14:00 | 121 | Mogbazar | 76 | 13:00 | 187 | Tasnim | 17 | 00:00
56 | Feni | 72 | 18:00 | 122 | Mongla | 42 | 19:00 | 188 | Thakurgaon | 91 | 19:00
57 | GPH | 5 | 13:00 | 123 | Motijheel | 41 | 13:00 | 189 | Tongi | 143 | 15:00
58 | Ghatail | 74 | 21:00 | 124 | Muktagacha | 35 | 20:00 | 190 | Ullahpara | 31 | 07:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 77 | 19:30 | 191 | Ullon | 54 | 18:30
60 | Ghorashal-230 | 104 | 18:30 | 126 | Muradnagar | 29 | 19:30 | 192 | Uttara | 64 | 13:00
61 | Goalpara | 33 | 21:00 | 127 | Mymensingh | 187 | 19:00 | 193 | UttaraNew | 32 | 13:00
62 | Gollamari | 88 | 19:00 | 128 | Naogaon | 119 | 09:00 | 194 | Zigatola | 62 | 12:00
63 | Gopalganj | 90 | 19:00 | 129 | Narail | 51 | 19:00
64 | Gulshan | 92 | 13:00 | 130 | Narinda | 58 | 13:00
65 | Halishahar | 77.5 | 14:00 | 131 | Narshingdi | 160 | 19:00
66 | HaripurSBU | 128 | 10:00 | 132 | Natore | 120 | 18:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 18-02-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 10193 | 35 |  | 10230
1:00 | 9580 | 33 |  | 9614
2:00 | 9194 | 25 |  | 9220
3:00 | 9068 | 0 |  | 9068
4:00 | 8615 | 0 |  | 8615
5:00 | 8392 | 0 |  | 8392
6:00 | 8918 | 61 |  | 8982
7:00 | 9767.78 | 81 |  | 9852.43
8:00 | 10930.76 | 77 |  | 11010.76
9:00 | 11336.2 | 64 |  | 11403.2
10:00 | 11305.34 | 66 |  | 11374.34
11:00 | 11471.38 | 59 |  | 11533.38
12:00 | 11870.07 | 71 |  | 11944.07
13:00 | 12247.3 | 73 |  | 12323.3
14:00 | 12134.39 | 76 |  | 12213.39
15:00 | 11898.32 | 62 |  | 11963.32
16:00 | 11250.39 | 69 |  | 11322.39
17:00 | 11157.81 | 64 |  | 11224.81
18:00 | 12097.26 | 60 |  | 12160.26
19:00 | 12935.25 | 63 |  | 13001.25
19:30 | 12766.66 | 52 |  | 12820.66
20:00 | 12608.76 | 0 |  | 12608.76
21:00 | 12171.28 | 0 |  | 12171.28
22:00 | 11946.25 | 0 |  | 11946.25
23:00 | 11348.48 | 40 |  | 11390.48
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 18-02-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5622 | 4571 | 10193 | DAILY GENERATION CURVE
00:30 | 5469 | 4417.5 | 9886.5
01:00 | 5316 | 4264 | 9580 | 18-02-2026
01:30 | 5175.5 | 4211.5 | 9387
02:00 | 5035 | 4159 | 9194
02:30 | 4981 | 4150 | 9131
03:00 | 4927 | 4141 | 9068
03:30 | 4731 | 4110.5 | 8841.5
04:00 | 4535 | 4080 | 8615
04:30 | 4490.5 | 4013 | 8503.5
05:00 | 4446 | 3946 | 8392
05:30 | 4570.5 | 4084.5 | 8655
06:00 | 4695 | 4223 | 8918
06:30 | 4912.54 | 4430.35 | 9342.89
07:00 | 5130.08 | 4637.7 | 9767.78
07:30 | 5333.715 | 5015.555 | 10349.27
08:00 | 5537.35 | 5393.41 | 10930.76
08:30 | 5582.64 | 5550.84 | 11133.48
09:00 | 5627.93 | 5708.27 | 11336.2
09:30 | 5629.045 | 5691.725 | 11320.77
10:00 | 5630.16 | 5675.18 | 11305.34
10:30 | 5673.97 | 5714.39 | 11388.36
11:00 | 5717.78 | 5753.6 | 11471.38
11:30 | 5769.065 | 5901.66 | 11670.725
12:00 | 5820.35 | 6049.72 | 11870.07
12:30 | 5942 | 6116.685 | 12058.685
13:00 | 6063.65 | 6183.65 | 12247.3
13:30 | 6043.205 | 6147.64 | 12190.845
14:00 | 6022.76 | 6111.63 | 12134.39
14:30 | 6009.835 | 6006.52 | 12016.355
15:00 | 5996.91 | 5901.41 | 11898.32
15:30 | 5878.21 | 5696.145 | 11574.355
16:00 | 5759.51 | 5490.88 | 11250.39
16:30 | 5729.52 | 5474.58 | 11204.1
17:00 | 5699.53 | 5458.28 | 11157.81
17:30 | 6081.765 | 5545.77 | 11627.535
18:00 | 6464 | 5633.26 | 12097.26
18:30 | 6752.7 | 5763.555 | 12516.255
19:00 | 7041.4 | 5893.85 | 12935.25
19:30 | 6954.4 | 5812.26 | 12766.66
20:00 | 6819.8 | 5788.96 | 12608.76
20:30 | 6650.5 | 5739.52 | 12390.02 |  | Executive Engineer
21:00 | 6481.2 | 5690.08 | 12171.28 |  | Network Operation Division
21:30 | 6398.35 | 5660.415 | 12058.765
22:00 | 6315.5 | 5630.75 | 11946.25
22:30 | 6058.75 | 5588.615 | 11647.365
23:00 | 5802 | 5546.48 | 11348.48

## En-Curve
QF-LDC-12
Date | 18-02-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3073 | 1377 | 900 | 0 | 102 | 952 | 70 | 3558 | 0 | 0 | 161 | 0 | 0 | 0 | 35 | DAILY ENERGY CURVE
00:30 | 3078 | 1331 | 900 | 0 | 100 | 892.5 | 70 | 3352.5 | 0 | 0 | 161 | 0 | 0 | 1.5 | 34 | 18-02-2026
01:00 | 3083 | 1285 | 900 | 0 | 98 | 833 | 70 | 3147 | 0 | 0 | 161 | 0 | 0 | 3 | 33
01:30 | 2965 | 1228 | 900 | 0 | 97 | 834 | 70 | 3129 | 0 | 0 | 161 | 0 | 0 | 3 | 29 | Energy Generated | 265.8057 |  | MKWHr
02:00 | 2847 | 1171 | 900 | 0 | 96 | 835 | 70 | 3111 | 0 | 0 | 161 | 0 | 0 | 3 | 25 | Energy not Served | 1.079 |  | MKWHr
02:30 | 2847.5 | 1126.5 | 900 | 0 | 95 | 835 | 70 | 3113.5 | 0 | 0 | 139 | 0 | 0 | 4.5 | 12.5 | Total Energy Requirement | 266.8847 |  | MKWHr
03:00 | 2848 | 1082 | 900 | 0 | 94 | 835 | 70 | 3116 | 0 | 0 | 117 | 0 | 0 | 6 | 0
03:30 | 2849.5 | 890.5 | 900 | 0 | 92 | 834.5 | 70 | 3105.5 | 0 | 0 | 92 | 0 | 0 | 7.5 | 0
04:00 | 2851 | 699 | 900 | 0 | 90 | 834 | 70 | 3095 | 0 | 0 | 67 | 0 | 0 | 9 | 0
04:30 | 2763.5 | 696.5 | 899.5 | 0 | 89 | 834 | 70 | 3074 | 0 | 0 | 66.5 | 0 | 0 | 10.5 | 0
05:00 | 2676 | 694 | 899 | 0 | 88 | 834 | 70 | 3053 | 0 | 0 | 66 | 0 | 0 | 12 | 0
05:30 | 2771 | 744.5 | 899.5 | 0 | 87 | 871.5 | 70 | 3132.5 | 0 | 0 | 71.5 | 0 | 0 | 7.5 | 30.5
06:00 | 2866 | 795 | 900 | 0 | 86 | 909 | 70 | 3212 | 0 | 0 | 77 | 0 | 0 | 3 | 61
06:30 | 2965 | 795 | 900 | 0 | 90 | 987 | 70 | 3444.5 | 12.39 | 0 | 77.5 | 0 | 0 | 1.5 | 71
07:00 | 3064 | 795 | 900 | 0 | 94 | 1065 | 70 | 3677 | 24.78 | 0 | 78 | 0 | 0 | 0 | 81
07:30 | 3090 | 821.5 | 829 | 0 | 101 | 1164 | 70 | 3980 | 109.27 | 63.5 | 121 | 0 | 0 | 0 | 79
08:00 | 3116 | 848 | 758 | 0 | 108 | 1263 | 70 | 4283 | 193.76 | 127 | 164 | 0 | 0 | 0 | 77
08:30 | 3102 | 864 | 771 | 0 | 108 | 1262.615 | 70 | 4322.5 | 292.365 | 138.5 | 202.5 | 0 | 0 | 0 | 70.5
09:00 | 3088 | 880 | 784 | 0 | 108 | 1262.23 | 70 | 4362 | 390.97 | 150 | 241 | 0 | 0 | 0 | 64
09:30 | 3088.5 | 872.5 | 842 | 0 | 110 | 1263.8 | 70 | 4237 | 472.97 | 150 | 214 | 0 | 0 | 0 | 65
10:00 | 3089 | 865 | 900 | 0 | 112 | 1265.37 | 70 | 4112 | 554.97 | 150 | 187 | 0 | 0 | 0 | 66
10:30 | 3115.5 | 862.5 | 900 | 0 | 113 | 1271.91 | 72.5 | 4106 | 609.95 | 150 | 187 | 0 | 0 | 0 | 62.5
11:00 | 3142 | 860 | 900 | 0 | 114 | 1278.45 | 75 | 4100 | 664.93 | 150 | 187 | 0 | 0 | 0 | 59
11:30 | 3147.5 | 870.5 | 900 | 0 | 119 | 1327.79 | 57.5 | 4212 | 682.435 | 150 | 204 | 0 | 0 | 0 | 65
12:00 | 3153 | 881 | 900 | 0 | 124 | 1377.13 | 40 | 4324 | 699.94 | 150 | 221 | 0 | 0 | 0 | 71
12:30 | 3150 | 906 | 900 | 0 | 119 | 1374.595 | 57.5 | 4397.5 | 680.09 | 149.5 | 324.5 | 0 | 0 | 0 | 72
13:00 | 3147 | 931 | 900 | 0 | 114 | 1372.06 | 75 | 4471 | 660.24 | 149 | 428 | 0 | 0 | 0 | 73
13:30 | 3128 | 962 | 900 | 0 | 120 | 1375.175 | 75 | 4471.5 | 631.57 | 149 | 378.1 | 0 | 0 | 0.5 | 74.5
14:00 | 3109 | 993 | 900 | 0 | 126 | 1378.29 | 75 | 4472 | 602.9 | 149 | 328.2 | 0 | 0 | 1 | 76
14:30 | 3128.5 | 1046 | 900 | 0 | 122 | 1349.55 | 75 | 4418.5 | 532.705 | 140.5 | 303.1 | 0 | 0 | 0.5 | 69
15:00 | 3148 | 1099 | 900 | 0 | 118 | 1320.81 | 75 | 4365 | 462.51 | 132 | 278 | 0 | 0 | 0 | 62
15:30 | 3131 | 1000.5 | 899.5 | 0 | 116 | 1275.53 | 75 | 4294 | 368.825 | 132 | 282 | 0 | 0 | 0 | 65.5
16:00 | 3114 | 902 | 899 | 0 | 114 | 1230.25 | 75 | 4223 | 275.14 | 132 | 286 | 0 | 0 | 0 | 69
16:30 | 3076.5 | 857.5 | 899 | 0 | 113 | 1273.12 | 75 | 4243.5 | 179.98 | 149 | 337.5 | 0 | 0 | 0 | 66.5
17:00 | 3039 | 813 | 899 | 0 | 112 | 1315.99 | 75 | 4264 | 84.82 | 166 | 389 | 0 | 0 | 0 | 64
17:30 | 3085 | 818.5 | 895 | 0 | 119 | 1389.075 | 75 | 4305 | 42.46 | 232 | 666.5 | 0 | 0 | 0 | 62
18:00 | 3131 | 824 | 891 | 0 | 126 | 1462.16 | 75 | 4346 | 0.1 | 298 | 944 | 0 | 0 | 0 | 60
18:30 | 3305 | 876.5 | 890.5 | 0 | 118 | 1457.005 | 75 | 4362.5 | 0.05 | 316 | 1115.7 | 0 | 0 | 0 | 61.5
19:00 | 3479 | 929 | 890 | 0 | 110 | 1451.85 | 75 | 4379 | 0 | 334 | 1287.4 | 0 | 0 | 0 | 63
19:30 | 3254 | 913 | 890 | 0 | 118 | 1453.26 | 75 | 4347 | 0 | 334 | 1382.4 | 0 | 0 | 0 | 52
20:00 | 3142 | 912 | 891 | 0 | 118 | 1447.96 | 75 | 4338 | 0 | 275 | 1409.8 | 0 | 0 | 0 | 0
20:30 | 3137.5 | 899 | 890.5 | 0 | 117 | 1454.02 | 75 | 4350.5 | 0 | 226.5 | 1240 | 0 | 0 | 0 | 0
21:00 | 3133 | 886 | 890 | 0 | 116 | 1460.08 | 75 | 4363 | 0 | 178 | 1070.2 | 0 | 0 | 0 | 0
21:30 | 3184.5 | 915.5 | 890 | 0 | 116 | 1454.415 | 75 | 4372 | 0 | 168 | 883.35 | 0 | 0 | 0 | 0
22:00 | 3236 | 945 | 890 | 0 | 116 | 1448.75 | 75 | 4381 | 0 | 158 | 696.5 | 0 | 0 | 0 | 0
22:30 | 3166.5 | 972.5 | 890.5 | 0 | 111 | 1451.115 | 75 | 4354 | 0 | 105 | 521.75 | 0 | 0 | 0 | 20
23:00 | 3097 | 1000 | 891 | 0 | 106 | 1453.48 | 75 | 4327 | 0 | 52 | 347 | 0 | 0 | 0 | 40
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 18-02-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 413 | 02:00 | 380 | 12:00 | Madunaghat | 413 | 02:00 | 395 | 13:00
Amtali | 421 | 02:00 | 408 | 12:00 | Meghnaghat | 413 | 02:00 | 377 | 12:00
Ashuganj | 418 | 2:00 | 392 | 11:00 | Payra | 422 | 01:00 | 409 | 16:00
Bhulta | 414 | 05:00 | 380 | 12:00 | Rahanpur | 420 | 04:00 | 405 | 08:00
Bibiana | 418 | 01:00 | 401 | 12:00 | Rampal | 416 | 02:00 | 395 | 12:00
BIPTC | 401 | 02:00 | 390 | 10:00
Bogura | 417 | 04:00 | 392 | 12:00
Gopalganj | 417 | 02:00 | 392 | 12:00
Kaliakoir | 406 | 02:00 | 374 | 12:00
Korerhat | 418 | 02:00 | 392 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 241 | 02:00 | 216 | 12:00 | Jhenaidah | 241 | 05:00 | 224 | 08:00
AKSML | 236 | 01:00 | 224.2 | 12:00 | Kachua | 239 | 02:00 | 224 | 12:00
Aminbazar | 240 | 04:00 | 217 | 12:00 | Kaliakoir | 243 | 02:00 | 221 | 12:00
Ashuganj | 241 | 05:00 | 226 | 13:00 | Keranigonj | 241 | 02:00 | 217 | 12:00
Ashuganj-400 | 241 | 05:00 | 226 | 13:00 | Khulna(S) | 244 | 05:00 | 228 | 12:00
Baghabari | 236 | 00:00 | 226 | 10:00 | Korerhat | 240 | 02:00 | 223 | 12:00
Barapukuria | 225 | 05:00 | 210 | 08:00 | Madunaghat | 238 | 01:00 | 225 | 12:00
Barapukuria-230 | 225 | 05:00 | 210 | 08:00 | Madunaghat-400 | 236 | 02:00 | 227 | 12:00
Barishal | 236 | 02:00 | 226 | 12:00 | Maniknagar | 241 | 02:00 | 222 | 23:00
Bheramara | 235 | 03:00 | 220 | 07:00 | Meghnaghat | 244 | 02:00 | 229 | 12:00
Bhulta | 241 | 02:00 | 220 | 12:00 | Meghnaghat-400 | 244 | 02:00 | 223 | 12:00
Bibiana | 244 | 02:00 | 231 | 12:00 | Mirsorai | 238 | 03:00 | 224 | 12:00
BIPTC | 239 | 04:00 | 222 | 07:00 | Rajshahi | 237 | 04:00 | 220 | 08:00
Bogura | 242 | 04:00 | 227 | 08:00 | Rampal | 241 | 03:00 | 225 | 12:00
Bogura-400 | 242 | 04:00 | 227 | 08:00 | Rampur | N/A | N/A | N/A | N/A
Borhanuddin | 237 | 01:00 | 232 | 11:00 | Rampura | 241 | 02:00 | 219 | 13:00
BSRM | 238 | 02:00 | 224 | 12:00 | Shikalbaha | 236 | 02:00 | 224 | 12:00
Chowmuhani | N/A | N/A | N/A | N/A | Shyampur | 241 | 02:00 | 219 | 12:00
Cumilla(N) | 240 | 02:00 | 223 | 13:00 | Siddhirganj | 239 | 00:00 | 224 | 15:00
Faridpur | 235 | 02:00 | 222 | 12:00 | Sirajgonj | 244 | 05:00 | 232 | 12:00
Fenchuganj | 242 | 02:00 | 233 | 17:00 | Sreepur | 237 | 02:00 | 221 | 12:00
Feni | 240 | 02:00 | 224 | 12:00 | Tongi | 235 | 04:00 | 222 | 12:00
Ghorashal | 238 | 00:00 | 225 | 13:00
Ghorashal-230 | 239 | 04:00 | 218 | 12:00
Gopalganj | 234 | 02:00 | 221 | 12:00
GPH | 238 | 18:00 | 225 | 12:00
Haripur | 242 | 02:00 | 222 | 12:00
Hasnabad | 241 | 02:00 | 217 | 12:00
Hathazari | 233 | 00:00 | 224 | 12:00
Ishurdi | 240 | 05:00 | 225 | 07:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 02:00 | 124 | 12:00 | Magura | 138 | 05:00 | 129 | 08:00
Agargaon | 137 | 02:00 | 122 | 12:00 | Mahasthangarh | 136 | 04:00 | 123 | 08:00
Agrabad | 135 | 00:00 | 127 | 12:00 | Maijdee | 134 | 02:00 | 125 | 12:00
AKS | 134 | 02:00 | 127 | 14:00 | Manikganj | 128 | 01:00 | 116 | 12:00
Aminbazar | 137 | 04:00 | 125 | 12:00 | Maniknagar | 136 | 02:00 | 122 | 12:00
Amnura | 140 | 02:00 | 128 | 08:00 | Matarbari | 132 | 03:00 | 119 | 14:00
Ashuganj | 141 | 03:00 | 133 | 12:00 | Matuail | 138 | 04:00 | 125 | 13:00
Bagerhat | 133 | 04:00 | 119 | 13:00 | Metrorail_Motijheel | 136 | 02:00 | 122 | 12:00
Bajitpur | 135 | 00:00 | 125 | 12:00 | Metrorail_Uttara | 132 | 01:00 | 122 | 10:00
Bakerganj | 137 | 00:00 | 133 | 12:00 | Millgate | 132 | 01:00 | 118 | 12:00
Bakulia | 136 | 01:00 | 126 | 19:30 | Mirpur | 136 | 01:00 | 124 | 12:00
Banani | 136 | 02:00 | 123 | 12:00 | Mirzapur | 136 | 02:00 | 124 | 12:00
Bangabhaban | 136 | 02:00 | 122 | 12:00 | Mithapukur | 136 | 04:00 | 121 | 08:00
Barapukuria | 137 | 03:00 | 126 | 08:00 | MI_Cement | 135 | 02:00 | 118 | 12:00
Barguna | 138 | 05:00 | 133 | 12:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 139 | 04:00 | 131 | 13:00 | Mogbazar | 137 | 01:00 | 125 | 12:00
Barishal-230 | 138 | 02:00 | 130 | 12:00 | Mongla | 135 | 04:00 | 120 | 12:00
Baroaulia | 136 | 20:00 | 129 | 12:00 | Motijheel | 136 | 02:00 | 122 | 12:00
Baroirhat | 136 | 01:00 | 127 | 12:00 | Muktagacha | 125 | 14:00 | 117 | 11:00
Bashundhara | 137 | 05:00 | 124 | 12:00 | Munshiganj | 135 | 01:00 | 125 | 12:00
BashundharaCement | 136 | 05:00 | 126 | 15:00 | Muradnagar | 137 | 02:00 | 124 | 13:00
Beanibazar | 134 | 04:00 | 127 | 12:00 | Mymensingh | 126 | 00:00 | 112 | 20:00
Benapole | 135 | 03:00 | 115 | 13:00 | Naogaon | 135 | 20:00 | 121 | 08:00
Bhaluka | 131 | 03:00 | 120 | 12:00 | Narail | 139 | 02:00 | 126 | 08:00
Bhandaria | 137 | 04:00 | 125 | 12:00 | Narinda | 136 | 02:00 | 122 | 12:00
Bhangura | 135 | 01:00 | 128 | 09:00 | Narshingdi | 134 | 04:00 | 124 | 12:00
Bheramara | 136 | 04:00 | 125 | 08:00 | Natore | 134 | 00:00 | 125 | 08:00
Bheramara(GK) | 134 | 04:00 | 126 | 09:00 | Nawabganj | 136 | 02:00 | 122 | 11:00
Bhulta | 129 | 00:00 | 121 | 12:00 | Netrakona | 125 | 00:00 | 109 | 18:00
Bog-Sherpur | 137 | 04:00 | 125 | 08:00 | New | 135 | 06:00 | 118 | 12:00
Bogura | 137 | 04:00 | 126 | 07:00 | Niamatpur | 140 | 02:00 | 133 | 07:00
Bogura-230 | 138 | 04:00 | 127 | 08:00 | Noapara | 136 | 03:00 | 120 | 13:00
Brahmanbaria | 134 | 02:00 | 126 | 12:00 | Pabna | 137 | 03:00 | 127 | 08:00
Cantonment | 136 | 01:00 | 121 | 12:00 | Palashbari | 134 | 04:00 | 118 | 08:00
Chandina | 139 | 02:00 | 128 | 13:00 | Panchagarh | 138 | 04:00 | 125 | 10:00
Chandpur | 136 | 20:00 | 128 | 11:00 | Patiya | 135 | 19:30 | 127 | 12:00
Chandraghona | 138 | 02:00 | 131 | 12:00 | Patuakhali | 136 | 18:30 | 132 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 140 | 02:00 | 133 | 08:00 | Payra | 138 | 01:00 | 134 | 12:00
Charsaidpur | 137 | 04:00 | 125 | 13:00 | PHP | 136 | 02:00 | 127 | 12:00
Chauddagram | 136 | 01:00 | 126 | 12:00 | Postogola | 137 | 03:00 | 121 | 12:00
Chhatak | 133 | 03:00 | 125 | 18:00 | Purbachal | 136 | 01:00 | 123 | 12:00
Chowmuhani | 132 | 02:00 | 125 | 12:00 | Purbasadipur | 132 | 04:00 | 119 | 08:00
Chuadanga | 139 | 03:00 | 127 | 08:00 | Rahanpur | 140 | 01:00 | 135 | 08:00
Coxsbazar | 126 | 00:00 | 119 | 13:00 | Rahanpur-400 | 141 | 02:00 | 135 | 08:00
Cumilla(N) | 139 | 02:00 | 128 | 13:00 | Rahim | 137 | 01:00 | 126 | 12:00
Cumilla(S) | 139 | 02:00 | 124 | 12:00 | Rajbari | 135 | 02:00 | 125 | 13:00
Daganbhuiyan | 135 | 01:00 | 126 | 12:00 | Rajendrapur | 133 | 05:00 | 120 | 14:00
Daudkandi | 136 | 04:00 | 123 | 12:00 | Rajshahi | 137 | 02:00 | 126 | 08:00
DhakaUniversity | 136 | 01:00 | 124 | 12:00 | Rajshahi-230 | 137 | 04:00 | 126 | 12:00
Dhamrai | 138 | 03:00 | 128 | 11:00 | Ramganj | 133 | 01:00 | 124 | 12:00
Dhanmondi | 138.4 | 06:00 | 127 | 12:00 | Rampur | 136 | 01:00 | 127 | 12:00
Dohazari | 136 | 12:00 | 128 | 11:00 | Rampura | 136 | 02:00 | 125 | 12:00
Faridpur | 135 | 01:00 | 128 | 13:00 | Rangamati | 137 | 02:00 | 126 | 10:00
Fatullah | 139 | 01:00 | 119 | 12:00 | Rangpur | 136 | 05:00 | 123 | 08:00
Fenchuganj | 138 | 02:00 | 132 | 17:00 | Ruppur | 140 | 06:00 | 129 | 09:00
Feni | 131 | 00:00 | 125 | 12:00 | Saidpur | 135 | 02:00 | 122 | 08:00
Feni-230 | 135 | 01:00 | 126 | 12:00 | Satkhira | 135 | 03:00 | 120 | 12:00
Ghatail | 127 | 02:00 | 118 | 07:00 | Satmasjid | 136 | 02:00 | 122 | 13:00
Ghorashal | 145 | 04:00 | 134 | 13:00 | Savar | 136 | 20:00 | 122 | 12:00
Goalpara | 138 | 03:00 | 124 | 12:00 | SevenRings | 145 | 02:00 | 132 | 12:00
Gollamari | 137 | 04:00 | 124 | 13:00 | ShahCement | 137 | 04:00 | 125 | 13:00
Gopalganj | 137 | 02:00 | 127 | 12:00 | Shahjadpur | 139 | 23:00 | 133 | 08:00
Gopalganj-400 | 139 | 02:00 | 131 | 12:00 | Shahjibazar | 135 | 06:00 | 126 | 13:00
Gulshan | 135 | 04:00 | 123 | 12:00 | Shahmirpur | 136 | 21:00 | 129 | 12:00
Halishahar | 137 | 01:00 | 128 | 12:00 | Shariatpur | 138 | 02:00 | 129 | 12:00
Haripur | 137 | 05:00 | 126 | 12:00 | Sherpur | 123 | 16:00 | 109 | 21:00
HaripurSBU | 137 | 05:00 | 126 | 12:00 | Shikalbaha | 125 | 21:00 | 118 | 12:00
Hasnabad | 136 | 04:00 | 121 | 12:00 | Shikalbaha-230 | 137 | 01:00 | 130 | 12:00
Hathazari | 136 | 00:00 | 132 | 12:00 | Shitalakhya | 135 | 02:00 | 118 | 12:00
Hatirjheel | 137 | 05:00 | 123 | 13:00 | Sholosohor | 137 | 01:00 | 130 | 12:00
Ishurdi | 139 | 03:00 | 129 | 08:00 | Shyampur | 137 | 04:00 | 133 | 09:00
Jaldhaka | 133 | 05:00 | 117 | 07:00 | Shyampur-230 | 140 | 02:00 | 125 | 12:00
Jamalpur | 127 | 16:00 | 115 | 05:00 | Siddhirganj | 137 | 01:00 | 125 | 12:00
Jashore | 136 | 03:00 | 116 | 13:00 | Sirajganj | 135 | 02:00 | 124 | 08:00
Jhenaidah | 139 | 03:00 | 110 | 08:00 | Sonargaon | 136 | 04:00 | 125 | 14:00
Jhenaidah-230 | 140 | 03:00 | 130 | 08:00 | Sreemongol | 136 | 06:00 | 128 | 12:00
Joydebpur | 143 | 01:00 | 129 | 15:00 | Sreepur | 135 | 02:00 | 125 | 12:00
Joypurhat | 134 | 05:00 | 117 | 08:00 | Srinagar | 136 | 01:00 | 122 | 11:00
Juldah | 135 | 03:00 | 128 | 12:00 | SSM | 140 | 00:00 | 126 | 11:00
Kabirpur | 138 | 03:00 | 115 | 12:00 | Sunamganj | 132 | 04:00 | 125 | 13:00
Kachua | 137 | 05:00 | 128 | 12:00 | Sylhet | 134 | 02:00 | 128 | 13:00
Kaliakoir | 142 | 01:00 | 130 | 12:00 | Sylhet-132 | 133 | 00:00 | 129 | 12:00
Kaliganj | 140 | 05:00 | 129 | 08:00 | Tangail | 128 | 02:00 | 119 | 12:00
Kallyanpur | 136 | 19:30 | 125 | 12:00 | Taraganj | 134 | 05:00 | 121 | 08:00
Kalurghat | 138 | 01:00 | 131 | 12:00 | Tasnim | 136 | 04:00 | 125 | 13:00
Kamrangirchar | 135 | 04:00 | 120 | 11:00 | Thakurgaon | 137 | 04:00 | 124 | 08:00
Kaptai | N/A | N/A | N/A | N/A | TK | 137 | 04:00 | 131 | 12:00
Kasba | 137 | 01:00 | 125 | 12:00 | Tongi | 131 | 04:00 | 120 | 11:00
Kazla | 136 | 04:00 | 120 | 13:00 | Ullahpara | 136 | 04:00 | 125 | 07:00
Keranigonj | 136 | 02:00 | 122 | 11:00 | Ullon | 136 | 02:00 | 124 | 12:00
Khagrachori | 134 | 00:00 | 130 | 12:00 | Uttara | 132 | 03:00 | 118 | 12:00
Khulna | 136 | 02:00 | 123 | 12:00 | UttaraNew | 132 | 01:00 | 117 | 12:00
Khulna(S) | 138 | 05:00 | 125 | 13:00 | Zigatola | 136 | 02:00 | 122 | 11:00
Khulshi | 134 | 00:00 | 127 | 12:00
Kishoreganj | 133 | 00:00 | 122 | 18:00
Kodda | 137 | 02:00 | 127 | 12:00
Korerhat | 139 | 02:00 | 129 | 12:00
KSRM | 136 | 02:00 | 128 | 12:00
Kulaura | 137 | 01:00 | 131 | 17:00
Kurigram | 132 | 05:00 | 117 | 08:00
Kushtia | 135 | 06:00 | 117 | 08:00
Laksam | 134 | 01:00 | 128 | 12:00
Lakshmipur | 134 | 02:00 | 125 | 12:00
Lalbag | 135 | 06:00 | 123 | 10:00
Lalmonirhat | 132 | 01:00 | 119 | 08:00
Madanganj | 136 | 05:00 | 126 | 15:00
Madaripur | 138 | 03:00 | 130 | 12:00
Madartek | 136 | 02:00 | 124 | 12:00
Madunaghat | 138 | 01:00 | 131 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division