## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 20-02-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-02-2026 | during | 20-02-2026 | during | 20-02-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Demand "0"MW due to gas restriction by Titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 321 | 293 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 285 | 277 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 15.4 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 30 | 15 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 24 | 17 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 8 | 8 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 98 | 87 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 51 | 35 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 16 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 480 | 300 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 400 | 295 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 142 | 160 | 160 | 52 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1820 | 1539.4 | 5945.22 | 5915.22 | 3098.05 | 3212.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | U#1 Under maintenance, U#2 Running
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 12 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 75 | 75 | 75 | 75 | 75 | 75 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 224 | 225 | 225 | 225 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 16 | 16 | 16 | 16 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 51 | 51 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 14 | 27 | 5 | 20 | 40 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.69 | 0 | 3.49 | 0 | 3.49 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 17 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 980 | 990 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 1 | 0 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 875 | 905 | 315 | 315 | 875 | 875 | ps availability is less
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2186.69 | 2250 | 3166.35 | 3158.86 | 3228.99 | 3206.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 201 | 193 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 320 | 285 | 353.35 | 353.35 | 353.35 | 353.35 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 345 | 325 | 318.81 | 318.81 | 318.81 | 318.81 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 25 | 0 | 46.7 | 46.7 | 0 | 50 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 5 | 0 | 55 | 55 | 0 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 20 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 42 | 42 | 42 | 42 | Machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 98 | 104 | 163 | 163 | 110 | 110 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 122 | 112 | 84 | 80 | 126 | 126 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 15 | 24.5 | 24.5 | 13 | 13 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1269 | 1085 | 2761.56 | 2687.56 | 1887.36 | 1922.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-02-2026 | during | 20-02-2026 | during | 20-02-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 20 | 19 | 157.5 | 157.5 | 35 | 35 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 28 | 10 | 28 | 20 | 20 | Fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 89 | 60 | 90 | 60 | 80 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 45.11 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 6 | 6 | Fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 151.11 | 142 | 351.2 | 352 | 185.2 | 158
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 41 | 42 | 42 | 0 | 0 | plant availability zero
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 23 | 23 | 23 | 23 | 23 | 23 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 159 | 151 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 98 | 96 | 100 | 100 | 100 | 100 | ST Under maint.
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 20 | 21 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 374 | 355 | 386 | 386 | 385 | 385 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1145 | 1099 | 1216 | 1216 | 1095 | 1096
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 900 | 900 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 44 | 44 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 280 | 254 | 410 | 410 | 300 | 300 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 33 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 772 | 974 | 1148.28 | 1148.28 | 1070 | 1070 | Plant availability less
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1985 | 2128 | 3507.28 | 3422.28 | 2564.1 | 2479.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 125 | 120 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 708 | 976 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 15 | 15 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 180 | 276 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.51 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2700.36 | 1233.51 | 1592 | 2003.32 | 2002.32 | 1868.32 | 1867.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 48.79 | 0 | 50 | 0 | 50 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 179 | 172 | 214 | 214 | 214 | 214 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 339 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.89 | 0 | 5.45 | 0 | 5.45 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1043.36 | 1370.18 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 54.38 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 100 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1844.42 | 1881.18 | 3137.32 | 2920.87 | 2576.94 | 2360.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 52 | 53 | 55 | 55 | 55 | 55 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 17 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.2 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 172 | 0 | 170.8 | 0 | 170.8 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 263.2 | 70 | 523 | 317 | 489 | 283
System Total |  |  |  |  | 28823.2 | 28385.703 | 11897.93 | 11786.58 | 22611.25 | 21992.11 | 16992.96 | 16584.82
Forecast Scenario (20-02-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11030 |  | 0 |  | 11030
|  |  |  | 1:00 | 10550 |  | 0 |  | 10550
|  |  |  | 2:00 | 10110 |  | 0 |  | 10110
|  |  |  | 3:00 | 10230 |  | 0 |  | 10230
|  |  |  | 4:00 | 10930 |  | 0 |  | 10930
|  |  |  | 5:00 | 9720 |  | 0 |  | 9720
|  |  |  | 6:00 | 8860 |  | 0 |  | 8860
|  |  |  | 7:00 | 8660 |  | 0 |  | 8660
|  |  |  | 8:00 | 8900 |  | 0 |  | 8900
|  |  |  | 9:00 | 9280 |  | 0 |  | 9280
|  |  |  | 10:00 | 9720 |  | 0 |  | 9720
|  |  |  | 11:00 | 9950 |  | 0 |  | 9950
|  |  |  | 12:00 | 10510 |  | 0 |  | 10510
|  |  |  | 13:00 | 10880 |  | 0 |  | 10880
|  |  |  | 14:00 | 9740 |  | 0 |  | 9740
|  |  |  | 15:00 | 9920 |  | 0 |  | 9920
|  |  |  | 16:00 | 10130 |  | 0 |  | 10130
|  |  |  | 17:00 | 10640 |  | 0 |  | 10640
|  |  |  | 18:00 | 10690 |  | 0 |  | 10690
|  |  |  | 18:30 | 10700 |  | 0 |  | 10700
|  |  |  | 19:00 | 10810 |  | 0 |  | 10810
|  |  |  | 19:30 | 10970 |  | 0 |  | 10970
|  |  |  | 20:00 | 10880 |  | 0 |  | 10880
|  |  |  | 21:00 | 10970 |  | 0 |  | 10970
|  |  |  | 22:00 | 10930 |  | 0 |  | 10930
|  |  |  | 23:00 | 10510 |  | 0 |  | 10510
Probable Maximum Temperature: |  |  | 29.80°C
Probable Maximum Demand at Day Peak: |  |  | 10510.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 10970.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10970.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 244.55 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:04 hrs on 20-02-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 19-02-2026 | [28 empty] | Date: | 19-02-2026 | [28 empty] | Date: | 19-02-2026 | [28 empty] | Date: | 19-02-2026 | [28 empty] | Date: | 19-02-2026 | [17 empty] | Date: | 19-02-2026
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [17 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 288 | 206 | 0 | 0 | 0 | 17 | 21 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 36 | 875 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 1045 | 0 | 0 | 0 | 0 | 290 | 320 | 51 | 0 | 193 | 0 | 0 | 104 | 0 | 0 | 18 | 0 | 98 | 0 | 0 | 0 | 290 | 0 | 311 | 41 | 23 | 142 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 100 | 0 | 59 | 19 | 17 | 0 | 0 | 6 | 5505 | 890 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 963 | 0 | 0 | 0 | 1176.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 130 | 220 | 0 | 0 | 920 | 0 | 5079.64 | 10584.64 | 93.41
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 206 | 0 | 0 | 0 | 17 | 22 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 35 | 720 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 968 | 0 | 0 | 0 | 0 | 290 | 320 | 51 | 0 | 194 | 0 | 0 | 104 | 0 | 0 | 18 | 0 | 90 | 0 | 0 | 0 | 290 | 0 | 322 | 41 | 23 | 135 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 100 | 0 | 59 | 19 | 19 | 0 | 0 | 6 | 5246 | 900 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 0 | 0 | 0 | 958.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 130 | 220 | 0 | 0 | 800 | 0 | 4551.77 | 9797.77 | 93.4
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 145 | 0 | 0 | 0 | 17 | 22 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 35 | 720 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 850 | 0 | 0 | 0 | 0 | 300 | 320 | 51 | 0 | 200 | 0 | 0 | 109 | 0 | 0 | 18 | 0 | 92 | 0 | 0 | 0 | 295 | 0 | 332 | 41 | 23 | 138 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 100 | 0 | 59 | 19 | 22 | 0 | 0 | 6 | 5145 | 900 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 775 | 0 | 0 | 0 | 864.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 130 | 220 | 0 | 0 | 700 | 0 | 4376.92 | 9521.92 | 93.4
03:00 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 46 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 143 | 0 | 0 | 35 | 17 | 22 | 0 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 3 | 875 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | 330 | 320 | 51 | 0 | 200 | 0 | 0 | 108 | 0 | 0 | 18 | 0 | 88 | 0 | 0 | 0 | 295 | 0 | 367 | 41 | 23 | 145 | 0 | 17 | 0 | 42 | 30 | 0 | 0 | 100 | 0 | 59 | 19 | 23 | 0 | 0 | 0 | 5577 | 900 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 0 | 0 | 0 | 959.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 130 | 220 | 0 | 0 | 730 | 0 | 4613.65 | 10190.65 | 93.39
04:00 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 82 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 211 | 0 | 0 | 35 | 17 | 22 | 0 | 331 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 24 | 875 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 1045 | 0 | 0 | 0 | 0 | 320 | 320 | 51 | 0 | 192 | 0 | 0 | 109 | 0 | 0 | 18 | 0 | 104 | 0 | 0 | 0 | 290 | 0 | 367 | 41 | 23 | 151 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 100 | 0 | 58 | 19 | 18 | 0 | 0 | 1 | 5910 | 900 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 0 | 0 | 0 | 1007.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 130 | 220 | 0 | 0 | 780 | 0 | 4793.21 | 10703.21 | 93.39
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 250 | 81 | 0 | 0 | 0 | 17 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 818 | 0 | 0 | 0 | 0 | 300 | 280 | 5 | 0 | 195 | 0 | 0 | 50 | 0 | 0 | 12 | 0 | 96 | 0 | 0 | 0 | 290 | 0 | 338 | 41 | 23 | 138 | 0 | 0 | 0 | 11 | 20 | 0 | 0 | 100 | 0 | 59 | 19 | 18 | 0 | 0 | 6 | 5147 | 900 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 762 | 0 | 0 | 0 | 823.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 110 | 180 | 0 | 0 | 500 | 0 | 4222.25 | 9369.25 | 93.38
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 250 | 81 | 0 | 0 | 0 | 16 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 610 | 0 | 0 | 0 | 0 | 290 | 220 | 5 | 0 | 140 | 0 | 0 | 50 | 0 | 0 | 12 | 0 | 76 | 0 | 0 | 0 | 285 | 0 | 315 | 41 | 23 | 133 | 0 | 0 | 0 | 11 | 20 | 0 | 0 | 100 | 0 | 59 | 19 | 20 | 0 | 0 | 6 | 4601 | 758 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 0 | 0 | 0 | 821.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3900.47 | 8501.47 | 93.38
07:00 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 299 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 250 | 0 | 0 | 1 | 0 | 16 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19 | 75 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 615 | 1 | 0 | 0 | 0 | 300 | 220 | 5 | 0 | 158 | 0 | 0 | 50 | 0 | 0 | 12 | 0 | 82 | 0 | 3 | 0 | 285 | 0 | 330 | 41 | 23 | 134 | 0 | 0 | 0 | 11 | 20 | 0 | 0 | 100 | 0 | 59 | 19 | 18 | 0 | 1.87 | 6 | 4570.06 | 899 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.73 | 767 | 0 | 0 | 0 | 821.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.82 | 3 | 0 | 0 | 1.72 | 134 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0.18 | 0 | 52 | 0 | 1 | 0 | 0 | 0 | 0 | 0.3 | 8 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 4151.23 | 8721.29 | 93.37
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 32 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 250 | 0 | 0 | 8 | 0 | 24 | 22 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.07 | 75 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 610 | 7 | 0 | 0 | 0 | 310 | 220 | 11 | 0 | 205 | 0 | 0 | 107 | 0 | 0 | 12 | 0 | 88 | 0 | 23 | 0 | 295 | 0 | 340 | 41 | 23 | 140 | 2 | 8 | 0 | 55 | 20 | 0 | 0 | 100 | 0 | 59 | 19 | 20 | 1 | 13.77 | 6 | 5180.84 | 759 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.75 | 781 | 0 | 0 | 0 | 821.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.9 | 23 | 0 | 0 | 14.04 | 166 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 52 | 0 | 8 | 0 | 0 | 0 | 0 | 1.5 | 46 | 0.13 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 4206.14 | 9386.98 | 93.37
09:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 60 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 265 | 0 | 0 | 17 | 0 | 24 | 22 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.17 | 75 | 0 | 14 | 720 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 635 | 13 | 0 | 0 | 0 | 330 | 300 | 51 | 0 | 201 | 0 | 0 | 103 | 0 | 0 | 12 | 0 | 102 | 0 | 43 | 0 | 305 | 0 | 365 | 41 | 23 | 149 | 3 | 17 | 0 | 86 | 20 | 0 | 0 | 100 | 0 | 59 | 19 | 20 | 1 | 28.17 | 6 | 5811.34 | 899 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 787 | 0 | 0 | 0 | 818.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.88 | 52 | 0 | 0 | 28.51 | 175 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 0 | 0 | 0 | 3.5 | 92 | 0.28 | 0 | 145 | 130 | 220 | 0 | 0 | 500 | 0 | 4688.94 | 10500.28 | 93.36
10:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 75 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 0 | 0 | 270 | 0 | 0 | 24 | 35 | 24 | 22 | 0 | 599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.02 | 75 | 0 | 12 | 720 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 700 | 17 | 0 | 0 | 0 | 325 | 330 | 51 | 0 | 199 | 0 | 0 | 103 | 0 | 0 | 13 | 0 | 106 | 0 | 57 | 0 | 305 | 0 | 362 | 41 | 23 | 153 | 9 | 17 | 0 | 83 | 20 | 0 | 0 | 100 | 0 | 59 | 19 | 20 | 2 | 36.84 | 6 | 6186.86 | 899 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 773 | 0 | 0 | 0 | 819.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.56 | 75 | 0 | 0 | 42.98 | 178 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.08 | 0 | 52 | 0 | 26 | 0 | 0 | 0 | 0 | 4.9 | 134 | 0.44 | 0 | 167 | 125 | 220 | 0 | 0 | 525 | 0 | 4846.17 | 11033.03 | 93.35
11:00 | 0 | 44 | 8 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 96 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 270 | 0 | 0 | 29 | 52 | 24 | 21 | 0 | 596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.52 | 75 | 0 | 11 | 800 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 780 | 20 | 0 | 5 | 0 | 300 | 330 | 51 | 1 | 199 | 10 | 0 | 100 | 0 | 0 | 13 | 0 | 116 | 0 | 63 | 0 | 310 | 0 | 369 | 42 | 23 | 158 | 11 | 17 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 59 | 19 | 20 | 2 | 44.31 | 6 | 6397.83 | 900 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 776 | 0 | 0 | 0 | 891.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.44 | 93 | 0 | 0 | 52.58 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.99 | 0 | 52 | 0 | 31 | 0 | 0 | 0 | 0 | 5.8 | 162 | 0.53 | 0 | 169 | 125 | 220 | 0 | 0 | 570 | 0 | 5060.43 | 11458.26 | 93.34
12:00 | 0 | 51 | 8 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 98 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 285 | 0 | 0 | 31 | 70 | 24 | 22 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.69 | 75 | 0 | 14 | 875 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 980 | 20 | 0 | 20 | 0 | 320 | 345 | 51 | 5 | 201 | 25 | 0 | 98 | 0 | 0 | 14 | 0 | 122 | 0 | 68 | 0 | 305 | 0 | 374 | 42 | 23 | 159 | 11 | 17 | 0 | 86 | 30 | 0 | 0 | 98 | 0 | 59 | 19 | 20 | 2 | 45.11 | 6 | 6571.8 | 900 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 772 | 0 | 0 | 0 | 1043.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.79 | 100 | 0 | 0 | 54.38 | 179 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.89 | 0 | 52 | 0 | 33 | 0 | 0 | 0 | 0 | 6.2 | 172 | 0.51 | 0 | 180 | 125 | 220 | 0 | 0 | 708 | 0 | 5326.13 | 11897.93 | 93.33
13:00 | 0 | 51 | 8 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 0 | 98 | 30 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 290 | 0 | 0 | 29 | 70 | 17 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.36 | 75 | 0 | 16 | 875 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1160 | 18 | 0 | 26 | 0 | 325 | 330 | 51 | 17 | 202 | 41 | 0 | 99 | 0 | 0 | 14 | 0 | 126 | 0 | 65 | 0 | 305 | 0 | 374 | 42 | 23 | 155 | 11 | 17 | 0 | 86 | 30 | 0 | 0 | 97 | 0 | 59 | 19 | 18 | 2 | 43.11 | 6 | 6613.47 | 900 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 824 | 0 | 0 | 0 | 1151.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.24 | 98 | 0 | 0 | 51.72 | 182 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 52 | 0 | 34 | 0 | 0 | 0 | 0 | 6 | 169 | 0.16 | 0 | 278 | 125 | 220 | 0 | 0 | 840 | 0 | 5758.52 | 12371.99 | 93.32
14:00 | 0 | 51 | 8 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 98 | 15 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 290 | 0 | 0 | 27 | 108 | 21 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.97 | 75 | 0 | 14 | 875 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1150 | 17 | 0 | 0 | 0 | 315 | 325 | 51 | 0 | 184 | 41 | 0 | 98 | 0 | 0 | 14 | 0 | 128 | 0 | 54 | 0 | 320 | 0 | 354 | 42 | 23 | 155 | 10 | 17 | 0 | 84 | 30 | 0 | 0 | 97 | 0 | 59 | 9 | 17 | 2 | 39.36 | 6 | 6505.33 | 900 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 904 | 0 | 0 | 0 | 1225.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.21 | 86 | 0 | 0 | 48.03 | 181 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 52 | 0 | 30 | 0 | 0 | 0 | 0 | 5.9 | 154 | 0.23 | 0 | 277 | 125 | 220 | 0 | 0 | 940 | 0 | 5929.44 | 12434.77 | 93.31
15:00 | 0 | 51 | 8 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 98 | 15 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 285 | 0 | 0 | 21 | 108 | 12 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.23 | 75 | 0 | 13 | 900 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1035 | 13 | 0 | 0 | 0 | 320 | 330 | 51 | 0 | 186 | 41 | 0 | 98 | 0 | 0 | 14 | 0 | 118 | 0 | 40 | 0 | 305 | 0 | 361 | 42 | 23 | 147 | 7 | 17 | 0 | 84 | 30 | 0 | 0 | 97 | 0 | 59 | 9 | 11 | 1 | 31.02 | 6 | 6299.25 | 899 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 888 | 0 | 0 | 0 | 1223.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.07 | 64 | 0 | 0 | 34.99 | 172 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 2.54 | 0 | 52 | 0 | 23 | 0 | 0 | 0 | 0 | 4.1 | 118 | 0.14 | 0 | 216 | 125 | 180 | 0 | 0 | 950 | 0 | 5668.8 | 11968.05 | 93.3
16:00 | 0 | 51 | 8 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 5 | 98 | 15 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 285 | 0 | 0 | 13 | 90 | 22 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.55 | 75 | 0 | 22 | 905 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1065 | 8 | 0 | 0 | 0 | 345 | 345 | 51 | 0 | 181 | 10 | 0 | 98 | 0 | 0 | 11 | 0 | 120 | 0 | 8 | 0 | 310 | 0 | 394 | 42 | 23 | 153 | 4 | 17 | 0 | 85 | 30 | 0 | 0 | 96 | 0 | 59 | 9 | 11 | 1 | 17.33 | 6 | 6380.88 | 899 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 882 | 0 | 0 | 0 | 1222.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.48 | 38 | 0 | 0 | 19.04 | 180 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 1.89 | 0 | 52 | 0 | 4 | 0 | 0 | 0 | 0 | 2.4 | 66 | 0.13 | 0 | 181 | 125 | 180 | 0 | 0 | 949 | 0 | 5505.72 | 11886.6 | 93.29
17:00 | 0 | 51 | 8 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 17 | 98 | 15 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 285 | 0 | 0 | 5 | 104 | 18 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 75 | 0 | 30 | 905 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1095 | 2 | 0 | 0 | 0 | 335 | 335 | 51 | 0 | 188 | 0 | 0 | 98 | 0 | 0 | 11 | 0 | 120 | 0 | 7 | 0 | 310 | 0 | 382 | 42 | 23 | 154 | 1 | 17 | 0 | 85 | 30 | 0 | 0 | 96 | 0 | 60 | 9 | 9 | 0 | 5.46 | 6 | 6407.79 | 900 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 919 | 0 | 0 | 0 | 1331.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.09 | 7 | 0 | 0 | 4.08 | 188 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.56 | 0 | 53 | 35 | 4 | 25 | 0 | 0 | 0 | 0.9 | 10 | 0.46 | 0 | 228 | 125 | 220 | 0 | 0 | 985 | 0 | 5743.36 | 12151.15 | 93.28
18:00 | 0 | 51 | 8 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 10 | 17 | 98 | 15 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 250 | 0 | 0 | 0 | 142 | 14 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 36 | 750 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 985 | 0 | 0 | 0 | 0 | 280 | 290 | 51 | 0 | 176 | 0 | 0 | 70 | 0 | 0 | 11 | 0 | 94 | 0 | 0 | 0 | 305 | 0 | 321 | 42 | 23 | 151 | 0 | 17 | 0 | 11 | 7 | 0 | 0 | 96 | 0 | 88 | 28 | 9 | 0 | 0 | 6 | 5756 | 900 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 994 | 0 | 0 | 0 | 1284.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 55 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 125 | 180 | 0 | 0 | 865 | 0 | 5389.36 | 11145.36 | 93.27
19:00 | 0 | 51 | 8 | 0 | 0 | 0 | 0 | 0 | 284 | 0 | 0 | 15.4 | 17 | 98 | 15 | 0 | 0 | 17 | 48 | 0 | 0 | 0 | 295 | 0 | 17 | 277 | 0 | 0 | 0 | 142 | 17 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 3 | 32 | 905 | 0 | 0 | 1 | 0 | 13 | 222 | 0 | 0 | 0 | 970 | 0 | 0 | 0 | 0 | 275 | 315 | 51 | 0 | 191 | 0 | 5 | 103 | 7 | 0 | 9 | 0 | 114 | 0 | 0 | 0 | 280 | 0 | 299 | 41 | 23 | 146 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 96 | 0 | 87 | 28 | 18 | 0 | 0 | 6 | 6071.4 | 900 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 953 | 0 | 0 | 0 | 1351.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 52 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 120 | 220 | 0 | 0 | 895 | 0 | 5582.62 | 11654.02 | 93.26
19:30 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 15.4 | 17 | 87 | 15 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 295 | 0 | 0 | 277 | 0 | 0 | 0 | 142 | 17 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 17 | 27 | 905 | 0 | 0 | 12 | 0 | 0 | 224 | 0 | 0 | 0 | 990 | 0 | 0 | 0 | 0 | 285 | 325 | 51 | 0 | 193 | 0 | 0 | 104 | 0 | 0 | 15 | 0 | 112 | 0 | 0 | 0 | 300 | 0 | 355 | 41 | 23 | 151 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 96 | 0 | 89 | 28 | 19 | 0 | 0 | 6 | 6115.4 | 900 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 974 | 0 | 0 | 0 | 1370.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 53 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 120 | 220 | 0 | 0 | 976 | 0 | 5671.18 | 11786.58
20:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 289 | 0 | 0 | 14.4 | 17 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 287 | 0 | 0 | 277 | 0 | 0 | 0 | 125 | 20 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 29 | 905 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 982 | 0 | 0 | 0 | 0 | 285 | 330 | 51 | 0 | 192 | 0 | 0 | 104 | 0 | 0 | 15 | 0 | 106 | 0 | 0 | 0 | 295 | 0 | 367 | 41 | 23 | 148 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 95 | 0 | 79 | 37 | 19 | 0 | 0 | 6 | 6021.4 | 899 | 256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 981 | 0 | 0 | 0 | 1363.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 130 | 220 | 0 | 0 | 978 | 0 | 5664.91 | 11686.31 | 93.25
21:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 275 | 0 | 0 | 0 | 70 | 20 | 22 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 29 | 905 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1026 | 0 | 0 | 0 | 0 | 345 | 355 | 51 | 0 | 208 | 0 | 0 | 104 | 0 | 0 | 15 | 0 | 110 | 0 | 0 | 0 | 300 | 0 | 402 | 41 | 23 | 154 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 95 | 0 | 79 | 37 | 19 | 0 | 0 | 6 | 6222 | 899 | 257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 962 | 0 | 0 | 0 | 1152.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221 | 130 | 220 | 0 | 0 | 900 | 0 | 5385.6 | 11607.6 | 93.24
22:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 265 | 0 | 0 | 0 | 52 | 19 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 27 | 905 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1010 | 0 | 0 | 0 | 0 | 330 | 335 | 51 | 0 | 203 | 0 | 0 | 105 | 0 | 0 | 15 | 0 | 106 | 0 | 0 | 0 | 305 | 0 | 380 | 41 | 23 | 161 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 98 | 0 | 79 | 37 | 19 | 0 | 0 | 6 | 6185 | 900 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 917 | 0 | 0 | 0 | 1135.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 130 | 220 | 0 | 0 | 900 | 0 | 5333.61 | 11518.61 | 93.23
23:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 259 | 0 | 0 | 0 | 35 | 19 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 31 | 905 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | 290 | 298 | 51 | 0 | 195 | 0 | 0 | 105 | 0 | 0 | 11 | 0 | 104 | 0 | 0 | 0 | 305 | 0 | 320 | 41 | 23 | 150 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 98 | 0 | 59 | 9 | 20 | 0 | 0 | 6 | 5889 | 900 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 838 | 0 | 0 | 0 | 1044.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 130 | 220 | 0 | 0 | 880 | 0 | 5053.35 | 10942.35 | 93.22
Total KWH | 0 | 731520 | 122880 | 0 | 0 | 0 | 0 | 0 | 7862400 | 0 | 0 | 38880 | 83160 | 1810800 | 313920 | 0 | 0 | 114606 | 33120 | 0 | 0 | 0 | 6636682 | 0 | 27108 | 6574657 | 1047000 | 0 | 206356 | 1284000 | 438600 | 498960 | 0 | 8430454.55 | 0 | 0 | 0 | 0 | 1920 | 0 | 0 | 0 | 0 | 0 | 23641 | 1800420 | 23418 | 465120 | 19883636.36 | 0 | 0 | 11040 | 0 | 40145 | 5179977 | 0 | 0 | 0 | 22161816 | 136350 | 0 | 33455 | 0 | 7874200 | 7582000 | 1106421 | 46560 | 4754000 | 161568 | 26880 | 2259553 | 26880 | 0 | 324610 | 0 | 2496960 | 0 | 396436 | 0 | 7298000 | 0 | 8792000 | 972000 | 586800 | 3552872.73 | 70174 | 344400 | 0 | 1625280 | 644736 | 0 | 0 | 2360020 | 0 | 1542000 | 453600 | 411840 | 13850 | 303690 | 142560 | 142185932.64 | 21565818 | 5592384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 511920 | 20247300 | 0 | 0 | 0 | 25249091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316516 | 655640 | 0 | 0 | 353248 | 4183909 | 0 | 0 | 0 | 0 | 0 | 9072872 | 0 | 19380 | 0 | 1214399 | 99337 | 225206 | 124492 | 0 | 0 | 0 | 39753.84 | 1112400 | 2986 | 0 | 4713000 | 2754000 | 5330120 | 0 | 0 | 19425454.55 | 0 | 122809226.39 | 264995159.03

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 19-02-2026
Power Supply Scenario
| Day Peak Generation |  |  | 11897.93 | MW | 12:00 Hr. | Energy Generated |  |  | 264.9952 |  | MKWHr.
| Day Peak Demand |  |  | 11933.93 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.725 |  | MKWHr.
| Evening Peak Generation |  |  | 11786.58 | MW | 19:30 Hr. | Energy Demand |  |  | 265.7202 |  | MKWHr.
| Evening Peak Demand |  |  | 11840.58 | MW | 19:30 Hr. | Maximum Temperature |  |  | 31 |  | °C
| Minimum Generation of the Day |  |  | 8501.47 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 838.07 |  | MMCFD
| Maximum Generation of the Day |  |  | 12434.77 | MW | 14:00 Hr. | Production Cost per KWHr |  |  | 5.4288 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 31.4888 | 0 | 4.56 | 0 | 0 | 0.20636 | 0 | 0 | 36.2551 | Gas | 114.7975 | Gas | 400254262.7751
| Chattogram Zone |  |  | 5.6451 | 42.0455 | 0.074603 | 0 | 1.8004 | 0.15999 | 0 | 0.00192 | 49.7275 | Coal | 87.6456 | Coal | 572459967.4198
| Cumilla Zone |  |  | 24.1424 | 0 | 0.05376 | 0 | 0 | 0.39644 | 2.497 | 0 | 27.0895 | HFO | 7.0503 | HFO | 122292643.79
| Mymensingh Zone |  |  | 0.41184 | 0 | 2.1382 | 0 | 0 | 0.31754 | 0 | 0 | 2.8675 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.1761 | 0 | 0 | 0 | 0 | 0.070174 | 0 | 0 | 26.2463 | Hydro | 1.8004 | Hydro | 180042
| Khulna Zone |  |  | 5.5924 | 20.2473 | 0 | 0 | 0 | 0.51192 | 21.5658 | 0 | 47.9174 | Solar | 4.3875 | Solar | 70743103.018
| Barishal Zone |  |  | 8.0841 | 24.1385 | 0 | 0 | 0 | 0.002986 | 0 | 0 | 32.2256 | Import | 49.3119 | Import | 272644488.51
| Rajshahi Zone |  |  | 13.2568 | 0 | 0 | 0 | 0 | 1.3448 | 25.2491 | 0 | 39.8507 | Wind | 0.00192 | Wind | 28243.2
| Rangpur Zone |  |  | 0 | 1.2144 | 0.22383 | 0 | 0 | 1.3774 | 0 | 0 | 2.8156
| Total |  |  | 114.7975 | 87.6456 | 7.0503 | 0 | 1.8004 | 4.3875 | 49.3119 | 0.00192 | 264.9952
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 400254262.7751 |  | Hydro | 180042
|  |  |  | Coal | 572459967.4198 |  | Solar | 70743103.018
|  |  |  | HFO | 122292643.79 |  | Import | 272644488.51
|  |  |  | HSD | 0 |  | Wind | 28243.2
[5 empty] | Total: | 143,86,02,750 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5658 | Peak Hr Flow | 900.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 34506002.07 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 25.2491 | Peak Hr Flow | 1370.18 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2112 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.497 | Peak Hr Flow | 112.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2341 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 49.3119 | Peak Hr Flow | 2382.18 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4362
|  |  |  | Chattogram |  | 0 |  | 1230
|  |  |  | Cumilla |  | 0 |  | 1031
|  |  |  | Mymensingh |  | 52 |  | 1045
|  |  |  | Sylhet |  | 0 |  | 412
|  |  |  | Khulna |  | 0 |  | 1309
|  |  |  | Barishal |  | 0 |  | 330
|  |  |  | Rajshahi |  | 0 |  | 1036
|  |  |  | Rangpur |  | 0 |  | 717
|  |  |  | Total |  | 52 |  | 11472
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:37 | 10:55 | Rajendrapur 132/33kV S/S MTR-1 LT Scheduled S/D
| 10:00 | 10:55 | Rajendrapur 132/33kV S/S MTR-1 HT Scheduled S/D
| 10:51 | 14:42 | Dhamrai-Kaliakoir 132 kV Ckt-2 Scheduled S/D from Dhamrai 132/33kV end Due to Kaliakoir
end
|  | 10:53 | BIPTC S/S 10CF16 is restored.
| 11:12 | 12:09 | Rajendrapur 132/33kV S/S MTR-3 LT Scheduled S/D
| 11:12 | 12:08 | Rajendrapur 132/33kV S/S MTR-3 HT Scheduled S/D
| 12:00 |  | Day Peak Generation: 11894 MW.
|  | 13:09 | Sirajganj 132/33kV S/S Solar Park 1 is restored.
| 14:25 | 15:08 | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to PBS DS Red hot maintenance | [7 empty] | 15.0MW load
interrup.
| 14:25 | 15:09 | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to PBS DS Red hot maintenance | [7 empty] | 15.0MW load
interrup.
| 14:43 | 16:02 | Dhamrai-Kaliakoir 132 kV Ckt-1 Scheduled S/D from Dhamrai 132/33kV end Due to Kaliakoir
End
|  | 15:24 | Kaliakoir 400/230/132kV S/S 132kV Bus 2 is restored.
| 16:20 | 19:48 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT Forced S/D Due to R-phase HT Bushing oil)
leakage
| 16:20 | 19:48 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 HT Forced S/D Due to R-Phase HT Bushing oil
leakage
| 19:30 |  | Evening Peak Generation: 11786 MW
| 19:30 |  | Evening Peak Generation: 11786 MW
| 05:21 |  | Siddhirgonj 335 MW CCPP SD due to filter change
| 07:00 |  | Minimum generation 8411 MW
| 07:08 |  | Agargaon 230/132kV S/S 230kV Transformer-2 ( 715T2) LT Scheduled S/D Due to Annual
Maintenance
| 07:09 |  | Agargaon 230/132kV S/S 230kV Transformer-2 ( 715T2) HT Scheduled S/D Due to Annual
Maintenance
| 07:55 |  | Noapara 132/33kV S/S T-1 LT Scheduled S/D Due to PBS Work | [7 empty] | 14.0MW load
interrup.
| 07:57 |  | Noapara 132/33kV S/S T-1 HT Scheduled S/D Due to PBS Work
| 08:00 |  | Noapara 132/33kV S/S Bus Section-1 Scheduled S/D Due to PBS Work | [7 empty] | 14.0MW load interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 19-02-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0"MW due to gas restriction by Titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 293 | 7862400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 1047000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 277 | 6574657 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 15.4 | 38880 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 15 | 313920 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 114606 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 27108 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17 | 438600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 498960 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 8 | 122880 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 87 | 1810800 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 35 | 731520 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 16 | 33120 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 206356 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 83160 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 300 | 8430454.55 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 295 | 6636682 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1284000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1539.4 | 36255103.55
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | U#1 Under maintenance, U#2 Running
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 136350 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 12 | 11040 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 75 | 1800420 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 224 | 5179977 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 40145 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 27 | 465120 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 23641 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 23418 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 990 | 22161816 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 1920 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 905 | 19883636.36 | ps availability is less
Chattogram Area Total |  |  |  |  | 4898.863 | 2250 | 49727483.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 193 | 4754000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 285 | 7874200 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 325 | 7582000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 161568 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 46560 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 33455 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1106421 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 104 | 2259553 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 26880 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 112 | 2496960 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 15 | 324610 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 26880 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 396436 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1085 | 27089523
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 19 | 411840 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13850 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 28 | 453600 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 89 | 1542000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 303690 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 142560 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 142 | 2867540
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 70174 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 972000 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 23 | 586800 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 151 | 3552872.73 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 644736 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1625280 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 96 | 2360020 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 344400 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7298000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 355 | 8792000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2325 | 1099 | 26246282.73
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 900 | 21565818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 254 | 5592384 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 511920 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 974 | 20247300 | Plant availability less
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2128 | 47917422
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2754000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 976 | 19425454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5330120 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 276 | 4713000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2986 | -
Barishal Area Total |  |  |  |  | 2700.36 | 1592 | 32225560.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 316516 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 172 | 4183909 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 339 | 9072872 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Machine problem and fuel shortage
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 19380 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1370.18 | 25249091 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 353248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 655640 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1881.18 | 39850656
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 53 | 1214399 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 17 | 124492 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 39753.84 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 99337 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 225206 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1112400 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 70 | 2815587.84
Eastern Grid Total |  |  |  |  | 17400.108 | 6115.4 | 142185932.64
Western Grid Total |  |  |  |  | 10985.595 | 5671.18 | 122809226.39
National Grid Total |  |  |  |  | 28385.703 | 11786.58 | 264995159.03
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 19-02-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8027.92 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3391.6 | MW
i) Dhaka area |  |  | 4361.62 |  | MW | i) Khulna area |  |  |  | 1309 | MW
ii) Chattogram area |  |  | 1230.3 |  | MW | ii) Barishal area |  |  |  | 329.8 | MW
iii) Cumilla area |  |  | 1031 |  | MW | iii) Rajshahi area |  |  |  | 1035.8 | MW
iv) Mymensingh area |  |  | 993 |  | MW | iv) Rangpur area |  |  |  | 717 | MW
v) Sylhet area |  |  | 412 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11419.52 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 8 | 14:00 | 67 | Hasnabad | 95 | 11:00 | 133 | Nawabganj | 37.6 | 13:00
2 | AKSML | 10.8 | 09:00 | 68 | Hathazari | 56 | 18:30 | 134 | Netrakona | 148 | 13:00
3 | Aftabnagar | 30 | 13:00 | 69 | Hatirjheel | 26 | 12:00 | 135 | New | 65.2 | 14:00
4 | Agargaon | 86 | 13:00 | 70 | Ishurdi | 54 | 03:00 | 136 | Niamatpur | 90 | 08:00
5 | Agrabad | 50 | 12:00 | 71 | Jaldhaka | 65 | 18:00 | 137 | Noapara | 38 | 19:00
6 | Amnura | 34 | 13:00 | 72 | Jamalpur | 106 | 08:00 | 138 | PHP | 8 | 06:00
7 | Ashuganj | 76 | 14:00 | 73 | Jashore | 107 | 19:00 | 139 | Pabna | 79 | 03:00
8 | BSRM | 204 | 03:00 | 74 | Jhenaidah | 81 | 18:00 | 140 | Palashbari | 95 | 13:00
9 | Bagerhat | 64 | 19:00 | 75 | Joydebpur | 119 | 14:00 | 141 | Panchagarh | 42 | 00:00
10 | Bajitpur | 67 | 19:00 | 76 | Joypurhat | 50 | 17:00 | 142 | Patiya | 7 | 18:30
11 | Bakerganj | 10.15 | 20:00 | 77 | Juldah | 18 | 15:00 | 143 | Patuakhali | 39.5 | 20:00
12 | Bakulia | 69 | 13:00 | 78 | KSRM | 11 | 03:00 | 144 | Payra | 28 | 19:00
13 | Banani | 44 | 13:00 | 79 | Kabirpur | 228 | 16:00 | 145 | Postogola | 44 | 14:00
14 | Bangabhaban | 12 | 10:00 | 80 | Kachua | 64 | 13:00 | 146 | Purbachal | 24 | 12:00
15 | Barapukuria | 66 | 13:00 | 81 | Kaliganj | 15 | 18:30 | 147 | Purbasadipur | 126 | 13:00
16 | Barguna | 14 | 18:30 | 82 | Kallyanpur | 90 | 17:00 | 148 | Rahanpur | 27 | 12:00
17 | Barishal | 80 | 13:00 | 83 | Kalurghat | 34 | 14:00 | 149 | Rahim | 45 | 14:00
18 | Barishal-230 | 68 | 18:30 | 84 | Kamrangirchar | 76 | 16:00 | 150 | Rajbari | 64 | 03:00
19 | Baroaulia | 60 | 10:00 | 85 | Kaptai | N/A | N/A | 151 | Rajendrapur | 126 | 12:00
20 | Baroirhat | 51 | 13:00 | 86 | Kasba | 29 | 13:00 | 152 | Rajshahi | 87 | 13:00
21 | Bashundhara | 168 | 13:00 | 87 | Kazla | 103 | 15:00 | 153 | Rajshahi-230 | 50 | 04:00
22 | BashundharaCement | 7 | 00:00 | 88 | Keranigonj | 69 | 19:30 | 154 | Ramganj | 80 | 04:00
23 | Beanibazar | 48 | 13:00 | 89 | Khagrachori | 28 | 13:00 | 155 | Rampur | 32 | 14:00
24 | Benapole | 48 | 09:00 | 90 | Khulna | 36 | 19:00 | 156 | Rangamati | 13 | 17:00
25 | Bhaluka | 138 | 14:00 | 91 | Khulshi | 161 | 13:00 | 157 | Rangpur | 128 | 17:00
26 | Bhandaria | 37 | 21:00 | 92 | Kishoreganj | 104 | 14:00 | 158 | Ruppur | 3.4 | 16:00
27 | Bhangura | 36 | 03:00 | 93 | Kodda | 278 | 17:00 | 159 | SSM | 0 | 00:00
28 | Bheramara(GK) | 40 | 13:00 | 94 | Kulaura | 30 | 16:00 | 160 | Saidpur | 105 | 17:00
29 | Bhulta | 211 | 14:00 | 95 | Kurigram | 64 | 17:00 | 161 | Satkhira | 107 | 18:00
30 | Bog-Sherpur | 68 | 03:00 | 96 | Kushtia | 113 | 13:00 | 162 | Satmasjid | 79 | 13:00
31 | Bogura | 125 | 18:00 | 97 | Laksam | 28 | 19:30 | 163 | Savar | 196 | 14:00
32 | Borhanuddin | 68 | 19:00 | 98 | Lakshmipur | 26 | 04:00 | 164 | SevenRings | 20.8 | 13:00
33 | Brahmanbaria | 95 | 18:30 | 99 | Lalbag | 68 | 13:00 | 165 | ShahCement | 33 | 19:30
34 | Cantonment | 78 | 14:00 | 100 | Lalmonirhat | 54 | 17:00 | 166 | Shahjadpur | 58 | 10:00
35 | Chandina | 27 | 05:00 | 101 | MI_Cement | 17.8 | 15:00 | 167 | Shahjibazar | 97 | 19:00
36 | Chandpur | 52 | 04:00 | 102 | Madanganj | 36 | 01:00 | 168 | Shahmirpur | 35 | 21:00
37 | Chandraghona | 28 | 18:30 | 103 | Madaripur | 81 | 13:00 | 169 | Shariatpur | 62 | 13:00
38 | Chapai | 67 | 03:00 | 104 | Madartek | 61 | 14:00 | 170 | Sherpur | 136 | 22:00
39 | Charsaidpur | 47 | 11:00 | 105 | Madunaghat | 43 | 13:00 | 171 | Shikalbaha | 23 | 12:00
40 | Chauddagram | 59 | 13:00 | 106 | Magura | 47 | 13:00 | 172 | Shitalakhya | 72.9 | 12:00
41 | Chhatak | 25 | 11:00 | 107 | Mahasthangarh | 68 | 03:00 | 173 | Sholosohor | 36 | 14:00
42 | Chowmuhani | 102 | 13:00 | 108 | Maijdee | 34 | 19:00 | 174 | Shyampur | 152 | 12:00
43 | Chuadanga | 84 | 03:00 | 109 | Manikganj | 97 | 21:00 | 175 | Siddhirganj | 116 | 14:00
44 | Coxsbazar | 107 | 17:00 | 110 | Maniknagar | 52 | 17:00 | 176 | Sirajganj | 92 | 10:00
45 | Cumilla(N) | 92 | 13:00 | 111 | Matarbari | 40 | 02:00 | 177 | Sonargaon | 149 | 12:00
46 | Cumilla(S) | 131 | 14:00 | 112 | Matuail | 59 | 12:00 | 178 | Sreemongol | 54 | 18:30
47 | Daganbhuiyan | 24 | 14:00 | 113 | Metrorail_Motijheel | 25 | 09:00 | 179 | Sreepur | 103 | 17:00
48 | Daudkandi | 118 | 21:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Srinagar | 34.04 | 14:00
49 | DhakaUniversity | 74 | 13:00 | 115 | Millgate | 80 | 14:00 | 181 | Sunamganj | 42 | 21:00
50 | Dhamrai | 116 | 09:00 | 116 | Mirpur | 122.5 | 14:00 | 182 | Sylhet | 41 | 13:00
51 | Dhanmondi | 92 | 13:00 | 117 | Mirsorai | 10 | 09:00 | 183 | Sylhet-132 | 76 | 14:00
52 | Dohazari | 73 | 18:30 | 118 | Mirzapur | 42 | 22:00 | 184 | TK | 17 | 18:30
53 | Faridpur | 115 | 19:00 | 119 | Mithapukur | 54 | 03:00 | 185 | Tangail | 154 | 13:00
54 | Fatullah | 99 | 12:00 | 120 | Modern | N/A | N/A | 186 | Taraganj | 20 | 18:00
55 | Fenchuganj | 25 | 18:30 | 121 | Mogbazar | 73.4 | 14:00 | 187 | Tasnim | 15 | 02:00
56 | Feni | 72 | 13:00 | 122 | Mongla | 47 | 12:00 | 188 | Thakurgaon | 80 | 17:00
57 | GPH | 76 | 17:00 | 123 | Motijheel | 41 | 13:00 | 189 | Tongi | 144 | 17:00
58 | Ghatail | 90 | 03:00 | 124 | Muktagacha | 38 | 13:00 | 190 | Ullahpara | 29 | 12:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 80 | 13:00 | 191 | Ullon | 53 | 17:00
60 | Ghorashal-230 | 103 | 16:00 | 126 | Muradnagar | 27 | 19:00 | 192 | Uttara | 64 | 13:00
61 | Goalpara | 30 | 13:00 | 127 | Mymensingh | 182 | 18:00 | 193 | UttaraNew | 31 | 18:00
62 | Gollamari | 86 | 19:00 | 128 | Naogaon | 116 | 13:00 | 194 | Zigatola | 59 | 15:00
63 | Gopalganj | 84 | 19:00 | 129 | Narail | 44 | 19:00
64 | Gulshan | 84 | 13:00 | 130 | Narinda | 56 | 14:00
65 | Halishahar | 73 | 14:00 | 131 | Narshingdi | 146 | 19:00
66 | HaripurSBU | 122 | 11:00 | 132 | Natore | 113 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 19-02-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 10584.64 | 0 |  | 10584.64
1:00 | 9797.77 | 0 |  | 9797.77
2:00 | 9521.92 | 0 |  | 9521.92
3:00 | 10190.65 | 57 |  | 10250.65
4:00 | 10703.21 | 35 |  | 10740.21
5:00 | 9369.25 | 0 |  | 9369.25
6:00 | 8501.47 | 0 |  | 8501.47
7:00 | 8721.29 | 0 |  | 8721.29
8:00 | 9386.98 | 0 |  | 9386.98
9:00 | 10500.28 | 22 |  | 10523.28
10:00 | 11033.03 | 34 |  | 11069.03
11:00 | 11458.26 | 34 |  | 11494.26
12:00 | 11897.93 | 34 |  | 11933.93
13:00 | 12371.99 | 48 |  | 12421.99
14:00 | 12434.77 | 84 |  | 12522.77
15:00 | 11968.05 | 62 |  | 12032.84
16:00 | 11886.6 | 64 |  | 11953.6
17:00 | 12151.15 | 69 |  | 12223.15
18:00 | 11145.36 | 63 |  | 11211.36
19:00 | 11654.02 | 54 |  | 11710.02
19:30 | 11786.58 | 52 |  | 11840.58
20:00 | 11686.31 | 33 |  | 11720.31
21:00 | 11607.6 | 0 |  | 11607.6
22:00 | 11518.61 | 0 |  | 11518.61
23:00 | 10942.35 | 32 |  | 10975.35
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## En-Curve
QF-LDC-12
Date | 19-02-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3115 | 1018 | 890 | 0 | 98 | 1176.64 | 75 | 4045 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3120.5 | 1014.5 | 895 | 0 | 94 | 1067.705 | 75 | 3768.5 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 19-02-2026
01:00 | 3126 | 1011 | 900 | 0 | 90 | 958.77 | 75 | 3492 | 0 | 0 | 145 | 0 | 0 | 0 | 0
01:30 | 3130 | 1035 | 900 | 0 | 91 | 911.845 | 75 | 3381 | 0 | 0 | 136 | 0 | 0 | 0 | 0 | Energy Generated | 264.9952 |  | MKWHr
02:00 | 3134 | 1059 | 900 | 0 | 92 | 864.92 | 75 | 3270 | 0 | 0 | 127 | 0 | 0 | 0 | 0 | Energy not Served | 0.725 |  | MKWHr
02:30 | 3232 | 1055 | 900 | 0 | 90 | 912.285 | 75 | 3440 | 0 | 26.5 | 125.5 | 0 | 0 | 0 | 28.5 | Total Energy Requirement | 265.7202 |  | MKWHr
03:00 | 3330 | 1051 | 900 | 0 | 88 | 959.65 | 75 | 3610 | 0 | 53 | 124 | 0 | 0 | 0 | 57
03:30 | 3397.5 | 1139 | 900 | 0 | 96 | 983.43 | 75 | 3650 | 0 | 63 | 142 | 0 | 0 | 1 | 46
04:00 | 3465 | 1227 | 900 | 0 | 104 | 1007.21 | 75 | 3690 | 0 | 73 | 160 | 0 | 0 | 2 | 35
04:30 | 3276 | 1171 | 900 | 0 | 100 | 915.23 | 75 | 3393 | 0 | 36.5 | 168.5 | 0 | 0 | 1 | 17.5
05:00 | 3087 | 1115 | 900 | 0 | 96 | 823.25 | 75 | 3096 | 0 | 0 | 177 | 0 | 0 | 0 | 0
05:30 | 2915 | 1112 | 829 | 0 | 86 | 822.36 | 75 | 2943.5 | 0 | 0 | 152 | 0 | 0 | 0.5 | 0
06:00 | 2743 | 1109 | 758 | 0 | 76 | 821.47 | 75 | 2791 | 0 | 0 | 127 | 0 | 0 | 1 | 0
06:30 | 2768.5 | 1118 | 828.5 | 0 | 79 | 821.475 | 75 | 2792.5 | 13.405 | 0.5 | 114 | 0 | 0 | 0.5 | 0
07:00 | 2794 | 1127 | 899 | 0 | 82 | 821.48 | 75 | 2794 | 26.81 | 1 | 101 | 0 | 0 | 0 | 0
07:30 | 2909.5 | 1293 | 829 | 0 | 85 | 821.65 | 75 | 2798.5 | 105.985 | 28 | 108.5 | 0 | 0 | 0 | 0
08:00 | 3025 | 1459 | 759 | 0 | 88 | 821.82 | 75 | 2803 | 185.16 | 55 | 116 | 0 | 0 | 0 | 0
08:30 | 3180 | 1649.5 | 829 | 0 | 95 | 820.295 | 75 | 2821 | 280.335 | 63.5 | 130 | 0 | 0 | 0 | 11
09:00 | 3335 | 1840 | 899 | 0 | 102 | 818.77 | 75 | 2839 | 375.51 | 72 | 144 | 0 | 0 | 0 | 22
09:30 | 3342 | 1939.5 | 899 | 0 | 104 | 818.99 | 75 | 2888 | 459.165 | 89.5 | 151.5 | 0 | 0 | 0 | 28
10:00 | 3349 | 2039 | 899 | 0 | 106 | 819.21 | 75 | 2937 | 542.82 | 107 | 159 | 0 | 0 | 0 | 34
10:30 | 3349 | 2024.5 | 899.5 | 0 | 111 | 855.15 | 75 | 3042 | 599.495 | 120.5 | 169.5 | 0 | 0 | 0 | 34
11:00 | 3349 | 2010 | 900 | 0 | 116 | 891.09 | 75 | 3147 | 656.17 | 134 | 180 | 0 | 0 | 0 | 34
11:30 | 3374 | 1913.5 | 900 | 0 | 119 | 967.225 | 75 | 3357 | 644.87 | 146.5 | 181 | 0 | 0 | 0 | 34
12:00 | 3399 | 1817 | 900 | 0 | 122 | 1043.36 | 75 | 3567 | 633.57 | 159 | 182 | 0 | 0 | 0 | 34
12:30 | 3401.5 | 1746.5 | 900 | 0 | 124 | 1097.38 | 75 | 3798 | 648.58 | 159 | 185 | 0 | 0 | 0 | 41
13:00 | 3404 | 1676 | 900 | 0 | 126 | 1151.4 | 75 | 4029 | 663.59 | 159 | 188 | 0 | 0 | 0 | 48
13:30 | 3376 | 1646.5 | 900 | 0 | 127 | 1188.235 | 75 | 4113.5 | 618.145 | 170.5 | 188.5 | 0 | 0 | 0 | 66
14:00 | 3348 | 1617 | 900 | 0 | 128 | 1225.07 | 75 | 4198 | 572.7 | 182 | 189 | 0 | 0 | 0 | 84
14:30 | 3312 | 1562.5 | 899.5 | 0 | 123 | 1224.515 | 75 | 4119.5 | 514.395 | 182 | 189 | 0 | 0 | 0 | 73
15:00 | 3276 | 1508 | 899 | 0 | 118 | 1223.96 | 75 | 4041 | 456.09 | 182 | 189 | 0 | 0 | 0 | 62
15:30 | 3329 | 1540 | 899 | 0 | 119 | 1223.37 | 75 | 4037.5 | 339.955 | 173 | 191.5 | 0 | 0 | 0 | 63
16:00 | 3382 | 1572 | 899 | 0 | 120 | 1222.78 | 75 | 4034 | 223.82 | 164 | 194 | 0 | 0 | 0 | 64
16:30 | 3394.5 | 1599.5 | 899.5 | 0 | 120 | 1277.025 | 75 | 4109.5 | 142.35 | 171 | 230.5 | 0 | 0 | 0 | 66.5
17:00 | 3407 | 1627 | 900 | 0 | 120 | 1331.27 | 75 | 4185 | 60.88 | 178 | 267 | 0 | 0 | 0 | 69
17:30 | 3168 | 1549.5 | 900 | 0 | 107 | 1308.065 | 75 | 4005.5 | 30.69 | 197 | 307.5 | 0 | 0 | 0 | 66
18:00 | 2929 | 1472 | 900 | 0 | 94 | 1284.86 | 75 | 3826 | 0.5 | 216 | 348 | 0 | 0 | 0 | 63
18:30 | 2978.5 | 1473.5 | 900 | 0 | 104 | 1318.24 | 75 | 3937 | 0.25 | 216 | 397.2 | 0 | 0 | 0 | 58.5
19:00 | 3028 | 1475 | 900 | 0 | 114 | 1351.62 | 75 | 4048 | 0 | 216 | 446.4 | 0 | 0 | 0 | 54
19:30 | 3150 | 1501 | 900 | 0 | 112 | 1370.18 | 75 | 4174 | 0 | 200 | 304.4 | 0 | 0 | 0 | 52
20:00 | 3172 | 1490 | 899 | 0 | 106 | 1363.91 | 75 | 4172 | 0 | 168 | 240.4 | 0 | 0 | 0 | 33
20:30 | 3292.5 | 1547 | 899 | 0 | 108 | 1258.255 | 75 | 4119 | 0 | 131.5 | 216.7 | 0 | 0 | 0 | 16.5
21:00 | 3413 | 1604 | 899 | 0 | 110 | 1152.6 | 75 | 4066 | 0 | 95 | 193 | 0 | 0 | 0 | 0
21:30 | 3403 | 1621 | 899.5 | 0 | 108 | 1144.105 | 75 | 4035 | 0 | 86 | 191.5 | 0 | 0 | 0 | 0
22:00 | 3393 | 1638 | 900 | 0 | 106 | 1135.61 | 75 | 4004 | 0 | 77 | 190 | 0 | 0 | 0 | 0
22:30 | 3261.5 | 1620 | 900 | 0 | 105 | 1089.98 | 75 | 3948.5 | 0 | 64.5 | 166 | 0 | 0 | 0 | 16
23:00 | 3130 | 1602 | 900 | 0 | 104 | 1044.35 | 75 | 3893 | 0 | 52 | 142 | 0 | 0 | 0 | 32
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 19-02-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 410 | 06:00 | 387 | 14:00 | Madunaghat | 414 | 07:00 | 397 | 14:00
Amtali | 421 | 06:00 | 410 | 14:00 | Meghnaghat | 407 | 06:00 | 386 | 14:00
Ashuganj | 418 | 6:00 | 389 | 14:00 | Payra | 423 | 05:00 | 412 | 14:00
Bhulta | 412 | 06:00 | 384 | 14:00 | Rahanpur | 423 | 05:00 | 403 | 17:00
Bibiana | 416 | 18:00 | 404 | 17:00 | Rampal | 417 | 06:00 | 400 | 13:00
BIPTC | 404 | 06:00 | 390 | 13:00
Bogura | 418 | 06:00 | 390 | 17:00
Gopalganj | 417 | 06:00 | 397 | 17:00
Kaliakoir | 402 | 06:00 | 381 | 17:00
Korerhat | 415 | 06:00 | 397 | 14:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 239 | 06:00 | 222 | 14:00 | Jhenaidah | 242 | 06:00 | 226 | 13:00
AKSML | 238.9 | 06:00 | 230.4 | 00:00 | Kachua | 239 | 06:00 | 224 | 14:00
Aminbazar | 239 | 06:00 | 222 | 14:00 | Kaliakoir | 240 | 05:00 | 224 | 16:00
Ashuganj | 239 | 06:00 | 225 | 16:00 | Keranigonj | 238 | 06:00 | 220 | 13:00
Ashuganj-400 | 239 | 6:00 | 223 | 14:00 | Khulna(S) | 245 | 06:00 | 228 | 17:00
Baghabari | 242 | 06:00 | 227 | 15:00 | Korerhat | 239 | 06:00 | 225 | 14:00
Barapukuria | 228 | 06:00 | 208 | 17:00 | Madunaghat | 233 | 04:00 | 226 | 13:00
Barapukuria-230 | 228 | 6:00 | 209 | 16:00 | Madunaghat-400 | 238 | 18:30 | 227 | 14:00
Barishal | 236 | 06:00 | 227 | 13:00 | Maniknagar | 239 | 06:00 | 222 | 14:00
Bheramara | 240 | 06:00 | 225 | 13:00 | Meghnaghat | 246 | 05:00 | 229 | 19:30
Bhulta | 240 | 06:00 | 222 | 14:00 | Meghnaghat-400 | 242 | 06:00 | 226 | 14:00
Bibiana | 242 | 05:00 | 233 | 13:00 | Mirsorai | 237 | 06:00 | 220 | 22:00
BIPTC | 242 | 06:00 | 225 | 17:00 | Rajshahi | 240 | 06:00 | 223 | 17:00
Bogura | 243 | 06:00 | 225 | 17:00 | Rampal | 242 | 06:00 | 227 | 13:00
Bogura-400 | 242 | 06:00 | 225 | 17:00 | Rampur | N/A | N/A | N/A | N/A
Borhanuddin | 239 | 01:00 | 233 | 13:00 | Rampura | 239 | 06:00 | 219 | 14:00
BSRM | 237 | 06:00 | 224 | 16:00 | Shikalbaha | 234 | 06:00 | 225 | 15:00
Chowmuhani | N/A | N/A | N/A | N/A | Shyampur | 239 | 06:00 | 222 | 14:00
Cumilla(N) | 238 | 06:00 | 224 | 13:00 | Siddhirganj | 240 | 03:00 | 224 | 13:00
Faridpur | 235 | 06:00 | 224 | 13:00 | Sirajgonj | 245 | 05:00 | 233 | 17:00
Fenchuganj | 244 | 11:00 | 237 | 13:00 | Sreepur | 235 | 06:00 | 221 | 14:00
Feni | 239 | 06:00 | 225 | 14:00 | Tongi | 238 | 05:00 | 219 | 17:00
Ghorashal | 240 | 03:00 | 225 | 14:00
Ghorashal-230 | 238 | 06:00 | 220 | 14:00
Gopalganj | 234 | 06:00 | 223 | 13:00
GPH | 236 | 06:00 | 225 | 17:00
Haripur | 239 | 05:00 | 223 | 14:00
Hasnabad | 239 | 05:00 | 222 | 15:00
Hathazari | 234 | 05:00 | 225 | 13:00
Ishurdi | 243 | 06:00 | 228 | 17:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 06:00 | 127 | 13:00 | Magura | 141 | 06:00 | 127 | 13:00
Agargaon | 135 | 06:00 | 125 | 13:00 | Mahasthangarh | 139 | 06:00 | 125 | 17:00
Agrabad | 135 | 05:00 | 128 | 13:00 | Maijdee | 133 | 06:00 | 125 | 13:00
AKS | 134 | 06:00 | 128 | 13:00 | Manikganj | 130 | 02:00 | 118 | 17:00
Aminbazar | 140 | 06:00 | 129 | 14:00 | Maniknagar | 135 | 06:00 | 122 | 14:00
Amnura | 140 | 03:00 | 128 | 17:00 | Matarbari | 132 | 03:00 | 117 | 17:00
Ashuganj | 140 | 05:00 | 133 | 14:00 | Matuail | 137.5 | 06:00 | 127.5 | 13:00
Bagerhat | 135 | 06:00 | 125 | 13:00 | Metrorail_Motijheel | 137 | 18:00 | 122 | 14:00
Bajitpur | 135 | 06:00 | 123 | 16:00 | Metrorail_Uttara | 134 | 07:00 | 121 | 17:00
Bakerganj | 138 | 05:00 | 134 | 13:00 | Millgate | 134 | 06:00 | 120 | 17:00
Bakulia | 135 | 07:00 | 128 | 13:00 | Mirpur | 139 | 06:00 | 128 | 14:00
Banani | 138 | 04:00 | 126 | 13:00 | Mirzapur | 135 | 18:00 | 126 | 17:00
Bangabhaban | 134 | 05:00 | 122 | 14:00 | Mithapukur | 137 | 06:00 | 121 | 17:00
Barapukuria | 140 | 06:00 | 124 | 17:00 | MI_Cement | 137 | 06:00 | 123 | 16:00
Barguna | 138 | 05:00 | 134 | 13:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 138 | 06:00 | 131 | 14:00 | Mogbazar | 140 | 05:00 | 124 | 10:00
Barishal-230 | 138 | 06:00 | 131 | 13:00 | Mongla | 134 | 06:00 | 124 | 12:00
Baroaulia | 135 | 03:00 | 130 | 13:00 | Motijheel | 134 | 05:00 | 122 | 14:00
Baroirhat | 134 | 01:00 | 128 | 14:00 | Muktagacha | 131 | 18:00 | 116 | 13:00
Bashundhara | 139 | 06:00 | 126 | 14:00 | Munshiganj | 136 | 06:00 | 125 | 14:00
BashundharaCement | 136 | 04:00 | 127 | 17:00 | Muradnagar | 135 | 07:00 | 126 | 13:00
Beanibazar | 133 | 09:00 | 128 | 13:00 | Mymensingh | 127 | 05:00 | 110 | 13:00
Benapole | 134 | 06:00 | 121 | 12:00 | Naogaon | 138 | 06:00 | 123 | 16:00
Bhaluka | 132 | 18:30 | 118 | 13:00 | Narail | 141 | 06:00 | 127 | 13:00
Bhandaria | 136 | 06:00 | 129 | 18:30 | Narinda | 135 | 6:00 | 122 | 14:00
Bhangura | 138 | 06:00 | 130 | 13:00 | Narshingdi | 135 | 04:00 | 122 | 14:00
Bheramara | 140 | 06:00 | 133 | 13:00 | Natore | 139 | 06:00 | 129 | 17:00
Bheramara(GK) | 140 | 06:00 | 133 | 17:00 | Nawabganj | 138 | 06:00 | 127 | 13:00
Bhulta | 130 | 05:00 | 121 | 14:00 | Netrakona | 125 | 01:00 | 108 | 16:00
Bog-Sherpur | 139 | 06:00 | 128 | 17:00 | New | 133 | 05:00 | 123 | 14:00
Bogura | 140 | 05:00 | 128 | 17:00 | Niamatpur | 142 | 05:00 | 133 | 17:00
Bogura-230 | 140 | 06:00 | 129 | 17:00 | Noapara | 136 | 06:00 | 125 | 13:00
Brahmanbaria | 135 | 05:00 | 125 | 14:00 | Pabna | 140 | 06:00 | 131 | 16:00
Cantonment | 134 | 05:00 | 124 | 14:00 | Palashbari | 135 | 06:00 | 120 | 17:00
Chandina | 138 | 06:00 | 129 | 13:00 | Panchagarh | 138 | 06:00 | 125 | 17:00
Chandpur | 135 | 07:00 | 126 | 14:00 | Patiya | 136 | 07:00 | 128 | 14:00
Chandraghona | 138 | 05:00 | 132 | 13:00 | Patuakhali | 138 | 04:00 | 133 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 140 | 06:00 | 133 | 17:00 | Payra | 138 | 05:00 | 135 | 13:00
Charsaidpur | 136 | 05:00 | 125 | 14:00 | PHP | 135 | 06:00 | 127 | 14:00
Chauddagram | 136 | 06:00 | 127 | 13:00 | Postogola | 138 | 05:00 | 125 | 14:00
Chhatak | 133 | 06:00 | 127 | 13:00 | Purbachal | 139 | 06:00 | 126 | 14:00
Chowmuhani | 134 | 06:00 | 125 | 13:00 | Purbasadipur | 132 | 06:00 | 118 | 17:00
Chuadanga | 140 | 06:00 | 127 | 13:00 | Rahanpur | 142 | 05:00 | 135 | 17:00
Coxsbazar | 129 | 06:00 | 118 | 17:00 | Rahanpur-400 | 142 | 02:00 | 135 | 17:00
Cumilla(N) | 138 | 06:00 | 128 | 13:00 | Rahim | 136 | 18:00 | 127 | 13:00
Cumilla(S) | 138 | 06:00 | 123 | 11:00 | Rajbari | 136 | 06:00 | 127 | 14:00
Daganbhuiyan | 134 | 06:00 | 126 | 14:00 | Rajendrapur | 132 | 06:00 | 120 | 14:00
Daudkandi | 134 | 04:00 | 123 | 13:00 | Rajshahi | 139 | 06:00 | 129 | 13:00
DhakaUniversity | 139 | 06:00 | 127 | 14:00 | Rajshahi-230 | 139 | 06:00 | 121 | 12:00
Dhamrai | 137 | 05:00 | 126 | 17:00 | Ramganj | 133 | 06:00 | 124 | 13:00
Dhanmondi | 139 | 05:00 | 127.5 | 13:00 | Rampur | 135 | 06:00 | 128 | 13:00
Dohazari | 134 | 06:00 | 126 | 13:00 | Rampura | 139 | 06:00 | 126 | 14:00
Faridpur | 135 | 05:00 | 129 | 13:00 | Rangamati | 137 | 03:00 | 131 | 13:00
Fatullah | 138 | 06:00 | 124 | 14:00 | Rangpur | 137 | 06:00 | 122 | 17:00
Fenchuganj | 137 | 08:00 | 134 | 00:00 | Ruppur | 141 | 06:00 | 133 | 17:00
Feni | 133 | 05:00 | 126 | 16:00 | Saidpur | 137 | 06:00 | 121 | 17:00
Feni-230 | 138 | 19:30 | 126 | 14:00 | Satkhira | 135 | 06:00 | 125 | 13:00
Ghatail | 128 | 18:00 | 118 | 17:00 | Satmasjid | 139 | 12:00 | 124 | 13:00
Ghorashal | 142 | 02:00 | 132 | 14:00 | Savar | 138 | 05:00 | 125 | 14:00
Goalpara | 138 | 06:00 | 128 | 12:00 | SevenRings | 143 | 06:00 | 132 | 14:00
Gollamari | 139 | 06:00 | 129 | 12:00 | ShahCement | 136 | 05:00 | 125 | 14:00
Gopalganj | 138 | 06:00 | 130 | 17:00 | Shahjadpur | 142 | 02:00 | 133 | 16:00
Gopalganj-400 | 139 | 06:00 | 132 | 17:00 | Shahjibazar | 135 | 08:00 | 126 | 17:00
Gulshan | 138 | 05:00 | 126 | 14:00 | Shahmirpur | 136 | 05:00 | 130 | 13:00
Halishahar | 136 | 06:00 | 128 | 14:00 | Shariatpur | 138 | 05:00 | 130 | 13:00
Haripur | 136 | 05:00 | 127 | 13:00 | Sherpur | 127 | 18:00 | 110 | 02:00
HaripurSBU | 136 | 04:00 | 127 | 14:00 | Shikalbaha | 125 | 02:00 | 119 | 13:00
Hasnabad | 139 | 06:00 | 126 | 13:00 | Shikalbaha-230 | 137 | 06:00 | 130 | 15:00
Hathazari | 137 | 04:00 | 131 | 13:00 | Shitalakhya | 137 | 06:00 | 123 | 16:00
Hatirjheel | 139 | 06:00 | 126 | 14:00 | Sholosohor | 137 | 06:00 | 131 | 14:00
Ishurdi | 142 | 06:00 | 134 | 17:00 | Shyampur | 135 | 00:00 | 127 | 16:00
Jaldhaka | 134 | 06:00 | 120 | 17:00 | Shyampur-230 | 138 | 05:00 | 128 | 14:00
Jamalpur | 125 | 10:00 | 116 | 14:00 | Siddhirganj | 137 | 04:00 | 127 | 14:00
Jashore | 135 | 06:00 | 122 | 12:00 | Sirajganj | 136 | 05:00 | 126 | 17:00
Jhenaidah | 142 | 05:00 | 119 | 13:00 | Sonargaon | 133 | 01:00 | 125 | 12:00
Jhenaidah-230 | 141 | 06:00 | 130 | 13:00 | Sreemongol | 135 | 08:00 | 127 | 17:00
Joydebpur | 140 | 06:00 | 128 | 14:00 | Sreepur | 137 | 15:00 | 124 | 13:00
Joypurhat | 135 | 05:00 | 120 | 17:00 | Srinagar | 138 | 05:00 | 127 | 14:00
Juldah | 135 | 05:00 | 129 | 13:00 | SSM | 140 | 00:00 | 135 | 09:00
Kabirpur | 139 | 04:00 | 119 | 16:00 | Sunamganj | 131 | 03:00 | 126 | 13:00
Kachua | 136 | 06:00 | 127 | 14:00 | Sylhet | 134 | 06:00 | 129 | 13:00
Kaliakoir | 142 | 18:00 | 129 | 16:00 | Sylhet-132 | 133 | 03:00 | 130 | 13:00
Kaliganj | 140 | 07:00 | 130 | 13:00 | Tangail | 130 | 18:00 | 121 | 17:00
Kallyanpur | 140 | 06:00 | 129 | 15:00 | Taraganj | 135 | 05:00 | 121 | 17:00
Kalurghat | 137 | 02:00 | 131 | 13:00 | Tasnim | 135 | 06:00 | 125 | 13:00
Kamrangirchar | 137 | 05:00 | 127 | 06:00 | Thakurgaon | 137 | 06:00 | 124 | 16:00
Kaptai | N/A | N/A | N/A | N/A | TK | 138 | 06:00 | 131 | 13:00
Kasba | 136 | 06:00 | 124 | 14:00 | Tongi | 136 | 05:00 | 123 | 17:00
Kazla | 133 | 05:00 | 122 | 14:00 | Ullahpara | 139 | 05:00 | 127 | 17:00
Keranigonj | 139 | 06:00 | 127 | 14:00 | Ullon | 139 | 06:00 | 126 | 14:00
Khagrachori | 136 | 08:00 | 130 | 13:00 | Uttara | 135 | 06:00 | 121 | 16:00
Khulna | 137 | 06:00 | 129 | 13:00 | UttaraNew | 134 | 06:00 | 121 | 16:00
Khulna(S) | 138 | 06:00 | 130 | 12:00 | Zigatola | 138 | 05:00 | 126 | 17:00
Khulshi | 134 | 05:00 | 127 | 14:00
Kishoreganj | 133 | 05:00 | 120 | 13:00
Kodda | 136 | 19:00 | 128 | 17:00
Korerhat | 140 | 06:00 | 130 | 16:00
KSRM | 136 | 05:00 | 130 | 13:00
Kulaura | 136 | 02:00 | 132 | 13:00
Kurigram | 131 | 04:00 | 113 | 17:00
Kushtia | 137 | 06:00 | 126 | 13:00
Laksam | 136 | 06:00 | 126 | 13:00
Lakshmipur | 133 | 06:00 | 125 | 13:00
Lalbag | 136 | 18:00 | 126 | 16:00
Lalmonirhat | 132 | 05:00 | 116 | 17:00
Madanganj | 136 | 04:00 | 127 | 17:00
Madaripur | 136 | 00:00 | 131 | 13:00
Madartek | 138 | 06:00 | 126 | 14:00
Madunaghat | 137 | 04:00 | 131 | 14:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division