## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 21-02-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-02-2026 | during | 21-02-2026 | during | 21-02-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 100 | Demand "0"MW due to gas restriction by Titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 337 | 336 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 13.5 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 22 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 40 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 29 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 500 | 500 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 445 | 545 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 17 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1422 | 1473.5 | 5611.22 | 5580.22 | 2872.05 | 2995.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | U#1 Under maintenance, U#2 Running
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 75 | 75 | 75 | 75 | 75 | 75 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 219 | 225 | 225 | 225 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 16 | 16 | 16 | 16 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 51 | 51 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 12 | 36 | 35 | 35 | 40 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.89 | 0 | 3.69 | 0 | 3.69 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 921 | 1160 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 3 | 0 | 2 | 14 | 2 | 14 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 365 | 600 | 620 | 620 | 875 | 875 | ps availability is less
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1617.89 | 2090 | 3502.55 | 3491.86 | 3230.19 | 3219.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 196 | 200 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 320 | 325 | 353.35 | 353.35 | 353.35 | 353.35 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 342 | 318.81 | 318.81 | 318.81 | 318.81 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 42 | 41.65 | 41.65 | 41.65 | 41.65 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 68 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 40 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 42 | 42 | 42 | 42 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 98 | 102 | 163 | 163 | 110 | 110 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 124 | 114 | 84 | 82 | 84 | 82 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 10 | 11 | 24.5 | 24.5 | 13 | 13 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 67 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1185 | 1255 | 2751.51 | 2684.51 | 2077.01 | 2065.01
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-02-2026 | during | 21-02-2026 | during | 21-02-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 23 | 24 | 157.5 | 157.5 | 35 | 35 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.3 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 48 | 20 | 50 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 98 | 60 | 115 | 60 | 80 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 22.58 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 131.88 | 176 | 361.2 | 399 | 185.2 | 158
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 41 | 42 | 42 | 0 | 0 | plant availability zero
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 23 | 23 | 23 | 23 | 23 | 23 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 155 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 86 | 86 | 86 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 99 | 98 | 0 | 0 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 20 | 21 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 378 | 386 | 385 | 385 | 385 | 385 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1141 | 1136 | 1115 | 1115 | 1095 | 1096
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 899 | 899 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 44 | 44 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 323 | 410 | 410 | 300 | 300 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 79.81 | 0 | 89 | 0 | 89 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 786 | 774 | 0 | 0 | 1070 | 1070 | Plant availability less
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2014.81 | 1996 | 2363 | 2274 | 2568.1 | 2479.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 127 | 130 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 700 | 1035 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 15 | 15 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 200 | 171 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.62 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2700.36 | 1247.62 | 1556 | 2003.32 | 2002.32 | 1868.32 | 1867.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 49.42 | 0 | 50 | 0 | 50 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 175 | 185 | 214 | 214 | 214 | 214 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 402 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | machine problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.81 | 0 | 5.45 | 0 | 5.45 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1059 | 930 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 29.97 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 97 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1815.2 | 1529 | 3105.32 | 2888.87 | 2576.94 | 2360.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 51 | 53 | 55 | 55 | 55 | 55 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 19 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 30 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 168 | 0 | 173.16 | 0 | 173.16 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 306 | 53 | 525.36 | 317 | 491.36 | 283
System Total |  |  |  |  | 28823.2 | 28385.703 | 10881.4 | 11264.5 | 21338.48 | 20752.78 | 16964.17 | 16523.47
Forecast Scenario (21-02-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 10500 |  | 0 |  | 10500
|  |  |  | 1:00 | 9900 |  | 0 |  | 9900
|  |  |  | 2:00 | 9400 |  | 0 |  | 9400
|  |  |  | 3:00 | 9600 |  | 0 |  | 9600
|  |  |  | 4:00 | 10200 |  | 0 |  | 10200
|  |  |  | 5:00 | 9100 |  | 0 |  | 9100
|  |  |  | 6:00 | 8400 |  | 0 |  | 8400
|  |  |  | 7:00 | 8600 |  | 0 |  | 8600
|  |  |  | 8:00 | 9400 |  | 0 |  | 9400
|  |  |  | 9:00 | 9960 |  | 0 |  | 9960
|  |  |  | 10:00 | 10260 |  | 0 |  | 10260
|  |  |  | 11:00 | 10740 |  | 0 |  | 10740
|  |  |  | 12:00 | 11070 |  | 0 |  | 11070
|  |  |  | 13:00 | 11480 |  | 0 |  | 11480
|  |  |  | 14:00 | 11730 |  | 0 |  | 11730
|  |  |  | 15:00 | 11680 |  | 0 |  | 11680
|  |  |  | 16:00 | 11540 |  | 0 |  | 11540
|  |  |  | 17:00 | 11880 |  | 0 |  | 11880
|  |  |  | 18:00 | 11850 |  | 0 |  | 11850
|  |  |  | 18:30 | 12000 |  | 0 |  | 12000
|  |  |  | 19:00 | 12290 |  | 0 |  | 12290
|  |  |  | 19:30 | 12260 |  | 0 |  | 12260
|  |  |  | 20:00 | 12280 |  | 0 |  | 12280
|  |  |  | 21:00 | 12270 |  | 0 |  | 12270
|  |  |  | 22:00 | 11730 |  | 0 |  | 11730
|  |  |  | 23:00 | 11460 |  | 0 |  | 11460
Probable Maximum Temperature: |  |  | 30.50°C
Probable Maximum Demand at Day Peak: |  |  | 11070.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12290.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12290.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 257.32 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:32 hrs on 21-02-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 20-02-2026
Power Supply Scenario
| Day Peak Generation |  |  | 10881.4 | MW | 12:00 Hr. | Energy Generated |  |  | 249.8072 |  | MKWHr.
| Day Peak Demand |  |  | 10881.4 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.161 |  | MKWHr.
| Evening Peak Generation |  |  | 11264.5 | MW | 21:00 Hr. | Energy Demand |  |  | 249.9682 |  | MKWHr.
| Evening Peak Demand |  |  | 11264.5 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32.5 |  | °C
| Minimum Generation of the Day |  |  | 8415.4 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 806.18 |  | MMCFD
| Maximum Generation of the Day |  |  | 11500.39 | MW | 13:00 Hr. | Production Cost per KWHr |  |  | 5.2504 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 30.5662 | 0 | 2.2268 | 0 | 0 | 0.1875 | 0 | 0 | 32.9805 | Gas | 112.8681 | Gas | 387804629.0459
| Chattogram Zone |  |  | 5.4686 | 36.2291 | 0.022582 | 0 | 1.7922 | 0.13437 | 0 | 0.03072 | 43.6776 | Coal | 80.186 | Coal | 523323941.8808
| Cumilla Zone |  |  | 23.5476 | 0 | 0.02784 | 0 | 0 | 0.4209 | 2.5027 | 0 | 26.4991 | HFO | 4.8972 | HFO | 83583801.17
| Mymensingh Zone |  |  | 0.51936 | 0 | 2.376 | 0 | 0 | 0.20017 | 0 | 0 | 3.0955 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 25.4381 | 0 | 0 | 0 | 0 | 0.06333 | 0 | 0 | 25.5014 | Hydro | 1.7922 | Hydro | 179224
| Khulna Zone |  |  | 6.2554 | 19.1854 | 0 | 0 | 0 | 0.55296 | 21.4495 | 0 | 47.4432 | Solar | 4.1453 | Solar | 66152899.276
| Barishal Zone |  |  | 8.095 | 23.537 | 0 | 0 | 0 | 0.003489 | 0 | 0 | 31.6355 | Import | 45.8876 | Import | 250094057.25
| Rajshahi Zone |  |  | 12.9779 | 0 | 0 | 0 | 0 | 1.3004 | 21.9354 | 0 | 36.2136 | Wind | 0.03072 | Wind | 451891.2
| Rangpur Zone |  |  | 0 | 1.2345 | 0.24401 | 0 | 0 | 1.2822 | 0 | 0 | 2.7607
| Total |  |  | 112.8681 | 80.186 | 4.8972 | 0 | 1.7922 | 4.1453 | 45.8876 | 0.03072 | 249.8072
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 387804629.0459 |  | Hydro | 179224
|  |  |  | Coal | 523323941.8808 |  | Solar | 66152899.276
|  |  |  | HFO | 83583801.17 |  | Import | 250094057.25
|  |  |  | HSD | 0 |  | Wind | 451891.2
[5 empty] | Total: | 131,15,90,443 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.4495 | Peak Hr Flow | 899.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 33512002.16 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 21.9354 | Peak Hr Flow | 930.00 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1773 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.5027 | Peak Hr Flow | 114.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2385 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 45.8876 | Peak Hr Flow | 1943.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4050
|  |  |  | Chattogram |  | 0 |  | 1171
|  |  |  | Cumilla |  | 0 |  | 1015
|  |  |  | Mymensingh |  | 0 |  | 991
|  |  |  | Sylhet |  | 0 |  | 418
|  |  |  | Khulna |  | 0 |  | 1240
|  |  |  | Barishal |  | 0 |  | 327
|  |  |  | Rajshahi |  | 0 |  | 1009
|  |  |  | Rangpur |  | 0 |  | 656
|  |  |  | Total |  | 0 |  | 10877
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:00 | 12:23 | Noapara 132/33kV S/S Bus Section-1 Scheduled S/D Due to PBS Work | [7 empty] | 14.0MW load
interrup.
| 09:35 | 10:12 | Kachua 230/132/33kV S/S TR-1 HT Tripped showing Relay-650 relays Due to the underground | [7 empty] | 15.0MW load
|  |  | cable of the Matlab feeder has burned. | [7 empty] | interrup.
|  | 09:55 | Maniknagar 132/33kV S/S Transformer GT-2 HT is restored.
| 10:01 | 15:41 | Bibiyana-Shahjibazar 230 kV Ckt-2 Forced S/D from Bibiana 400/230kV end Due to Triping
Issues
| 10:15 | 10:25 | Kachua 230/132/33kV S/S TR-1 HT Tripped showing Relay-650 relays Due to 33 kv bus side | [7 empty] | 18.0MW load
|  |  | D/S contact failure causing overcurrent. | [7 empty] | interrup.
| 10:25 | 16:40 | Kachua 230/132/33kV S/S TR-1 LT Forced S/D Due to 33 kv bus side D/S contact poin | [7 empty] | 15.0MW load
|  |  | maintenance. | [7 empty] | interrup.
|  | 11:22 | Noapara 132/33kV S/S T-1 HT is restored.
|  | 11:23 | Noapara 132/33kV S/S T-1 LT is restored.
| 11:32 | 12:22 | Noapara 132/33kV S/S T-2 LT Scheduled S/D | [7 empty] | 7.0MW load
interrup.
| 11:33 | 12:21 | Noapara 132/33kV S/S T-2 HT Scheduled S/D
| 12:00 |  | Day Peak Generation: 10876 MW.
|  | 12:27 | Agargaon 230/132kV S/S 230kV Transformer-2 ( 715T2) HT is restored.
|  | 12:29 | Agargaon 230/132kV S/S 230kV Transformer-2 ( 715T2) LT is restored.
| 13:00 |  | Madunaghat 132/33kV S/S TR-1(507T) HT Forced S/D
| 13:00 |  | Madunaghat 132/33kV S/S TR-1(507T) LT Forced S/D Due to Oil Leakage from TR-1 LT bushing
R-ph. The bushing is damaged and needs to be changed.
| 21:00 |  | Evening Peak Generation: 11264 MW
| 07:00 |  | Minimum Generation: 8168 MW.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 20-02-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0"MW due to gas restriction by Titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 336 | 7880400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 1298037 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 38520 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 51360 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 13.5 | 358200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 487080 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 83040 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 40 | 892512 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 197760 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 21600 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 187502 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 500 | 10562727.27 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 545 | 9979727 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 17 | 942000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1473.5 | 32980465.27
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | U#1 Under maintenance, U#2 Running
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 113130 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 75 | 1792240 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 4920920 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 22582 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 36 | 547680 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21238 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1160 | 21785453 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 30720 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 600 | 14443636.36 | ps availability is less
Chattogram Area Total |  |  |  |  | 4898.863 | 2090 | 43677599.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 200 | 4778000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 325 | 7948500 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 342 | 7520000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 42 | 340992 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 68 | 200727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 688560 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 102 | 1809234 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 15360 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 114 | 2502720 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 11 | 261620 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 12480 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 420900 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1255 | 26499093
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 24 | 519360 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 48 | 590400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 98 | 1670400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 191970 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 115200 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 176 | 3095530
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 63330 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 985000 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 23 | 571080 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3528409 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 579648 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1068480 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 98 | 2381100 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 302400 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7146000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 386 | 8876000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1136 | 25501447
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 899 | 21449454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 323 | 6255360 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 552960 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 774 | 19185450 | Plant availability less
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1996 | 47443224
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 2923000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 1035 | 19152000 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5171980 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 171 | 4385000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3489 | -
Barishal Area Total |  |  |  |  | 2700.36 | 1556 | 31635469
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 315680 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 185 | 4060545 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 8917309 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 26580 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 930 | 21935421 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 277504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 680610 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1529 | 36213649
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 53 | 1234472 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 119184 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 38443.08 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 124823 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 212728 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1031040 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 53 | 2760690.08
Eastern Grid Total |  |  |  |  | 17400.108 | 6130.5 | 131754134.63
Western Grid Total |  |  |  |  | 10985.595 | 5134 | 118053032.08
National Grid Total |  |  |  |  | 28385.703 | 11264.5 | 249807166.71
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 20-02-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7645.14 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3232.2 | MW
i) Dhaka area |  |  | 4049.74 |  | MW | i) Khulna area |  |  |  | 1240 | MW
ii) Chattogram area |  |  | 1171.4 |  | MW | ii) Barishal area |  |  |  | 327.4 | MW
iii) Cumilla area |  |  | 1015 |  | MW | iii) Rajshahi area |  |  |  | 1008.8 | MW
iv) Mymensingh area |  |  | 991 |  | MW | iv) Rangpur area |  |  |  | 656 | MW
v) Sylhet area |  |  | 418 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10877.34 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 12 | 15:00 | 67 | Hasnabad | 85 | 13:00 | 133 | Nawabganj | 37 | 13:00
2 | AKSML | 11.4 | 21:00 | 68 | Hathazari | 64 | 12:00 | 134 | Netrakona | 148 | 17:00
3 | Aftabnagar | 30 | 13:00 | 69 | Hatirjheel | 27 | 12:00 | 135 | New | 56 | 11:00
4 | Agargaon | 81 | 13:00 | 70 | Ishurdi | 56 | 04:00 | 136 | Niamatpur | 89 | 12:00
5 | Agrabad | 46 | 19:30 | 71 | Jaldhaka | 62 | 18:00 | 137 | Noapara | 30 | 18:30
6 | Amnura | 39 | 09:00 | 72 | Jamalpur | 106 | 04:00 | 138 | PHP | 8 | 07:00
7 | Ashuganj | 70 | 13:00 | 73 | Jashore | 106 | 13:00 | 139 | Pabna | 69 | 04:00
8 | BSRM | 195 | 17:00 | 74 | Jhenaidah | 83 | 18:30 | 140 | Palashbari | 98 | 12:00
9 | Bagerhat | 61 | 19:00 | 75 | Joydebpur | 94 | 12:00 | 141 | Panchagarh | 42 | 17:00
10 | Bajitpur | 71 | 13:00 | 76 | Joypurhat | 53 | 10:00 | 142 | Patiya | 7 | 21:00
11 | Bakerganj | 9.8 | 20:00 | 77 | Juldah | 13 | 19:30 | 143 | Patuakhali | 40.7 | 20:00
12 | Bakulia | 65 | 20:00 | 78 | KSRM | 12 | 19:00 | 144 | Payra | 28 | 19:00
13 | Banani | 34 | 13:00 | 79 | Kabirpur | 201 | 17:00 | 145 | Postogola | 39 | 00:00
14 | Bangabhaban | 4 | 13:00 | 80 | Kachua | 55 | 17:00 | 146 | Purbachal | 22 | 12:00
15 | Barapukuria | 60 | 08:00 | 81 | Kaliganj | 16 | 09:00 | 147 | Purbasadipur | 125 | 12:00
16 | Barguna | 14 | 18:30 | 82 | Kallyanpur | 87 | 12:00 | 148 | Rahanpur | 27 | 10:00
17 | Barishal | 70 | 13:00 | 83 | Kalurghat | 25 | 14:00 | 149 | Rahim | 41 | 01:00
18 | Barishal-230 | 66 | 13:00 | 84 | Kamrangirchar | 65 | 00:00 | 150 | Rajbari | 55 | 04:00
19 | Baroaulia | 52 | 15:00 | 85 | Kaptai | N/A | N/A | 151 | Rajendrapur | 116 | 12:00
20 | Baroirhat | 48 | 13:00 | 86 | Kasba | 31 | 13:00 | 152 | Rajshahi | 83 | 04:00
21 | Bashundhara | 157 | 12:00 | 87 | Kazla | 86 | 12:00 | 153 | Rajshahi-230 | 49 | 05:00
22 | BashundharaCement | 7 | 00:00 | 88 | Keranigonj | 63 | 13:00 | 154 | Ramganj | 76 | 04:00
23 | Beanibazar | 46 | 13:00 | 89 | Khagrachori | 26 | 18:30 | 155 | Rampur | 30 | 00:00
24 | Benapole | 48 | 13:00 | 90 | Khulna | 33 | 18:00 | 156 | Rangamati | 14 | 18:30
25 | Bhaluka | 119 | 12:00 | 91 | Khulshi | 142 | 16:00 | 157 | Rangpur | 116 | 17:00
26 | Bhandaria | 38 | 21:00 | 92 | Kishoreganj | 109 | 13:00 | 158 | Ruppur | 3 | 11:00
27 | Bhangura | 33 | 13:00 | 93 | Kodda | 220 | 17:00 | 159 | SSM | 0 | 00:00
28 | Bheramara(GK) | 39 | 13:00 | 94 | Kulaura | 30 | 13:00 | 160 | Saidpur | 88 | 11:00
29 | Bhulta | 196 | 03:00 | 95 | Kurigram | 65 | 17:00 | 161 | Satkhira | 107 | 18:00
30 | Bog-Sherpur | 60 | 04:00 | 96 | Kushtia | 106 | 19:30 | 162 | Satmasjid | 76 | 13:00
31 | Bogura | 111 | 18:00 | 97 | Laksam | 24 | 12:00 | 163 | Savar | 154 | 15:00
32 | Borhanuddin | 65 | 20:00 | 98 | Lakshmipur | 27 | 13:00 | 164 | SevenRings | 17.19 | 01:00
33 | Brahmanbaria | 96 | 21:00 | 99 | Lalbag | 60 | 00:00 | 165 | ShahCement | 35 | 15:00
34 | Cantonment | 72 | 13:00 | 100 | Lalmonirhat | 48 | 17:00 | 166 | Shahjadpur | 45 | 17:00
35 | Chandina | 27 | 04:00 | 101 | MI_Cement | 16.1 | 06:00 | 167 | Shahjibazar | 97 | 21:00
36 | Chandpur | 68 | 13:00 | 102 | Madanganj | 34 | 12:00 | 168 | Shahmirpur | 33 | 18:30
37 | Chandraghona | 28 | 18:00 | 103 | Madaripur | 83 | 13:00 | 169 | Shariatpur | 66 | 13:00
38 | Chapai | 59 | 12:00 | 104 | Madartek | 62 | 13:00 | 170 | Sherpur | 146 | 19:00
39 | Charsaidpur | 44 | 01:00 | 105 | Madunaghat | 42 | 13:00 | 171 | Shikalbaha | 19.5 | 12:00
40 | Chauddagram | 66 | 13:00 | 106 | Magura | 45 | 19:00 | 172 | Shitalakhya | 51.3 | 11:00
41 | Chhatak | 27 | 13:00 | 107 | Mahasthangarh | 56 | 03:00 | 173 | Sholosohor | 33 | 12:00
42 | Chowmuhani | 91 | 18:00 | 108 | Maijdee | 34 | 19:00 | 174 | Shyampur | 136 | 15:00
43 | Chuadanga | 79 | 03:00 | 109 | Manikganj | 90 | 22:00 | 175 | Siddhirganj | 100 | 13:00
44 | Coxsbazar | 115 | 13:00 | 110 | Maniknagar | 45 | 13:00 | 176 | Sirajganj | 86 | 04:00
45 | Cumilla(N) | 90 | 16:00 | 111 | Matarbari | 38 | 13:00 | 177 | Sonargaon | 131 | 02:00
46 | Cumilla(S) | 125 | 13:00 | 112 | Matuail | 50 | 00:00 | 178 | Sreemongol | 52 | 21:00
47 | Daganbhuiyan | 28 | 13:00 | 113 | Metrorail_Motijheel | 14 | 18:00 | 179 | Sreepur | 89 | 12:00
48 | Daudkandi | 106 | 12:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Srinagar | 38.78 | 13:00
49 | DhakaUniversity | 44 | 12:00 | 115 | Millgate | 68 | 11:00 | 181 | Sunamganj | 41 | 21:00
50 | Dhamrai | 106 | 04:00 | 116 | Mirpur | 117 | 13:00 | 182 | Sylhet | 42 | 13:00
51 | Dhanmondi | 78 | 16:00 | 117 | Mirsorai | 9 | 09:00 | 183 | Sylhet-132 | 69 | 21:00
52 | Dohazari | 72 | 20:00 | 118 | Mirzapur | 40 | 19:00 | 184 | TK | 14 | 00:00
53 | Faridpur | 108 | 21:00 | 119 | Mithapukur | 56 | 17:00 | 185 | Tangail | 144 | 13:00
54 | Fatullah | 82 | 10:00 | 120 | Modern | N/A | N/A | 186 | Taraganj | 20 | 17:00
55 | Fenchuganj | 26 | 13:00 | 121 | Mogbazar | 59.8 | 13:00 | 187 | Tasnim | 13 | 11:00
56 | Feni | 68 | 14:00 | 122 | Mongla | 42 | 00:00 | 188 | Thakurgaon | 76 | 12:00
57 | GPH | 76 | 20:00 | 123 | Motijheel | 34 | 13:00 | 189 | Tongi | 113 | 15:00
58 | Ghatail | 76 | 13:00 | 124 | Muktagacha | 36 | 13:00 | 190 | Ullahpara | 27 | 19:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 85 | 13:00 | 191 | Ullon | 54 | 12:00
60 | Ghorashal-230 | 91 | 00:00 | 126 | Muradnagar | 27 | 13:00 | 192 | Uttara | 61 | 19:00
61 | Goalpara | 27 | 18:00 | 127 | Mymensingh | 180 | 18:00 | 193 | UttaraNew | 32 | 13:00
62 | Gollamari | 76 | 19:00 | 128 | Naogaon | 109 | 09:00 | 194 | Zigatola | 60 | 13:00
63 | Gopalganj | 81 | 19:30 | 129 | Narail | 42 | 18:00
64 | Gulshan | 66 | 19:00 | 130 | Narinda | 42 | 12:00
65 | Halishahar | 59 | 19:00 | 131 | Narshingdi | 139 | 19:30
66 | HaripurSBU | 116 | 02:00 | 132 | Natore | 101 | 18:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 20-02-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 10240.39 | 0 |  | 10240.39
1:00 | 9742.79 | 0 |  | 9742.79
2:00 | 9418.08 | 0 |  | 9418.08
3:00 | 9723.88 | 0 |  | 9723.88
4:00 | 10667.85 | 0 |  | 10667.85
5:00 | 9616.24 | 0 |  | 9616.24
6:00 | 8588.31 | 0 |  | 8588.31
7:00 | 8415.4 | 0 |  | 8415.4
8:00 | 8814.7 | 0 |  | 8814.7
9:00 | 9421.71 | 0 |  | 9421.71
10:00 | 9806.52 | 0 |  | 9806.52
11:00 | 10197.62 | 0 |  | 10197.62
12:00 | 10881.4 | 0 |  | 10881.4
13:00 | 11500.39 | 52 |  | 11554.39
14:00 | 10207.47 | 30 |  | 10238.47
15:00 | 10451.25 | 30 |  | 10482.25
16:00 | 10813.24 | 20 |  | 10834.24
17:00 | 11108.89 | 29 |  | 11138.89
18:00 | 10473 | 0 |  | 10473
19:00 | 11037.5 | 0 |  | 11037.5
19:30 | 11217.5 | 0 |  | 11217.5
20:00 | 11182.5 | 0 |  | 11182.5
21:00 | 11264.5 | 0 |  | 11264.5
22:00 | 11140.5 | 0 |  | 11140.5
23:00 | 10467.5 | 0 |  | 10467.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 20-02-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5475 | 4765.39 | 10240.39 | DAILY GENERATION CURVE
00:30 | 5354 | 4637.59 | 9991.59
01:00 | 5233 | 4509.79 | 9742.79 | 20-02-2026
01:30 | 5176.5 | 4403.935 | 9580.435
02:00 | 5120 | 4298.08 | 9418.08
02:30 | 5242 | 4328.98 | 9570.98
03:00 | 5364 | 4359.88 | 9723.88
03:30 | 5645.5 | 4550.365 | 10195.865
04:00 | 5927 | 4740.85 | 10667.85
04:30 | 5582.5 | 4559.545 | 10142.045
05:00 | 5238 | 4378.24 | 9616.24
05:30 | 4840.5 | 4261.775 | 9102.275
06:00 | 4443 | 4145.31 | 8588.31
06:30 | 4404.13 | 4097.725 | 8501.855
07:00 | 4365.26 | 4050.14 | 8415.4
07:30 | 4556.635 | 4058.415 | 8615.05
08:00 | 4748.01 | 4066.69 | 8814.7
08:30 | 4869.095 | 4249.11 | 9118.205
09:00 | 4990.18 | 4431.53 | 9421.71
09:30 | 5008.06 | 4606.055 | 9614.115
10:00 | 5025.94 | 4780.58 | 9806.52
10:30 | 5155.75 | 4846.32 | 10002.07
11:00 | 5285.56 | 4912.06 | 10197.62
11:30 | 5391.665 | 5147.845 | 10539.51
12:00 | 5497.77 | 5383.63 | 10881.4
12:30 | 5556.585 | 5634.31 | 11190.895
13:00 | 5615.4 | 5884.99 | 11500.39
13:30 | 5308.61 | 5545.32 | 10853.93
14:00 | 5001.82 | 5205.65 | 10207.47
14:30 | 5149.355 | 5180.005 | 10329.36
15:00 | 5296.89 | 5154.36 | 10451.25
15:30 | 5534.6 | 5097.645 | 10632.245
16:00 | 5772.31 | 5040.93 | 10813.24
16:30 | 5839.78 | 5121.285 | 10961.065
17:00 | 5907.25 | 5201.64 | 11108.89
17:30 | 5633.125 | 5157.82 | 10790.945
18:00 | 5359 | 5114 | 10473
18:30 | 5558.25 | 5197 | 10755.25
19:00 | 5757.5 | 5280 | 11037.5
19:30 | 5936.5 | 5281 | 11217.5
20:00 | 5950.5 | 5232 | 11182.5
20:30 | 6040.5 | 5183 | 11223.5 |  | Executive Engineer
21:00 | 6130.5 | 5134 | 11264.5 |  | Network Operation Division
21:30 | 6093 | 5109.5 | 11202.5
22:00 | 6055.5 | 5085 | 11140.5
22:30 | 5869 | 4935 | 10804
23:00 | 5682.5 | 4785 | 10467.5

## En-Curve
QF-LDC-12
Date | 20-02-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3057 | 1538 | 900 | 0 | 90 | 908.39 | 75 | 3534 | 0 | 17 | 121 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3020.5 | 1459 | 900 | 0 | 90 | 863.59 | 75 | 3452 | 0 | 17 | 114.5 | 0 | 0 | 0 | 0 | 20-02-2026
01:00 | 2984 | 1380 | 900 | 0 | 90 | 818.79 | 75 | 3370 | 0 | 17 | 108 | 0 | 0 | 0 | 0
01:30 | 2920.5 | 1354.5 | 900 | 0 | 92 | 819.435 | 75 | 3295 | 0 | 17 | 107 | 0 | 0 | 0 | 0 | Energy Generated | 249.8072 |  | MKWHr
02:00 | 2857 | 1329 | 900 | 0 | 94 | 820.08 | 75 | 3220 | 0 | 17 | 106 | 0 | 0 | 0 | 0 | Energy not Served | 0.161 |  | MKWHr
02:30 | 2944.5 | 1386 | 899.5 | 0 | 88 | 822.48 | 75 | 3220 | 0 | 27.5 | 107 | 0 | 0 | 1 | 0 | Total Energy Requirement | 249.9682 |  | MKWHr
03:00 | 3032 | 1443 | 899 | 0 | 82 | 824.88 | 75 | 3220 | 0 | 38 | 108 | 0 | 0 | 2 | 0
03:30 | 3165.5 | 1552.5 | 899 | 0 | 87 | 873.865 | 75 | 3336.5 | 0 | 48 | 157.5 | 0 | 0 | 1 | 0
04:00 | 3299 | 1662 | 899 | 0 | 92 | 922.85 | 75 | 3453 | 0 | 58 | 207 | 0 | 0 | 0 | 0
04:30 | 3157 | 1581.5 | 899 | 0 | 90 | 876.045 | 75 | 3258.5 | 0 | 29 | 175.5 | 0 | 0 | 0.5 | 0
05:00 | 3015 | 1501 | 899 | 0 | 88 | 829.24 | 75 | 3064 | 0 | 0 | 144 | 0 | 0 | 1 | 0
05:30 | 2749 | 1405.5 | 899 | 0 | 85 | 826.775 | 75 | 2955.5 | 0 | 0 | 106 | 0 | 0 | 0.5 | 0
06:00 | 2483 | 1310 | 899 | 0 | 82 | 824.31 | 75 | 2847 | 0 | 0 | 68 | 0 | 0 | 0 | 0
06:30 | 2484.5 | 1241 | 899.5 | 0 | 80 | 824.805 | 75 | 2815 | 14.05 | 0 | 68 | 0 | 0 | 0 | 0
07:00 | 2486 | 1172 | 900 | 0 | 78 | 825.3 | 75 | 2783 | 28.1 | 0 | 68 | 0 | 0 | 0 | 0
07:30 | 2531.5 | 1318 | 829 | 0 | 81 | 825.76 | 75 | 2797 | 88.79 | 0 | 68 | 0 | 0 | 1 | 0
08:00 | 2577 | 1464 | 758 | 0 | 84 | 826.22 | 75 | 2811 | 149.48 | 0 | 68 | 0 | 0 | 2 | 0
08:30 | 2698.5 | 1509 | 757.5 | 0 | 87 | 825.65 | 75 | 2833 | 261.055 | 0 | 68 | 0 | 0 | 3.5 | 0
09:00 | 2820 | 1554 | 757 | 0 | 90 | 825.08 | 75 | 2855 | 372.63 | 0 | 68 | 0 | 0 | 5 | 0
09:30 | 2896 | 1553 | 828 | 0 | 95 | 827.04 | 75 | 2824 | 431.575 | 8.5 | 73.5 | 0 | 0 | 2.5 | 0
10:00 | 2972 | 1552 | 899 | 0 | 100 | 829 | 75 | 2793 | 490.52 | 17 | 79 | 0 | 0 | 0 | 0
10:30 | 3046 | 1676 | 899 | 0 | 106 | 827.5 | 75 | 2739 | 526.07 | 26 | 81.5 | 0 | 0 | 0 | 0
11:00 | 3120 | 1800 | 899 | 0 | 112 | 826 | 75 | 2685 | 561.62 | 35 | 84 | 0 | 0 | 0 | 0
11:30 | 3084.5 | 1815 | 899 | 0 | 118 | 942.5 | 75 | 2854 | 589.01 | 52.5 | 108.5 | 0 | 0 | 1.5 | 0
12:00 | 3049 | 1830 | 899 | 0 | 124 | 1059 | 75 | 3023 | 616.4 | 70 | 133 | 0 | 0 | 3 | 0
12:30 | 2990.5 | 1809 | 898.5 | 0 | 128 | 1114 | 75 | 3281.5 | 625.395 | 88 | 178 | 0 | 0 | 3 | 26
13:00 | 2932 | 1788 | 898 | 0 | 132 | 1169 | 75 | 3540 | 634.39 | 106 | 223 | 0 | 0 | 3 | 52
13:30 | 2871.5 | 1561 | 898.5 | 0 | 123 | 1071.5 | 75 | 3398 | 583.93 | 107 | 162 | 0 | 0 | 2.5 | 41
14:00 | 2811 | 1334 | 899 | 0 | 114 | 974 | 75 | 3256 | 533.47 | 108 | 101 | 0 | 0 | 2 | 30
14:30 | 2831.5 | 1490.5 | 898.5 | 0 | 115 | 985 | 75 | 3234 | 484.36 | 113 | 101 | 0 | 0 | 1.5 | 30
15:00 | 2852 | 1647 | 898 | 0 | 116 | 996 | 75 | 3212 | 435.25 | 118 | 101 | 0 | 0 | 1 | 30
15:30 | 2982 | 1760.5 | 898 | 0 | 116 | 958 | 75 | 3258 | 338.745 | 123.5 | 122 | 0 | 0 | 0.5 | 25
16:00 | 3112 | 1874 | 898 | 0 | 116 | 920 | 75 | 3304 | 242.24 | 129 | 143 | 0 | 0 | 0 | 20
16:30 | 3105.5 | 1887.5 | 898 | 0 | 118 | 969 | 75 | 3440.5 | 161.065 | 129 | 177.5 | 0 | 0 | 0 | 24.5
17:00 | 3099 | 1901 | 898 | 0 | 120 | 1018 | 75 | 3577 | 79.89 | 129 | 212 | 0 | 0 | 0 | 29
17:30 | 2764 | 1719 | 898 | 0 | 110 | 1068.5 | 75 | 3674 | 39.945 | 162 | 279 | 0 | 0 | 1.5 | 14.5
18:00 | 2429 | 1537 | 898 | 0 | 100 | 1119 | 75 | 3771 | 0 | 195 | 346 | 0 | 0 | 3 | 0
18:30 | 2746.5 | 1605.75 | 898.5 | 0 | 105 | 1098 | 75 | 3763.5 | 0 | 145 | 316.5 | 0 | 0 | 1.5 | 0
19:00 | 3064 | 1674.5 | 899 | 0 | 110 | 1077 | 75 | 3756 | 0 | 95 | 287 | 0 | 0 | 0 | 0
19:30 | 3071 | 1912.5 | 899 | 0 | 110 | 1084 | 75 | 3802 | 0 | 60 | 202 | 0 | 0 | 2 | 0
20:00 | 3128 | 1943.5 | 899 | 0 | 110 | 1018 | 75 | 3737 | 0 | 60 | 211 | 0 | 0 | 1 | 0
20:30 | 3174 | 1984 | 899 | 0 | 112 | 974 | 75 | 3765 | 0 | 38.5 | 201.5 | 0 | 0 | 0.5 | 0
21:00 | 3220 | 2024.5 | 899 | 0 | 114 | 930 | 75 | 3793 | 0 | 17 | 192 | 0 | 0 | 0 | 0
21:30 | 3194 | 2016 | 899 | 0 | 116 | 912.5 | 75 | 3783.5 | 0 | 17 | 189 | 0 | 0 | 0.5 | 0
22:00 | 3168 | 2007.5 | 899 | 0 | 118 | 895 | 75 | 3774 | 0 | 17 | 186 | 0 | 0 | 1 | 0
22:30 | 3088.5 | 1975.5 | 898.5 | 0 | 111 | 860.5 | 75 | 3624.5 | 0 | 17 | 151.5 | 0 | 0 | 2 | 0
23:00 | 3009 | 1943.5 | 898 | 0 | 104 | 826 | 75 | 3475 | 0 | 17 | 117 | 0 | 0 | 3 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 20-02-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 409 | 06:00 | 396 | 11:00 | Madunaghat | 412 | 06:00 | 406 | 00:00
Amtali | 422 | 06:00 | 414 | 13:00 | Meghnaghat | 407 | 07:00 | 400 | 13:00
Ashuganj | 417 | 06:00 | 406 | 13:00 | Payra | 422 | 05:00 | 417 | 12:00
Bhulta | 413 | 18:00 | 399 | 12:00 | Rahanpur | 421 | 00:00 | 408 | 13:00
Bibiana | 417 | 05:00 | 411 | 12:00 | Rampal | 417 | 06:00 | 405 | 13:00
BIPTC | 401 | 01:00 | 391 | 10:00
Bogura | 415 | 06:00 | 401 | 17:00
Gopalganj | 417 | 06:00 | 406 | 13:00
Kaliakoir | 402 | 05:00 | 392 | 12:00
Korerhat | 416 | 06:00 | 408 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 239 | 06:00 | 231 | 12:00 | Jhenaidah | 242 | 06:00 | 230 | 13:00
AKSML | 238.9 | 06:00 | 231 | 17:00 | Kachua | 237 | 04:00 | 231 | 17:00
Aminbazar | 239 | 06:00 | 232 | 00:00 | Kaliakoir | 240 | 05:00 | 233 | 12:00
Ashuganj | 239 | 03:00 | 232 | 13:00 | Keranigonj | 238 | 06:00 | 229 | 13:00
Ashuganj-400 | 239 | 03:00 | 232 | 13:00 | Khulna(S) | 245 | 06:00 | 232 | 13:00
Baghabari | 241 | 00:00 | 233 | 12:00 | Korerhat | 238 | 08:00 | 230 | 12:00
Barapukuria | 227 | 06:00 | 216 | 09:00 | Madunaghat | 236 | 06:00 | 232 | 12:00
Barapukuria-230 | 227 | 06:00 | 216 | 09:00 | Madunaghat-400 | 236 | 06:00 | 231 | 00:00
Barishal | 236 | 06:00 | 231 | 13:00 | Maniknagar | 239 | 06:00 | 231 | 12:00
Bheramara | 240 | 06:00 | 231 | 13:00 | Meghnaghat | 245 | 05:00 | 241 | 00:00
Bhulta | 240 | 18:00 | 231 | 12:00 | Meghnaghat-400 | 241 | 05:00 | 233 | 12:00
Bibiana | 242 | 06:00 | 236 | 13:00 | Mirsorai | 237 | 06:00 | 231 | 13:00
BIPTC | 243 | 06:00 | 231 | 13:00 | Rajshahi | 240 | 06:00 | 230 | 13:00
Bogura | 242 | 06:00 | 233 | 10:00 | Rampal | 241 | 02:00 | 230 | 13:00
Bogura-400 | 241 | 06:00 | 232 | 17:00 | Rampur | N/A | N/A | N/A | N/A
Borhanuddin | 239 | 06:00 | 235 | 18:30 | Rampura | 238 | 05:00 | 230 | 12:00
BSRM | 237 | 06:00 | 231 | 17:00 | Shikalbaha | 234 | 05:00 | 229 | 12:00
Chowmuhani | N/A | N/A | N/A | N/A | Shyampur | 239 | 06:00 | 232 | 12:00
Cumilla(N) | 238 | 06:00 | 232 | 12:00 | Siddhirganj | 240 | 18:00 | 232 | 13:00
Faridpur | 236 | 06:00 | 228 | 12:00 | Sirajgonj | 244 | 02:00 | 240 | 09:00
Fenchuganj | 243 | 00:00 | 240 | 01:00 | Sreepur | 235 | 18:00 | 229 | 10:00
Feni | 239 | 06:00 | 233 | 13:00 | Tongi | 236 | 04:00 | 231 | 11:00
Ghorashal | 240 | 04:00 | 235 | 00:00
Ghorashal-230 | 237 | 06:00 | 229 | 12:00
Gopalganj | 234 | 06:00 | 227 | 13:00
GPH | 237 | 06:00 | 23 | 18:00
Haripur | 240 | 06:00 | 233 | 12:00
Hasnabad | 238 | 04:00 | 233 | 13:00
Hathazari | 236 | 06:00 | 228 | 18:30
Ishurdi | 243 | 06:00 | 233 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 05:00 | 133 | 13:00 | Magura | 140 | 06:00 | 131 | 13:00
Agargaon | 135 | 06:00 | 128 | 12:00 | Mahasthangarh | 138 | 06:00 | 130 | 17:00
Agrabad | 135 | 01:00 | 132 | 12:00 | Maijdee | 134 | 06:00 | 130 | 12:00
AKS | 133 | 05:00 | 131 | 00:00 | Manikganj | 130 | 05:00 | 125 | 16:00
Aminbazar | 140 | 06:00 | 134 | 11:00 | Maniknagar | 134 | 05:00 | 130 | 00:00
Amnura | 139 | 00:00 | 133 | 13:00 | Matarbari | 129 | 09:00 | 120 | 13:00
Ashuganj | 140 | 05:00 | 136 | 13:00 | Matuail | 138 | 18:00 | 133 | 12:00
Bagerhat | 137 | 05:00 | 129 | 17:00 | Metrorail_Motijheel | 134 | 04:00 | 130 | 00:00
Bajitpur | 135 | 06:00 | 126 | 13:00 | Metrorail_Uttara | 134 | 06:00 | 128 | 13:00
Bakerganj | 138 | 02:00 | 135 | 17:00 | Millgate | 134 | 06:00 | 127 | 12:00
Bakulia | 137 | 06:00 | 132 | 13:00 | Mirpur | 138 | 05:00 | 133 | 12:00
Banani | 139 | 06:00 | 133 | 12:00 | Mirzapur | 135 | 04:00 | 129 | 17:00
Bangabhaban | 135 | 03:00 | 129 | 12:00 | Mithapukur | 136 | 01:00 | 128 | 09:00
Barapukuria | 139 | 05:00 | 130 | 09:00 | MI_Cement | 136.8 | 06:00 | 132 | 17:00
Barguna | 139 | 06:00 | 135 | 17:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 139 | 07:00 | 133 | 13:00 | Mogbazar | 140 | 06:00 | 134 | 12:00
Barishal-230 | 138 | 06:00 | 133 | 13:00 | Mongla | 137 | 06:00 | 129 | 13:00
Baroaulia | 136 | 07:00 | 134 | 00:00 | Motijheel | 135 | 03:00 | 129 | 12:00
Baroirhat | 136 | 02:00 | 133 | 00:00 | Muktagacha | 132 | 04:00 | 117 | 17:00
Bashundhara | 139 | 06:00 | 132 | 12:00 | Munshiganj | 135 | 05:00 | 130 | 12:00
BashundharaCement | 136 | 18:30 | 133 | 00:00 | Muradnagar | 136 | 06:00 | 131 | 13:00
Beanibazar | 133 | 05:00 | 130 | 12:00 | Mymensingh | 127 | 05:00 | 115 | 13:00
Benapole | 138 | 06:00 | 123 | 13:00 | Naogaon | 135 | 00:00 | 128 | 09:00
Bhaluka | 133 | 18:30 | 124 | 13:00 | Narail | 140 | 06:00 | 131 | 18:00
Bhandaria | 137 | 06:00 | 130 | 14:00 | Narinda | 134 | 05:00 | 130 | 00:00
Bhangura | 139 | 02:00 | 133 | 13:00 | Narshingdi | 135 | 18:00 | 129 | 17:00
Bheramara | 140 | 02:00 | 136 | 12:00 | Natore | 139 | 06:00 | 133 | 17:00
Bheramara(GK) | 140 | 02:00 | 136 | 11:00 | Nawabganj | 138 | 06:00 | 133 | 12:00
Bhulta | 130 | 18:00 | 126 | 00:00 | Netrakona | 126 | 01:00 | 112 | 17:00
Bog-Sherpur | 139 | 06:00 | 133 | 10:00 | New | 135 | 06:00 | 128 | 12:00
Bogura | 139 | 01:00 | 133 | 10:00 | Niamatpur | 140 | 00:00 | 135 | 12:00
Bogura-230 | 140 | 02:00 | 134 | 10:00 | Noapara | 139 | 02:00 | 130 | 13:00
Brahmanbaria | 135 | 06:00 | 130 | 13:00 | Pabna | 140 | 06:00 | 135 | 12:00
Cantonment | 135 | 06:00 | 127 | 13:00 | Palashbari | 134 | 06:00 | 126 | 09:00
Chandina | 138 | 06:00 | 134 | 12:00 | Panchagarh | 138 | 06:00 | 127 | 10:00
Chandpur | 134 | 03:00 | 131 | 13:00 | Patiya | 136 | 06:00 | 131 | 18:30
Chandraghona | 138 | 07:00 | 135 | 12:00 | Patuakhali | 138 | 05:00 | 134 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 140 | 01:00 | 0.14 | 00:00 | Payra | 139 | 05:00 | 137 | 00:00
Charsaidpur | 136 | 06:00 | 131 | 17:00 | PHP | 136 | 08:00 | 131 | 13:00
Chauddagram | 136 | 07:00 | 131 | 13:00 | Postogola | 138 | 06:00 | 133 | 12:00
Chhatak | 132 | 04:00 | 128 | 13:00 | Purbachal | 138 | 04:00 | 133 | 12:00
Chowmuhani | 132 | 22:00 | 129 | 00:00 | Purbasadipur | 133 | 01:00 | 122 | 09:00
Chuadanga | 141 | 06:00 | 130 | 17:00 | Rahanpur | 141 | 00:00 | 136 | 12:00
Coxsbazar | 127 | 09:00 | 121 | 13:00 | Rahanpur-400 | 142 | 00:00 | 137 | 10:00
Cumilla(N) | 139 | 06:00 | 134 | 12:00 | Rahim | 136 | 05:00 | 132 | 12:00
Cumilla(S) | 137 | 04:00 | 123 | 11:00 | Rajbari | 136 | 06:00 | 130 | 13:00
Daganbhuiyan | 134 | 06:00 | 130 | 13:00 | Rajendrapur | 132 | 06:00 | 124 | 13:00
Daudkandi | 134 | 18:00 | 128 | 12:00 | Rajshahi | 139 | 06:00 | 133 | 12:00
DhakaUniversity | 139 | 05:00 | 133 | 17:00 | Rajshahi-230 | 139 | 06:00 | 132 | 13:00
Dhamrai | 137 | 00:00 | 133 | 12:00 | Ramganj | 133 | 06:00 | 129 | 12:00
Dhanmondi | 139 | 06:00 | 133.5 | 12:00 | Rampur | 136 | 06:00 | 131 | 12:00
Dohazari | 134 | 05:00 | 128 | 13:00 | Rampura | 138 | 05:00 | 133 | 12:00
Faridpur | 136 | 06:00 | 131 | 13:00 | Rangamati | 137 | 06:00 | 134 | 01:00
Fatullah | 138 | 04:00 | 133 | 00:00 | Rangpur | 137 | 06:00 | 128 | 09:00
Fenchuganj | 137 | 00:00 | 135 | 15:00 | Ruppur | 140 | 06:00 | 136 | 17:00
Feni | 134 | 07:00 | 130 | 00:00 | Saidpur | 136 | 06:00 | 126 | 10:00
Feni-230 | 135 | 06:00 | 130 | 13:00 | Satkhira | 139 | 06:00 | 128 | 13:00
Ghatail | 129 | 18:00 | 118 | 17:00 | Satmasjid | 134 | 05:00 | 128 | 12:00
Ghorashal | 142 | 04:00 | 137 | 14:00 | Savar | 139 | 18:00 | 132 | 12:00
Goalpara | 142 | 06:00 | 132 | 13:00 | SevenRings | 142 | 05:00 | 138 | 12:00
Gollamari | 141 | 06:00 | 133 | 13:00 | ShahCement | 136 | 06:00 | 131 | 17:00
Gopalganj | 140 | 06:00 | 132 | 13:00 | Shahjadpur | 142 | 01:00 | 136 | 10:00
Gopalganj-400 | 140 | 06:00 | 135 | 13:00 | Shahjibazar | 134 | 06:00 | 130 | 14:00
Gulshan | 138 | 06:00 | 133 | 12:00 | Shahmirpur | 136 | 06:00 | 132 | 21:00
Halishahar | 137 | 06:00 | 133 | 12:00 | Shariatpur | 139 | 06:00 | 132 | 13:00
Haripur | 137 | 06:00 | 133 | 12:00 | Sherpur | 124 | 18:30 | 110 | 17:00
HaripurSBU | 137 | 18:00 | 132 | 17:00 | Shikalbaha | 126 | 09:00 | 122 | 12:00
Hasnabad | 138 | 05:00 | 132 | 12:00 | Shikalbaha-230 | 137 | 06:00 | 133 | 12:00
Hathazari | 138 | 06:00 | 134 | 17:00 | Shitalakhya | 136.8 | 06:00 | 132 | 11:00
Hatirjheel | 138 | 06:00 | 134 | 12:00 | Sholosohor | 137 | 05:00 | 134 | 13:00
Ishurdi | 142 | 02:00 | 138 | 12:00 | Shyampur | 137 | 18:00 | 133 | 12:00
Jaldhaka | 133 | 05:00 | 124 | 09:00 | Shyampur-230 | 139 | 06:00 | 134 | 12:00
Jamalpur | 128 | 05:00 | 113 | 15:00 | Siddhirganj | 137 | 05:00 | 133 | 12:00
Jashore | 139 | 06:00 | 125 | 13:00 | Sirajganj | 137 | 05:00 | 132 | 17:00
Jhenaidah | 141 | 06:00 | 122 | 13:00 | Sonargaon | 133 | 04:00 | 128 | 02:00
Jhenaidah-230 | 141 | 06:00 | 133 | 13:00 | Sreemongol | 134 | 05:00 | 131 | 17:00
Joydebpur | 141 | 06:00 | 135 | 15:00 | Sreepur | 134 | 02:00 | 130 | 10:00
Joypurhat | 134 | 05:00 | 124 | 10:00 | Srinagar | 139 | 06:00 | 133 | 12:00
Juldah | 135 | 05:00 | 132 | 19:30 | SSM | 140 | 00:00 | 138 | 18:00
Kabirpur | 140 | 18:00 | 127 | 12:00 | Sunamganj | 131 | 06:00 | 126 | 12:00
Kachua | 136 | 07:00 | 132 | 17:00 | Sylhet | 134 | 06:00 | 131 | 13:00
Kaliakoir | 142 | 18:00 | 134 | 12:00 | Sylhet-132 | 134 | 06:00 | 131 | 12:00
Kaliganj | 141 | 03:00 | 133 | 13:00 | Tangail | 130 | 18:30 | 121 | 17:00
Kallyanpur | 140 | 18:00 | 134 | 12:00 | Taraganj | 135 | 04:00 | 126 | 17:00
Kalurghat | 137 | 06:00 | 134 | 17:00 | Tasnim | 135 | 06:00 | 131 | 16:00
Kamrangirchar | 138 | 06:00 | 132 | 12:00 | Thakurgaon | 137 | 06:00 | 126 | 10:00
Kaptai | N/A | N/A | N/A | N/A | TK | 137 | 03:00 | 135 | 10:00
Kasba | 136 | 06:00 | 130 | 13:00 | Tongi | 136 | 04:00 | 131 | 11:00
Kazla | 134 | 06:00 | 129 | 13:00 | Ullahpara | 138 | 01:00 | 133 | 17:00
Keranigonj | 139 | 06:00 | 134 | 12:00 | Ullon | 138 | 06:00 | 133 | 12:00
Khagrachori | 136 | 06:00 | 133 | 17:00 | Uttara | 134 | 06:00 | 128 | 12:00
Khulna | 141 | 06:00 | 132 | 17:00 | UttaraNew | 134 | 06:00 | 128 | 13:00
Khulna(S) | 142 | 06:00 | 133 | 13:00 | Zigatola | 139 | 07:00 | 132 | 00:00
Khulshi | 135 | 06:00 | 131 | 18:30
Kishoreganj | 134 | 06:00 | 124 | 13:00
Kodda | 139 | 18:00 | 129 | 12:00
Korerhat | 138 | 01:00 | 133 | 12:00
KSRM | 137 | 05:00 | 133 | 17:00
Kulaura | 137 | 04:00 | 134 | 15:00
Kurigram | 134 | 03:00 | 120 | 09:00
Kushtia | 137 | 06:00 | 129 | 13:00
Laksam | 135 | 03:00 | 130 | 13:00
Lakshmipur | 133 | 06:00 | 129 | 13:00
Lalbag | 138 | 18:00 | 1.34 | 09:00
Lalmonirhat | 133 | 18:00 | 123 | 09:00
Madanganj | 136 | 18:30 | 133 | 00:00
Madaripur | 139 | 06:00 | 134 | 13:00
Madartek | 137 | 04:00 | 132 | 12:00
Madunaghat | 138 | 06:00 | 134 | 17:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 20-02-2026 | [28 empty] | Date: | 20-02-2026 | [28 empty] | Date: | 20-02-2026 | [28 empty] | Date: | 20-02-2026 | [28 empty] | Date: | 20-02-2026 | [17 empty] | Date: | 20-02-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [17 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 257 | 0 | 0 | 0 | 17 | 12 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 24 | 800 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 855 | 0 | 0 | 0 | 0 | 295 | 294 | 51 | 0 | 198 | 0 | 0 | 51 | 0 | 0 | 11 | 0 | 90 | 0 | 0 | 0 | 310 | 0 | 323 | 41 | 23 | 135 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 100 | 0 | 59 | 9 | 20 | 0 | 0 | 6 | 5475 | 900 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 808 | 0 | 0 | 0 | 908.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 130 | 180 | 0 | 0 | 800 | 0 | 4765.39 | 10240.39 | 93.21
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 243 | 0 | 0 | 0 | 17 | 12 | 22 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 31 | 800 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 295 | 295 | 5 | 0 | 200 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 90 | 0 | 0 | 0 | 305 | 0 | 337 | 41 | 23 | 137 | 0 | 17 | 0 | 5 | 7 | 0 | 0 | 100 | 0 | 59 | 9 | 20 | 0 | 0 | 6 | 5233 | 900 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 0 | 0 | 0 | 818.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 110 | 180 | 0 | 0 | 700 | 0 | 4509.79 | 9742.79 | 93.2
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 243 | 0 | 0 | 0 | 17 | 12 | 22 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 31 | 750 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 842 | 0 | 0 | 0 | 0 | 295 | 295 | 5 | 0 | 196 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 94 | 0 | 0 | 0 | 305 | 0 | 327 | 41 | 23 | 136 | 0 | 17 | 0 | 5 | 7 | 0 | 0 | 100 | 0 | 59 | 9 | 21 | 0 | 0 | 4 | 5120 | 900 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 0 | 0 | 0 | 820.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 100 | 180 | 0 | 0 | 600 | 0 | 4298.08 | 9418.08 | 93.19
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 0 | 34 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 243 | 0 | 0 | 0 | 35 | 12 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 38 | 750 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 0 | 0 | 850 | 0 | 0 | 0 | 0 | 300 | 305 | 10 | 0 | 201 | 0 | 0 | 106 | 0 | 0 | 11 | 0 | 82 | 0 | 0 | 0 | 300 | 0 | 341 | 41 | 23 | 138 | 0 | 17 | 0 | 60 | 7 | 0 | 0 | 100 | 0 | 59 | 9 | 21 | 0 | 0 | 6 | 5364 | 899 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 0 | 0 | 824.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 100 | 180 | 0 | 0 | 600 | 0 | 4359.88 | 9723.88 | 93.18
04:00 | 0 | 16 | 7 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 240 | 0 | 0 | 0 | 35 | 12 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 38 | 800 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 910 | 0 | 0 | 0 | 0 | 325 | 320 | 51 | 0 | 198 | 0 | 0 | 108 | 0 | 0 | 11 | 0 | 92 | 0 | 0 | 0 | 305 | 0 | 401 | 41 | 23 | 150 | 0 | 17 | 0 | 86 | 25 | 0 | 0 | 100 | 0 | 88 | 55 | 21 | 0 | 0 | 6 | 5927 | 899 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 0 | 0 | 0 | 922.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 130 | 220 | 0 | 0 | 680 | 0 | 4740.85 | 10667.85 | 93.17
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 236 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 39 | 750 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 735 | 0 | 0 | 0 | 0 | 285 | 280 | 10 | 0 | 193 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 88 | 0 | 0 | 0 | 305 | 0 | 337 | 41 | 23 | 150 | 0 | 17 | 0 | 5 | 25 | 0 | 0 | 100 | 0 | 88 | 56 | 22 | 0 | 0 | 0 | 5238 | 899 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 829.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 120 | 180 | 0 | 0 | 600 | 0 | 4378.24 | 9616.24 | 93.16
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 31 | 720 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 615 | 0 | 0 | 0 | 0 | 270 | 240 | 10 | 0 | 184 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 82 | 0 | 0 | 0 | 290 | 0 | 316 | 41 | 23 | 137 | 0 | 17 | 0 | 5 | 25 | 0 | 0 | 100 | 0 | 59 | 9 | 23 | 0 | 0 | 0 | 4443 | 899 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 824.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 560 | 0 | 4145.31 | 8588.31 | 93.15
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 12 | 22 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27 | 75 | 0 | 2 | 720 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 605 | 1 | 0 | 0 | 0 | 320 | 240 | 0 | 0 | 140 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 78 | 0 | 6 | 0 | 240 | 0 | 356 | 41 | 23 | 110 | 1 | 0 | 0 | 5 | 30 | 0 | 0 | 100 | 0 | 59 | 9 | 23 | 0 | 0.99 | 0 | 4365.26 | 900 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.76 | 766 | 0 | 0 | 0 | 825.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 3 | 0 | 0 | 2.76 | 130 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0.25 | 0 | 52 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 3 | 0.07 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 4050.14 | 8415.4 | 93.15
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 13 | 22 | 0 | 465 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0.82 | 75 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 611 | 6 | 0 | 0 | 0 | 310 | 309 | 0 | 0 | 140 | 0 | 0 | 50 | 0 | 0 | 10 | 0 | 84 | 0 | 24 | 0 | 285 | 0 | 340 | 42 | 23 | 139 | 3 | 0 | 0 | 5 | 7 | 0 | 0 | 100 | 0 | 59 | 9 | 23 | 0 | 16.19 | 0 | 4748.01 | 758 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.82 | 788 | 0 | 0 | 0 | 826.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.68 | 25 | 0 | 0 | 4.08 | 130 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0.44 | 0 | 52 | 0 | 8 | 0 | 0 | 0 | 0 | 1.4 | 13 | 0.05 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 4066.69 | 8814.7 | 93.15
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 13 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 1.98 | 75 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 610 | 11 | 0 | 0 | 0 | 330 | 305 | 0 | 0 | 197 | 0 | 0 | 50 | 0 | 0 | 10 | 0 | 90 | 0 | 40 | 0 | 295 | 0 | 363 | 41 | 23 | 144 | 6 | 0 | 0 | 5 | 7 | 0 | 0 | 100 | 0 | 59 | 9 | 23 | 1 | 15.2 | 0 | 4990.18 | 757 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.42 | 772 | 0 | 0 | 0 | 825.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.49 | 53 | 0 | 0 | 33.88 | 160 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 2.22 | 0 | 52 | 0 | 18 | 0 | 0 | 0 | 0 | 3.3 | 96 | 0.14 | 0 | 171 | 100 | 180 | 0 | 0 | 530 | 0 | 4431.53 | 9421.71 | 93.14
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 3 | 17 | 13 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.71 | 75 | 0 | 0 | 630 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 610 | 16 | 0 | 0 | 0 | 340 | 305 | 0 | 0 | 204 | 0 | 0 | 50 | 0 | 0 | 10 | 0 | 100 | 0 | 52 | 0 | 230 | 0 | 389 | 41 | 23 | 142 | 7 | 0 | 0 | 5 | 7 | 0 | 0 | 100 | 0 | 59 | 19 | 23 | 2 | 16.23 | 1 | 5025.94 | 899 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.61 | 769 | 0 | 0 | 0 | 829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.92 | 76 | 0 | 0 | 40.84 | 164 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.99 | 0 | 52 | 0 | 26 | 0 | 0 | 0 | 0 | 4.8 | 135 | 0.42 | 0 | 172 | 100 | 180 | 0 | 0 | 560 | 0 | 4780.58 | 9806.52 | 93.14
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455 | 0 | 0 | 0 | 0 | 0 | 25 | 35 | 20 | 21 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 75 | 0 | 10 | 440 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 678 | 19 | 0 | 0 | 0 | 335 | 350 | 1 | 0 | 203 | 0 | 0 | 98 | 0 | 0 | 10 | 0 | 112 | 0 | 25 | 0 | 325 | 0 | 389 | 42 | 23 | 152 | 10 | 0 | 0 | 86 | 30 | 0 | 0 | 100 | 0 | 59 | 19 | 23 | 1 | 40.86 | 6 | 5285.56 | 899 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.89 | 772 | 0 | 0 | 0 | 826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.58 | 93 | 0 | 0 | 23.1 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.39 | 0 | 52 | 0 | 30 | 0 | 0 | 0 | 0 | 5.6 | 156 | 0.5 | 0 | 173 | 127 | 220 | 0 | 0 | 570 | 0 | 4912.06 | 10197.62 | 93.13
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 445 | 0 | 0 | 0 | 0 | 0 | 29 | 70 | 20 | 21 | 0 | 500 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3.89 | 75 | 0 | 12 | 365 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 921 | 19 | 0 | 0 | 0 | 320 | 330 | 40 | 0 | 196 | 0 | 0 | 98 | 0 | 0 | 10 | 0 | 124 | 0 | 67 | 0 | 305 | 0 | 378 | 42 | 23 | 155 | 7 | 17 | 0 | 85 | 30 | 0 | 0 | 99 | 0 | 59 | 19 | 23 | 2.3 | 22.58 | 6 | 5497.77 | 899 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.81 | 786 | 0 | 0 | 0 | 1059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.42 | 97 | 0 | 0 | 29.97 | 175 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 2.81 | 0 | 51 | 30 | 32 | 19 | 0 | 0 | 0 | 6 | 168 | 0.62 | 0 | 200 | 127 | 220 | 0 | 0 | 700 | 0 | 5383.63 | 10881.4 | 93.13
13:00 | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 12 | 0 | 33 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 475 | 0 | 0 | 0 | 0 | 0 | 24 | 90 | 18 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 2.73 | 75 | 0 | 26 | 365 | 0 | 0 | 0 | 0 | 6 | 218 | 0 | 0 | 0 | 1064 | 18 | 0 | 8 | 0 | 290 | 295 | 51 | 0 | 189 | 10 | 1 | 99 | 3 | 0 | 10 | 0 | 132 | 0 | 66 | 0 | 305 | 0 | 361 | 41 | 23 | 152 | 8 | 17 | 0 | 85 | 30 | 0 | 0 | 99 | 0 | 59 | 19 | 20 | 2 | 19.67 | 6 | 5615.4 | 898 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.72 | 924 | 0 | 0 | 0 | 1169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.76 | 107 | 0 | 0 | 54.07 | 176 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 5.09 | 0 | 51 | 35 | 32 | 34 | 0 | 0 | 0 | 5.8 | 158 | 0.55 | 0 | 276 | 127 | 220 | 0 | 0 | 860 | 0 | 5884.99 | 11500.39 | 93.12
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 24 | 108 | 18 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1.81 | 75 | 0 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 965 | 16 | 0 | 0 | 0 | 325 | 320 | 0 | 0 | 210 | 10 | 0 | 51 | 0 | 0 | 11 | 0 | 114 | 0 | 55 | 0 | 290 | 0 | 361 | 42 | 23 | 134 | 8 | 0 | 0 | 0 | 20 | 0 | 0 | 98 | 0 | 59 | 19 | 22 | 1 | 27.01 | 6 | 5001.82 | 899 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.49 | 819 | 0 | 0 | 0 | 974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.18 | 85 | 0 | 0 | 32.14 | 160 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 2.68 | 0 | 52 | 0 | 28 | 0 | 0 | 0 | 0 | 4.7 | 135 | 0.46 | 0 | 185 | 100 | 180 | 0 | 0 | 850 | 0 | 5205.65 | 10207.47 | 93.12
15:00 | 0 | 30 | 2 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 0 | 0 | 0 | 0 | 0 | 19 | 70 | 15 | 14 | 0 | 533 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2.11 | 75 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 960 | 12 | 0 | 0 | 0 | 320 | 315 | 0 | 0 | 213 | 10 | 0 | 50 | 0 | 0 | 11 | 0 | 116 | 0 | 44 | 0 | 305 | 0 | 349 | 42 | 23 | 149 | 4 | 0 | 0 | 0 | 20 | 0 | 0 | 96 | 0 | 59 | 19 | 22 | 1 | 17.78 | 6 | 5296.89 | 898 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.73 | 785 | 0 | 0 | 0 | 996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.25 | 71 | 0 | 0 | 37.55 | 179 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 3.97 | 0 | 52 | 0 | 22 | 0 | 0 | 0 | 0 | 3.5 | 104 | 0.36 | 0 | 187 | 100 | 180 | 0 | 0 | 850 | 0 | 5154.36 | 10451.25 | 93.11
16:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 59 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 12 | 70 | 15 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.16 | 75 | 0 | 22 | 515 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 940 | 0 | 0 | 0 | 0 | 320 | 340 | 31 | 0 | 197 | 41 | 0 | 96 | 0 | 0 | 9 | 0 | 116 | 0 | 25 | 0 | 310 | 0 | 392 | 42 | 23 | 150 | 2 | 17 | 0 | 86 | 30 | 0 | 0 | 97 | 0 | 59 | 19 | 22 | 1 | 10.15 | 6 | 5772.31 | 898 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.29 | 767 | 0 | 0 | 0 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.3 | 43 | 0 | 0 | 20.31 | 179 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 1.63 | 0 | 53 | 0 | 11 | 0 | 0 | 0 | 0 | 2.2 | 57 | 0.2 | 0 | 179 | 125 | 220 | 0 | 0 | 850 | 0 | 5040.93 | 10813.24 | 93.11
17:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 71 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 495 | 0 | 0 | 0 | 0 | 0 | 5 | 70 | 17 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36 | 75 | 0 | 25 | 515 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1081 | 2 | 0 | 0 | 0 | 320 | 330 | 51 | 0 | 195 | 41 | 0 | 98 | 0 | 0 | 11 | 0 | 120 | 0 | 7 | 0 | 310 | 0 | 378 | 41 | 23 | 155 | 1 | 17 | 0 | 86 | 30 | 0 | 0 | 97 | 0 | 59 | 19 | 22 | 0 | 4.89 | 6 | 5907.25 | 898 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 797 | 0 | 0 | 0 | 1018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 14 | 0 | 0 | 5.44 | 187 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0.54 | 0 | 53 | 35 | 4 | 22 | 0 | 0 | 0 | 0.7 | 19 | 0.06 | 0 | 255 | 125 | 220 | 0 | 0 | 876 | 0 | 5201.64 | 11108.89 | 93.11
18:00 | 0 | 35 | 18 | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 0 | 10 | 0 | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 13 | 14 | 0 | 320 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 28 | 515 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 1118 | 0 | 0 | 0 | 0 | 280 | 240 | 5 | 0 | 177 | 5 | 0 | 51 | 0 | 0 | 11 | 0 | 100 | 0 | 0 | 0 | 310 | 0 | 300 | 42 | 23 | 152 | 0 | 17 | 0 | 22 | 20 | 0 | 0 | 97 | 0 | 98 | 47 | 23 | 0 | 0 | 6 | 5359 | 898 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 909 | 0 | 0 | 0 | 1119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 53 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 100 | 180 | 0 | 0 | 957 | 0 | 5114 | 10473 | 93.1
19:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 17.5 | 22 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 21 | 515 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1150 | 0 | 0 | 11 | 0 | 315 | 310 | 28 | 0 | 194 | 42 | 0 | 102 | 0 | 0 | 13 | 0 | 110 | 0 | 0 | 0 | 280 | 0 | 356 | 42 | 23 | 149 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 97 | 0 | 98 | 46 | 24 | 0 | 0 | 6 | 5757.5 | 899 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 837 | 0 | 0 | 0 | 1077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223 | 130 | 220 | 0 | 0 | 978 | 0 | 5280 | 11037.5 | 93.09
19:30 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17.5 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 24 | 515 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1160 | 0 | 0 | 24 | 0 | 315 | 330 | 51 | 0 | 193 | 42 | 0 | 101 | 0 | 0 | 11 | 0 | 110 | 0 | 0 | 0 | 310 | 0 | 382 | 42 | 23 | 140 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 97 | 0 | 98 | 46 | 24 | 0 | 0 | 6 | 5936.5 | 899 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 854 | 0 | 0 | 0 | 1084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 130 | 220 | 0 | 0 | 1020 | 0 | 5281 | 11217.5
20:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17.5 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 33 | 515 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1144 | 0 | 0 | 46 | 0 | 315 | 330 | 51 | 0 | 194 | 42 | 0 | 102 | 0 | 0 | 11 | 0 | 110 | 0 | 0 | 0 | 305 | 0 | 372 | 41 | 23 | 145 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 97 | 0 | 98 | 46 | 24 | 0 | 0 | 6 | 5950.5 | 899 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 837 | 0 | 0 | 0 | 1018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 130 | 220 | 0 | 0 | 1020 | 0 | 5232 | 11182.5 | 93.09
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 13.5 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 36 | 600 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1160 | 0 | 0 | 68 | 0 | 325 | 342 | 51 | 0 | 200 | 42 | 0 | 102 | 0 | 0 | 11 | 0 | 114 | 0 | 0 | 0 | 300 | 0 | 386 | 41 | 23 | 155 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 98 | 0 | 98 | 48 | 24 | 0 | 0 | 6 | 6130.5 | 899 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 774 | 0 | 0 | 0 | 930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 130 | 220 | 0 | 0 | 1035 | 0 | 5134 | 11264.5 | 93.09
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 13.5 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 34 | 600 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1156 | 0 | 0 | 45 | 0 | 325 | 330 | 51 | 0 | 190 | 42 | 0 | 102 | 0 | 0 | 11 | 0 | 118 | 0 | 0 | 0 | 305 | 0 | 354 | 41 | 23 | 158 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 99 | 0 | 98 | 48 | 24 | 0 | 0 | 6 | 6055.5 | 899 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773 | 0 | 0 | 0 | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 130 | 220 | 0 | 0 | 1024 | 0 | 5085 | 11140.5 | 93.08
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 13.5 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 36 | 600 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 994 | 0 | 0 | 8 | 0 | 315 | 290 | 51 | 0 | 185 | 42 | 0 | 102 | 0 | 0 | 11 | 0 | 104 | 0 | 0 | 0 | 295 | 0 | 361 | 42 | 23 | 154 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 100 | 0 | 59 | 18 | 24 | 0 | 0 | 6 | 5682.5 | 898 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 761 | 0 | 0 | 0 | 826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 130 | 220 | 0 | 0 | 900 | 0 | 4785 | 10467.5 | 93.07
Total KWH | 0 | 197760 | 83040 | 0 | 0 | 0 | 0 | 0 | 7880400 | 0 | 0 | 38520 | 0 | 892512 | 51360 | 0 | 0 | 0 | 21600 | 0 | 0 | 0 | 9979727 | 0 | 0 | 1298037 | 0 | 0 | 187502 | 942000 | 358200 | 487080 | 0 | 10562727.27 | 0 | 0 | 0 | 0 | 30720 | 0 | 0 | 0 | 0 | 0 | 21238 | 1792240 | 0 | 547680 | 14443636.36 | 0 | 0 | 0 | 0 | 22582 | 4920920 | 0 | 0 | 0 | 21785453 | 113130 | 0 | 200727 | 0 | 7948500 | 7520000 | 688560 | 0 | 4778000 | 340992 | 12480 | 1809234 | 15360 | 0 | 261620 | 0 | 2502720 | 0 | 420900 | 0 | 7146000 | 0 | 8876000 | 985000 | 571080 | 3528409 | 63330 | 302400 | 0 | 1068480 | 579648 | 0 | 0 | 2381100 | 0 | 1670400 | 590400 | 519360 | 8200 | 191970 | 115200 | 131754134.63 | 21449454 | 6255360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 552960 | 19185450 | 0 | 0 | 0 | 21935421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315680 | 680610 | 0 | 0 | 277504 | 4060545 | 0 | 0 | 0 | 0 | 0 | 8917309 | 0 | 26580 | 0 | 1234472 | 124823 | 212728 | 119184 | 0 | 0 | 0 | 38443.08 | 1031040 | 3489 | 0 | 4385000 | 2923000 | 5171980 | 0 | 0 | 19152000 | 0 | 118053032.08 | 249807166.71