## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 22-02-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-02-2026 | during | 22-02-2026 | during | 22-02-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 322 | 339 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 16 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 9.5 | 11.5 | 33 | 33 | 23 | 23 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 16 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 52 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 595 | 520 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 290 | 400 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 108 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1285.5 | 1517.5 | 5610.22 | 5580.22 | 2871.05 | 2895.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | U#1 Under maintenance, U#2 Running
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 75 | 75 | 75 | 75 | 75 | 75 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 223 | 225 | 225 | 225 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 32 | 32 | 16 | 16 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 3 | 12 | 51 | 51 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 38 | 42 | 5 | 20 | 40 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.34 | 0 | 3.72 | 0 | 3.72 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 0 | 0 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 839 | 1154 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 3 | 5 | 3 | 6 | 3 | 6 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 620 | 620 | 905 | 905 | 875 | 875 | ps availability is less
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1817.34 | 2131 | 3664.58 | 3659.86 | 3231.22 | 3211.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 196 | 201 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 320 | 335 | 353.35 | 353.35 | 353.35 | 353.35 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 345 | 305 | 318.81 | 318.81 | 318.81 | 318.81
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 41 | 25 | 41.65 | 41.65 | 41.65 | 41.65 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 11 | 5 | 55 | 55 | 5 | 5 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 25 | 8 | 195 | 195 | 40 | 40 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 44 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 42 | 42 | 42 | 42 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 163 | 163 | 110 | 110 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 108 | 110 | 84 | 80 | 132 | 132 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 20 | 24.5 | 24.5 | 13 | 13 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 66 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1278 | 1153 | 2751.51 | 2682.51 | 1975.01 | 1910.01
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-02-2026 | during | 22-02-2026 | during | 22-02-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 68 | 101 | 157.5 | 157.5 | 35 | 35 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 46 | 20 | 50 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 97 | 60 | 115 | 60 | 80 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 39.91 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 186.91 | 250 | 358 | 399 | 182 | 158
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 41 | 0 | 0 | 0 | 0 | plant availability zero
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 23 | 23 | 23 | 23 | 23 | 23 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 137 | 154 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 20 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 83 | 86 | 86 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 97 | 100 | 100 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 20 | 21 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 372 | 390 | 0 | 0 | 385 | 385 | -
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1121 | 1140 | 768 | 768 | 1095 | 1096
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 857 | 857 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 44 | 44 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 300 | 362 | 410 | 410 | 300 | 300 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 79 | 0 | 78 | 0 | 78 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 857 | 1005 | 0 | 0 | 1070 | 1070 | Plant availability less
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2093 | 2224 | 2352 | 2274 | 2557.1 | 2479.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 125 | 125 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 500 | 470 | 622 | 622 | 622 | 622 | Unit1 Under Maintenance
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 15 | 15 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 198 | 249 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.53 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2700.36 | 1043.53 | 1064 | 1540 | 1539 | 1405 | 1404
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 49.22 | 0 | 51 | 0 | 51 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 173 | 178 | 214 | 214 | 214 | 214 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 345 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 16 | 16 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.25 | 0 | 5.45 | 0 | 5.45 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 826.29 | 1165.22 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 54.14 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 104 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1556.9 | 1757.22 | 3122.32 | 2904.87 | 2577.94 | 2360.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 51 | 53 | 55 | 55 | 55 | 55 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 49 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.3 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 27 | 0 | 0 | 0 | 0 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 163 | 0 | 175.2 | 0 | 175.2 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 247.3 | 137 | 483.4 | 303 | 463.4 | 283
System Total |  |  |  |  | 28823.2 | 28385.703 | 10629.48 | 11373.72 | 20650.03 | 20110.46 | 16357.72 | 15797.15
Forecast Scenario (22-02-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 10580 |  | 0 |  | 10580
|  |  |  | 1:00 | 9790 |  | 0 |  | 9790
|  |  |  | 2:00 | 9520 |  | 0 |  | 9520
|  |  |  | 3:00 | 10250 |  | 0 |  | 10250
|  |  |  | 4:00 | 10740 |  | 0 |  | 10740
|  |  |  | 5:00 | 9360 |  | 0 |  | 9360
|  |  |  | 6:00 | 8500 |  | 0 |  | 8500
|  |  |  | 7:00 | 8720 |  | 0 |  | 8720
|  |  |  | 8:00 | 9380 |  | 0 |  | 9380
|  |  |  | 9:00 | 10520 |  | 0 |  | 10520
|  |  |  | 10:00 | 11060 |  | 0 |  | 11060
|  |  |  | 11:00 | 11490 |  | 0 |  | 11490
|  |  |  | 12:00 | 11930 |  | 0 |  | 11930
|  |  |  | 13:00 | 12420 |  | 0 |  | 12420
|  |  |  | 14:00 | 12520 |  | 0 |  | 12520
|  |  |  | 15:00 | 12030 |  | 0 |  | 12030
|  |  |  | 16:00 | 11950 |  | 0 |  | 11950
|  |  |  | 17:00 | 12220 |  | 0 |  | 12220
|  |  |  | 18:00 | 11210 |  | 0 |  | 11210
|  |  |  | 18:30 | 11500 |  | 0 |  | 11500
|  |  |  | 19:00 | 11710 |  | 0 |  | 11710
|  |  |  | 19:30 | 11840 |  | 0 |  | 11840
|  |  |  | 20:00 | 11720 |  | 0 |  | 11720
|  |  |  | 21:00 | 11600 |  | 0 |  | 11600
|  |  |  | 22:00 | 11510 |  | 0 |  | 11510
|  |  |  | 23:00 | 10970 |  | 0 |  | 10970
Probable Maximum Temperature: |  |  | 31.10°C
Probable Maximum Demand at Day Peak: |  |  | 11930.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11840.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11840.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 261.70 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:45 hrs on 22-02-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 21-02-2026 | [28 empty] | Date: | 21-02-2026 | [28 empty] | Date: | 21-02-2026 | [28 empty] | Date: | 21-02-2026 | [28 empty] | Date: | 21-02-2026 | [17 empty] | Date: | 21-02-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 37 | 600 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 900 | 0 | 0 | 8 | 0 | 310 | 280 | 5 | 0 | 192 | 42 | 0 | 102 | 0 | 0 | 11 | 0 | 102 | 0 | 0 | 0 | 290 | 0 | 361 | 41 | 23 | 154 | 0 | 17 | 0 | 11 | 30 | 0 | 0 | 99 | 0 | 59 | 18 | 24 | 0 | 0 | 6 | 5330.5 | 898 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 130 | 180 | 0 | 0 | 800 | 0 | 4642 | 9972.5 | 93.07
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 37 | 600 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 728 | 0 | 0 | 8 | 0 | 290 | 280 | 5 | 0 | 192 | 42 | 0 | 51 | 0 | 0 | 11 | 0 | 98 | 0 | 0 | 0 | 295 | 0 | 313 | 41 | 23 | 144 | 0 | 17 | 0 | 11 | 30 | 0 | 0 | 99 | 0 | 59 | 18 | 24 | 0 | 0 | 6 | 4838.5 | 898 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 130 | 180 | 0 | 0 | 750 | 0 | 4580 | 9418.5 | 93.06
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 37 | 600 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 730 | 0 | 0 | 8 | 0 | 290 | 285 | 5 | 0 | 194 | 42 | 0 | 51 | 0 | 0 | 11 | 0 | 96 | 0 | 0 | 0 | 300 | 0 | 302 | 41 | 23 | 137 | 0 | 17 | 0 | 11 | 7 | 0 | 0 | 99 | 0 | 59 | 18 | 35 | 0 | 0 | 6 | 4631.5 | 898 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 750 | 0 | 4495 | 9126.5 | 93.05
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 37 | 600 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 736 | 0 | 0 | 8 | 0 | 300 | 345 | 5 | 0 | 200 | 42 | 0 | 104 | 0 | 0 | 11 | 0 | 94 | 0 | 0 | 0 | 295 | 0 | 326 | 41 | 23 | 138 | 0 | 17 | 0 | 11 | 7 | 0 | 0 | 102 | 0 | 59 | 19 | 35 | 0 | 0 | 6 | 4852.5 | 899 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 768 | 0 | 0 | 0 | 827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 100 | 180 | 0 | 0 | 750 | 0 | 4494 | 9346.5 | 93.04
04:00 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 37 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 13.5 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 37 | 600 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 731 | 0 | 0 | 8 | 0 | 325 | 350 | 26 | 0 | 199 | 40 | 0 | 104 | 0 | 0 | 11 | 0 | 108 | 0 | 0 | 0 | 310 | 0 | 386 | 41 | 23 | 156 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 101 | 0 | 96 | 47 | 35 | 0 | 0 | 3 | 5621.5 | 898 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 841 | 0 | 0 | 0 | 829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 130 | 220 | 0 | 0 | 737 | 0 | 4866 | 10487.5 | 93.03
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 631 | 0 | 0 | 8 | 0 | 335 | 330 | 5 | 0 | 202 | 40 | 0 | 104 | 0 | 0 | 11 | 0 | 106 | 0 | 0 | 0 | 295 | 0 | 359 | 41 | 23 | 156 | 0 | 0 | 0 | 11 | 20 | 0 | 0 | 100 | 0 | 98 | 47 | 35 | 0 | 0 | 6 | 5120.5 | 898 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 837 | 0 | 0 | 0 | 827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 115 | 180 | 0 | 0 | 550 | 0 | 4385 | 9505.5 | 93.02
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 530 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 620 | 0 | 0 | 0 | 0 | 300 | 250 | 5 | 0 | 150 | 10 | 0 | 50 | 0 | 0 | 11 | 0 | 90 | 0 | 0 | 0 | 290 | 0 | 326 | 41 | 23 | 143 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 100 | 0 | 58 | 19 | 11 | 0 | 0 | 0 | 4233.5 | 899 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 769 | 0 | 0 | 0 | 824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 4044 | 8277.5 | 93.01
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 12.5 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0.15 | 75 | 0 | 0 | 520 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 618 | 1 | 0 | 0 | 0 | 330 | 250 | 5 | 0 | 150 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 76 | 0 | 3 | 0 | 265 | 0 | 326 | 41 | 23 | 140 | 1 | 0 | 0 | 0 | 20 | 0 | 0 | 100 | 0 | 45 | 19 | 20 | 0 | 1.77 | 0 | 4126.42 | 892 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 776 | 0 | 0 | 0 | 827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.68 | 4 | 0 | 0 | 3.99 | 130 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0.36 | 0 | 52 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 4 | 0.21 | 0 | 140 | 100 | 180 | 0 | 0 | 480 | 0 | 4045.34 | 8171.76 | 93
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 11.5 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0.6 | 75 | 0 | 2 | 520 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 620 | 6 | 0 | 0 | 0 | 305 | 305 | 5 | 0 | 202 | 0 | 0 | 50 | 0 | 0 | 9 | 0 | 80 | 0 | 12 | 0 | 240 | 0 | 326 | 41 | 23 | 144 | 2 | 0 | 0 | 0 | 20 | 0 | 0 | 100 | 0 | 49 | 19 | 20 | 0 | 13.17 | 0 | 4545.27 | 749 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 785 | 0 | 0 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.69 | 24 | 0 | 0 | 8.14 | 130 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0.57 | 0 | 52 | 0 | 5 | 0 | 0 | 0 | 0 | 0.8 | 29 | 0.13 | 0 | 140 | 100 | 180 | 0 | 0 | 480 | 0 | 4113.33 | 8658.6 | 93
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 9.5 | 22 | 0 | 603 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1.28 | 75 | 0 | 4 | 520 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 620 | 11 | 0 | 0 | 0 | 320 | 315 | 5 | 0 | 209 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 86 | 0 | 35 | 0 | 270 | 0 | 339 | 41 | 23 | 153 | 5 | 0 | 0 | 0 | 20 | 0 | 0 | 100 | 0 | 59 | 19 | 33 | 1 | 19.78 | 0 | 4847.56 | 866 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 792 | 0 | 0 | 0 | 825.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.27 | 52 | 0 | 0 | 21.71 | 157 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 2.74 | 0 | 52 | 0 | 8 | 0 | 0 | 0 | 0 | 2.8 | 52 | 0.26 | 0 | 140 | 110 | 220 | 0 | 0 | 480 | 0 | 4483.44 | 9331 | 92.99
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 23 | 17 | 9.5 | 22 | 0 | 603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.04 | 75 | 0 | 3 | 585 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 680 | 16 | 0 | 0 | 0 | 295 | 290 | 14 | 0 | 197 | 31 | 0 | 100 | 0 | 0 | 11 | 0 | 100 | 0 | 50 | 0 | 305 | 0 | 339 | 41 | 23 | 159 | 7 | 0 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 59 | 19 | 70 | 0 | 34.16 | 0 | 5254.7 | 857 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 798 | 0 | 0 | 0 | 827.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.74 | 75 | 0 | 0 | 40.69 | 169 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 4 | 0 | 52 | 0 | 17 | 0 | 0 | 0 | 0 | 4.5 | 71 | 0.4 | 0 | 200 | 130 | 220 | 0 | 0 | 480 | 0 | 4693.02 | 9947.72 | 92.99
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 28 | 17 | 9.5 | 22 | 0 | 595 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3.16 | 75 | 0 | 32 | 620 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 710 | 18 | 0 | 3 | 0 | 335 | 305 | 51 | 0 | 204 | 38 | 0 | 100 | 0 | 0 | 15 | 0 | 104 | 0 | 52 | 0 | 295 | 0 | 327 | 42 | 23 | 141 | 9 | 0 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 59 | 19 | 56 | 2 | 37.61 | 0 | 5388.27 | 858 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 856 | 0 | 0 | 0 | 827.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.33 | 92 | 0 | 0 | 48.69 | 161 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 4.73 | 0 | 52 | 0 | 29 | 0 | 0 | 0 | 0 | 5.8 | 90 | 0.53 | 0 | 202 | 125 | 220 | 0 | 0 | 480 | 0 | 4792.64 | 10180.91 | 92.98
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 31 | 17 | 9.5 | 21 | 0 | 595 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 0 | 0 | 0 | 3.34 | 75 | 0 | 38 | 620 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 839 | 19 | 0 | 25 | 0 | 320 | 345 | 51 | 11 | 196 | 41 | 0 | 100 | 0 | 0 | 15 | 0 | 108 | 0 | 66 | 0 | 305 | 0 | 372 | 42 | 23 | 137 | 9 | 17 | 0 | 86 | 30 | 0 | 0 | 100 | 0 | 58 | 19 | 68 | 2 | 39.91 | 0 | 5688.75 | 857 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 857 | 0 | 0 | 0 | 826.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.22 | 104 | 0 | 0 | 54.14 | 173 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 5.25 | 0 | 51 | 0 | 27 | 0 | 0 | 0 | 0 | 6.3 | 163 | 0.53 | 0 | 198 | 125 | 220 | 0 | 0 | 500 | 0 | 4940.73 | 10629.48 | 92.98
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 29 | 35 | 12.5 | 14 | 0 | 590 | 0 | 0 | 0 | 0 | 10 | 2 | 0 | 0 | 0 | 0 | 3.06 | 75 | 0 | 42 | 620 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 964 | 19 | 0 | 58 | 0 | 325 | 335 | 51 | 40 | 204 | 40 | 0 | 99 | 0 | 0 | 15 | 0 | 112 | 0 | 62 | 0 | 320 | 0 | 392 | 42 | 23 | 155 | 10 | 17 | 0 | 85 | 30 | 0 | 0 | 100 | 0 | 58 | 19 | 67 | 2 | 39.62 | 0 | 5971.18 | 857 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 872 | 0 | 0 | 0 | 927.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.4 | 101 | 0 | 0 | 55.33 | 182 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.34 | 0 | 51 | 0 | 22 | 0 | 0 | 0 | 0 | 6 | 155 | 0.5 | 0 | 260 | 125 | 220 | 0 | 0 | 550 | 0 | 5325.07 | 11296.25 | 92.97
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 27 | 52 | 13.5 | 21 | 0 | 590 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 2.65 | 75 | 0 | 42 | 620 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1094 | 15 | 0 | 93 | 0 | 290 | 290 | 51 | 44 | 190 | 40 | 0 | 98 | 0 | 0 | 19 | 0 | 114 | 0 | 53 | 0 | 310 | 0 | 296 | 42 | 23 | 146 | 8 | 17 | 0 | 85 | 30 | 0 | 0 | 100 | 0 | 58 | 19 | 81 | 2 | 33.22 | 5 | 5936.37 | 858 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 959 | 0 | 0 | 0 | 1036.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.64 | 88 | 0 | 0 | 27.99 | 174 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 3.17 | 0 | 51 | 0 | 20 | 0 | 0 | 0 | 0 | 5.7 | 133 | 0.45 | 0 | 277 | 125 | 220 | 0 | 0 | 550 | 0 | 5391.35 | 11327.72 | 92.97
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 21 | 52 | 13.5 | 21 | 0 | 590 | 0 | 0 | 0 | 0 | 14 | 4 | 0 | 0 | 0 | 0 | 1.78 | 75 | 0 | 42 | 620 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1090 | 11 | 0 | 83 | 0 | 290 | 290 | 51 | 10 | 190 | 40 | 0 | 98 | 0 | 0 | 19 | 0 | 104 | 0 | 42 | 0 | 305 | 0 | 310 | 42 | 23 | 135 | 6 | 17 | 0 | 82 | 30 | 0 | 0 | 97 | 0 | 58 | 19 | 78 | 1 | 26.89 | 6 | 5816.17 | 857 | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 954 | 0 | 0 | 0 | 961.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.44 | 70 | 0 | 0 | 31.11 | 154 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 3.01 | 0 | 52 | 0 | 20 | 0 | 0 | 0 | 0 | 5 | 82 | 0.34 | 0 | 248 | 125 | 180 | 0 | 0 | 500 | 0 | 5067.18 | 10883.35 | 92.96
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 13 | 52 | 13.5 | 20 | 0 | 545 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0.97 | 75 | 0 | 40 | 620 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1100 | 7 | 0 | 35 | 0 | 315 | 320 | 51 | 10 | 179 | 40 | 0 | 98 | 0 | 0 | 19 | 0 | 104 | 0 | 24 | 0 | 315 | 0 | 356 | 42 | 23 | 139 | 3 | 17 | 0 | 82 | 30 | 0 | 0 | 97 | 0 | 58 | 19 | 81 | 1 | 12.12 | 6 | 5839.59 | 857 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 956 | 0 | 0 | 0 | 978.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.86 | 42 | 0 | 0 | 21.1 | 161 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 2.11 | 0 | 52 | 0 | 11 | 0 | 0 | 0 | 0 | 2.9 | 46 | 0.2 | 0 | 250 | 125 | 180 | 0 | 0 | 500 | 0 | 4999.27 | 10838.86 | 92.96
17:00 | 0 | 4 | 2 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 11 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 4 | 108 | 13.5 | 21 | 0 | 546 | 0 | 0 | 0 | 0 | 7 | 4 | 0 | 0 | 0 | 0 | 0.27 | 75 | 0 | 42 | 620 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1100 | 2 | 0 | 8 | 0 | 315 | 320 | 51 | 9 | 208 | 25 | 0 | 98 | 0 | 0 | 19 | 0 | 108 | 0 | 6 | 0 | 320 | 0 | 400 | 42 | 23 | 149 | 1 | 17 | 0 | 83 | 30 | 0 | 0 | 97 | 0 | 58 | 19 | 100 | 0 | 5.34 | 6 | 6120.11 | 857 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 960 | 0 | 0 | 0 | 1067.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.42 | 10 | 0 | 0 | 6.5 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.62 | 0 | 52 | 30 | 3 | 25 | 0 | 0 | 0 | 1 | 31 | 0.07 | 0 | 249 | 125 | 220 | 0 | 0 | 500 | 0 | 5130.66 | 11250.77 | 92.95
18:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 10 | 0 | 40 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 13.5 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 4 | 14 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 20 | 585 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 1109 | 0 | 0 | 8 | 0 | 270 | 240 | 20 | 5 | 201 | 25 | 0 | 80 | 0 | 0 | 19 | 0 | 102 | 0 | 0 | 0 | 325 | 0 | 366 | 41 | 23 | 157 | 0 | 17 | 0 | 11 | 20 | 0 | 0 | 97 | 0 | 97 | 46 | 100 | 0 | 0 | 6 | 5731.5 | 857 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 1028 | 0 | 0 | 0 | 1163.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 53 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 125 | 180 | 0 | 0 | 450 | 0 | 5062.49 | 10793.99 | 92.94
19:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 17 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 11.5 | 21 | 0 | 520 | 0 | 0 | 0 | 0 | 5 | 12 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 42 | 620 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1154 | 0 | 0 | 8 | 0 | 335 | 305 | 44 | 5 | 201 | 25 | 0 | 100 | 0 | 0 | 20 | 0 | 110 | 0 | 0 | 0 | 315 | 0 | 390 | 41 | 23 | 154 | 0 | 17 | 0 | 83 | 20 | 0 | 0 | 97 | 0 | 97 | 46 | 101 | 0 | 0 | 6 | 6191.5 | 857 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005 | 0 | 0 | 0 | 1165.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 53 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 125 | 220 | 0 | 0 | 470 | 0 | 5182.22 | 11373.72 | 92.93
19:30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 493 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 11.5 | 21 | 0 | 520 | 0 | 0 | 0 | 0 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 42 | 620 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1160 | 0 | 0 | 8 | 0 | 320 | 330 | 51 | 5 | 193 | 25 | 0 | 100 | 0 | 0 | 20 | 0 | 118 | 0 | 0 | 0 | 310 | 0 | 374 | 41 | 23 | 160 | 0 | 17 | 0 | 83 | 20 | 0 | 0 | 97 | 0 | 97 | 46 | 102 | 0 | 0 | 6 | 6193.5 | 857 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 0 | 0 | 0 | 1167.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 125 | 220 | 0 | 0 | 510 | 0 | 5178.47 | 11371.97
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 11.5 | 22 | 0 | 520 | 0 | 0 | 0 | 0 | 1 | 11 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 42 | 620 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1150 | 0 | 0 | 8 | 0 | 315 | 330 | 51 | 5 | 194 | 25 | 0 | 100 | 0 | 0 | 19 | 0 | 118 | 0 | 0 | 0 | 310 | 0 | 376 | 41 | 23 | 157 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 97 | 0 | 98 | 48 | 102 | 0 | 0 | 0 | 6153.5 | 857 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 996 | 0 | 0 | 0 | 1176.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 125 | 220 | 0 | 0 | 525 | 0 | 5184.81 | 11338.31 | 92.92
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 11.5 | 22 | 0 | 520 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 42 | 620 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1160 | 0 | 0 | 8 | 0 | 335 | 350 | 51 | 5 | 202 | 25 | 0 | 101 | 0 | 0 | 20 | 0 | 118 | 0 | 0 | 0 | 310 | 0 | 392 | 41 | 23 | 157 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 97 | 0 | 98 | 16 | 102 | 0 | 0 | 0 | 6177.5 | 857 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 916 | 0 | 0 | 0 | 1170.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 125 | 220 | 0 | 0 | 555 | 0 | 5132.46 | 11309.96 | 92.91
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 12 | 22 | 0 | 520 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 42 | 620 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1150 | 0 | 0 | 8 | 0 | 320 | 330 | 51 | 5 | 194 | 25 | 0 | 101 | 0 | 0 | 20 | 0 | 114 | 0 | 0 | 0 | 320 | 0 | 373 | 41 | 23 | 160 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 97 | 0 | 98 | 16 | 102 | 0 | 0 | 0 | 6086 | 856 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 903 | 0 | 0 | 0 | 1171.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 125 | 220 | 0 | 0 | 555 | 0 | 5123.54 | 11209.54 | 92.9
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 42 | 620 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 950 | 0 | 0 | 8 | 0 | 320 | 330 | 51 | 5 | 194 | 42 | 0 | 102 | 0 | 0 | 20 | 0 | 108 | 0 | 0 | 0 | 310 | 0 | 373 | 41 | 23 | 153 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 97 | 0 | 59 | 19 | 103 | 0 | 0 | 0 | 5757 | 857 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 893 | 0 | 0 | 0 | 955.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 130 | 220 | 0 | 0 | 555 | 0 | 4870.99 | 10627.99 | 92.89
Total KWH | 0 | 45120 | 38400 | 0 | 0 | 0 | 0 | 0 | 7840800 | 0 | 0 | 29160 | 0 | 307440 | 31680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9171364 | 0 | 0 | 0 | 0 | 0 | 200739 | 754800 | 294600 | 510840 | 0 | 11764090.91 | 0 | 0 | 0 | 0 | 148320 | 97923 | 0 | 0 | 0 | 0 | 19680 | 1794340 | 0 | 721440 | 14385454.55 | 0 | 0 | 0 | 0 | 0 | 4867446 | 0 | 0 | 0 | 21147271 | 122445 | 0 | 434909 | 0 | 7871300 | 7516000 | 853316 | 166560 | 4811000 | 718848 | 0 | 2068322 | 0 | 0 | 339590 | 0 | 2435520 | 0 | 414627 | 0 | 7307000 | 0 | 8665000 | 979000 | 613800 | 3575455 | 60448 | 280608 | 0 | 1254720 | 633792 | 0 | 0 | 2374050 | 0 | 1648800 | 573600 | 1445760 | 11700 | 250560 | 70080 | 131667718.46 | 20856000 | 7895232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 538560 | 20923700 | 0 | 0 | 0 | 22645125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315748 | 686450 | 0 | 0 | 335248 | 4108636 | 0 | 0 | 0 | 0 | 0 | 9016000 | 0 | 32820 | 0 | 1204363 | 92894 | 160322 | 130800 | 0 | 0 | 0 | 40677 | 867600 | 3418 | 0 | 5084000 | 2870000 | 5252690 | 0 | 0 | 13982545.45 | 0 | 117042828.45 | 248710546.91

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 21-02-2026
Power Supply Scenario
| Day Peak Generation |  |  | 10629.48 | MW | 12:00 Hr. | Energy Generated |  |  | 248.7105 |  | MKWHr.
| Day Peak Demand |  |  | 10629.48 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.097 |  | MKWHr.
| Evening Peak Generation |  |  | 11373.72 | MW | 19:00 Hr. | Energy Demand |  |  | 248.8075 |  | MKWHr.
| Evening Peak Demand |  |  | 11373.72 | MW | 19:00 Hr. | Maximum Temperature |  |  | 31.9 |  | °C
| Minimum Generation of the Day |  |  | 8171.76 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 847.08 |  | MMCFD
| Maximum Generation of the Day |  |  | 11373.72 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.1782 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 29.5817 | 0 | 1.2066 | 0 | 0 | 0.20074 | 0 | 0 | 30.989 | Gas | 116.2222 | Gas | 401951777.9047
| Chattogram Zone |  |  | 5.5889 | 35.5327 | 0.097923 | 0 | 1.7943 | 0.14213 | 0 | 0.14832 | 43.3043 | Coal | 76.7273 | Coal | 502070049.1125
| Cumilla Zone |  |  | 24.7798 | 0 | 0 | 0 | 0 | 0.41463 | 2.4355 | 0 | 27.63 | HFO | 3.8207 | HFO | 65110560.16
| Mymensingh Zone |  |  | 1.4458 | 0 | 2.2925 | 0 | 0 | 0.26226 | 0 | 0 | 4.0005 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 25.6834 | 0 | 0 | 0 | 0 | 0.060448 | 0 | 0 | 25.7439 | Hydro | 1.7943 | Hydro | 179434
| Khulna Zone |  |  | 7.8952 | 20.9237 | 0 | 0 | 0 | 0.53856 | 20.856 | 0 | 50.2135 | Solar | 4.061 | Solar | 64375287.43
| Barishal Zone |  |  | 8.1227 | 19.0665 | 0 | 0 | 0 | 0.003418 | 0 | 0 | 27.1927 | Import | 45.9366 | Import | 252001531.05
| Rajshahi Zone |  |  | 13.1246 | 0 | 0 | 0 | 0 | 1.3703 | 22.6451 | 0 | 37.14 | Wind | 0.14832 | Wind | 2181787.2
| Rangpur Zone |  |  | 0 | 1.2044 | 0.22369 | 0 | 0 | 1.0686 | 0 | 0 | 2.4967
| Total |  |  | 116.2222 | 76.7273 | 3.8207 | 0 | 1.7943 | 4.061 | 45.9366 | 0.14832 | 248.7105
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 401951777.9047 |  | Hydro | 179434
|  |  |  | Coal | 502070049.1125 |  | Solar | 64375287.43
|  |  |  | HFO | 65110560.16 |  | Import | 252001531.05
|  |  |  | HSD | 0 |  | Wind | 2181787.2
[5 empty] | Total: | 128,78,70,426 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.856 | Peak Hr Flow | 857.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 31694002.15 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 22.6451 | Peak Hr Flow | 1165.22 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1628 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.4355 | Peak Hr Flow | 110.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2029 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 45.9366 | Peak Hr Flow | 2132.22 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4042
|  |  |  | Chattogram |  | 0 |  | 1204
|  |  |  | Cumilla |  | 0 |  | 1013
|  |  |  | Mymensingh |  | 0 |  | 1031
|  |  |  | Sylhet |  | 0 |  | 415
|  |  |  | Khulna |  | 0 |  | 1304
|  |  |  | Barishal |  | 0 |  | 325
|  |  |  | Rajshahi |  | 0 |  | 1071
|  |  |  | Rangpur |  | 0 |  | 709
|  |  |  | Total |  | 0 |  | 11114
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:50 |  | Sirajganj-Ullahpara 132KV Ckt-1 Forced S/D from Ullahpara 132/33kV end Due to Over Load
| 09:57 |  | Sirajganj-Ullahpara 132KV Ckt-2 Forced S/D from Ullahpara 132/33kV end Due to Over Load
| 10:36 | 15:42 | Chandina 132/33kV S/S TR-3 LT Project Work S/D Due to Due to oil leakage inspection,
Clearance by CNEEC
| 10:36 | 15:41 | Chandina 132/33kV S/S TR-3 HT Project Work S/D Due to Due to oil leakage inspection,
Clearance by CNEEC
| 13:24 | 14:22 | Naogaon-Niyamatpur 132kV Ckt-1 Project Work S/D from Niamatpur 132/33kV end Due to
Project Work Purpose( As per instruction ALDC)
| 19:00 |  | Evening Peak Generation: 11373 MW.
| 04:00 |  | Sehri peak generation: 10521 MW
| 06:25 | 06:48 | Cumilla(S) 132/33kV S/S TR-2 HT Tripped showing RET 650 relays. | [7 empty] | 21.0MW load
interrup.
| 06:25 | 06:48 | Cumilla(S) 132/33kV S/S TR-1 LT Tripped showing REF615 relays. | [7 empty] | 21.0MW load
interrup.
| 07:14 |  | Cumilla(S) 132/33kV S/S TR-2 HT Tripped showing RET650 relays. | [7 empty] | 21.0MW load
interrup.
| 07:14 |  | Cumilla(S) 132/33kV S/S TR-2 LT Tripped showing REF615 relays. | [7 empty] | 21.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 21-02-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0"MW due to gas restriction by Titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 339 | 7840800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 29160 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 16 | 31680 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 11.5 | 294600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 510840 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 38400 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 52 | 307440 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 45120 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 200739 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 520 | 11764090.91 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 400 | 9171364 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 108 | 754800 | -
Dhaka Area Total |  |  |  |  | 6668.974 | 1517.5 | 30989033.91
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | U#1 Under maintenance, U#2 Running
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 122445 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 75 | 1794340 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 223 | 4867446 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 12 | 97923 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 42 | 721440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 19680 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1154 | 21147271 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 5 | 148320 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 620 | 14385454.55 | ps availability is less
Chattogram Area Total |  |  |  |  | 4898.863 | 2131 | 43304319.55
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 201 | 4811000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 335 | 7871300 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 305 | 7516000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 25 | 718848 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 166560 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 434909 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 853316 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2068322 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 110 | 2435520 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 339590 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 414627 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1153 | 27629992
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 101 | 1445760 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11700 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 46 | 573600 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 97 | 1648800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 250560 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 70080 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 250 | 4000500
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 60448 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 979000 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 23 | 613800 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 154 | 3575455 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 20 | 633792 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1254720 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 97 | 2374050 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 280608 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7307000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 390 | 8665000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1140 | 25743873
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 857 | 20856000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 362 | 7895232 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 538560 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1005 | 20923700 | Plant availability less
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2224 | 50213492
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 125 | 2870000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 470 | 13982545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5252690 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 249 | 5084000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3418 | -
Barishal Area Total |  |  |  |  | 2700.36 | 1064 | 27192653.45
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 315748 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 178 | 4108636 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9016000 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | machine problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 32820 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1165.22 | 22645125 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 335248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 686450 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1757.22 | 37140027
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 53 | 1204363 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 130800 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 40677 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 92894 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 160322 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 867600 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 137 | 2496656
Eastern Grid Total |  |  |  |  | 17400.108 | 6191.5 | 131667718.46
Western Grid Total |  |  |  |  | 10985.595 | 5182.22 | 117042828.45
National Grid Total |  |  |  |  | 28385.703 | 11373.72 | 248710546.91
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 21-02-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7704.59 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3409.5 | MW
i) Dhaka area |  |  | 4042.09 |  | MW | i) Khulna area |  |  |  | 1304 | MW
ii) Chattogram area |  |  | 1203.5 |  | MW | ii) Barishal area |  |  |  | 324.8 | MW
iii) Cumilla area |  |  | 1013 |  | MW | iii) Rajshahi area |  |  |  | 1071.4 | MW
iv) Mymensingh area |  |  | 1031 |  | MW | iv) Rangpur area |  |  |  | 709.3 | MW
v) Sylhet area |  |  | 415 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11114.09 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 7 | 05:00 | 67 | Hasnabad | 84.5 | 14:00 | 133 | Nawabganj | 36.4 | 13:00
2 | AKSML | 11.1 | 04:00 | 68 | Hathazari | 60 | 18:00 | 134 | Netrakona | 146 | 17:00
3 | Aftabnagar | 32 | 22:00 | 69 | Hatirjheel | 27 | 13:00 | 135 | New | 46 | 00:00
4 | Agargaon | 79 | 19:00 | 70 | Ishurdi | 53 | 04:00 | 136 | Niamatpur | 88 | 09:00
5 | Agrabad | 42 | 19:00 | 71 | Jaldhaka | 60 | 17:00 | 137 | Noapara | 32 | 18:30
6 | Amnura | 34 | 13:00 | 72 | Jamalpur | 108 | 18:00 | 138 | PHP | 8 | 05:00
7 | Ashuganj | 78 | 14:00 | 73 | Jashore | 111 | 18:00 | 139 | Pabna | 68 | 04:00
8 | BSRM | 191 | 07:00 | 74 | Jhenaidah | 90 | 18:30 | 140 | Palashbari | 96 | 11:00
9 | Bagerhat | 71 | 19:00 | 75 | Joydebpur | 85 | 18:00 | 141 | Panchagarh | 45 | 18:00
10 | Bajitpur | 69 | 13:00 | 76 | Joypurhat | 54 | 09:00 | 142 | Patiya | 6.5 | 19:30
11 | Bakerganj | 10.17 | 20:00 | 77 | Juldah | 11.5 | 00:00 | 143 | Patuakhali | 41 | 21:00
12 | Bakulia | 70 | 21:00 | 78 | KSRM | 16 | 06:00 | 144 | Payra | 28 | 14:00
13 | Banani | 34 | 18:30 | 79 | Kabirpur | 155 | 18:00 | 145 | Postogola | 41 | 14:00
14 | Bangabhaban | 4 | 11:00 | 80 | Kachua | 54 | 18:00 | 146 | Purbachal | 22 | 13:00
15 | Barapukuria | 55 | 13:00 | 81 | Kaliganj | 16 | 18:00 | 147 | Purbasadipur | 122 | 13:00
16 | Barguna | 14 | 18:00 | 82 | Kallyanpur | 87 | 13:00 | 148 | Rahanpur | 27 | 11:00
17 | Barishal | 71 | 14:00 | 83 | Kalurghat | 23 | 14:00 | 149 | Rahim | 11 | 00:00
18 | Barishal-230 | 62 | 18:30 | 84 | Kamrangirchar | 69 | 17:00 | 150 | Rajbari | 56 | 04:00
19 | Baroaulia | 49 | 12:00 | 85 | Kaptai | N/A | N/A | 151 | Rajendrapur | 101 | 18:00
20 | Baroirhat | 42 | 13:00 | 86 | Kasba | 28 | 14:00 | 152 | Rajshahi | 85 | 19:00
21 | Bashundhara | 158 | 19:30 | 87 | Kazla | 91 | 15:00 | 153 | Rajshahi-230 | 48 | 05:00
22 | BashundharaCement | 7 | 01:00 | 88 | Keranigonj | 61 | 13:00 | 154 | Ramganj | 80 | 04:00
23 | Beanibazar | 48 | 18:30 | 89 | Khagrachori | 26 | 18:00 | 155 | Rampur | 30 | 18:30
24 | Benapole | 48 | 13:00 | 90 | Khulna | 34 | 19:00 | 156 | Rangamati | 13 | 18:00
25 | Bhaluka | 110 | 18:00 | 91 | Khulshi | 160 | 22:00 | 157 | Rangpur | 120 | 17:00
26 | Bhandaria | 38 | 21:00 | 92 | Kishoreganj | 104 | 19:00 | 158 | Ruppur | 1.8 | 10:00
27 | Bhangura | 32 | 04:00 | 93 | Kodda | 188 | 04:00 | 159 | SSM | 0 | 00:00
28 | Bheramara(GK) | 44 | 18:00 | 94 | Kulaura | 29 | 14:00 | 160 | Saidpur | 88 | 17:00
29 | Bhulta | 196 | 10:00 | 95 | Kurigram | 62 | 17:00 | 161 | Satkhira | 108 | 18:00
30 | Bog-Sherpur | 54 | 04:00 | 96 | Kushtia | 100 | 13:00 | 162 | Satmasjid | 75 | 14:00
31 | Bogura | 134 | 18:00 | 97 | Laksam | 24 | 13:00 | 163 | Savar | 122 | 13:00
32 | Borhanuddin | 67 | 20:00 | 98 | Lakshmipur | 22 | 12:00 | 164 | SevenRings | 19.8 | 09:00
33 | Brahmanbaria | 97 | 22:00 | 99 | Lalbag | 59 | 12:00 | 165 | ShahCement | 33 | 23:00
34 | Cantonment | 72 | 19:00 | 100 | Lalmonirhat | 46 | 18:00 | 166 | Shahjadpur | 57 | 16:00
35 | Chandina | 13 | 04:00 | 101 | MI_Cement | 16.6 | 23:00 | 167 | Shahjibazar | 100 | 21:00
36 | Chandpur | 66 | 13:00 | 102 | Madanganj | 34 | 00:00 | 168 | Shahmirpur | 31 | 00:00
37 | Chandraghona | 28 | 18:30 | 103 | Madaripur | 78 | 20:00 | 169 | Shariatpur | 61 | 13:00
38 | Chapai | 60 | 13:00 | 104 | Madartek | 64 | 13:00 | 170 | Sherpur | 160 | 18:00
39 | Charsaidpur | 41 | 23:00 | 105 | Madunaghat | 48 | 14:00 | 171 | Shikalbaha | 24 | 16:00
40 | Chauddagram | 60 | 13:00 | 106 | Magura | 45 | 19:00 | 172 | Shitalakhya | 66.9 | 15:00
41 | Chhatak | 24 | 04:00 | 107 | Mahasthangarh | 58 | 09:00 | 173 | Sholosohor | 31 | 14:00
42 | Chowmuhani | 92 | 13:00 | 108 | Maijdee | 36 | 19:00 | 174 | Shyampur | 152 | 13:00
43 | Chuadanga | 79 | 13:00 | 109 | Manikganj | 83 | 04:00 | 175 | Siddhirganj | 101 | 18:30
44 | Coxsbazar | 115 | 18:00 | 110 | Maniknagar | 43 | 22:00 | 176 | Sirajganj | 94 | 17:00
45 | Cumilla(N) | 93 | 12:00 | 111 | Matarbari | 39 | 04:00 | 177 | Sonargaon | 126 | 00:00
46 | Cumilla(S) | 117 | 19:30 | 112 | Matuail | 51 | 14:00 | 178 | Sreemongol | 58 | 18:30
47 | Daganbhuiyan | 24 | 13:00 | 113 | Metrorail_Motijheel | 18 | 13:00 | 179 | Sreepur | 82 | 04:00
48 | Daudkandi | 116 | 20:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Srinagar | 33.8 | 13:00
49 | DhakaUniversity | 50 | 13:00 | 115 | Millgate | 56 | 15:00 | 181 | Sunamganj | 42 | 17:00
50 | Dhamrai | 96 | 04:00 | 116 | Mirpur | 110.5 | 14:00 | 182 | Sylhet | 39 | 22:00
51 | Dhanmondi | 76 | 19:00 | 117 | Mirsorai | 45 | 06:00 | 183 | Sylhet-132 | 75 | 14:00
52 | Dohazari | 74 | 18:30 | 118 | Mirzapur | 39 | 18:00 | 184 | TK | 18 | 18:30
53 | Faridpur | 107 | 19:30 | 119 | Mithapukur | 52 | 04:00 | 185 | Tangail | 148 | 18:00
54 | Fatullah | 75 | 00:00 | 120 | Modern | N/A | N/A | 186 | Taraganj | 20 | 17:00
55 | Fenchuganj | 24 | 13:00 | 121 | Mogbazar | 60 | 13:00 | 187 | Tasnim | 11 | 01:00
56 | Feni | 72 | 13:00 | 122 | Mongla | 27 | 19:00 | 188 | Thakurgaon | 76 | 17:00
57 | GPH | 78 | 06:00 | 123 | Motijheel | 34 | 13:00 | 189 | Tongi | 103 | 17:00
58 | Ghatail | 90 | 03:00 | 124 | Muktagacha | 36 | 13:00 | 190 | Ullahpara | 35 | 03:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 82 | 13:00 | 191 | Ullon | 54 | 19:00
60 | Ghorashal-230 | 90 | 16:00 | 126 | Muradnagar | 29 | 18:30 | 192 | Uttara | 62 | 19:00
61 | Goalpara | 27 | 13:00 | 127 | Mymensingh | 179 | 17:00 | 193 | UttaraNew | 29 | 21:00
62 | Gollamari | 84 | 18:30 | 128 | Naogaon | 114 | 13:00 | 194 | Zigatola | 57 | 14:00
63 | Gopalganj | 83 | 19:00 | 129 | Narail | 45 | 19:00
64 | Gulshan | 66 | 14:00 | 130 | Narinda | 48 | 13:00
65 | Halishahar | 54 | 16:00 | 131 | Narshingdi | 142 | 22:00
66 | HaripurSBU | 118 | 15:00 | 132 | Natore | 114 | 04:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 21-02-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 9972.5 | 0 |  | 9972.5
1:00 | 9418.5 | 0 |  | 9418.5
2:00 | 9126.5 | 0 |  | 9126.5
3:00 | 9346.5 | 0 |  | 9346.5
4:00 | 10487.5 | 0 |  | 10487.5
5:00 | 9505.5 | 0 |  | 9505.5
6:00 | 8277.5 | 0 |  | 8277.5
7:00 | 8171.76 | 0 |  | 8171.76
8:00 | 8658.6 | 0 |  | 8658.6
9:00 | 9331 | 0 |  | 9331
10:00 | 9947.72 | 25 |  | 9973.72
11:00 | 10180.91 | 13 |  | 10194.91
12:00 | 10629.48 | 0 |  | 10629.48
13:00 | 11296.25 | 0 |  | 11296.25
14:00 | 11327.72 | 21 |  | 11349.72
15:00 | 10883.35 | 19 |  | 10903.35
16:00 | 10838.86 | 19 |  | 10858.86
17:00 | 11250.77 | 0 |  | 11250.77
18:00 | 10793.99 | 0 |  | 10793.99
19:00 | 11373.72 | 0 |  | 11373.72
19:30 | 11371.97 | 0 |  | 11371.97
20:00 | 11338.31 | 0 |  | 11338.31
21:00 | 11309.96 | 0 |  | 11309.96
22:00 | 11209.54 | 0 |  | 11209.54
23:00 | 10627.99 | 0 |  | 10627.99
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 21-02-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5330.5 | 4642 | 9972.5 | DAILY GENERATION CURVE
00:30 | 5084.5 | 4611 | 9695.5
01:00 | 4838.5 | 4580 | 9418.5 | 21-02-2026
01:30 | 4735 | 4537.5 | 9272.5
02:00 | 4631.5 | 4495 | 9126.5
02:30 | 4742 | 4494.5 | 9236.5
03:00 | 4852.5 | 4494 | 9346.5
03:30 | 5237 | 4680 | 9917
04:00 | 5621.5 | 4866 | 10487.5
04:30 | 5371 | 4625.5 | 9996.5
05:00 | 5120.5 | 4385 | 9505.5
05:30 | 4677 | 4214.5 | 8891.5
06:00 | 4233.5 | 4044 | 8277.5
06:30 | 4179.96 | 4044.67 | 8224.63
07:00 | 4126.42 | 4045.34 | 8171.76
07:30 | 4335.845 | 4079.335 | 8415.18
08:00 | 4545.27 | 4113.33 | 8658.6
08:30 | 4696.415 | 4298.385 | 8994.8
09:00 | 4847.56 | 4483.44 | 9331
09:30 | 5051.13 | 4588.23 | 9639.36
10:00 | 5254.7 | 4693.02 | 9947.72
10:30 | 5321.485 | 4742.83 | 10064.315
11:00 | 5388.27 | 4792.64 | 10180.91
11:30 | 5538.51 | 4866.685 | 10405.195
12:00 | 5688.75 | 4940.73 | 10629.48
12:30 | 5829.965 | 5132.9 | 10962.865
13:00 | 5971.18 | 5325.07 | 11296.25
13:30 | 5953.775 | 5358.21 | 11311.985
14:00 | 5936.37 | 5391.35 | 11327.72
14:30 | 5876.27 | 5229.265 | 11105.535
15:00 | 5816.17 | 5067.18 | 10883.35
15:30 | 5827.88 | 5033.225 | 10861.105
16:00 | 5839.59 | 4999.27 | 10838.86
16:30 | 5979.85 | 5064.965 | 11044.815
17:00 | 6120.11 | 5130.66 | 11250.77
17:30 | 5925.805 | 5096.575 | 11022.38
18:00 | 5731.5 | 5062.49 | 10793.99
18:30 | 5961.5 | 5122.355 | 11083.855
19:00 | 6191.5 | 5182.22 | 11373.72
19:30 | 6193.5 | 5178.47 | 11371.97
20:00 | 6153.5 | 5184.81 | 11338.31
20:30 | 6165.5 | 5158.635 | 11324.135 |  | Executive Engineer
21:00 | 6177.5 | 5132.46 | 11309.96 |  | Network Operation Division
21:30 | 6131.75 | 5128 | 11259.75
22:00 | 6086 | 5123.54 | 11209.54
22:30 | 5921.5 | 4997.265 | 10918.765
23:00 | 5757 | 4870.99 | 10627.99

## En-Curve
QF-LDC-12
Date | 21-02-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2998 | 1678.5 | 898 | 0 | 102 | 824 | 75 | 3279 | 0 | 0 | 117 | 0 | 0 | 1 | 0 | DAILY ENERGY CURVE
00:30 | 2946.5 | 1586 | 898 | 0 | 100 | 824.5 | 75 | 3153.5 | 0 | 0 | 110 | 0 | 0 | 2 | 0 | 21-02-2026
01:00 | 2895 | 1493.5 | 898 | 0 | 98 | 825 | 75 | 3028 | 0 | 0 | 103 | 0 | 0 | 3 | 0
01:30 | 2818.5 | 1417.5 | 898 | 0 | 97 | 825.5 | 75 | 3030 | 0 | 0 | 101.5 | 0 | 0 | 9.5 | 0 | Energy Generated | 248.7105 |  | MKWHr
02:00 | 2742 | 1341.5 | 898 | 0 | 96 | 826 | 75 | 3032 | 0 | 0 | 100 | 0 | 0 | 16 | 0 | Energy not Served | 0.097 |  | MKWHr
02:30 | 2802.5 | 1372 | 898.5 | 0 | 95 | 826.5 | 75 | 3054 | 0 | 0 | 100.5 | 0 | 0 | 12.5 | 0 | Total Energy Requirement | 248.8075 |  | MKWHr
03:00 | 2863 | 1402.5 | 899 | 0 | 94 | 827 | 75 | 3076 | 0 | 0 | 101 | 0 | 0 | 9 | 0
03:30 | 3076 | 1654.5 | 898.5 | 0 | 101 | 828 | 75 | 3118 | 0 | 17 | 142 | 0 | 0 | 7 | 0
04:00 | 3289 | 1906.5 | 898 | 0 | 108 | 829 | 75 | 3160 | 0 | 34 | 183 | 0 | 0 | 5 | 0
04:30 | 3169.5 | 1743.5 | 898 | 0 | 107 | 828 | 75 | 2985 | 0 | 17 | 167 | 0 | 0 | 6.5 | 0
05:00 | 3050 | 1580.5 | 898 | 0 | 106 | 827 | 75 | 2810 | 0 | 0 | 151 | 0 | 0 | 8 | 0
05:30 | 2746 | 1412 | 898.5 | 0 | 98 | 825.5 | 75 | 2710.5 | 0 | 0 | 114 | 0 | 0 | 12 | 0
06:00 | 2442 | 1243.5 | 899 | 0 | 90 | 824 | 75 | 2611 | 0 | 0 | 77 | 0 | 0 | 16 | 0
06:30 | 2445.5 | 1204.5 | 895.5 | 0 | 83 | 825.5 | 75 | 2598.5 | 13.13 | 0 | 70.5 | 0 | 0 | 13.5 | 0
07:00 | 2449 | 1165.5 | 892 | 0 | 76 | 827 | 75 | 2586 | 26.26 | 0 | 64 | 0 | 0 | 11 | 0
07:30 | 2573 | 1292 | 820.5 | 0 | 78 | 826 | 75 | 2591.5 | 83.68 | 0 | 66 | 0 | 0 | 9.5 | 0
08:00 | 2697 | 1418.5 | 749 | 0 | 80 | 825 | 75 | 2597 | 141.1 | 0 | 68 | 0 | 0 | 8 | 0
08:30 | 2792.5 | 1515.5 | 807.5 | 0 | 83 | 825.33 | 75 | 2600.5 | 217.97 | 0 | 73 | 0 | 0 | 4.5 | 0
09:00 | 2888 | 1612.5 | 866 | 0 | 86 | 825.66 | 75 | 2604 | 294.84 | 0 | 78 | 0 | 0 | 1 | 0
09:30 | 2952.5 | 1676 | 861.5 | 0 | 93 | 826.675 | 75 | 2699.5 | 368.185 | 8.5 | 78 | 0 | 0 | 0.5 | 12.5
10:00 | 3017 | 1739.5 | 857 | 0 | 100 | 827.69 | 75 | 2795 | 441.53 | 17 | 78 | 0 | 0 | 0 | 25
10:30 | 3007 | 1750.5 | 857.5 | 0 | 102 | 827.625 | 75 | 2857.5 | 491.69 | 17 | 78 | 0 | 0 | 0.5 | 19
11:00 | 2997 | 1761.5 | 858 | 0 | 104 | 827.56 | 75 | 2920 | 541.85 | 17 | 78 | 0 | 0 | 1 | 13
11:30 | 3058 | 1791 | 857.5 | 0 | 106 | 826.925 | 75 | 2992.5 | 600.27 | 18.5 | 77.5 | 0 | 0 | 2 | 6.5
12:00 | 3119 | 1820.5 | 857 | 0 | 108 | 826.29 | 75 | 3065 | 658.69 | 20 | 77 | 0 | 0 | 3 | 0
12:30 | 3222.5 | 1870 | 857 | 0 | 110 | 876.895 | 75 | 3191 | 648.47 | 28.5 | 77 | 0 | 0 | 6.5 | 0
13:00 | 3326 | 1919.5 | 857 | 0 | 112 | 927.5 | 75 | 3317 | 638.25 | 37 | 77 | 0 | 0 | 10 | 0
13:30 | 3197.5 | 1933 | 857.5 | 0 | 113 | 981.95 | 75 | 3434 | 585.535 | 44.5 | 79.5 | 0 | 0 | 10.5 | 10.5
14:00 | 3069 | 1946.5 | 858 | 0 | 114 | 1036.4 | 75 | 3551 | 532.82 | 52 | 82 | 0 | 0 | 11 | 21
14:30 | 3045 | 1892.5 | 857.5 | 0 | 109 | 998.84 | 75 | 3507.5 | 471.195 | 54 | 82.5 | 0 | 0 | 12.5 | 20
15:00 | 3021 | 1838.5 | 857 | 0 | 104 | 961.28 | 75 | 3464 | 409.57 | 56 | 83 | 0 | 0 | 14 | 19
15:30 | 3091.5 | 1815 | 857 | 0 | 104 | 969.69 | 75 | 3471 | 323.915 | 59 | 83 | 0 | 0 | 12 | 19
16:00 | 3162 | 1791.5 | 857 | 0 | 104 | 978.1 | 75 | 3478 | 238.26 | 62 | 83 | 0 | 0 | 10 | 19
16:30 | 3236 | 1885 | 857 | 0 | 106 | 1022.575 | 75 | 3479.5 | 163.24 | 96 | 116 | 0 | 0 | 8.5 | 9.5
17:00 | 3310 | 1978.5 | 857 | 0 | 108 | 1067.05 | 75 | 3481 | 88.22 | 130 | 149 | 0 | 0 | 7 | 0
17:30 | 3141.5 | 1842.5 | 857 | 0 | 105 | 1115.205 | 75 | 3470 | 44.175 | 150.5 | 216 | 0 | 0 | 5.5 | 0
18:00 | 2973 | 1706.5 | 857 | 0 | 102 | 1163.36 | 75 | 3459 | 0.13 | 171 | 283 | 0 | 0 | 4 | 0
18:30 | 3126 | 1783.5 | 857 | 0 | 106 | 1164.29 | 75 | 3505 | 0.065 | 170 | 292.5 | 0 | 0 | 4.5 | 0
19:00 | 3279 | 1860.5 | 857 | 0 | 110 | 1165.22 | 75 | 3551 | 0 | 169 | 302 | 0 | 0 | 5 | 0
19:30 | 3246 | 1961.5 | 857 | 0 | 118 | 1167.47 | 75 | 3620 | 0 | 113 | 210 | 0 | 0 | 4 | 0
20:00 | 3269 | 1955.5 | 857 | 0 | 118 | 1176.81 | 75 | 3619 | 0 | 81 | 186 | 0 | 0 | 1 | 0
20:30 | 3305 | 1961 | 857 | 0 | 118 | 1173.635 | 75 | 3600 | 0 | 75 | 159 | 0 | 0 | 0.5 | 0
21:00 | 3341 | 1966.5 | 857 | 0 | 118 | 1170.46 | 75 | 3581 | 0 | 69 | 132 | 0 | 0 | 0 | 0
21:30 | 3315.5 | 1973.25 | 856.5 | 0 | 116 | 1171 | 75 | 3569 | 0 | 60.5 | 123 | 0 | 0 | 0 | 0
22:00 | 3290 | 1980 | 856 | 0 | 114 | 1171.54 | 75 | 3557 | 0 | 52 | 114 | 0 | 0 | 0 | 0
22:30 | 3276 | 1964 | 856.5 | 0 | 111 | 1063.765 | 75 | 3450.5 | 0 | 26 | 96 | 0 | 0 | 0 | 0
23:00 | 3262 | 1948 | 857 | 0 | 108 | 955.99 | 75 | 3344 | 0 | 0 | 78 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 21-02-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 415 | 06:00 | 395 | 13:00 | Madunaghat | 415 | 07:00 | 400 | 14:00
Amtali | 423 | 06:00 | 414 | 13:00 | Meghnaghat | 413 | 05:00 | 395 | 14:00
Ashuganj | 422 | 5:00 | 398 | 16:00 | Payra | 423 | 05:00 | 415 | 12:00
Bhulta | 417 | 05:00 | 393 | 13:00 | Rahanpur | 419 | 01:00 | 405 | 13:00
Bibiana | 420 | 05:00 | 407 | 13:00 | Rampal | 418 | 07:00 | 403 | 14:00
BIPTC | 401 | 03:00 | 391 | 10:00
Bogura | 417 | 06:00 | 398 | 13:00
Gopalganj | 419 | 05:00 | 404 | 13:00
Kaliakoir | 406 | 06:00 | 388 | 13:00
Korerhat | 419 | 06:00 | 402 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 242 | 06:00 | 228 | 13:00 | Jhenaidah | 242 | 02:00 | 229 | 13:00
AKSML | 239 | 05:00 | 227 | 17:00 | Kachua | 240 | 06:00 | 229 | 14:00
Aminbazar | 242 | 04:00 | 228 | 13:00 | Kaliakoir | 243 | 05:00 | 230 | 13:00
Ashuganj | 243 | 05:00 | 232 | 13:00 | Keranigonj | 241 | 05:00 | 227 | 13:00
Ashuganj-400 | 243 | 05:00 | 232 | 13:00 | Khulna(S) | 245 | 06:00 | 230 | 13:00
Baghabari | 243 | 06:00 | 232 | 14:00 | Korerhat | 238 | 03:00 | 229 | 13:00
Barapukuria | 229 | 06:00 | 212 | 15:00 | Madunaghat | 237 | 06:00 | 228 | 13:00
Barapukuria-230 | 229 | 06:00 | 212 | 15:00 | Madunaghat-400 | 238 | 07:00 | 230 | 14:00
Barishal | 239 | 06:00 | 229 | 14:00 | Maniknagar | 242 | 03:00 | 225 | 14:00
Bheramara | 241 | 06:00 | 229 | 13:00 | Meghnaghat | 248 | 04:00 | 237 | 15:00
Bhulta | 242 | 05:00 | 228 | 13:00 | Meghnaghat-400 | 244 | 05:00 | 230 | 14:00
Bibiana | 250 | 21:00 | 234 | 13:00 | Mirsorai | 239 | 07:00 | 229 | 16:00
BIPTC | 244 | 06:00 | 229 | 17:00 | Rajshahi | 241 | 06:00 | 227 | 17:00
Bogura | 243 | 06:00 | 230 | 17:00 | Rampal | 241 | 06:00 | 229 | 14:00
Bogura-400 | 242 | 06:00 | 230 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Borhanuddin | 239 | 05:00 | 233 | 16:00 | Rampura | 241 | 05:00 | 227 | 14:00
BSRM | 238 | 06:00 | 229 | 13:00 | Shikalbaha | 235 | 05:00 | 227 | 13:00
Chowmuhani | N/A | N/A | N/A | N/A | Shyampur | 242 | 06:00 | 229 | 13:00
Cumilla(N) | 241 | 05:00 | 230 | 13:00 | Siddhirganj | 243 | 05:00 | 229 | 13:00
Faridpur | 237 | 06:00 | 226 | 13:00 | Sirajgonj | 246 | 05:00 | 238 | 13:00
Fenchuganj | 246 | 06:00 | 237 | 17:00 | Sreepur | 237 | 05:00 | 227 | 13:00
Feni | 240 | 03:00 | 230 | 13:00 | Tongi | 240 | 04:00 | 228 | 13:00
Ghorashal | 242 | 05:00 | 240 | 00:00
Ghorashal-230 | 240 | 05:00 | 228 | 13:00
Gopalganj | 235 | 06:00 | 226 | 13:00
GPH | 238 | 06:00 | 229 | 13:00
Haripur | 243 | 05:00 | 229 | 14:00
Hasnabad | 243 | 05:00 | 228 | 15:00
Hathazari | 233 | 01:00 | 223 | 10:00
Ishurdi | 245 | 06:00 | 232 | 17:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 141 | 06:00 | 131 | 13:00 | Magura | 140 | 06:00 | 129 | 13:00
Agargaon | 137 | 06:00 | 128 | 14:00 | Mahasthangarh | 138 | 02:00 | 128 | 13:00
Agrabad | 137 | 06:00 | 131 | 16:00 | Maijdee | 134 | 05:00 | 128 | 13:00
AKS | 134 | 06:00 | 129 | 13:00 | Manikganj | 133 | 06:00 | 127 | 16:00
Aminbazar | 142 | 04:00 | 134 | 13:00 | Maniknagar | 136 | 05:00 | 127 | 13:00
Amnura | 140 | 06:00 | 132 | 13:00 | Matarbari | 129 | 06:00 | 119 | 20:00
Ashuganj | 140 | 01:00 | 135 | 15:00 | Matuail | 138 | 07:00 | 131 | 13:00
Bagerhat | 139 | 06:00 | 126 | 13:00 | Metrorail_Motijheel | 136 | 05:00 | 127 | 13:00
Bajitpur | 135 | 01:00 | 127 | 16:00 | Metrorail_Uttara | 135 | 05:00 | 127 | 17:00
Bakerganj | 138 | 05:00 | 134 | 13:00 | Millgate | 137 | 06:00 | 128 | 13:00
Bakulia | 137 | 06:00 | 130 | 17:00 | Mirpur | 141 | 06:00 | 132 | 13:00
Banani | 140 | 05:00 | 130 | 14:00 | Mirzapur | 137 | 05:00 | 128 | 13:00
Bangabhaban | 136 | 03:00 | 127 | 13:00 | Mithapukur | 137 | 02:00 | 126 | 10:00
Barapukuria | 141 | 06:00 | 127 | 15:00 | MI_Cement | 139 | 05:00 | 129 | 13:00
Barguna | 139 | 05:00 | 135 | 13:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 139 | 06:00 | 133 | 13:00 | Mogbazar | 140 | 03:00 | 132 | 13:00
Barishal-230 | 140 | 06:00 | 133 | 13:00 | Mongla | 139 | 06:00 | 128 | 13:00
Baroaulia | 138 | 06:00 | 132 | 13:00 | Motijheel | 136 | 03:00 | 127 | 13:00
Baroirhat | 137 | 06:00 | 131 | 13:00 | Muktagacha | 134 | 18:00 | 120 | 09:00
Bashundhara | 140 | 05:00 | 130 | 14:00 | Munshiganj | 137 | 05:00 | 128 | 17:00
BashundharaCement | 136 | 00:00 | 130 | 13:00 | Muradnagar | 138 | 06:00 | 129 | 14:00
Beanibazar | 134 | 05:00 | 129 | 13:00 | Mymensingh | 132 | 18:30 | 117 | 13:00
Benapole | 137 | 06:00 | 123 | 13:00 | Naogaon | 138 | 23:00 | 125 | 13:00
Bhaluka | 133 | 06:00 | 124 | 13:00 | Narail | 140 | 06:00 | 129 | 13:00
Bhandaria | 139 | 06:00 | 130 | 13:00 | Narinda | 136 | 05:00 | 127 | 13:00
Bhangura | 139 | 02:00 | 132 | 13:00 | Narshingdi | 136 | 05:00 | 127 | 14:00
Bheramara | 140 | 02:00 | 135 | 13:00 | Natore | 138 | 00:00 | 131 | 13:00
Bheramara(GK) | 140 | 02:00 | 134 | 13:00 | Nawabganj | 140 | 03:00 | 130 | 15:00
Bhulta | 132 | 05:00 | 126 | 14:00 | Netrakona | 127 | 02:00 | 110 | 13:00
Bog-Sherpur | 140 | 02:00 | 129 | 17:00 | New | 137 | 06:00 | 128 | 17:00
Bogura | 140 | 06:00 | 131 | 13:00 | Niamatpur | 140 | 05:00 | 134 | 13:00
Bogura-230 | 140 | 01:00 | 132 | 13:00 | Noapara | 139 | 06:00 | 127 | 13:00
Brahmanbaria | 136 | 06:00 | 129 | 13:00 | Pabna | 140 | 02:00 | 133 | 13:00
Cantonment | 136 | 05:00 | 128 | 13:00 | Palashbari | 136 | 02:00 | 124 | 13:00
Chandina | 140 | 05:00 | 133 | 13:00 | Panchagarh | 138 | 00:00 | 126 | 11:00
Chandpur | 135 | 03:00 | 130 | 13:00 | Patiya | 137 | 08:00 | 131 | 13:00
Chandraghona | 138 | 04:00 | 133 | 13:00 | Patuakhali | 137 | 05:00 | 134 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 140 | 01:00 | 133 | 13:00 | Payra | 139 | 05:00 | 136 | 13:00
Charsaidpur | 137 | 05:00 | 124 | 12:00 | PHP | 137 | 06:00 | 130 | 14:00
Chauddagram | 137 | 05:00 | 129 | 13:00 | Postogola | 141 | 05:00 | 131 | 14:00
Chhatak | 133 | 05:00 | 127 | 13:00 | Purbachal | 140 | 05:00 | 130 | 16:00
Chowmuhani | 135 | 04:00 | 127 | 14:00 | Purbasadipur | 132 | 01:00 | 122 | 13:00
Chuadanga | 139 | 05:00 | 119 | 14:00 | Rahanpur | 140 | 00:00 | 135 | 17:00
Coxsbazar | 129 | 07:00 | 118 | 18:00 | Rahanpur-400 | 141 | 00:00 | 135 | 17:00
Cumilla(N) | 140 | 03:00 | 132 | 13:00 | Rahim | 138 | 04:00 | 130 | 14:00
Cumilla(S) | 139 | 02:00 | 123 | 11:00 | Rajbari | 136 | 05:00 | 129 | 14:00
Daganbhuiyan | 135 | 05:00 | 129 | 13:00 | Rajendrapur | 133 | 02:00 | 125 | 13:00
Daudkandi | 136 | 05:00 | 127 | 15:00 | Rajshahi | 140 | 06:00 | 131 | 13:00
DhakaUniversity | 140 | 04:00 | 131 | 13:00 | Rajshahi-230 | 139 | 01:00 | 131 | 13:00
Dhamrai | 140 | 05:00 | 132 | 13:00 | Ramganj | 134 | 06:00 | 127 | 14:00
Dhanmondi | 140.5 | 05:00 | 131.5 | 14:00 | Rampur | 136 | 03:00 | 124 | 12:00
Dohazari | 134 | 07:00 | 128 | 14:00 | Rampura | 140 | 05:00 | 131 | 13:00
Faridpur | 136 | 05:00 | 129 | 13:00 | Rangamati | 137 | 05:00 | 132 | 13:00
Fatullah | 140 | 04:00 | 129 | 13:00 | Rangpur | 137 | 06:00 | 127 | 11:00
Fenchuganj | 139 | 06:00 | 134 | 13:00 | Ruppur | 141 | 05:00 | 135 | 16:00
Feni | 135 | 06:00 | 128 | 13:00 | Saidpur | 136 | 06:00 | 125 | 10:00
Feni-230 | 136 | 04:00 | 129 | 13:00 | Satkhira | 138 | 06:00 | 126 | 17:00
Ghatail | 132 | 05:00 | 118 | 13:00 | Satmasjid | 136 | 03:00 | 128 | 13:00
Ghorashal | 144 | 05:00 | 136 | 17:00 | Savar | 140 | 05:00 | 132 | 13:00
Goalpara | 141 | 03:00 | 130 | 13:00 | SevenRings | 144 | 05:00 | 137 | 13:00
Gollamari | 141 | 06:00 | 131 | 13:00 | ShahCement | 137 | 06:00 | 129 | 14:00
Gopalganj | 139 | 06:00 | 132 | 13:00 | Shahjadpur | 142 | 01:00 | 136 | 13:00
Gopalganj-400 | 140 | 05:00 | 132 | 00:00 | Shahjibazar | 135 | 04:00 | 129 | 16:00
Gulshan | 140 | 05:00 | 131 | 13:00 | Shahmirpur | 137 | 05:00 | 132 | 13:00
Halishahar | 137 | 06:00 | 131 | 14:00 | Shariatpur | 139 | 03:00 | 132 | 13:00
Haripur | 138 | 05:00 | 131 | 13:00 | Sherpur | 126 | 05:00 | 110 | 08:00
HaripurSBU | 138 | 05:00 | 131 | 13:00 | Shikalbaha | 124 | 00:00 | 121 | 18:00
Hasnabad | 140 | 04:00 | 131 | 13:00 | Shikalbaha-230 | 138 | 06:00 | 132 | 11:00
Hathazari | 138 | 06:00 | 133 | 13:00 | Shitalakhya | 140 | 07:00 | 129 | 13:00
Hatirjheel | 140 | 05:00 | 131 | 13:00 | Sholosohor | 137 | 01:00 | 132 | 17:00
Ishurdi | 143 | 06:00 | 136 | 17:00 | Shyampur | 139 | 07:00 | 132 | 14:00
Jaldhaka | 135 | 06:00 | 123 | 10:00 | Shyampur-230 | 140 | 04:00 | 131 | 13:00
Jamalpur | 130 | 05:00 | 114 | 08:00 | Siddhirganj | 138 | 05:00 | 131 | 13:00
Jashore | 138 | 06:00 | 124 | 13:00 | Sirajganj | 137 | 00:00 | 125 | 17:00
Jhenaidah | 142 | 06:00 | 121 | 13:00 | Sonargaon | 134 | 18:00 | 129 | 14:00
Jhenaidah-230 | 142 | 06:00 | 132 | 13:00 | Sreemongol | 135 | 06:00 | 130 | 15:00
Joydebpur | 141 | 05:00 | 134 | 13:00 | Sreepur | 136 | 05:00 | 129 | 12:00
Joypurhat | 134 | 01:00 | 121 | 13:00 | Srinagar | 141 | 06:00 | 131 | 13:00
Juldah | 136 | 03:00 | 131 | 13:00 | SSM | 140 | 00:00 | 135 | 13:00
Kabirpur | 140 | 03:00 | 123 | 22:00 | Sunamganj | 132 | 06:00 | 126 | 16:00
Kachua | 137 | 06:00 | 130 | 14:00 | Sylhet | 135 | 07:00 | 130 | 13:00
Kaliakoir | 143 | 06:00 | 134 | 13:00 | Sylhet-132 | 134 | 01:00 | 130 | 16:00
Kaliganj | 142 | 06:00 | 132 | 13:00 | Tangail | 133 | 05:00 | 122 | 13:00
Kallyanpur | 142 | 04:00 | 133 | 13:00 | Taraganj | 136 | 06:00 | 124 | 17:00
Kalurghat | 138 | 04:00 | 133 | 13:00 | Tasnim | 137 | 06:00 | 129 | 14:00
Kamrangirchar | 140 | 05:00 | 130 | 13:00 | Thakurgaon | 137 | 06:00 | 125 | 09:00
Kaptai | N/A | N/A | N/A | N/A | TK | 137 | 04:00 | 133 | 13:00
Kasba | 137 | 02:00 | 129 | 14:00 | Tongi | 137 | 04:00 | 130 | 13:00
Kazla | 136 | 06:00 | 126 | 16:00 | Ullahpara | 139 | 05:00 | 133 | 09:00
Keranigonj | 141 | 06:00 | 131 | 13:00 | Ullon | 139 | 02:00 | 130 | 16:00
Khagrachori | 137 | 07:00 | 131 | 13:00 | Uttara | 136 | 06:00 | 128 | 13:00
Khulna | 140 | 04:00 | 130 | 13:00 | UttaraNew | 135 | 05:00 | 127 | 17:00
Khulna(S) | 141 | 06:00 | 131 | 13:00 | Zigatola | 141 | 06:00 | 131 | 13:00
Khulshi | 136 | 06:00 | 129 | 15:00
Kishoreganj | 133 | 04:00 | 125 | 13:00
Kodda | 139 | 18:00 | 127 | 16:00
Korerhat | 138 | 03:00 | 132 | 17:00
KSRM | 137 | 03:00 | 132 | 13:00
Kulaura | 138 | 05:00 | 134 | 13:00
Kurigram | 133 | 06:00 | 119 | 13:00
Kushtia | 137 | 04:00 | 127 | 13:00
Laksam | 136 | 04:00 | 130 | 14:00
Lakshmipur | 135 | 06:00 | 128 | 13:00
Lalbag | 140 | 05:00 | 130 | 11:00
Lalmonirhat | 134 | 06:00 | 123 | 12:00
Madanganj | 136 | 00:00 | 130 | 13:00
Madaripur | 139 | 06:00 | 133 | 16:00
Madartek | 139 | 03:00 | 130 | 13:00
Madunaghat | 138 | 03:00 | 133 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division