## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 24-02-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-02-2026 | during | 24-02-2026 | during | 24-02-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Demand "0"MW due to gas restriction by Titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 312 | 324 | 412 | 412 | 412 | 412 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 270 | 300 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 9 | 16 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 1 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 19 | 33 | 33 | 29 | 29 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 20 | 17 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 60 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 34 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 46 | 20 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 14 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 400 | 400 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 350 | 340 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 90 | 160 | 160 | 160 | 160 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1562 | 1679 | 5945.22 | 5915.22 | 3153.75 | 3141.75
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 2 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 75 | 75 | 75 | 75 | 75 | 75 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 218 | 220 | 220 | 220 | 220 | 220 | Plant availability less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 30 | 105 | 105 | 95 | 95 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 32 | 32 | 32 | 32 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 68 | 68 | 68 | 68 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 4 | 34 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.43 | 0 | 3.35 | 0 | 3.35 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 975 | 1161 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 6 | 7 | 6 | 29 | 6 | 29 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 520 | 905 | 905 | 905 | 905 | 905 | ps availability is less
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1823.43 | 2468 | 3788.21 | 3804.86 | 3255.85 | 3272.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 199 | 219 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 335 | 320 | 353.35 | 353.35 | 317.35 | 317.35 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 340 | 320 | 318.81 | 318.81 | 318.81 | 318.81 | FGMO ON
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 230 | 230 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 10 | 10 | 41.65 | 41.65 | 41.65 | 41.65 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 0 | 195 | 195 | 100 | 100 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 42 | 42 | 42 | 42 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 99 | 102 | 163 | 163 | 110 | 110 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 6 | 17 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 140 | 126 | 84 | 80 | 146 | 146 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 2 | 15 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 58 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1268 | 1200 | 2746.51 | 2682.51 | 2295.01 | 2235.01
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-02-2026 | during | 24-02-2026 | during | 24-02-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 31 | 33 | 157.5 | 157.5 | 70 | 70 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 28 | 50 | 50 | 20 | 50 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 115 | 60 | 115 | 60 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 42 | 0 | 45.12 | 0 | 45.12 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0.36 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 153.36 | 199 | 391.22 | 399 | 220.22 | 258
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 41 | 42 | 42 | 42 | 42 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 53 | 53 | 53 | 53 | 53 | 53 | GT3,4 are not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 140 | 156 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 86 | 86 | 86 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 98 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 22 | 22 | 25 | 25 | 21 | 21 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 390 | 374 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1030 | 1135 | 1215 | 1215 | 1110 | 1110
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 861 | 861 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 319 | 260 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 78 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1020 | 1088 | 0 | 0 | 1070 | 1070 | FGMO, plant availability zero
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2278 | 2209 | 2352 | 2272 | 2667.1 | 2587.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 130 | 130 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 515 | 530 | 622 | 622 | 622 | 622 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 15 | 15 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 277 | 273 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.48 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2700.36 | 1142.48 | 1153 | 1540 | 1539 | 1405 | 1404
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 40.85 | 0 | 50 | 0 | 50 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 189 | 172 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 30 | 30 | 30 | 30 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.39 | 0 | 5.45 | 0 | 5.45 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1321 | 1443 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 42.64 | 0 | 54 | 0 | 54 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 69 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2079.88 | 2029 | 3128.32 | 2918.87 | 3018.54 | 2809.09
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 49 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.4 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 175 | 0 | 146.25 | 0 | 146.25 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 212.4 | 84 | 443.45 | 262 | 409.45 | 228
System Total |  |  |  |  | 28823.2 | 28385.703 | 11549.55 | 12156 | 21549.93 | 21008.46 | 17534.92 | 17045.45
Forecast Scenario (24-02-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 10910 |  | 0 |  | 10910
|  |  |  | 1:00 | 10330 |  | 0 |  | 10330
|  |  |  | 2:00 | 9990 |  | 0 |  | 9990
|  |  |  | 3:00 | 10260 |  | 0 |  | 10260
|  |  |  | 4:00 | 11090 |  | 0 |  | 11090
|  |  |  | 5:00 | 9900 |  | 0 |  | 9900
|  |  |  | 6:00 | 9030 |  | 0 |  | 9030
|  |  |  | 7:00 | 9230 |  | 0 |  | 9230
|  |  |  | 8:00 | 10010 |  | 0 |  | 10010
|  |  |  | 9:00 | 10750 |  | 0 |  | 10750
|  |  |  | 10:00 | 11140 |  | 0 |  | 11140
|  |  |  | 11:00 | 11480 |  | 0 |  | 11480
|  |  |  | 12:00 | 11660 |  | 0 |  | 11660
|  |  |  | 13:00 | 12350 |  | 0 |  | 12350
|  |  |  | 14:00 | 12600 |  | 0 |  | 12600
|  |  |  | 15:00 | 12140 |  | 0 |  | 12140
|  |  |  | 16:00 | 12170 |  | 0 |  | 12170
|  |  |  | 17:00 | 12400 |  | 0 |  | 12400
|  |  |  | 18:00 | 11830 |  | 0 |  | 11830
|  |  |  | 18:30 | 12000 |  | 0 |  | 12000
|  |  |  | 19:00 | 12200 |  | 0 |  | 12200
|  |  |  | 19:30 | 12250 |  | 0 |  | 12250
|  |  |  | 20:00 | 12230 |  | 0 |  | 12230
|  |  |  | 21:00 | 12210 |  | 0 |  | 12210
|  |  |  | 22:00 | 12010 |  | 0 |  | 12010
|  |  |  | 23:00 | 11600 |  | 0 |  | 11600
Probable Maximum Temperature: |  |  | 31.40°C
Probable Maximum Demand at Day Peak: |  |  | 11660.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12250.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12250.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 269.52 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:40 hrs on 24-02-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 23-02-2026
Power Supply Scenario
| Day Peak Generation |  |  | 11549.55 | MW | 12:00 Hr. | Energy Generated |  |  | 271.1699 |  | MKWHr.
| Day Peak Demand |  |  | 11559.55 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.157 |  | MKWHr.
| Evening Peak Generation |  |  | 12156 | MW | 19:30 Hr. | Energy Demand |  |  | 271.3269 |  | MKWHr.
| Evening Peak Demand |  |  | 12156 | MW | 19:30 Hr. | Maximum Temperature |  |  | 31.8 |  | °C
| Minimum Generation of the Day |  |  | 8932 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 858.8 |  | MMCFD
| Maximum Generation of the Day |  |  | 12502.02 | MW | 14:00 Hr. | Production Cost per KWHr |  |  | 5.4147 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.2316 | 0 | 3.9516 | 0 | 0 | 0.13944 | 0 | 0 | 37.3226 | Gas | 121.0428 | Gas | 416199345.6887
| Chattogram Zone |  |  | 5.7611 | 42.2618 | 0.85537 | 0 | 1.7725 | 0.15032 | 0 | 0.20976 | 51.0109 | Coal | 83.818 | Coal | 546928166.5409
| Cumilla Zone |  |  | 25.5257 | 0 | 0.68496 | 0 | 0 | 0.38076 | 2.8426 | 0 | 29.434 | HFO | 8.8229 | HFO | 146104392.03
| Mymensingh Zone |  |  | 0.93792 | 0 | 2.3978 | 0 | 0 | 0.25114 | 0 | 0 | 3.5869 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.2275 | 0 | 0 | 0 | 0 | 0.057677 | 0 | 0 | 26.2851 | Hydro | 1.7725 | Hydro | 177250
| Khulna Zone |  |  | 7.0433 | 23.12 | 0 | 0 | 0 | 0.52056 | 20.6138 | 0 | 51.2977 | Solar | 3.9734 | Solar | 64621020.146
| Barishal Zone |  |  | 8.3948 | 17.8541 | 0 | 0 | 0 | 0.003135 | 0 | 0 | 26.252 | Import | 51.5305 | Import | 291176582.44
| Rajshahi Zone |  |  | 13.9209 | 0 | 0 | 0 | 0 | 1.0642 | 28.0741 | 0 | 43.0591 | Wind | 0.20976 | Wind | 3085569.6
| Rangpur Zone |  |  | 0 | 0.58211 | 0.93317 | 0 | 0 | 1.4063 | 0 | 0 | 2.9215
| Total |  |  | 121.0428 | 83.818 | 8.8229 | 0 | 1.7725 | 3.9734 | 51.5305 | 0.20976 | 271.1699
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 416199345.6887 |  | Hydro | 177250
|  |  |  | Coal | 546928166.5409 |  | Solar | 64621020.146
|  |  |  | HFO | 146104392.03 |  | Import | 291176582.44
|  |  |  | HSD | 0 |  | Wind | 3085569.6
[5 empty] | Total: | 146,82,92,326 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.6138 | Peak Hr Flow | 861.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 26680002.24 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 28.0741 | Peak Hr Flow | 1443.00 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1873 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.8426 | Peak Hr Flow | 126.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2368 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 51.5305 | Peak Hr Flow | 2430.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4554
|  |  |  | Chattogram |  | 0 |  | 1242
|  |  |  | Cumilla |  | 0 |  | 1000
|  |  |  | Mymensingh |  | 0 |  | 1017
|  |  |  | Sylhet |  | 0 |  | 394
|  |  |  | Khulna |  | 0 |  | 1346
|  |  |  | Barishal |  | 0 |  | 333
|  |  |  | Rajshahi |  | 0 |  | 1090
|  |  |  | Rangpur |  | 0 |  | 716
|  |  |  | Total |  | 0 |  | 11692
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:40 | 16:38 | GPH 230/33kV S/S ABUL KHAIR Scheduled S/D Due to Insulator Disk Changing
| 09:02 | 09:34 | Sylhet 132/33kV S/S T2 HT Tripped showing E/F relays Due to 33 KV Batteshwar & IC-1
Feeder Fault
| 09:02 | 09:35 | Sylhet 132/33kV S/S T2 LT Tripped showing E/F relays Due to 33 KV Batteshwar and IC-2
Fault
| 09:07 | 15:09 | Madunaghat 132/33kV S/S TR-1(507T) HT Scheduled S/D Due to Due to oil centrifuging
| 09:07 | 16:22 | Madunaghat 132/33kV S/S TR-1(507T) LT Scheduled S/D
| 09:42 | 19:13 | Sylhet-Sylhet (South) 132KV Ckt-2 Project Work S/D from Sylhet 132/33kV end Due to SD by
Sylhet (South) Grid SS due to LILO Works
|  | 10:02 | Fenchuganj -Sylhet 132kV Ckt-1 is restored.
| 10:20 | 11:13 | Bhangura 132/33kV S/S Tr-1(403T) LT Forced S/D Due to Red hot removing | [7 empty] | 10.0MW load
interrup.
| 10:21 | 11:12 | Bhangura 132/33kV S/S Tr-1(403T) HT Forced S/D Due to Red hot removing | [7 empty] | 10.0MW load
interrup.
| 11:15 |  | Madunaghat-Sikalbaha 132kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end Due to
Maintenance work at Shikalbaha end.
| 12:00 |  | Day Peak Generation: 11546 MW.
| 12:06 | 14:10 | Cumilla(S) 132/33kV S/S TR-1 LT Scheduled S/D Due to Conservator oil leakage maintenance
| 12:07 | 14:10 | Cumilla(S) 132/33kV S/S TR-1 HT Scheduled S/D
| 12:30 | 17:10 | Jamalpur 132/33kV S/S T-3 HT Scheduled S/D Due to Project work
| 12:30 | 17:10 | Jamalpur 132/33kV S/S T-3 LT Scheduled S/D Due to Project work
|  | 12:50 | Sirajganj 132/33kV S/S Solar Park 2 is restored.
| 13:02 | 13:12 | Sylhet 132/33kV S/S T2 LT Tripped showing E/F relays Due to 33 KV Batteshwar Feeder Fault
| 13:02 | 13:11 | Sylhet 132/33kV S/S T2 HT Tripped showing E/F relays Due to 33 KV Batteshwar Feeder Fault
| 15:49 | 16:07 | Kalurghat 132/33kV S/S TRFO-01(506T) LT Forced S/D Due to Tap change | [7 empty] | 5.0MW load
interrup.
| 15:55 |  | Bagabari -Bhangura 132 KV-2 S/D.
| 19:30 |  | Evening peak generation 12156 MW
| 06:38 | 07:11 | Mymensingh 132/33kV S/S T-1 Bus Scheduled S/D | [7 empty] | 25.0MW load
interrup.
| 07:40 |  | Bashundhara-Tongi 132 kV Ckt-1 Project Work S/D from Tongi 230/132/33kV end.
| 07:55 |  | Bakulia-Sikalbaha 132 kV Ckt-2 Scheduled S/D from Shikalbaha 230/132kV end Due to Gas
Purication work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 23-02-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0"MW due to gas restriction by Titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 324 | 7938000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 5338302 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 16 | 257040 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 61440 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 252484 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 105870 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 443400 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 17 | 457920 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 274560 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 36633 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 60 | 738864 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 318720 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 20 | 519840 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 139438 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 135720 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 10034090.91 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 340 | 9019900 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 90 | 1250400 | -
Dhaka Area Total |  |  |  |  | 6668.974 | 1679 | 37322621.91
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | U#1 Under maintenance, U#2 Running
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 128520 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 243840 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 75 | 1772500 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5277751 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 30 | 380545 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 42990 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 43200 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 34 | 483360 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21805 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 92000 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 52800 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1161 | 23869089 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 7 | 209760 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 905 | 18392727.27 | ps availability is less
Chattogram Area Total |  |  |  |  | 4898.863 | 2468 | 51010887.27
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 219 | 4927000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 320 | 8214300 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 320 | 7996000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 10 | 367704 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 133818 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1127074 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 102 | 2302241 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 362400 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 126 | 2842560 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 457600 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 15 | 322560 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 380755 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1200 | 29434012
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 33 | 937920 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12300 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 28 | 518400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 115 | 1612800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 238840 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 52080 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 214560 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 199 | 3586900
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 57677 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 986000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 53 | 1347000 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 156 | 3566045.45 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1581120 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 98 | 2002220 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 22 | 430080 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7165000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 374 | 9150000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1135 | 26285142.45
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 861 | 20613818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 260 | 7043328 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 520560 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1088 | 23120000 | plant availability zero
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2209 | 51297706
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 3011000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 530 | 12029090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5383790 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 273 | 5825000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3135 | -
Barishal Area Total |  |  |  |  | 2700.36 | 1153 | 26252015.91
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 223144 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 172 | 4284273 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9636581 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | machine problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 25680 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1443 | 28074088 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 270000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 545330 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2029 | 43059096
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 582109 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 474240 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 32282.88 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 458926 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 208303 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1165680 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 84 | 2921540.88
Eastern Grid Total |  |  |  |  | 17400.108 | 6681 | 147639563.63
Western Grid Total |  |  |  |  | 10985.595 | 5475 | 123530358.79
National Grid Total |  |  |  |  | 28385.703 | 12156 | 271169922.42
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 23-02-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8207.81 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3485.8 | MW
i) Dhaka area |  |  | 4554.41 |  | MW | i) Khulna area |  |  |  | 1346 | MW
ii) Chattogram area |  |  | 1242.5 |  | MW | ii) Barishal area |  |  |  | 333.4 | MW
iii) Cumilla area |  |  | 1000 |  | MW | iii) Rajshahi area |  |  |  | 1090.4 | MW
iv) Mymensingh area |  |  | 1017 |  | MW | iv) Rangpur area |  |  |  | 716 | MW
v) Sylhet area |  |  | 393.9 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11693.61 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 8 | 00:00 | 67 | Hasnabad | 81 | 17:00 | 133 | Nawabganj | 34.2 | 13:00
2 | AKSML | 14 | 22:00 | 68 | Hathazari | 63 | 13:00 | 134 | Netrakona | 141 | 17:00
3 | Aftabnagar | 32 | 13:00 | 69 | Hatirjheel | 34 | 13:00 | 135 | New | 65.4 | 14:00
4 | Agargaon | 91 | 13:00 | 70 | Ishurdi | 57 | 04:00 | 136 | Niamatpur | 91 | 09:00
5 | Agrabad | 50 | 13:00 | 71 | Jaldhaka | 59 | 18:00 | 137 | Noapara | 37 | 19:00
6 | Amnura | 32 | 09:00 | 72 | Jamalpur | 106 | 09:00 | 138 | PHP | 9 | 13:00
7 | Ashuganj | 75 | 00:00 | 73 | Jashore | 112 | 18:00 | 139 | Pabna | 75 | 17:00
8 | BSRM | 194 | 03:00 | 74 | Jhenaidah | 77 | 13:00 | 140 | Palashbari | 91 | 14:00
9 | Bagerhat | 66 | 18:30 | 75 | Joydebpur | 121 | 14:00 | 141 | Panchagarh | 44 | 17:00
10 | Bajitpur | 72 | 18:00 | 76 | Joypurhat | 55 | 10:00 | 142 | Patiya | 7 | 18:30
11 | Bakerganj | 9.9 | 21:00 | 77 | Juldah | 14 | 10:00 | 143 | Patuakhali | 41 | 21:00
12 | Bakulia | 74 | 11:00 | 78 | KSRM | 33 | 15:00 | 144 | Payra | 28 | 18:30
13 | Banani | 46 | 13:00 | 79 | Kabirpur | 225 | 17:00 | 145 | Postogola | 45 | 13:00
14 | Bangabhaban | 14 | 10:00 | 80 | Kachua | 62 | 19:30 | 146 | Purbachal | 24 | 12:00
15 | Barapukuria | 65 | 13:00 | 81 | Kaliganj | 20 | 18:30 | 147 | Purbasadipur | 117 | 13:00
16 | Barguna | 14 | 18:00 | 82 | Kallyanpur | 93 | 13:00 | 148 | Rahanpur | 27 | 12:00
17 | Barishal | 79 | 14:00 | 83 | Kalurghat | 35 | 14:00 | 149 | Rahim | 42 | 15:00
18 | Barishal-230 | 68 | 18:30 | 84 | Kamrangirchar | 79 | 17:00 | 150 | Rajbari | 62 | 04:00
19 | Baroaulia | 52 | 14:00 | 85 | Kaptai | N/A | N/A | 151 | Rajendrapur | 128 | 14:00
20 | Baroirhat | 58 | 13:00 | 86 | Kasba | 25 | 13:00 | 152 | Rajshahi | 88 | 18:00
21 | Bashundhara | 172 | 13:00 | 87 | Kazla | 102 | 13:00 | 153 | Rajshahi-230 | 56 | 18:00
22 | BashundharaCement | 7 | 00:00 | 88 | Keranigonj | 75 | 19:30 | 154 | Ramganj | 80 | 13:00
23 | Beanibazar | 48 | 12:00 | 89 | Khagrachori | 26 | 18:30 | 155 | Rampur | 32 | 18:30
24 | Benapole | 48 | 09:00 | 90 | Khulna | 39 | 19:00 | 156 | Rangamati | 15 | 18:30
25 | Bhaluka | 124 | 16:00 | 91 | Khulshi | 176 | 14:00 | 157 | Rangpur | 128 | 18:00
26 | Bhandaria | 37 | 19:30 | 92 | Kishoreganj | 110 | 18:00 | 158 | Ruppur | 2.4 | 10:00
27 | Bhangura | 34 | 04:00 | 93 | Kodda | 251 | 09:00 | 159 | SSM | 12 | 01:00
28 | Bheramara(GK) | 47 | 18:00 | 94 | Kulaura | 29 | 14:00 | 160 | Saidpur | 102 | 17:00
29 | Bhulta | 217 | 19:30 | 95 | Kurigram | 64 | 17:00 | 161 | Satkhira | 114 | 18:00
30 | Bog-Sherpur | 66 | 04:00 | 96 | Kushtia | 114 | 13:00 | 162 | Satmasjid | 81 | 14:00
31 | Bogura | 125 | 18:00 | 97 | Laksam | 26 | 18:30 | 163 | Savar | 204 | 15:00
32 | Borhanuddin | 66 | 04:00 | 98 | Lakshmipur | 17 | 18:30 | 164 | SevenRings | 6.21 | 19:30
33 | Brahmanbaria | 96 | 21:00 | 99 | Lalbag | 68 | 13:00 | 165 | ShahCement | 36 | 00:00
34 | Cantonment | 80 | 14:00 | 100 | Lalmonirhat | 56 | 17:00 | 166 | Shahjadpur | 67 | 17:00
35 | Chandina | 18 | 10:00 | 101 | MI_Cement | 16.5 | 01:00 | 167 | Shahjibazar | 101 | 22:00
36 | Chandpur | 54 | 13:00 | 102 | Madanganj | 37 | 21:00 | 168 | Shahmirpur | 44 | 15:00
37 | Chandraghona | 28 | 18:00 | 103 | Madaripur | 77 | 19:30 | 169 | Shariatpur | 59 | 13:00
38 | Chapai | 70 | 03:00 | 104 | Madartek | 62 | 21:00 | 170 | Sherpur | 150 | 18:00
39 | Charsaidpur | 41 | 03:00 | 105 | Madunaghat | 39 | 17:00 | 171 | Shikalbaha | 23 | 13:00
40 | Chauddagram | 61 | 14:00 | 106 | Magura | 46 | 19:00 | 172 | Shitalakhya | 77.4 | 15:00
41 | Chhatak | 28 | 23:00 | 107 | Mahasthangarh | 56 | 09:00 | 173 | Sholosohor | 40 | 14:00
42 | Chowmuhani | 98 | 19:00 | 108 | Maijdee | 34 | 19:30 | 174 | Shyampur | 136 | 06:00
43 | Chuadanga | 81 | 18:00 | 109 | Manikganj | 97 | 21:00 | 175 | Siddhirganj | 120 | 14:00
44 | Coxsbazar | 119 | 17:00 | 110 | Maniknagar | 48 | 18:00 | 176 | Sirajganj | 96 | 09:00
45 | Cumilla(N) | 102 | 14:00 | 111 | Matarbari | 40 | 18:30 | 177 | Sonargaon | 148 | 11:00
46 | Cumilla(S) | 142 | 13:00 | 112 | Matuail | 62 | 15:00 | 178 | Sreemongol | 56 | 21:00
47 | Daganbhuiyan | 32 | 13:00 | 113 | Metrorail_Motijheel | 25 | 18:00 | 179 | Sreepur | 106 | 14:00
48 | Daudkandi | 123 | 04:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Srinagar | 34.2 | 18:00
49 | DhakaUniversity | 78 | 13:00 | 115 | Millgate | 86 | 14:00 | 181 | Sunamganj | 40 | 17:00
50 | Dhamrai | 110 | 17:00 | 116 | Mirpur | 125 | 14:00 | 182 | Sylhet | 37 | 00:00
51 | Dhanmondi | 97 | 13:00 | 117 | Mirsorai | 45 | 03:00 | 183 | Sylhet-132 | 106 | 17:00
52 | Dohazari | 78 | 21:00 | 118 | Mirzapur | 41 | 13:00 | 184 | TK | 16 | 21:00
53 | Faridpur | 118 | 19:00 | 119 | Mithapukur | 52 | 04:00 | 185 | Tangail | 146 | 13:00
54 | Fatullah | 100 | 15:00 | 120 | Modern | N/A | N/A | 186 | Taraganj | 22 | 17:00
55 | Fenchuganj | 30 | 21:00 | 121 | Mogbazar | 87.5 | 14:00 | 187 | Tasnim | 12 | 11:00
56 | Feni | 70 | 13:00 | 122 | Mongla | 46 | 20:00 | 188 | Thakurgaon | 76 | 17:00
57 | GPH | 76 | 01:00 | 123 | Motijheel | 42 | 13:00 | 189 | Tongi | 160 | 12:00
58 | Ghatail | 80 | 18:00 | 124 | Muktagacha | 33 | 14:00 | 190 | Ullahpara | 39 | 03:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 81 | 14:00 | 191 | Ullon | 49 | 00:00
60 | Ghorashal-230 | 104 | 17:00 | 126 | Muradnagar | 27 | 18:00 | 192 | Uttara | 68 | 13:00
61 | Goalpara | 30 | 13:00 | 127 | Mymensingh | 191 | 18:00 | 193 | UttaraNew | 31 | 17:00
62 | Gollamari | 88 | 19:00 | 128 | Naogaon | 120 | 13:00 | 194 | Zigatola | 60 | 13:00
63 | Gopalganj | 86 | 19:00 | 129 | Narail | 45 | 19:00
64 | Gulshan | 90 | 13:00 | 130 | Narinda | 60 | 13:00
65 | Halishahar | 77 | 12:00 | 131 | Narshingdi | 146 | 19:00
66 | HaripurSBU | 132 | 12:00 | 132 | Natore | 120 | 04:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 23-02-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 10819.16 | 0 |  | 10819.16
1:00 | 10236 | 0 |  | 10236
2:00 | 9896 | 0 |  | 9896
3:00 | 10164 | 0 |  | 10164
4:00 | 10992 | 0 |  | 10992
5:00 | 9800 | 0 |  | 9800
6:00 | 8932 | 0 |  | 8932
7:00 | 9134.78 | 0 |  | 9134.78
8:00 | 9909.79 | 0 |  | 9909.79
9:00 | 10659.13 | 0 |  | 10659.13
10:00 | 11029.41 | 15 |  | 11045.09
11:00 | 11377.71 | 10 |  | 11387.71
12:00 | 11549.55 | 10 |  | 11559.55
13:00 | 12233.87 | 15 |  | 12249.87
14:00 | 12502.02 | 0 |  | 12502.02
15:00 | 12044.51 | 0 |  | 12044.51
16:00 | 12029.92 | 47 |  | 12078.92
17:00 | 12239.97 | 60 |  | 12302.97
18:00 | 11734.3 | 0 |  | 11734.3
19:00 | 12106 | 0 |  | 12106
19:30 | 12156 | 0 |  | 12156
20:00 | 12138 | 0 |  | 12138
21:00 | 12113 | 0 |  | 12113
22:00 | 11911.5 | 0 |  | 11911.5
23:00 | 11408 | 0 |  | 11408
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 23-02-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6058 | 4761.16 | 10819.16 | DAILY GENERATION CURVE
00:30 | 5939.5 | 4588.08 | 10527.58
01:00 | 5821 | 4415 | 10236 | 23-02-2026
01:30 | 5715.5 | 4350.5 | 10066
02:00 | 5610 | 4286 | 9896
02:30 | 5735.5 | 4294.5 | 10030
03:00 | 5861 | 4303 | 10164
03:30 | 6087 | 4491 | 10578
04:00 | 6313 | 4679 | 10992
04:30 | 5817.5 | 4578.5 | 10396
05:00 | 5322 | 4478 | 9800
05:30 | 5079 | 4287 | 9366
06:00 | 4836 | 4096 | 8932
06:30 | 4859.38 | 4174.01 | 9033.39
07:00 | 4882.76 | 4252.02 | 9134.78
07:30 | 5117.175 | 4405.11 | 9522.285
08:00 | 5351.59 | 4558.2 | 9909.79
08:30 | 5562.6 | 4721.86 | 10284.46
09:00 | 5773.61 | 4885.52 | 10659.13
09:30 | 5741.11 | 5103.16 | 10844.27
10:00 | 5708.61 | 5320.8 | 11029.41
10:30 | 5750.74 | 5452.82 | 11203.56
11:00 | 5792.87 | 5584.84 | 11377.71
11:30 | 5814.83 | 5648.8 | 11463.63
12:00 | 5836.79 | 5712.76 | 11549.55
12:30 | 6117.58 | 5774.13 | 11891.71
13:00 | 6398.37 | 5835.5 | 12233.87
13:30 | 6530.365 | 5837.58 | 12367.945
14:00 | 6662.36 | 5839.66 | 12502.02
14:30 | 6603.235 | 5670.03 | 12273.265
15:00 | 6544.11 | 5500.4 | 12044.51
15:30 | 6610.595 | 5426.62 | 12037.215
16:00 | 6677.08 | 5352.84 | 12029.92
16:30 | 6804.85 | 5330.095 | 12134.945
17:00 | 6932.62 | 5307.35 | 12239.97
17:30 | 6736.46 | 5250.675 | 11987.135
18:00 | 6540.3 | 5194 | 11734.3
18:30 | 6619.15 | 5301 | 11920.15
19:00 | 6698 | 5408 | 12106
19:30 | 6681 | 5475 | 12156
20:00 | 6633 | 5505 | 12138
20:30 | 6624.5 | 5501 | 12125.5 |  | Executive Engineer
21:00 | 6616 | 5497 | 12113 |  | Network Operation Division
21:30 | 6512.25 | 5500 | 12012.25
22:00 | 6408.5 | 5503 | 11911.5
22:30 | 6307.25 | 5352.5 | 11659.75
23:00 | 6206 | 5202 | 11408

## En-Curve
QF-LDC-12
Date | 23-02-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3090 | 1869 | 861 | 0 | 116 | 1013.16 | 75 | 3708 | 0 | 0 | 77 | 0 | 0 | 10 | 0 | DAILY ENERGY CURVE
00:30 | 3098.5 | 1826.5 | 860.5 | 0 | 112 | 967.58 | 75 | 3499 | 0 | 0 | 77 | 0 | 0 | 11.5 | 0 | 23-02-2026
01:00 | 3107 | 1784 | 860 | 0 | 108 | 922 | 75 | 3290 | 0 | 0 | 77 | 0 | 0 | 13 | 0
01:30 | 3063 | 1687.5 | 860 | 0 | 106 | 921.5 | 75 | 3263.5 | 0 | 0 | 77.5 | 0 | 0 | 12 | 0 | Energy Generated | 271.1699 |  | MKWHr
02:00 | 3019 | 1591 | 860 | 0 | 104 | 921 | 75 | 3237 | 0 | 0 | 78 | 0 | 0 | 11 | 0 | Energy not Served | 0.157 |  | MKWHr
02:30 | 3030 | 1596 | 860 | 0 | 103 | 920.5 | 75 | 3300 | 0 | 30.5 | 101 | 0 | 0 | 14 | 0 | Total Energy Requirement | 271.3269 |  | MKWHr
03:00 | 3041 | 1601 | 860 | 0 | 102 | 920 | 75 | 3363 | 0 | 61 | 124 | 0 | 0 | 17 | 0
03:30 | 3168 | 1750 | 860 | 0 | 107 | 966.5 | 75 | 3444 | 0 | 48 | 143 | 0 | 0 | 16.5 | 0
04:00 | 3295 | 1899 | 860 | 0 | 112 | 1013 | 75 | 3525 | 0 | 35 | 162 | 0 | 0 | 16 | 0
04:30 | 3236.5 | 1793.5 | 860 | 0 | 113 | 974.5 | 75 | 3194 | 0 | 17.5 | 114 | 0 | 0 | 18 | 0
05:00 | 3178 | 1688 | 860 | 0 | 114 | 936 | 75 | 2863 | 0 | 0 | 66 | 0 | 0 | 20 | 0
05:30 | 3079 | 1596 | 860 | 0 | 107 | 876 | 75 | 2712.5 | 0 | 0 | 41 | 0 | 0 | 19.5 | 0
06:00 | 2980 | 1504 | 860 | 0 | 100 | 816 | 75 | 2562 | 0 | 0 | 16 | 0 | 0 | 19 | 0
06:30 | 3179 | 1484 | 860.5 | 0 | 99 | 820.5 | 75 | 2461.5 | 12.39 | 0 | 16 | 0 | 0 | 25.5 | 0
07:00 | 3378 | 1464 | 861 | 0 | 98 | 825 | 75 | 2361 | 24.78 | 0 | 16 | 0 | 0 | 32 | 0
07:30 | 3416.5 | 1531 | 790 | 0 | 100 | 923 | 75 | 2536.5 | 89.285 | 9.5 | 27 | 0 | 0 | 24.5 | 0
08:00 | 3455 | 1598 | 719 | 0 | 102 | 1021 | 75 | 2712 | 153.79 | 19 | 38 | 0 | 0 | 17 | 0
08:30 | 3491.5 | 1604.5 | 779 | 0 | 109 | 1020.5 | 75 | 2878 | 228.96 | 26 | 59.5 | 0 | 0 | 12.5 | 0
09:00 | 3528 | 1611 | 839 | 0 | 116 | 1020 | 75 | 3044 | 304.13 | 33 | 81 | 0 | 0 | 8 | 0
09:30 | 3488 | 1624.5 | 850 | 0 | 117 | 1074 | 75 | 3099 | 381.77 | 41.5 | 88 | 0 | 0 | 5.5 | 7.5
10:00 | 3448 | 1638 | 861 | 0 | 118 | 1128 | 75 | 3154 | 459.41 | 50 | 95 | 0 | 0 | 3 | 15
10:30 | 3422 | 1641.5 | 861 | 0 | 121 | 1171.5 | 75 | 3226 | 509.56 | 76.5 | 95 | 0 | 0 | 4.5 | 12.5
11:00 | 3396 | 1645 | 861 | 0 | 124 | 1215 | 75 | 3298 | 559.71 | 103 | 95 | 0 | 0 | 6 | 10
11:30 | 3373.5 | 1637.5 | 861 | 0 | 132 | 1268 | 75 | 3302.5 | 576.95 | 103 | 128.18 | 0 | 0 | 6 | 10
12:00 | 3351 | 1630 | 861 | 0 | 140 | 1321 | 75 | 3307 | 594.19 | 103 | 161.36 | 0 | 0 | 6 | 10
12:30 | 3349 | 1639 | 861 | 0 | 141 | 1321 | 75 | 3435 | 601.53 | 113 | 350.18 | 0 | 0 | 6 | 12.5
13:00 | 3347 | 1648 | 861 | 0 | 142 | 1321 | 75 | 3563 | 608.87 | 123 | 539 | 0 | 0 | 6 | 15
13:30 | 3375 | 1610 | 861 | 0 | 135 | 1322 | 75 | 3697 | 569.695 | 132 | 585.25 | 0 | 0 | 6 | 7.5
14:00 | 3403 | 1572 | 861 | 0 | 128 | 1323 | 75 | 3831 | 530.52 | 141 | 631.5 | 0 | 0 | 6 | 0
14:30 | 3348 | 1521.5 | 861 | 0 | 134 | 1292.5 | 75 | 3850 | 477.115 | 141 | 569.65 | 0 | 0 | 3.5 | 0
15:00 | 3293 | 1471 | 861 | 0 | 140 | 1262 | 75 | 3869 | 423.71 | 141 | 507.8 | 0 | 0 | 1 | 0
15:30 | 3309.5 | 1577.5 | 861 | 0 | 137 | 1264.5 | 75 | 3814 | 329.965 | 142.5 | 524.75 | 0 | 0 | 1.5 | 23.5
16:00 | 3326 | 1684 | 861 | 0 | 134 | 1267 | 75 | 3759 | 236.22 | 144 | 541.7 | 0 | 0 | 2 | 47
16:30 | 3355.5 | 1719.5 | 861 | 0 | 131 | 1266 | 75 | 3812 | 155.745 | 163.5 | 593.2 | 0 | 0 | 2.5 | 53.5
17:00 | 3385 | 1755 | 861 | 0 | 128 | 1265 | 75 | 3865 | 75.27 | 183 | 644.7 | 0 | 0 | 3 | 60
17:30 | 3166 | 1655 | 861 | 0 | 125 | 1331 | 75 | 3858 | 37.635 | 200 | 674 | 0 | 0 | 4.5 | 30
18:00 | 2947 | 1555 | 861 | 0 | 122 | 1397 | 75 | 3851 | 0 | 217 | 703.3 | 0 | 0 | 6 | 0
18:30 | 3180 | 1590 | 861 | 0 | 125 | 1386 | 75 | 3858 | 0 | 208.5 | 632.15 | 0 | 0 | 4.5 | 0
19:00 | 3413 | 1625 | 861 | 0 | 128 | 1375 | 75 | 3865 | 0 | 200 | 561 | 0 | 0 | 3 | 0
19:30 | 3390 | 1670 | 861 | 0 | 126 | 1443 | 75 | 3957 | 0 | 166 | 461 | 0 | 0 | 7 | 0
20:00 | 3385 | 1677 | 861 | 0 | 132 | 1468 | 75 | 3988 | 0 | 132 | 413 | 0 | 0 | 7 | 0
20:30 | 3400.5 | 1676 | 861 | 0 | 129 | 1460.5 | 75 | 3991 | 0 | 122 | 406 | 0 | 0 | 4.5 | 0
21:00 | 3416 | 1675 | 861 | 0 | 126 | 1453 | 75 | 3994 | 0 | 112 | 399 | 0 | 0 | 2 | 0
21:30 | 3393.5 | 1680 | 861.5 | 0 | 128 | 1454.5 | 75 | 3994.5 | 0 | 86 | 338.25 | 0 | 0 | 1 | 0
22:00 | 3371 | 1685 | 862 | 0 | 130 | 1456 | 75 | 3995 | 0 | 60 | 277.5 | 0 | 0 | 0 | 0
22:30 | 3344.5 | 1668 | 861.5 | 0 | 125 | 1392 | 75 | 3945.5 | 0 | 38.5 | 209.25 | 0 | 0 | 0.5 | 0
23:00 | 3318 | 1651 | 861 | 0 | 120 | 1328 | 75 | 3896 | 0 | 17 | 141 | 0 | 0 | 1 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 23-02-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 412 | 06:00 | 387 | 11:00 | Madunaghat | 410 | 06:00 | 37 | 22:00
Amtali | 424 | 06:00 | 410 | 13:00 | Meghnaghat | 412 | 06:00 | 387 | 15:00
Ashuganj | 417 | 06:00 | 398 | 12:00 | Payra | 425 | 06:00 | 411 | 13:00
Bhulta | 412 | 06:00 | 381 | 15:00 | Rahanpur | 418 | 06:00 | 397 | 12:00
Bibiana | 417 | 06:00 | 402 | 14:00 | Rampal | 416 | 03:00 | 398 | 14:00
BIPTC | 402 | 02:00 | 390 | 13:00
Bogura | 415 | 02:00 | 387 | 12:00
Gopalganj | 417 | 06:00 | 398 | 12:00
Kaliakoir | 404 | 06:00 | 379 | 15:00
Korerhat | 416 | 06:00 | 396 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 240 | 06:00 | 222 | 16:00 | Jhenaidah | 241 | 06:00 | 224 | 13:00
AKSML | 235 | 06:00 | 225 | 17:00 | Kachua | 238 | 06:00 | 226 | 15:00
Aminbazar | 238 | 03:00 | 223 | 14:00 | Kaliakoir | 241 | 06:00 | 224 | 15:00
Ashuganj | 241 | 05:00 | 224 | 16:00 | Keranigonj | 239 | 06:00 | 221 | 15:00
Ashuganj-400 | 241 | 05:00 | 224 | 16:00 | Khulna(S) | 242 | 02:00 | 226 | 16:00
Baghabari | 242 | 05:00 | 227 | 12:00 | Korerhat | 237 | 03:00 | 226 | 14:00
Barapukuria | 226 | 06:00 | 206 | 12:00 | Madunaghat | 235 | 06:00 | 226 | 15:00
Barapukuria-230 | 226 | 06:00 | 206 | 12:00 | Madunaghat-400 | 235 | 06:00 | 227 | 15:00
Barishal | 237 | 06:00 | 227 | 13:00 | Maniknagar | 238 | 04:00 | 222 | 15:00
Bheramara | 240 | 06:00 | 224 | 17:00 | Meghnaghat | 244 | 05:00 | 231 | 16:00
Bhulta | 239 | 06:00 | 221 | 15:00 | Meghnaghat-400 | 243 | 06:00 | 226 | 15:00
Bibiana | 243 | 06:00 | 231 | 16:00 | Mirsorai | 235 | 05:00 | 225 | 15:00
BIPTC | 243 | 06:00 | 224 | 17:00 | Rajshahi | 240 | 06:00 | 222 | 17:00
Bogura | 241 | 06:00 | 225 | 12:00 | Rampal | 239 | 02:00 | 225 | 14:00
Bogura-400 | 240 | 06:00 | 224 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Borhanuddin | 239 | 06:00 | 233 | 12:00 | Rampura | 239 | 06:00 | 219 | 15:00
BSRM | 238 | 06:00 | 226 | 15:00 | Shikalbaha | 233 | 06:00 | 224 | 14:00
Chowmuhani | N/A | N/A | N/A | N/A | Shyampur | 240 | 06:00 | 223 | 15:00
Cumilla(N) | 239 | 06:00 | 225 | 13:00 | Siddhirganj | 240 | 05:00 | 224 | 15:00
Faridpur | 234 | 05:00 | 223 | 12:00 | Sirajgonj | 245 | 06:00 | 233 | 12:00
Fenchuganj | 245 | 06:00 | 235 | 16:00 | Sreepur | 239 | 02:00 | 220 | 12:00
Feni | 237 | 05:00 | 226 | 15:00 | Tongi | 266 | 19:00 | 220 | 15:00
Ghorashal | 240 | 01:00 | 225 | 10:00
Ghorashal-230 | 237 | 06:00 | 219 | 13:00
Gopalganj | 234 | 06:00 | 223 | 13:00
GPH | 235 | 07:00 | 225 | 15:00
Haripur | 233 | 18:00 | 223 | 15:00
Hasnabad | 240 | 06:00 | 223 | 15:00
Hathazari | 233 | 05:00 | 222 | 22:00
Ishurdi | 244 | 06:00 | 227 | 17:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 04:00 | 125 | 15:00 | Magura | 139 | 06:00 | 126 | 13:00
Agargaon | 134 | 03:00 | 125 | 15:00 | Mahasthangarh | 137 | 06:00 | 125 | 12:00
Agrabad | 135 | 05:00 | 129 | 15:00 | Maijdee | 133 | 06:00 | 126 | 16:00
AKS | 134 | 04:00 | 128 | 14:00 | Manikganj | 129 | 02:00 | 116 | 12:00
Aminbazar | 140 | 03:00 | 130 | 11:00 | Maniknagar | 135 | 06:00 | 123 | 14:00
Amnura | 139 | 06:00 | 129 | 12:00 | Matarbari | 128 | 07:00 | 115 | 21:00
Ashuganj | 140 | 06:00 | 132 | 17:00 | Matuail | 136 | 05:00 | 126 | 15:00
Bagerhat | 136 | 05:00 | 123 | 12:00 | Metrorail_Motijheel | 135 | 06:00 | 123 | 14:00
Bajitpur | 135 | 06:00 | 124 | 16:00 | Metrorail_Uttara | 134 | 06:00 | 120 | 14:00
Bakerganj | 138 | 02:00 | 133 | 12:00 | Millgate | 134 | 06:00 | 120 | 15:00
Bakulia | 134 | 04:00 | 129 | 22:00 | Mirpur | 139 | 06:00 | 128 | 15:00
Banani | 138 | 06:00 | 125 | 13:00 | Mirzapur | 137 | 03:00 | 127 | 15:00
Bangabhaban | 135 | 06:00 | 123 | 15:00 | Mithapukur | 136 | 06:00 | 124 | 12:00
Barapukuria | 139 | 18:00 | 125 | 12:00 | MI_Cement | 137 | 06:00 | 124 | 15:00
Barguna | 139 | 05:00 | 133 | 15:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 138 | 06:00 | 131 | 13:00 | Mogbazar | 140 | 06:00 | 126 | 15:00
Barishal-230 | 138 | 06:00 | 131 | 13:00 | Mongla | 136 | 05:00 | 122 | 17:00
Baroaulia | 135 | 07:00 | 130 | 14:00 | Motijheel | 135 | 06:00 | 123 | 15:00
Baroirhat | 136 | 07:00 | 129 | 15:00 | Muktagacha | 132 | 03:00 | 116 | 16:00
Bashundhara | 138 | 04:00 | 125 | 12:00 | Munshiganj | 134 | 05:00 | 125 | 15:00
BashundharaCement | 134 | 07:00 | 128 | 16:00 | Muradnagar | 136 | 06:00 | 126 | 13:00
Beanibazar | 133 | 06:00 | 129 | 13:00 | Mymensingh | 131 | 06:00 | 111 | 13:00
Benapole | 135 | 02:00 | 116 | 12:00 | Naogaon | 140 | 02:00 | 123 | 12:00
Bhaluka | 131 | 02:00 | 117 | 13:00 | Narail | 139 | 06:00 | 12 | 14:00
Bhandaria | 135 | 01:00 | 126 | 17:00 | Narinda | 135 | 06:00 | 123 | 14:00
Bhangura | 139 | 06:00 | 130 | 13:00 | Narshingdi | 132 | 18:00 | 123 | 14:00
Bheramara | 140 | 06:00 | 133 | 12:00 | Natore | 138 | 06:00 | 129 | 12:00
Bheramara(GK) | 140 | 02:00 | 133 | 12:00 | Nawabganj | 138 | 05:00 | 126 | 15:00
Bhulta | 130 | 04:00 | 121 | 15:00 | Netrakona | 126 | 00:00 | 107 | 17:00
Bog-Sherpur | 138 | 06:00 | 126 | 12:00 | New | 135 | 04:00 | 121 | 15:00
Bogura | 138 | 02:00 | 128 | 18:00 | Niamatpur | 140 | 01:00 | 131 | 12:00
Bogura-230 | 140 | 06:00 | 129 | 12:00 | Noapara | 137 | 05:00 | 122 | 12:00
Brahmanbaria | 134 | 04:00 | 125 | 15:00 | Pabna | 140 | 06:00 | 131 | 13:00
Cantonment | 133 | 02:00 | 124 | 15:00 | Palashbari | 134 | 02:00 | 121 | 12:00
Chandina | 139 | 06:00 | 130 | 15:00 | Panchagarh | 138 | 18:00 | 123 | 12:00
Chandpur | 134 | 06:00 | 129 | 15:00 | Patiya | 135 | 06:00 | 128 | 19:30
Chandraghona | 137 | 05:00 | 132 | 15:00 | Patuakhali | 136 | 05:00 | 132 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 138 | 00:00 | 130 | 17:00 | Payra | 139 | 03:00 | 135 | 12:00
Charsaidpur | 136 | 06:00 | 126 | 15:00 | PHP | 135 | 06:00 | 128 | 13:00
Chauddagram | 136 | 06:00 | 127 | 15:00 | Postogola | 138 | 06:00 | 127 | 12:00
Chhatak | 133 | 05:00 | 124 | 12:00 | Purbachal | 138 | 05:00 | 125 | 15:00
Chowmuhani | 134 | 06:00 | 126 | 14:00 | Purbasadipur | 135 | 06:00 | 117 | 12:00
Chuadanga | 139 | 06:00 | 126 | 13:00 | Rahanpur | 140 | 05:00 | 132 | 16:00
Coxsbazar | 128 | 07:00 | 116 | 14:00 | Rahanpur-400 | 140 | 02:00 | 132 | 12:00
Cumilla(N) | 138 | 06:00 | 130 | 15:00 | Rahim | 135 | 03:00 | 126 | 15:00
Cumilla(S) | 137 | 05:00 | 122 | 13:00 | Rajbari | 136 | 06:00 | 127 | 13:00
Daganbhuiyan | 134 | 06:00 | 127 | 15:00 | Rajendrapur | 138 | 07:00 | 118 | 13:00
Daudkandi | 134 | 06:00 | 122 | 17:00 | Rajshahi | 139 | 06:00 | 128 | 18:00
DhakaUniversity | 139 | 06:00 | 126 | 15:00 | Rajshahi-230 | 139 | 06:00 | 128 | 13:00
Dhamrai | 134 | 04:00 | 127 | 17:00 | Ramganj | 132 | 06:00 | 126 | 15:00
Dhanmondi | 139 | 06:00 | 127.6 | 15:00 | Rampur | 135 | 05:00 | 129 | 15:00
Dohazari | 133 | 06:00 | 125 | 17:00 | Rampura | 138 | 06:00 | 126 | 13:00
Faridpur | 135 | 05:00 | 128 | 17:00 | Rangamati | 136 | 05:00 | 131 | 15:00
Fatullah | 139 | 06:00 | 125 | 15:00 | Rangpur | 137 | 06:00 | 123 | 12:00
Fenchuganj | 138 | 06:00 | 133 | 12:00 | Ruppur | 141 | 05:00 | 133 | 17:00
Feni | 133 | 06:00 | 127 | 17:00 | Saidpur | 136 | 18:30 | 123 | 12:00
Feni-230 | 133 | 05:00 | 127 | 15:00 | Satkhira | 136 | 05:00 | 122 | 17:00
Ghatail | 132 | 02:00 | 118 | 17:00 | Satmasjid | 135 | 06:00 | 124 | 13:00
Ghorashal | 142 | 06:00 | 131 | 11:00 | Savar | 138 | 06:00 | 128 | 10:00
Goalpara | 139 | 02:00 | 127 | 12:00 | SevenRings | 142 | 06:00 | 131 | 13:00
Gollamari | 138 | 03:00 | 127 | 12:00 | ShahCement | 136 | 06:00 | 126 | 15:00
Gopalganj | 139 | 06:00 | 128 | 13:00 | Shahjadpur | 140 | 00:00 | 134 | 12:00
Gopalganj-400 | 139 | 05:00 | 132 | 12:00 | Shahjibazar | 134 | 06:00 | 126 | 15:00
Gulshan | 138 | 06:00 | 126 | 13:00 | Shahmirpur | 137 | 06:00 | 130 | 14:00
Halishahar | 136 | 06:00 | 129 | 15:00 | Shariatpur | 139 | 06:00 | 130 | 13:00
Haripur | 132 | 18:00 | 126 | 15:00 | Sherpur | 127 | 04:00 | 109 | 17:00
HaripurSBU | 136 | 06:00 | 127 | 15:00 | Shikalbaha | 125 | 05:00 | 119 | 15:00
Hasnabad | 138 | 04:00 | 127 | 13:00 | Shikalbaha-230 | 137 | 06:00 | 130 | 14:00
Hathazari | 136 | 04:00 | 131 | 15:00 | Shitalakhya | 137 | 06:00 | 124 | 15:00
Hatirjheel | 139 | 06:00 | 126 | 13:00 | Sholosohor | 137 | 06:00 | 131 | 15:00
Ishurdi | 142 | 06:00 | 134 | 13:00 | Shyampur | 135 | 01:00 | 127 | 15:00
Jaldhaka | 134 | 06:00 | 120 | 12:00 | Shyampur-230 | 139 | 06:00 | 129 | 15:00
Jamalpur | 129 | 01:00 | 114 | 17:00 | Siddhirganj | 136 | 05:00 | 127 | 12:00
Jashore | 135 | 05:00 | 118 | 12:00 | Sirajganj | 135 | 02:00 | 120 | 17:00
Jhenaidah | 140 | 05:00 | 119 | 13:00 | Sonargaon | 134 | 06:00 | 128 | 10:00
Jhenaidah-230 | 141 | 06:00 | 129 | 13:00 | Sreemongol | 134 | 06:00 | 127 | 16:00
Joydebpur | 137 | 18:30 | 127 | 12:00 | Sreepur | 135 | 06:00 | 123 | 13:00
Joypurhat | 133 | 06:00 | 119 | 12:00 | Srinagar | 139 | 06:00 | 126 | 16:00
Juldah | 135 | 07:00 | 129 | 15:00 | SSM | 140 | 07:00 | 134 | 15:00
Kabirpur | 140 | 06:00 | 117 | 17:00 | Sunamganj | 130 | 01:00 | 123 | 13:00
Kachua | 135 | 06:00 | 129 | 15:00 | Sylhet | 134 | 06:00 | 127 | 20:00
Kaliakoir | 142 | 06:00 | 129 | 17:00 | Sylhet-132 | 133 | 05:00 | 127 | 12:00
Kaliganj | 141 | 06:00 | 129 | 17:00 | Tangail | 132 | 03:00 | 122 | 15:00
Kallyanpur | 139 | 04:00 | 130 | 15:00 | Taraganj | 134 | 06:00 | 122 | 12:00
Kalurghat | 137 | 06:00 | 132 | 13:00 | Tasnim | 135 | 06:00 | 126 | 17:00
Kamrangirchar | 138 | 06:00 | 125 | 16:00 | Thakurgaon | 136 | 18:30 | 121 | 12:00
Kaptai | N/A | N/A | N/A | N/A | TK | 137 | 05:00 | 132 | 15:00
Kasba | 137 | 06:00 | 126 | 14:00 | Tongi | 135 | 04:00 | 123 | 17:00
Kazla | 133 | 05:00 | 122 | 13:00 | Ullahpara | 139 | 05:00 | 130 | 12:00
Keranigonj | 139 | 06:00 | 127 | 15:00 | Ullon | 138 | 06:00 | 125 | 15:00
Khagrachori | 136 | 06:00 | 130 | 15:00 | Uttara | 134 | 05:00 | 120 | 15:00
Khulna | 138 | 05:00 | 124 | 12:00 | UttaraNew | 134 | 06:00 | 120 | 14:00
Khulna(S) | 139 | 02:00 | 128 | 12:00 | Zigatola | 138 | 06:00 | 127 | 15:00
Khulshi | 134 | 06:00 | 128 | 15:00
Kishoreganj | 133 | 03:00 | 121 | 17:00
Kodda | 138 | 06:00 | 124 | 12:00
Korerhat | 138 | 03:00 | 131 | 14:00
KSRM | 134 | 02:00 | 130 | 13:00
Kulaura | 137 | 03:00 | 132 | 14:00
Kurigram | 133 | 06:00 | 119 | 12:00
Kushtia | 136 | 06:00 | 125 | 13:00
Laksam | 138 | 13:00 | 128 | 15:00
Lakshmipur | 133 | 06:00 | 126 | 15:00
Lalbag | 137 | 04:00 | 126 | 15:00
Lalmonirhat | 133 | 06:00 | 122 | 09:00
Madanganj | 136 | 06:00 | 128 | 16:00
Madaripur | 138 | 06:00 | 130 | 12:00
Madartek | 138 | 06:00 | 126 | 14:00
Madunaghat | 137 | 06:00 | 131 | 15:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 23-02-2026 | [28 empty] | Date: | 23-02-2026 | [28 empty] | Date: | 23-02-2026 | [28 empty] | Date: | 23-02-2026 | [28 empty] | Date: | 23-02-2026 | [17 empty] | Date: | 23-02-2026
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [17 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 13 | 18 | 0 | 500 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 37 | 905 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1141 | 0 | 0 | 8 | 0 | 315 | 285 | 51 | 0 | 194 | 10 | 0 | 104 | 0 | 0 | 20 | 0 | 116 | 0 | 0 | 0 | 300 | 0 | 359 | 41 | 53 | 155 | 0 | 21 | 0 | 86 | 0 | 0 | 0 | 98 | 0 | 58 | 19 | 70 | 0 | 0 | 0 | 6058 | 861 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 860 | 0 | 0 | 0 | 1013.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 130 | 220 | 0 | 0 | 500 | 0 | 4761.16 | 10819.16 | 92.69
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 435 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 520 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 36 | 800 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1054 | 0 | 0 | 8 | 0 | 310 | 305 | 51 | 0 | 206 | 10 | 0 | 104 | 0 | 0 | 20 | 0 | 108 | 0 | 0 | 0 | 290 | 0 | 382 | 41 | 53 | 141 | 0 | 17 | 0 | 11 | 0 | 0 | 0 | 98 | 0 | 58 | 19 | 69 | 0 | 0 | 0 | 5821 | 860 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764 | 0 | 0 | 0 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 130 | 220 | 0 | 0 | 450 | 0 | 4415 | 10236 | 92.69
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 36 | 800 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1052 | 0 | 0 | 8 | 0 | 295 | 295 | 51 | 0 | 198 | 10 | 0 | 104 | 0 | 0 | 20 | 0 | 104 | 0 | 0 | 0 | 290 | 0 | 338 | 41 | 53 | 143 | 0 | 17 | 0 | 11 | 0 | 0 | 0 | 98 | 0 | 59 | 19 | 71 | 0 | 0 | 0 | 5610 | 860 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 762 | 0 | 0 | 0 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 130 | 180 | 0 | 0 | 400 | 0 | 4286 | 9896 | 92.68
03:00 | 0 | 3 | 8 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 13 | 20 | 0 | 415 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 36 | 880 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1100 | 0 | 0 | 8 | 0 | 305 | 335 | 51 | 0 | 201 | 10 | 0 | 104 | 0 | 0 | 20 | 0 | 102 | 0 | 0 | 0 | 300 | 0 | 328 | 41 | 53 | 140 | 0 | 17 | 0 | 11 | 0 | 0 | 0 | 99 | 0 | 72 | 47 | 72 | 0 | 0 | 0 | 5861 | 860 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 761 | 0 | 0 | 0 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 130 | 180 | 0 | 0 | 400 | 0 | 4303 | 10164 | 92.67
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475 | 0 | 0 | 56 | 0 | 0 | 0 | 35 | 13 | 20 | 0 | 500 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 37 | 800 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1160 | 0 | 0 | 8 | 0 | 335 | 350 | 51 | 0 | 201 | 10 | 0 | 105 | 0 | 0 | 20 | 0 | 112 | 0 | 0 | 0 | 295 | 0 | 387 | 41 | 53 | 157 | 0 | 17 | 0 | 86 | 0 | 0 | 0 | 98 | 0 | 98 | 47 | 72 | 0 | 0 | 0 | 6313 | 860 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 831 | 0 | 0 | 0 | 1013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 252 | 130 | 220 | 0 | 0 | 430 | 0 | 4679 | 10992 | 92.66
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 13 | 20 | 0 | 440 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 23 | 740 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 535 | 0 | 0 | 8 | 0 | 315 | 335 | 5 | 0 | 204 | 10 | 0 | 105 | 0 | 0 | 20 | 0 | 114 | 0 | 0 | 0 | 290 | 0 | 367 | 41 | 53 | 152 | 0 | 17 | 0 | 5 | 0 | 0 | 0 | 99 | 0 | 58 | 8 | 69 | 0 | 0 | 0 | 5322 | 860 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 828 | 0 | 0 | 0 | 936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258 | 130 | 220 | 0 | 0 | 450 | 0 | 4478 | 9800 | 92.64
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 13 | 20 | 0 | 400 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 5 | 720 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 422 | 0 | 0 | 8 | 0 | 290 | 295 | 5 | 0 | 192 | 10 | 0 | 50 | 0 | 0 | 14 | 0 | 100 | 0 | 0 | 0 | 290 | 0 | 336 | 41 | 53 | 152 | 0 | 17 | 0 | 5 | 0 | 0 | 0 | 99 | 0 | 8 | 8 | 65 | 0 | 0 | 0 | 4836 | 860 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 793 | 0 | 0 | 0 | 816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 110 | 180 | 0 | 0 | 400 | 0 | 4096 | 8932 | 92.63
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 240 | 0 | 0 | 1 | 0 | 13 | 20 | 0 | 435 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0.21 | 75 | 0 | 5 | 575 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 430 | 1 | 0 | 8 | 0 | 350 | 350 | 5 | 0 | 209 | 10 | 0 | 50 | 0 | 0 | 14 | 0 | 98 | 0 | 4 | 0 | 295 | 0 | 405 | 41 | 53 | 142 | 1 | 17 | 0 | 5 | 0 | 0 | 0 | 99 | 0 | 8 | 8 | 65 | 0 | 1.55 | 0 | 4882.76 | 861 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.78 | 771 | 0 | 0 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 2 | 0 | 0 | 1.52 | 175 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.19 | 0 | 52 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 6 | 0.03 | 0 | 183 | 100 | 180 | 0 | 0 | 350 | 0 | 4252.02 | 9134.78 | 92.62
08:00 | 0 | 17 | 2 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 240 | 0 | 0 | 5 | 0 | 23 | 20 | 0 | 400 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 1.03 | 75 | 0 | 6 | 585 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 718 | 7 | 0 | 8 | 0 | 315 | 330 | 27 | 0 | 192 | 33 | 0 | 106 | 0 | 0 | 14 | 0 | 102 | 0 | 18 | 0 | 290 | 0 | 360 | 41 | 53 | 142 | 3 | 17 | 0 | 86 | 0 | 0 | 0 | 99 | 0 | 19 | 18 | 65 | 1 | 6.56 | 0 | 5351.59 | 719 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 802 | 0 | 0 | 0 | 1021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3 | 18 | 0 | 0 | 9.52 | 184 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0.85 | 0 | 52 | 0 | 8 | 0 | 0 | 0 | 0 | 1.4 | 47 | 0.13 | 0 | 215 | 130 | 220 | 0 | 0 | 340 | 0 | 4558.2 | 9909.79 | 92.61
09:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 240 | 0 | 0 | 10 | 0 | 23 | 20 | 0 | 400 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1.92 | 75 | 0 | 4 | 600 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 941 | 12 | 0 | 8 | 0 | 335 | 345 | 51 | 0 | 202 | 42 | 0 | 102 | 0 | 0 | 14 | 0 | 116 | 0 | 34 | 0 | 290 | 0 | 385 | 41 | 53 | 140 | 5 | 0 | 0 | 86 | 0 | 0 | 0 | 99 | 0 | 46 | 18 | 65 | 1 | 18.69 | 0 | 5773.61 | 839 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 852 | 0 | 0 | 0 | 1020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.46 | 39 | 0 | 0 | 12.64 | 184 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.37 | 0 | 52 | 0 | 17 | 0 | 0 | 0 | 0 | 2.8 | 92 | 0.25 | 0 | 219 | 130 | 220 | 0 | 0 | 380 | 0 | 4885.52 | 10659.13 | 92.6
10:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 270 | 0 | 0 | 19 | 17 | 20 | 20 | 0 | 420 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 2.7 | 75 | 0 | 4 | 520 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 940 | 16 | 0 | 8 | 0 | 340 | 350 | 51 | 0 | 205 | 42 | 0 | 100 | 0 | 0 | 8 | 0 | 118 | 0 | 49 | 0 | 295 | 0 | 388 | 41 | 53 | 144 | 7 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 59 | 19 | 34 | 1 | 24.91 | 0 | 5708.61 | 861 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 952 | 0 | 0 | 0 | 1128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.73 | 61 | 0 | 0 | 24.79 | 190 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.01 | 0 | 52 | 0 | 25 | 0 | 0 | 0 | 0 | 3.9 | 135 | 0.37 | 0 | 278 | 130 | 220 | 0 | 0 | 412 | 0 | 5320.8 | 11029.41 | 92.6
11:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 270 | 0 | 0 | 19 | 70 | 20 | 20 | 0 | 400 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 3.21 | 75 | 0 | 4 | 520 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 970 | 18 | 0 | 8 | 0 | 330 | 340 | 51 | 0 | 200 | 37 | 0 | 99 | 0 | 0 | 20 | 0 | 124 | 0 | 56 | 0 | 295 | 0 | 388 | 41 | 53 | 142 | 8 | 22 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 59 | 19 | 34 | 2 | 37.66 | 0 | 5792.87 | 861 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 1030 | 0 | 0 | 0 | 1215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.25 | 78 | 0 | 0 | 25.29 | 188 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.14 | 0 | 50 | 0 | 30 | 0 | 0 | 0 | 0 | 4.7 | 166 | 0.46 | 0 | 278 | 130 | 220 | 0 | 0 | 450 | 0 | 5584.84 | 11377.71 | 92.59
12:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 9 | 0 | 17 | 0 | 0 | 0 | 1 | 46 | 0 | 0 | 0 | 350 | 0 | 0 | 270 | 0 | 0 | 14 | 70 | 20 | 20 | 0 | 400 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 3.43 | 75 | 0 | 4 | 520 | 0 | 0 | 2 | 0 | 0 | 218 | 0 | 0 | 0 | 975 | 20 | 0 | 8 | 0 | 335 | 340 | 51 | 0 | 199 | 10 | 2 | 99 | 6 | 0 | 20 | 0 | 140 | 0 | 58 | 0 | 290 | 0 | 390 | 42 | 53 | 140 | 8 | 22 | 0 | 85 | 0 | 0 | 0 | 0 | 0.36 | 59 | 19 | 31 | 2 | 42 | 0 | 5836.79 | 861 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 1020 | 0 | 0 | 0 | 1321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.85 | 69 | 0 | 0 | 42.64 | 189 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.39 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 5.4 | 175 | 0.48 | 0 | 277 | 130 | 220 | 0 | 0 | 515 | 0 | 5712.76 | 11549.55 | 92.59
13:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 27 | 14 | 34 | 0 | 0 | 0 | 18 | 84 | 0 | 0 | 0 | 365 | 0 | 17 | 270 | 0 | 0 | 19 | 90 | 18 | 20 | 0 | 400 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 3.36 | 75 | 8 | 12 | 650 | 0 | 0 | 24 | 0 | 55 | 215 | 0 | 0 | 0 | 1051 | 19 | 0 | 5 | 0 | 320 | 330 | 51 | 0 | 201 | 10 | 47 | 98 | 48 | 0 | 20 | 0 | 142 | 0 | 56 | 0 | 300 | 0 | 379 | 42 | 53 | 144 | 9 | 8 | 0 | 85 | 0 | 0 | 0 | 35 | 16 | 59 | 19 | 30 | 2 | 37.01 | 0 | 6398.37 | 861 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 1030 | 0 | 0 | 0 | 1321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.56 | 79 | 0 | 0 | 48.64 | 185 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.42 | 0 | 0 | 35 | 32 | 34 | 0 | 0 | 0 | 5.4 | 175 | 0.48 | 0 | 277 | 130 | 220 | 0 | 0 | 555 | 0 | 5835.5 | 12233.87 | 92.58
14:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 30.5 | 17 | 52 | 0 | 0 | 0 | 35 | 88 | 0 | 0 | 0 | 340 | 0 | 17 | 330 | 0 | 0 | 12 | 108 | 23 | 20 | 0 | 350 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 2.93 | 75 | 14 | 4 | 780 | 0 | 0 | 25 | 0 | 66 | 216 | 0 | 0 | 0 | 1100 | 14 | 0 | 0 | 0 | 320 | 325 | 51 | 0 | 212 | 10 | 61 | 98 | 62 | 0 | 20 | 0 | 128 | 0 | 47 | 0 | 295 | 0 | 365 | 42 | 53 | 155 | 8 | 8 | 0 | 86 | 0 | 0 | 0 | 97 | 17 | 59 | 19 | 30 | 2 | 30.93 | 0 | 6662.36 | 861 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 1123 | 0 | 0 | 0 | 1323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.34 | 78 | 0 | 0 | 42.64 | 176 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 4.07 | 0 | 0 | 35 | 27 | 34 | 0 | 0 | 0 | 4.2 | 156 | 0.41 | 0 | 273 | 130 | 220 | 0 | 0 | 555 | 0 | 5839.66 | 12502.02 | 92.58
15:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 30.8 | 17 | 52 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 300 | 0 | 17 | 280 | 0 | 0 | 14 | 108 | 23 | 18 | 0 | 320 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2.5 | 75 | 14 | 4 | 800 | 0 | 0 | 27 | 0 | 34 | 214 | 0 | 0 | 0 | 1160 | 12 | 0 | 0 | 0 | 335 | 345 | 51 | 0 | 210 | 10 | 34 | 97 | 34 | 0 | 20 | 0 | 140 | 0 | 33 | 0 | 300 | 0 | 392 | 42 | 53 | 156 | 5 | 13 | 0 | 86 | 0 | 0 | 0 | 97 | 17 | 59 | 18 | 28 | 2 | 23.81 | 0 | 6544.11 | 861 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 1085 | 0 | 0 | 0 | 1262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.64 | 63 | 0 | 0 | 54.55 | 178 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 3.32 | 0 | 0 | 35 | 20 | 34 | 0 | 0 | 0 | 2.6 | 108 | 0.29 | 0 | 269 | 125 | 180 | 0 | 0 | 555 | 0 | 5500.4 | 12044.51 | 92.57
16:00 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 33.7 | 17 | 43 | 0 | 0 | 0 | 35 | 49 | 0 | 0 | 0 | 345 | 0 | 17 | 250 | 0 | 0 | 9 | 108 | 23 | 17 | 0 | 420 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 12 | 24 | 1.19 | 75 | 16 | 12 | 800 | 0 | 0 | 32 | 0 | 32 | 214 | 0 | 0 | 0 | 1160 | 7 | 0 | 8 | 0 | 340 | 345 | 51 | 0 | 180 | 10 | 33 | 97 | 34 | 0 | 20 | 0 | 134 | 0 | 19 | 0 | 305 | 0 | 400 | 42 | 53 | 155 | 3 | 22 | 0 | 86 | 0 | 0 | 0 | 97 | 17 | 58 | 18 | 20 | 1 | 14.19 | 2 | 6677.08 | 861 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 1015 | 0 | 0 | 0 | 1267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.51 | 37 | 0 | 0 | 19.36 | 188 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 1.91 | 0 | 0 | 35 | 11 | 34 | 0 | 0 | 0 | 1.9 | 66 | 0.16 | 0 | 229 | 125 | 220 | 0 | 0 | 555 | 0 | 5352.84 | 12029.92 | 92.57
17:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 33.7 | 17 | 66 | 16 | 15 | 0 | 35 | 51 | 0 | 0 | 0 | 405 | 0 | 17 | 250 | 0 | 0 | 3 | 108 | 23 | 18 | 0 | 435 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 24 | 24 | 0.31 | 75 | 16 | 25 | 905 | 0 | 0 | 32 | 0 | 32 | 215 | 0 | 0 | 0 | 1165 | 2 | 0 | 0 | 0 | 350 | 345 | 51 | 0 | 184 | 10 | 32 | 98 | 34 | 0 | 20 | 0 | 128 | 0 | 6 | 0 | 295 | 0 | 407 | 42 | 53 | 155 | 1 | 22 | 0 | 86 | 0 | 0 | 0 | 97 | 17 | 58 | 18 | 18 | 0 | 4.61 | 6 | 6932.62 | 861 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 1008 | 0 | 0 | 0 | 1265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 12 | 0 | 0 | 4.07 | 189 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.52 | 0 | 0 | 70 | 3 | 47 | 0 | 0 | 0 | 0.5 | 23 | 0.06 | 0 | 232 | 123 | 220 | 0 | 0 | 555 | 0 | 5307.35 | 12239.97 | 92.56
18:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 32.3 | 17 | 70 | 16 | 15 | 0 | 30 | 66 | 0 | 0 | 0 | 440 | 0 | 0 | 250 | 0 | 0 | 0 | 125 | 17 | 18 | 0 | 320 | 0 | 0 | 0 | 0 | 6 | 17 | 0 | 0 | 0 | 12 | 0 | 75 | 12 | 34 | 905 | 0 | 0 | 32 | 0 | 40 | 187 | 0 | 0 | 0 | 1105 | 0 | 0 | 0 | 0 | 290 | 320 | 10 | 0 | 196 | 10 | 33 | 50 | 38 | 0 | 20 | 0 | 122 | 0 | 0 | 0 | 295 | 0 | 328 | 42 | 53 | 155 | 0 | 22 | 0 | 44 | 0 | 0 | 0 | 97 | 17 | 115 | 28 | 16 | 0 | 0 | 6 | 6540.3 | 861 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1055 | 0 | 0 | 0 | 1397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 266 | 110 | 180 | 0 | 0 | 520 | 0 | 5194 | 11734.3 | 92.56
19:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 16 | 17 | 70 | 16 | 0 | 0 | 17 | 33 | 0 | 0 | 0 | 335 | 0 | 0 | 300 | 0 | 0 | 0 | 108 | 19 | 17 | 0 | 420 | 0 | 0 | 0 | 0 | 3 | 17 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 32 | 905 | 0 | 0 | 19 | 0 | 33 | 221 | 0 | 0 | 0 | 1107 | 0 | 0 | 0 | 0 | 340 | 335 | 32 | 0 | 218 | 10 | 16 | 100 | 34 | 0 | 20 | 0 | 128 | 0 | 0 | 0 | 280 | 0 | 377 | 41 | 53 | 142 | 0 | 22 | 0 | 86 | 0 | 0 | 0 | 98 | 17 | 115 | 28 | 22 | 0 | 0 | 6 | 6698 | 861 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1046 | 0 | 0 | 0 | 1375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 125 | 220 | 0 | 0 | 530 | 0 | 5408 | 12106 | 92.55
19:30 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 16 | 17 | 60 | 0 | 0 | 0 | 17 | 20 | 0 | 0 | 0 | 340 | 0 | 0 | 300 | 0 | 0 | 0 | 90 | 19 | 17 | 0 | 400 | 0 | 0 | 0 | 0 | 7 | 17 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 34 | 905 | 0 | 0 | 19 | 0 | 30 | 220 | 0 | 0 | 0 | 1161 | 0 | 0 | 0 | 0 | 320 | 320 | 51 | 0 | 219 | 10 | 15 | 102 | 17 | 0 | 20 | 0 | 126 | 0 | 0 | 0 | 305 | 0 | 374 | 41 | 53 | 156 | 0 | 22 | 0 | 86 | 0 | 0 | 0 | 98 | 17 | 115 | 28 | 33 | 0 | 0 | 6 | 6681 | 861 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 0 | 0 | 0 | 1443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 130 | 220 | 0 | 0 | 530 | 0 | 5475 | 12156
20:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 16 | 0 | 61 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 350 | 0 | 0 | 300 | 0 | 0 | 0 | 90 | 20 | 17 | 0 | 400 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 35 | 905 | 0 | 0 | 19 | 0 | 17 | 220 | 0 | 0 | 0 | 1162 | 0 | 0 | 0 | 0 | 325 | 325 | 51 | 0 | 198 | 10 | 15 | 103 | 17 | 0 | 20 | 0 | 132 | 0 | 0 | 0 | 300 | 0 | 377 | 42 | 53 | 156 | 0 | 22 | 0 | 86 | 0 | 0 | 0 | 98 | 17 | 115 | 28 | 33 | 0 | 0 | 6 | 6633 | 861 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 0 | 0 | 1468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 130 | 220 | 0 | 0 | 550 | 0 | 5505 | 12138 | 92.55
21:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 16 | 0 | 51 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 350 | 0 | 0 | 300 | 0 | 0 | 0 | 70 | 19 | 17 | 0 | 400 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 34 | 905 | 0 | 0 | 19 | 0 | 15 | 223 | 0 | 0 | 0 | 1162 | 0 | 0 | 0 | 0 | 335 | 340 | 51 | 0 | 200 | 10 | 14 | 103 | 17 | 0 | 20 | 0 | 126 | 0 | 0 | 0 | 300 | 0 | 377 | 41 | 53 | 156 | 0 | 22 | 0 | 86 | 0 | 0 | 0 | 98 | 17 | 115 | 28 | 32 | 0 | 0 | 6 | 6616 | 861 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 1453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 130 | 220 | 0 | 0 | 550 | 0 | 5497 | 12113 | 92.54
22:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 16.5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 300 | 0 | 0 | 0 | 52 | 19 | 16 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 34 | 905 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1162 | 0 | 0 | 0 | 0 | 325 | 320 | 51 | 0 | 190 | 10 | 0 | 104 | 0 | 0 | 20 | 0 | 130 | 0 | 0 | 0 | 305 | 0 | 376 | 41 | 53 | 157 | 0 | 22 | 0 | 86 | 0 | 0 | 0 | 98 | 17 | 90 | 28 | 21 | 0 | 0 | 6 | 6408.5 | 862 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1102 | 0 | 0 | 0 | 1456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 130 | 220 | 0 | 0 | 550 | 0 | 5503 | 11911.5 | 92.54
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 19 | 17 | 0 | 400 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 34 | 905 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 0 | 320 | 320 | 51 | 0 | 199 | 0 | 0 | 104 | 0 | 0 | 20 | 0 | 120 | 0 | 0 | 0 | 300 | 0 | 358 | 41 | 53 | 147 | 0 | 22 | 0 | 86 | 0 | 0 | 0 | 100 | 17 | 59 | 19 | 19 | 0 | 0 | 6 | 6206 | 861 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 0 | 0 | 0 | 1328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243 | 130 | 220 | 0 | 0 | 500 | 0 | 5202 | 11408 | 92.53
Total KWH | 0 | 318720 | 274560 | 0 | 0 | 0 | 0 | 0 | 7938000 | 0 | 0 | 257040 | 135720 | 738864 | 61440 | 36633 | 0 | 252484 | 519840 | 0 | 0 | 0 | 9019900 | 0 | 105870 | 5338302 | 0 | 0 | 139438 | 1250400 | 443400 | 457920 | 0 | 10034090.91 | 0 | 0 | 0 | 0 | 209760 | 42990 | 0 | 0 | 43200 | 52800 | 21805 | 1772500 | 92000 | 483360 | 18392727.27 | 0 | 0 | 243840 | 0 | 380545 | 5277751 | 0 | 0 | 0 | 23869089 | 128520 | 0 | 133818 | 0 | 8214300 | 7996000 | 1127074 | 0 | 4927000 | 367704 | 322560 | 2302241 | 362400 | 0 | 457600 | 0 | 2842560 | 0 | 380755 | 0 | 7165000 | 0 | 9150000 | 986000 | 1347000 | 3566045.45 | 57677 | 430080 | 0 | 1581120 | 0 | 0 | 0 | 2002220 | 214560 | 1612800 | 518400 | 937920 | 12300 | 238840 | 52080 | 147639563.63 | 20613818 | 7043328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520560 | 23120000 | 0 | 0 | 0 | 28074088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223144 | 545330 | 0 | 0 | 270000 | 4284273 | 0 | 0 | 0 | 0 | 0 | 9636581 | 0 | 25680 | 0 | 582109 | 458926 | 208303 | 474240 | 0 | 0 | 0 | 32282.88 | 1165680 | 3135 | 0 | 5825000 | 3011000 | 5383790 | 0 | 0 | 12029090.91 | 0 | 123530358.79 | 271169922.42