## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 25-02-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-02-2026 | during | 25-02-2026 | during | 25-02-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 320 | 303 | 412 | 412 | 412 | 412 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 333 | 335 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 16.2 | 32.2 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 30 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20.8 | 15 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 19 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 42 | 16 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 45 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 51 | 87 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 17 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 99 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 15 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 325 | 350 | 584 | 584 | 584 | 584 | FGMO
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 405 | 396 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 90 | 125 | 160 | 160 | 52 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1701 | 1938.2 | 5945.22 | 5915.22 | 3136.05 | 3214.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | U#1 Under maintenance, U#2 Running
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 20 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 75 | 75 | 75 | 75 | 75 | 75 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 219 | 220 | 220 | 220 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 64 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 32 | 32 | 32 | 32 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 68 | 68 | 68 | 68 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 3 | 11 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.4 | 0 | 3.4 | 0 | 3.4 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 51 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 15 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1183 | 1150 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 16 | 9 | 3 | 12 | 3 | 12 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 720 | 720 | 905 | 905 | 905 | 905 | ps availability is less
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2257.4 | 2364 | 3786.26 | 3787.86 | 3264.9 | 3266.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 127 | 192 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 270 | 290 | 353.35 | 353.35 | 353.35 | 353.35 | FGMO
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 210 | 0 | 318.81 | 318.81 | 318.81 | 318.81 | FGMO ON
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 20 | 160 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 41.65 | 41.65 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 100 | 100 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 51 | 51 | 51 | 51 | 51 | Machine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 60 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 42 | 42 | 42 | 42 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 98 | 90 | 163 | 163 | 110 | 110 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 78 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 132 | 134 | 84 | 80 | 146 | 146 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 62 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 41 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 962 | 1137 | 2746.51 | 2682.51 | 2521.01 | 2461.01
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-02-2026 | during | 25-02-2026 | during | 25-02-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 10 | 0 | 157.5 | 157.5 | 70 | 70 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 47 | 67 | 50 | 50 | 20 | 50 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 107 | 60 | 115 | 60 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 14.3 | 0 | 45.12 | 0 | 45.12 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 138.3 | 180 | 391.22 | 399 | 220.22 | 258
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 42 | 42 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 53 | 53 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 141 | 154 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 85 | 86 | 86 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 98 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 404 | 354 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1158 | 1113 | 1162 | 1162 | 1074 | 1074
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 861 | 860 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 209 | 164 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 28 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1028 | 1063 | 1148.28 | 1148.28 | 1070 | 1070 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2126 | 2087 | 3500.28 | 3420.28 | 2667.1 | 2587.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 125 | 130 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 537 | 555 | 622 | 622 | 622 | 622 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 15 | 15 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 284 | 274 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.34 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2700.36 | 1166.34 | 1179 | 1539 | 1539 | 1404 | 1404
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 22.12 | 0 | 50 | 0 | 50 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 165 | 160 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | machine problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 30 | 30 | 30 | 30 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.33 | 0 | 5.45 | 0 | 5.45 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1379.02 | 1453.43 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 22.6 | 0 | 0 | 0 | 0 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 60 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2066.07 | 2062.43 | 3106.32 | 2950.87 | 2985.94 | 2830.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.8 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 16 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 169 | 0 | 167.86 | 0 | 167.86 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 188.8 | 120 | 451.06 | 248 | 431.06 | 228
System Total |  |  |  |  | 28823.2 | 28385.703 | 11763.91 | 12180.63 | 22627.87 | 22104.74 | 17704.28 | 17323.15
Forecast Scenario (25-02-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 10810 |  | 0 |  | 10810
|  |  |  | 1:00 | 10370 |  | 0 |  | 10370
|  |  |  | 2:00 | 9990 |  | 0 |  | 9990
|  |  |  | 3:00 | 10170 |  | 0 |  | 10170
|  |  |  | 4:00 | 11120 |  | 0 |  | 11120
|  |  |  | 5:00 | 10090 |  | 0 |  | 10090
|  |  |  | 6:00 | 9120 |  | 0 |  | 9120
|  |  |  | 7:00 | 9150 |  | 0 |  | 9150
|  |  |  | 8:00 | 9750 |  | 0 |  | 9750
|  |  |  | 9:00 | 10640 |  | 0 |  | 10640
|  |  |  | 10:00 | 11170 |  | 0 |  | 11170
|  |  |  | 11:00 | 11480 |  | 0 |  | 11480
|  |  |  | 12:00 | 11760 |  | 0 |  | 11760
|  |  |  | 13:00 | 12160 |  | 0 |  | 12160
|  |  |  | 14:00 | 12510 |  | 0 |  | 12510
|  |  |  | 15:00 | 12160 |  | 0 |  | 12160
|  |  |  | 16:00 | 12080 |  | 0 |  | 12080
|  |  |  | 17:00 | 12360 |  | 0 |  | 12360
|  |  |  | 18:00 | 11620 |  | 0 |  | 11620
|  |  |  | 18:30 | 11800 |  | 0 |  | 11800
|  |  |  | 19:00 | 12050 |  | 0 |  | 12050
|  |  |  | 19:30 | 12180 |  | 0 |  | 12180
|  |  |  | 20:00 | 12140 |  | 0 |  | 12140
|  |  |  | 21:00 | 12110 |  | 0 |  | 12110
|  |  |  | 22:00 | 11950 |  | 0 |  | 11950
|  |  |  | 23:00 | 11400 |  | 0 |  | 11400
Probable Maximum Temperature: |  |  | 31.90°C
Probable Maximum Demand at Day Peak: |  |  | 11760.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12180.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12180.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 268.16 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:08 hrs on 25-02-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 24-02-2026 | [28 empty] | Date: | 24-02-2026 | [28 empty] | Date: | 24-02-2026 | [28 empty] | Date: | 24-02-2026 | [28 empty] | Date: | 24-02-2026 | [17 empty] | Date: | 24-02-2026
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [17 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 18 | 17 | 0 | 400 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 36 | 905 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1005 | 0 | 0 | 0 | 0 | 330 | 280 | 51 | 0 | 150 | 0 | 0 | 104 | 0 | 0 | 20 | 0 | 112 | 0 | 0 | 0 | 305 | 0 | 375 | 41 | 53 | 141 | 0 | 22 | 0 | 86 | 0 | 0 | 0 | 100 | 17 | 59 | 19 | 19 | 0 | 0 | 6 | 6008 | 861 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 0 | 0 | 0 | 1117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 130 | 220 | 0 | 0 | 450 | 0 | 4803 | 10811 | 92.53
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 18 | 18 | 0 | 350 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 36 | 905 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 900 | 0 | 0 | 0 | 0 | 305 | 280 | 51 | 0 | 150 | 0 | 0 | 104 | 0 | 0 | 20 | 0 | 116 | 0 | 0 | 0 | 305 | 0 | 340 | 41 | 53 | 141 | 0 | 17 | 0 | 86 | 0 | 0 | 0 | 101 | 17 | 59 | 19 | 9 | 0 | 0 | 6 | 5749 | 861 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 971 | 0 | 0 | 0 | 1027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 130 | 220 | 0 | 0 | 450 | 0 | 4623 | 10372 | 92.52
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 18 | 18 | 0 | 330 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 36 | 905 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 900 | 0 | 0 | 0 | 0 | 305 | 280 | 51 | 0 | 150 | 0 | 0 | 105 | 0 | 0 | 20 | 0 | 114 | 0 | 0 | 0 | 310 | 0 | 339 | 41 | 53 | 142 | 0 | 17 | 0 | 22 | 0 | 0 | 0 | 100 | 17 | 59 | 19 | 9 | 0 | 0 | 6 | 5522 | 861 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 906 | 0 | 0 | 0 | 1030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 130 | 180 | 0 | 0 | 450 | 0 | 4476 | 9998 | 92.51
03:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 300 | 0 | 0 | 0 | 35 | 18 | 18 | 0 | 310 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 36 | 905 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 900 | 0 | 0 | 0 | 0 | 305 | 280 | 51 | 0 | 150 | 0 | 0 | 105 | 0 | 0 | 20 | 0 | 106 | 0 | 0 | 0 | 305 | 0 | 340 | 41 | 53 | 140 | 0 | 17 | 0 | 86 | 0 | 0 | 0 | 100 | 17 | 76 | 47 | 9 | 0 | 0 | 6 | 5677 | 861 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 899 | 0 | 0 | 0 | 1025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 130 | 220 | 0 | 0 | 450 | 0 | 4496 | 10173 | 92.5
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 18 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 37 | 905 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1106 | 0 | 0 | 0 | 20 | 295 | 260 | 51 | 0 | 150 | 0 | 0 | 105 | 0 | 0 | 20 | 0 | 118 | 0 | 0 | 0 | 305 | 0 | 360 | 41 | 53 | 155 | 0 | 17 | 0 | 86 | 0 | 0 | 0 | 100 | 17 | 98 | 47 | 9 | 0 | 0 | 3 | 6218 | 861 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 990 | 0 | 0 | 0 | 1119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 130 | 220 | 0 | 0 | 480 | 0 | 4902 | 11120 | 92.49
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 18 | 17 | 0 | 420 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 36 | 805 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 962 | 0 | 0 | 0 | 25 | 310 | 260 | 5 | 0 | 150 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 112 | 0 | 0 | 0 | 300 | 0 | 341 | 41 | 53 | 155 | 0 | 17 | 0 | 11 | 0 | 0 | 0 | 100 | 17 | 59 | 19 | 7 | 0 | 0 | 6 | 5575 | 861 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 979 | 0 | 0 | 0 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 130 | 180 | 0 | 0 | 510 | 0 | 4519 | 10094 | 92.48
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 18 | 18 | 0 | 300 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 37 | 720 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 841 | 0 | 0 | 0 | 25 | 295 | 260 | 5 | 0 | 150 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 102 | 0 | 0 | 0 | 310 | 0 | 326 | 41 | 53 | 142 | 0 | 17 | 0 | 11 | 0 | 0 | 0 | 100 | 17 | 59 | 19 | 5 | 0 | 0 | 6 | 5110 | 862 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 811 | 0 | 0 | 0 | 822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 100 | 180 | 0 | 0 | 370 | 0 | 4017 | 9127 | 92.47
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 240 | 0 | 0 | 1 | 0 | 17 | 18 | 0 | 330 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0.24 | 75 | 0 | 10 | 720 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 870 | 2 | 0 | 0 | 24 | 320 | 260 | 5 | 0 | 177 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 96 | 0 | 4 | 0 | 310 | 0 | 356 | 41 | 53 | 142 | 1 | 17 | 0 | 11 | 0 | 0 | 0 | 100 | 0 | 59 | 19 | 9 | 0 | 1.85 | 6 | 5177.09 | 861 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 769 | 0 | 0 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 2.24 | 140 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.12 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.2 | 7 | 0.03 | 0 | 140 | 100 | 180 | 0 | 0 | 310 | 0 | 3980.29 | 9157.38 | 92.46
08:00 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 240 | 0 | 0 | 4 | 0 | 21 | 18 | 0 | 330 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1 | 75 | 0 | 6 | 720 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 1056 | 7 | 0 | 0 | 20 | 320 | 260 | 34 | 0 | 187 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 98 | 0 | 18 | 0 | 305 | 0 | 354 | 41 | 53 | 152 | 3 | 17 | 0 | 81 | 0 | 0 | 0 | 100 | 0 | 59 | 19 | 11 | 0 | 5.84 | 6 | 5517.84 | 839 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 769 | 0 | 0 | 0 | 1032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.25 | 2 | 0 | 0 | 6.78 | 140 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0.62 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0.9 | 37 | 0.17 | 0 | 201 | 100 | 180 | 0 | 0 | 300 | 0 | 4237.72 | 9755.56 | 92.45
09:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 335 | 0 | 0 | 6 | 0 | 20.8 | 17 | 0 | 300 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1.85 | 75 | 0 | 6 | 720 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1150 | 12 | 0 | 0 | 20 | 280 | 230 | 51 | 0 | 166 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 106 | 0 | 35 | 0 | 305 | 0 | 376 | 41 | 53 | 145 | 5 | 17 | 0 | 83 | 0 | 0 | 0 | 100 | 0 | 59 | 19 | 11 | 0 | 9.37 | 6 | 5876.02 | 843 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 840 | 0 | 0 | 0 | 1179.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.67 | 11 | 0 | 0 | 7.11 | 149 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.78 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 2.4 | 66 | 0.19 | 0 | 274 | 130 | 220 | 0 | 0 | 325 | 0 | 4727.89 | 10603.91 | 92.44
10:00 | 0 | 17 | 21 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 10 | 5 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 335 | 0 | 0 | 7 | 70 | 20.8 | 14 | 0 | 300 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 2.25 | 75 | 0 | 4 | 720 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1146 | 16 | 0 | 0 | 20 | 280 | 230 | 44 | 0 | 170 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 108 | 0 | 50 | 0 | 310 | 0 | 367 | 42 | 53 | 140 | 9 | 17 | 0 | 83 | 0 | 0 | 0 | 100 | 0 | 59 | 19 | 10 | 1 | 15.71 | 6 | 6011.76 | 860 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 912 | 0 | 0 | 0 | 1318.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.85 | 62 | 0 | 0 | 7.77 | 155 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.76 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 3.8 | 50 | 0.19 | 0 | 273 | 125 | 220 | 0 | 0 | 415 | 0 | 5113.12 | 11124.88 | 92.44
11:00 | 0 | 35 | 52 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 16.6 | 17 | 51 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 335 | 0 | 0 | 10 | 70 | 20.5 | 14 | 0 | 300 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 3.24 | 75 | 0 | 3 | 720 | 0 | 0 | 1 | 0 | 0 | 219 | 0 | 0 | 0 | 1160 | 19 | 0 | 0 | 20 | 280 | 230 | 44 | 0 | 173 | 0 | 0 | 99 | 0 | 0 | 20 | 0 | 122 | 0 | 41 | 0 | 305 | 0 | 389 | 42 | 53 | 138 | 7 | 17 | 0 | 83 | 0 | 0 | 0 | 100 | 0 | 59 | 47 | 10 | 2 | 11.54 | 6 | 6139.88 | 860 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 973 | 0 | 0 | 0 | 1325.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.61 | 43 | 0 | 0 | 10.73 | 163 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 2.41 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 2.7 | 169 | 0.39 | 0 | 276 | 125 | 220 | 0 | 0 | 475 | 0 | 5341.36 | 11481.24 | 92.43
12:00 | 0 | 35 | 42 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 16.2 | 17 | 51 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 333 | 0 | 0 | 15 | 90 | 20.8 | 14 | 0 | 325 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 3.4 | 75 | 0 | 3 | 720 | 0 | 0 | 20 | 0 | 0 | 217 | 0 | 0 | 0 | 1183 | 20 | 0 | 0 | 20 | 270 | 210 | 44 | 0 | 127 | 0 | 0 | 98 | 0 | 0 | 20 | 0 | 132 | 0 | 41 | 0 | 310 | 0 | 404 | 42 | 53 | 141 | 8 | 17 | 0 | 83 | 0 | 0 | 0 | 100 | 0 | 59 | 47 | 10 | 2 | 14.3 | 6 | 6216.7 | 861 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 1028 | 0 | 0 | 0 | 1379.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.12 | 60 | 0 | 0 | 22.6 | 165 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.33 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 3.8 | 169 | 0.34 | 0 | 284 | 125 | 220 | 0 | 0 | 537 | 0 | 5547.21 | 11763.91 | 92.43
13:00 | 0 | 35 | 42 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 25 | 17 | 72 | 0 | 30 | 0 | 17 | 76 | 0 | 0 | 0 | 440 | 0 | 17 | 333 | 0 | 0 | 26 | 90 | 20.8 | 14 | 0 | 325 | 10 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 3.34 | 75 | 10 | 0 | 720 | 0 | 0 | 0 | 0 | 15 | 215 | 0 | 0 | 0 | 1160 | 19 | 13 | 0 | 20 | 270 | 44 | 44 | 0 | 128 | 0 | 6 | 98 | 11 | 0 | 20 | 0 | 144 | 0 | 44 | 0 | 315 | 0 | 397 | 42 | 53 | 143 | 7 | 17 | 0 | 85 | 0 | 0 | 0 | 97 | 0 | 59 | 47 | 6 | 2 | 26.01 | 6 | 6317.15 | 860 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 1100 | 0 | 0 | 0 | 1461.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.1 | 96 | 0 | 0 | 49.61 | 163 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.31 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 6 | 159 | 0.41 | 0 | 307 | 125 | 220 | 0 | 0 | 575 | 0 | 5850.3 | 12167.45 | 92.42
14:00 | 0 | 35 | 42 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 33 | 17 | 87 | 0 | 80 | 0 | 21 | 146 | 0 | 0 | 0 | 450 | 0 | 17 | 333 | 0 | 0 | 8 | 108 | 20.8 | 14 | 0 | 400 | 15 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 3.09 | 75 | 18 | 0 | 720 | 0 | 0 | 3 | 0 | 48 | 215 | 0 | 0 | 0 | 1160 | 17 | 35 | 0 | 15 | 290 | 0 | 44 | 0 | 212 | 0 | 37 | 97 | 41 | 0 | 20 | 0 | 144 | 0 | 57 | 0 | 315 | 0 | 382 | 42 | 53 | 149 | 4 | 17 | 0 | 85 | 0 | 0 | 0 | 98 | 0 | 59 | 47 | 6 | 2 | 21.34 | 6 | 6710.23 | 860 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 1110 | 0 | 0 | 0 | 1455.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.11 | 74 | 0 | 0 | 47.19 | 160 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.25 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 4.9 | 140 | 0.39 | 0 | 307 | 125 | 220 | 0 | 0 | 595 | 0 | 5804.98 | 12515.21 | 92.42
15:00 | 0 | 35 | 42 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 29.4 | 17 | 87 | 0 | 95 | 0 | 35 | 103 | 0 | 0 | 0 | 385 | 0 | 17 | 333 | 0 | 0 | 7 | 108 | 19 | 15 | 0 | 400 | 13 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 2.14 | 75 | 32 | 2 | 720 | 0 | 0 | 33 | 0 | 64 | 216 | 0 | 0 | 0 | 1150 | 0 | 60 | 0 | 65 | 290 | 0 | 44 | 0 | 191 | 0 | 34 | 97 | 51 | 0 | 20 | 0 | 136 | 0 | 30 | 0 | 305 | 0 | 370 | 41 | 53 | 160 | 8 | 17 | 0 | 85 | 0 | 0 | 0 | 97 | 0 | 59 | 48 | 0 | 1 | 18.78 | 6 | 6650.32 | 859 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1072 | 0 | 0 | 0 | 1460.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.34 | 68 | 0 | 0 | 34.36 | 162 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 3.33 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 3.7 | 103 | 0.3 | 0 | 273 | 125 | 180 | 0 | 0 | 560 | 0 | 5493.5 | 12143.82 | 92.41
16:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 32.2 | 17 | 87 | 0 | 95 | 0 | 35 | 102 | 0 | 0 | 0 | 345 | 0 | 17 | 333 | 0 | 0 | 8 | 108 | 20 | 19 | 0 | 420 | 15 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 1.69 | 75 | 32 | 5 | 720 | 0 | 0 | 48 | 0 | 62 | 215 | 0 | 0 | 0 | 1167 | 7 | 60 | 0 | 70 | 290 | 0 | 51 | 0 | 206 | 0 | 29 | 97 | 46 | 0 | 20 | 0 | 126 | 0 | 21 | 0 | 310 | 0 | 400 | 42 | 53 | 158 | 4 | 17 | 0 | 85 | 0 | 0 | 0 | 97 | 0 | 59 | 48 | 0 | 1 | 11.94 | 6 | 6698.83 | 860 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 1092 | 0 | 0 | 0 | 1445.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.07 | 39 | 0 | 0 | 9.99 | 159 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 1.16 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 2.2 | 61 | 0.15 | 0 | 278 | 125 | 180 | 0 | 0 | 550 | 0 | 5374.29 | 12073.12 | 92.4
17:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 36 | 17 | 87 | 0 | 95 | 0 | 35 | 104 | 0 | 0 | 0 | 390 | 0 | 17 | 333 | 0 | 0 | 3 | 108 | 17 | 19 | 0 | 428 | 16 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0.39 | 75 | 33 | 6 | 720 | 0 | 0 | 50 | 0 | 67 | 215 | 0 | 0 | 0 | 1174 | 2 | 60 | 0 | 90 | 290 | 0 | 51 | 0 | 208 | 0 | 34 | 99 | 51 | 0 | 20 | 0 | 126 | 0 | 7 | 0 | 325 | 0 | 404 | 42 | 53 | 156 | 1 | 17 | 0 | 86 | 0 | 0 | 0 | 97 | 0 | 59 | 48 | 0 | 0 | 6.82 | 6 | 6812.21 | 860 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1110 | 0 | 0 | 0 | 1456.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.64 | 11 | 0 | 0 | 6.05 | 164 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.56 | 0 | 0 | 40 | 4 | 49 | 0 | 0 | 0 | 0.9 | 20 | 0.06 | 0 | 307 | 125 | 220 | 0 | 0 | 570 | 0 | 5533.26 | 12345.47 | 92.39
18:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 33.7 | 17 | 87 | 30 | 95 | 0 | 35 | 105 | 0 | 0 | 0 | 450 | 0 | 17 | 270 | 0 | 0 | 0 | 142 | 15 | 19 | 0 | 340 | 16 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 45 | 16 | 720 | 0 | 0 | 50 | 0 | 66 | 187 | 0 | 0 | 0 | 1122 | 0 | 60 | 0 | 120 | 270 | 0 | 51 | 0 | 178 | 0 | 60 | 50 | 72 | 0 | 20 | 0 | 116 | 0 | 0 | 0 | 315 | 0 | 344 | 42 | 53 | 157 | 0 | 17 | 0 | 28 | 0 | 0 | 0 | 97 | 0 | 107 | 48 | 0 | 0 | 0 | 6 | 6543.7 | 861 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 1346.6 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 110 | 180 | 0 | 0 | 500 | 0 | 5078.6 | 11622.3 | 92.38
19:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 32.2 | 17 | 87 | 30 | 95 | 0 | 35 | 103 | 0 | 0 | 0 | 340 | 0 | 17 | 335 | 0 | 0 | 0 | 142 | 15 | 20 | 0 | 350 | 15 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 50 | 6 | 720 | 0 | 0 | 50 | 0 | 65 | 219 | 0 | 0 | 0 | 1160 | 0 | 60 | 0 | 150 | 270 | 0 | 51 | 0 | 198 | 0 | 67 | 90 | 83 | 0 | 20 | 0 | 130 | 0 | 0 | 0 | 285 | 0 | 376 | 42 | 53 | 145 | 0 | 17 | 0 | 86 | 0 | 0 | 0 | 97 | 0 | 109 | 67 | 0 | 0 | 0 | 6 | 6770.2 | 860 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 1434.18 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 125 | 220 | 0 | 0 | 555 | 0 | 5283.18 | 12053.38 | 92.37
19:30 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 32.2 | 17 | 87 | 30 | 45 | 0 | 35 | 99 | 0 | 0 | 0 | 396 | 0 | 17 | 335 | 0 | 0 | 0 | 125 | 15 | 19 | 0 | 350 | 15 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 51 | 11 | 720 | 0 | 0 | 50 | 0 | 64 | 219 | 0 | 0 | 0 | 1150 | 0 | 60 | 0 | 160 | 290 | 0 | 51 | 0 | 192 | 0 | 62 | 90 | 78 | 0 | 20 | 0 | 134 | 0 | 0 | 0 | 310 | 0 | 354 | 42 | 53 | 154 | 0 | 17 | 0 | 85 | 0 | 0 | 0 | 98 | 0 | 107 | 67 | 0 | 0 | 0 | 6 | 6732.2 | 860 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1063 | 0 | 0 | 0 | 1453.43 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 130 | 220 | 0 | 0 | 555 | 0 | 5448.43 | 12180.63
20:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 30.5 | 17 | 87 | 0 | 15 | 0 | 35 | 99 | 0 | 0 | 0 | 390 | 0 | 17 | 335 | 0 | 0 | 0 | 108 | 20 | 19 | 0 | 350 | 15 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 50 | 18 | 720 | 0 | 0 | 50 | 0 | 64 | 221 | 0 | 0 | 0 | 1132 | 0 | 30 | 0 | 220 | 280 | 0 | 51 | 0 | 192 | 0 | 64 | 102 | 78 | 0 | 20 | 0 | 134 | 0 | 0 | 0 | 310 | 0 | 357 | 42 | 53 | 156 | 0 | 17 | 0 | 85 | 0 | 0 | 0 | 98 | 0 | 108 | 68 | 0 | 0 | 0 | 6 | 6682.5 | 860 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1078 | 0 | 0 | 0 | 1449.39 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 130 | 220 | 0 | 0 | 555 | 0 | 5459.39 | 12141.89 | 92.36
21:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 30.1 | 17 | 60 | 0 | 0 | 0 | 35 | 97 | 0 | 0 | 0 | 395 | 0 | 17 | 335 | 0 | 0 | 0 | 90 | 15 | 19 | 0 | 350 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 15 | 27 | 720 | 0 | 0 | 19 | 0 | 63 | 222 | 0 | 0 | 0 | 1162 | 0 | 0 | 0 | 340 | 300 | 0 | 51 | 0 | 198 | 0 | 63 | 101 | 51 | 0 | 17 | 0 | 132 | 0 | 0 | 0 | 310 | 0 | 380 | 42 | 53 | 157 | 0 | 17 | 0 | 85 | 0 | 0 | 0 | 98 | 0 | 108 | 45 | 0 | 0 | 0 | 6 | 6663.1 | 860 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1082 | 0 | 0 | 0 | 1444.35 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 130 | 220 | 0 | 0 | 555 | 0 | 5452.35 | 12115.45 | 92.35
22:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 29.8 | 17 | 30 | 0 | 0 | 0 | 17 | 72 | 0 | 0 | 0 | 400 | 0 | 17 | 335 | 0 | 0 | 0 | 70 | 15 | 20 | 0 | 400 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 15 | 25 | 720 | 0 | 0 | 19 | 0 | 65 | 223 | 0 | 0 | 0 | 1161 | 0 | 0 | 0 | 300 | 300 | 0 | 51 | 0 | 200 | 0 | 64 | 102 | 49 | 0 | 17 | 0 | 126 | 0 | 0 | 0 | 315 | 0 | 378 | 41 | 53 | 160 | 0 | 17 | 0 | 85 | 0 | 0 | 0 | 98 | 0 | 95 | 35 | 0 | 0 | 0 | 6 | 6573.8 | 860 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1092 | 0 | 0 | 0 | 1448.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 130 | 220 | 0 | 0 | 555 | 0 | 5376.78 | 11950.58 | 92.34
23:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 299 | 0 | 0 | 17.2 | 0 | 17 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 0 | 385 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 15 | 20 | 0 | 400 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 26 | 720 | 0 | 0 | 0 | 0 | 34 | 222 | 0 | 0 | 0 | 1140 | 0 | 0 | 0 | 280 | 280 | 0 | 51 | 0 | 199 | 0 | 40 | 102 | 17 | 0 | 17 | 0 | 132 | 0 | 0 | 0 | 305 | 0 | 352 | 41 | 53 | 154 | 0 | 17 | 0 | 85 | 0 | 0 | 0 | 97 | 0 | 59 | 19 | 0 | 0 | 0 | 6 | 6117.2 | 868 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1077 | 0 | 0 | 0 | 1450.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 130 | 220 | 0 | 0 | 555 | 0 | 5329.38 | 11446.58 | 92.33
Total KWH | 0 | 403200 | 430080 | 0 | 0 | 0 | 0 | 0 | 7898400 | 0 | 0 | 378720 | 241920 | 1061712 | 51840 | 608705 | 0 | 363242 | 1077120 | 0 | 0 | 0 | 9017733 | 0 | 187850 | 7550067 | 0 | 0 | 94829 | 1480800 | 420600 | 416520 | 0 | 8720454.55 | 124200 | 0 | 0 | 0 | 278880 | 0 | 0 | 0 | 0 | 0 | 21359 | 1799580 | 356300 | 448800 | 18327272.73 | 0 | 0 | 393120 | 0 | 678291 | 4943471 | 0 | 0 | 0 | 25936362 | 121095 | 456654 | 0 | 2097000 | 7441200 | 3392000 | 1082052 | 0 | 4290000 | 0 | 557760 | 2222966 | 595200 | 0 | 470900 | 0 | 2893440 | 0 | 383682 | 0 | 7477000 | 0 | 9010000 | 984000 | 1335840 | 3594272.73 | 61786 | 401832 | 0 | 1657920 | 0 | 0 | 0 | 2369130 | 121320 | 1738800 | 885600 | 120960 | 10450 | 178840 | 145680 | 149808808.01 | 20656727 | 4926240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303840 | 23890910 | 0 | 0 | 0 | 29541091 | 0 | 0 | 0 | 0 | 162432 | 0 | 0 | 0 | 0 | 156380 | 456643 | 0 | 0 | 224240 | 3818000 | 0 | 0 | 0 | 0 | 0 | 9496072 | 0 | 21360 | 0 | 0 | 344395 | 153410 | 439728 | 0 | 0 | 0 | 32362.68 | 938160 | 2836 | 0 | 6088000 | 2862000 | 5306210 | 0 | 0 | 12178909.09 | 0 | 121999945.77 | 271808753.78

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 24-02-2026
Power Supply Scenario
| Day Peak Generation |  |  | 11763.91 | MW | 12:00 Hr. | Energy Generated |  |  | 271.8088 |  | MKWHr.
| Day Peak Demand |  |  | 11763.91 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.135 |  | MKWHr.
| Evening Peak Generation |  |  | 12180.63 | MW | 19:30 Hr. | Energy Demand |  |  | 271.9438 |  | MKWHr.
| Evening Peak Demand |  |  | 12180.63 | MW | 19:30 Hr. | Maximum Temperature |  |  | 32.1 |  | °C
| Minimum Generation of the Day |  |  | 9127 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 826.01 |  | MMCFD
| Maximum Generation of the Day |  |  | 12515.21 | MW | 14:00 Hr. | Production Cost per KWHr |  |  | 5.6204 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.0238 | 0 | 6.2852 | 0 | 0 | 0.094829 | 0 | 0 | 40.4038 | Gas | 113.7716 | Gas | 391290107.8251
| Chattogram Zone |  |  | 5.3923 | 44.2636 | 1.5519 | 0 | 1.7996 | 0.14245 | 0 | 0.27888 | 53.4287 | Coal | 86.4215 | Coal | 562161229.7591
| Cumilla Zone |  |  | 20.9961 | 0 | 1.6096 | 0 | 0 | 0.38368 | 2.8934 | 0 | 25.8829 | HFO | 13.2847 | HFO | 217538567.56
| Mymensingh Zone |  |  | 0.12096 | 0 | 2.8914 | 0 | 0 | 0.18929 | 0 | 0 | 3.2016 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.83 | 0 | 0 | 0 | 0 | 0.061786 | 0 | 0 | 26.8918 | Hydro | 1.7996 | Hydro | 179958
| Khulna Zone |  |  | 4.9262 | 23.8909 | 0 | 0 | 0 | 0.30384 | 20.6567 | 0 | 49.7777 | Solar | 3.1613 | Solar | 50768082.916
| Barishal Zone |  |  | 8.1682 | 18.2669 | 0 | 0 | 0 | 0.002836 | 0 | 0 | 26.438 | Import | 53.0913 | Import | 301621443.37
| Rajshahi Zone |  |  | 13.3141 | 0 | 0.16243 | 0 | 0 | 0.85862 | 29.5411 | 0 | 43.8762 | Wind | 0.27888 | Wind | 4102324.8
| Rangpur Zone |  |  | 0 | 0 | 0.78412 | 0 | 0 | 1.1239 | 0 | 0 | 1.9081
| Total |  |  | 113.7716 | 86.4215 | 13.2847 | 0 | 1.7996 | 3.1613 | 53.0913 | 0.27888 | 271.8088
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 391290107.8251 |  | Hydro | 179958
|  |  |  | Coal | 562161229.7591 |  | Solar | 50768082.916
|  |  |  | HFO | 217538567.56 |  | Import | 301621443.37
|  |  |  | HSD | 0 |  | Wind | 4102324.8
[5 empty] | Total: | 152,76,61,714 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.6567 | Peak Hr Flow | 860.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 34050002.15 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 29.5411 | Peak Hr Flow | 1453.43 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1839 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.8934 | Peak Hr Flow | 134.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2288 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.0913 | Peak Hr Flow | 2447.43 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4637
|  |  |  | Chattogram |  | 0 |  | 1320
|  |  |  | Cumilla |  | 0 |  | 1023
|  |  |  | Mymensingh |  | 0 |  | 994
|  |  |  | Sylhet |  | 0 |  | 414
|  |  |  | Khulna |  | 0 |  | 1285
|  |  |  | Barishal |  | 0 |  | 339
|  |  |  | Rajshahi |  | 0 |  | 1118
|  |  |  | Rangpur |  | 0 |  | 715
|  |  |  | Total |  | 0 |  | 11845
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:57 | 15:49 | Bakulia-Sikalbaha 132 kV Ckt-2 Project Work S/D from Bakulia 132/33kV end Due to Shutdown
taken by Shikalbaha 230KV Grid S/S for their maintenance work.
| 10:06 | 12:11 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) LT Scheduled S/D Due to Maintenance work
at T-4 (25/41 MVA) Buchholz relay oil lekage
| 10:07 | 12:10 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) HT Scheduled S/D Due to Maintenance work
at T-4 (25/41 MVA) Buchholz relay oil lekage
|  | 10:07 | Sirajganj-Ullahpara 132KV Ckt-1 is restored.
| 10:21 | 14:35 | Madanganj 132/33kV S/S Madanganj -Bashundhara 132 kv Ckt Forced S/D Due to Main Bus DS PI | [7 empty] | 7.0MW load
|  |  | damage | [7 empty] | interrup.
| 10:34 |  | APL Godda 400 KV Bus Reactor was shut down.
| 10:36 | 12:02 | Goalpara 132/33kV S/S Goalpara-NWPGCL Scheduled S/D Due to Maintenance
| 12:00 |  | Day Peak Generation: 11760 MW.
| 12:01 | 13:08 | Patuakhali 132/33kV S/S 415T (T-2) HT Scheduled S/D Due to Oil leakage maintenance.
| 12:01 | 13:09 | Patuakhali 132/33kV S/S 415T (T-2) LT Scheduled S/D Due to Oil leakage maintenance.
| 13:24 |  | Ashuganj (South) 360 MW CCPP was shut down due to gas shortage.
| 14:35 |  | Rooppur Nuclear Power Plant 230KV BUS-2 Charged
|  | 15:49 | Bakulia-Sikalbaha 132 kV Ckt-2 is restored.
|  | 19:14 | Baghabari-Ullahpara 132 kV Ckt-1 is restored.
| 19:14 |  | Baghabari--Ullahpara 132 kv ckt Syn at 19:14 (S/D from 19/12/2025)
|  | 19:15 | Sirajganj-Ullahpara 132KV Ckt-2 is restored.
| 19:30 |  | Evening Peak Generation: 12180 MW.
| 06:00 |  | Minimum generation 9125 MW
| 07:19 |  | Sirajgonj 225MW CCPP Unit-1 Shutdown with remarks:- ST
| 07:49 |  | Kaliakoir 400/230/132kV S/S 400kV Bus 1 Scheduled S/D Due to BBK Project work.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 24-02-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0"MW due to gas restriction by Titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 303 | 7898400 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7550067 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 32.2 | 378720 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 30 | 51840 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 363242 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 187850 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 15 | 420600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 19 | 416520 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 430080 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 45 | 608705 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 87 | 1061712 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 403200 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 99 | 1077120 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 94829 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 241920 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 350 | 8720454.55 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 396 | 9017733 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 125 | 1480800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1938.2 | 40403792.55
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 121095 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 393120 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 75 | 1799580 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 4943471 | Plant availability less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 64 | 678291 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 11 | 448800 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21359 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 51 | 356300 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 15 | 124200 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1150 | 25936362 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 9 | 278880 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 720 | 18327272.73 | ps availability is less
Chattogram Area Total |  |  |  |  | 4898.863 | 2364 | 53428730.73
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 192 | 4290000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 290 | 7441200 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 3392000 | FGMO ON
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 160 | 2097000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1082052 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 60 | 456654 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2222966 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 78 | 595200 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 134 | 2893440 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 470900 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 62 | 557760 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 383682 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1137 | 25882854
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 120960 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 67 | 885600 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 107 | 1738800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 178840 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 145680 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 121320 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 180 | 3201650
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 61786 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 984000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 53 | 1335840 | GT3,4 are not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 154 | 3594272.73 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1657920 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 98 | 2369130 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 401832 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7477000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 354 | 9010000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1113 | 26891780.73
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 860 | 20656727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 164 | 4926240 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 303840 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1063 | 23890910 | FGMO, plant availability zero
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2087 | 49777717
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 2862000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 555 | 12178909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5306210 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 274 | 6088000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2836 | -
Barishal Area Total |  |  |  |  | 2700.36 | 1179 | 26437955.09
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 156380 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 160 | 3818000 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9496072 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 162432 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 21360 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1453.43 | 29541091 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 224240 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 456643 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2062.43 | 43876218
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 439728 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 32362.68 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 344395 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 153410 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 938160 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 120 | 1908055.68
Eastern Grid Total |  |  |  |  | 17400.108 | 6732.2 | 149808808.01
Western Grid Total |  |  |  |  | 10985.595 | 5448.43 | 121999945.77
National Grid Total |  |  |  |  | 28385.703 | 12180.63 | 271808753.78
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 24-02-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8388.19 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3456.5 | MW
i) Dhaka area |  |  | 4637.39 |  | MW | i) Khulna area |  |  |  | 1285 | MW
ii) Chattogram area |  |  | 1319.8 |  | MW | ii) Barishal area |  |  |  | 338.9 | MW
iii) Cumilla area |  |  | 1023 |  | MW | iii) Rajshahi area |  |  |  | 1117.6 | MW
iv) Mymensingh area |  |  | 994 |  | MW | iv) Rangpur area |  |  |  | 715 | MW
v) Sylhet area |  |  | 414 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11844.69 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 79 | 19:00 | 133 | Nawabganj | 31.6 | 14:00
2 | AKSML | 12 | 09:00 | 68 | Hathazari | 62 | 21:00 | 134 | Netrakona | 135 | 17:00
3 | Aftabnagar | 32 | 13:00 | 69 | Hatirjheel | 35 | 14:00 | 135 | New | 68 | 14:00
4 | Agargaon | 88 | 13:00 | 70 | Ishurdi | 57 | 04:00 | 136 | Niamatpur | 91 | 11:00
5 | Agrabad | 48 | 12:00 | 71 | Jaldhaka | 62 | 18:00 | 137 | Noapara | 36 | 19:00
6 | Amnura | 34 | 13:00 | 72 | Jamalpur | 111 | 04:00 | 138 | PHP | 9 | 14:00
7 | Ashuganj | 72 | 14:00 | 73 | Jashore | 102 | 18:00 | 139 | Pabna | 72 | 18:00
8 | BSRM | 197 | 19:30 | 74 | Jhenaidah | 74 | 18:00 | 140 | Palashbari | 94 | 14:00
9 | Bagerhat | 63 | 19:00 | 75 | Joydebpur | 112 | 12:00 | 141 | Panchagarh | 43 | 18:00
10 | Bajitpur | 67 | 18:30 | 76 | Joypurhat | 54 | 09:00 | 142 | Patiya | 7.5 | 20:00
11 | Bakerganj | 10.08 | 20:00 | 77 | Juldah | 20 | 15:00 | 143 | Patuakhali | 40.5 | 21:00
12 | Bakulia | 78 | 19:30 | 78 | KSRM | 28 | 13:00 | 144 | Payra | 30 | 20:00
13 | Banani | 45.6 | 13:00 | 79 | Kabirpur | 240 | 16:00 | 145 | Postogola | 46 | 13:00
14 | Bangabhaban | 14 | 10:00 | 80 | Kachua | 61 | 19:00 | 146 | Purbachal | 24 | 13:00
15 | Barapukuria | 65 | 13:00 | 81 | Kaliganj | 18 | 18:00 | 147 | Purbasadipur | 117 | 14:00
16 | Barguna | 16 | 21:00 | 82 | Kallyanpur | 90 | 14:00 | 148 | Rahanpur | 25 | 04:00
17 | Barishal | 79 | 14:00 | 83 | Kalurghat | 37 | 15:00 | 149 | Rahim | 42 | 15:00
18 | Barishal-230 | 68 | 18:30 | 84 | Kamrangirchar | 77 | 16:00 | 150 | Rajbari | 57 | 04:00
19 | Baroaulia | 64 | 15:00 | 85 | Kaptai | N/A | N/A | 151 | Rajendrapur | 119 | 19:00
20 | Baroirhat | 51 | 13:00 | 86 | Kasba | 27 | 04:00 | 152 | Rajshahi | 84 | 21:00
21 | Bashundhara | 170 | 14:00 | 87 | Kazla | 98 | 13:00 | 153 | Rajshahi-230 | 54 | 17:00
22 | BashundharaCement | 8 | 08:00 | 88 | Keranigonj | 78 | 13:00 | 154 | Ramganj | 84 | 19:00
23 | Beanibazar | 48 | 19:30 | 89 | Khagrachori | 26 | 18:00 | 155 | Rampur | 33 | 19:00
24 | Benapole | 48 | 13:00 | 90 | Khulna | 39 | 10:00 | 156 | Rangamati | 15 | 18:30
25 | Bhaluka | 126 | 14:00 | 91 | Khulshi | 175 | 15:00 | 157 | Rangpur | 120 | 17:00
26 | Bhandaria | 38 | 21:00 | 92 | Kishoreganj | 101 | 20:00 | 158 | Ruppur | 3.2 | 15:00
27 | Bhangura | 33 | 04:00 | 93 | Kodda | 276 | 11:00 | 159 | SSM | 2 | 04:00
28 | Bheramara(GK) | 44 | 18:00 | 94 | Kulaura | 29 | 18:00 | 160 | Saidpur | 100 | 16:00
29 | Bhulta | 215 | 12:00 | 95 | Kurigram | 64 | 17:00 | 161 | Satkhira | 100 | 18:30
30 | Bog-Sherpur | 68 | 04:00 | 96 | Kushtia | 109 | 17:00 | 162 | Satmasjid | 81 | 14:00
31 | Bogura | 127 | 18:00 | 97 | Laksam | 24 | 13:00 | 163 | Savar | 202 | 12:00
32 | Borhanuddin | 67 | 22:00 | 98 | Lakshmipur | 17 | 19:00 | 164 | SevenRings | 17.85 | 20:00
33 | Brahmanbaria | 99 | 22:00 | 99 | Lalbag | 70 | 13:00 | 165 | ShahCement | 31 | 06:00
34 | Cantonment | 76 | 13:00 | 100 | Lalmonirhat | 44 | 18:30 | 166 | Shahjadpur | 65 | 17:00
35 | Chandina | 7 | 04:00 | 101 | MI_Cement | 17.1 | 15:00 | 167 | Shahjibazar | 100 | 22:00
36 | Chandpur | 54 | 19:30 | 102 | Madanganj | 43 | 16:00 | 168 | Shahmirpur | 47 | 23:00
37 | Chandraghona | 29 | 18:30 | 103 | Madaripur | 77 | 20:00 | 169 | Shariatpur | 58 | 19:30
38 | Chapai | 62 | 04:00 | 104 | Madartek | 68 | 18:00 | 170 | Sherpur | 148 | 18:00
39 | Charsaidpur | 42 | 02:00 | 105 | Madunaghat | 39 | 12:00 | 171 | Shikalbaha | 23 | 13:00
40 | Chauddagram | 62 | 14:00 | 106 | Magura | 45 | 19:00 | 172 | Shitalakhya | 76.7 | 15:00
41 | Chhatak | 27 | 05:00 | 107 | Mahasthangarh | 58 | 11:00 | 173 | Sholosohor | 39 | 14:00
42 | Chowmuhani | 95 | 18:00 | 108 | Maijdee | 34 | 18:30 | 174 | Shyampur | 162 | 12:00
43 | Chuadanga | 88 | 03:00 | 109 | Manikganj | 100 | 13:00 | 175 | Siddhirganj | 119 | 14:00
44 | Coxsbazar | 119 | 20:00 | 110 | Maniknagar | 48 | 22:00 | 176 | Sirajganj | 100 | 17:00
45 | Cumilla(N) | 99 | 14:00 | 111 | Matarbari | 42 | 17:00 | 177 | Sonargaon | 147 | 17:00
46 | Cumilla(S) | 145 | 14:00 | 112 | Matuail | 61 | 14:00 | 178 | Sreemongol | 56 | 21:00
47 | Daganbhuiyan | 24 | 19:00 | 113 | Metrorail_Motijheel | 0 | 00:00 | 179 | Sreepur | 108 | 16:00
48 | Daudkandi | 103 | 23:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Srinagar | 34 | 13:00
49 | DhakaUniversity | 78 | 13:00 | 115 | Millgate | 84 | 12:00 | 181 | Sunamganj | 40 | 18:00
50 | Dhamrai | 120 | 14:00 | 116 | Mirpur | 127 | 14:00 | 182 | Sylhet | 35 | 14:00
51 | Dhanmondi | 92 | 14:00 | 117 | Mirsorai | 42 | 06:00 | 183 | Sylhet-132 | 78 | 14:00
52 | Dohazari | 81 | 19:00 | 118 | Mirzapur | 41 | 18:00 | 184 | TK | 18 | 18:30
53 | Faridpur | 115 | 19:00 | 119 | Mithapukur | 54 | 04:00 | 185 | Tangail | 148 | 04:00
54 | Fatullah | 100 | 12:00 | 120 | Modern | N/A | N/A | 186 | Taraganj | 20 | 18:00
55 | Fenchuganj | 31 | 21:00 | 121 | Mogbazar | 82.6 | 13:00 | 187 | Tasnim | 23 | 19:00
56 | Feni | 75 | 18:30 | 122 | Mongla | 40 | 19:00 | 188 | Thakurgaon | 76 | 18:00
57 | GPH | 77 | 04:00 | 123 | Motijheel | 41 | 13:00 | 189 | Tongi | 157 | 11:00
58 | Ghatail | 88 | 03:00 | 124 | Muktagacha | 34 | 04:00 | 190 | Ullahpara | 31 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 79 | 14:00 | 191 | Ullon | 47 | 19:00
60 | Ghorashal-230 | 106 | 15:00 | 126 | Muradnagar | 29 | 20:00 | 192 | Uttara | 69 | 13:00
61 | Goalpara | 27 | 13:00 | 127 | Mymensingh | 186 | 18:00 | 193 | UttaraNew | 33 | 17:00
62 | Gollamari | 86 | 19:00 | 128 | Naogaon | 117 | 13:00 | 194 | Zigatola | 62 | 16:00
63 | Gopalganj | 81 | 19:00 | 129 | Narail | 43 | 19:00
64 | Gulshan | 90 | 13:00 | 130 | Narinda | 59 | 13:00
65 | Halishahar | 81 | 11:00 | 131 | Narshingdi | 146 | 19:30
66 | HaripurSBU | 121 | 19:30 | 132 | Natore | 109 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 24-02-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 10811 | 0 |  | 10811
1:00 | 10372 | 0 |  | 10372
2:00 | 9998 | 0 |  | 9998
3:00 | 10173 | 0 |  | 10173
4:00 | 11120 | 0 |  | 11120
5:00 | 10094 | 0 |  | 10094
6:00 | 9127 | 0 |  | 9127
7:00 | 9157.38 | 0 |  | 9157.38
8:00 | 9755.56 | 0 |  | 9755.56
9:00 | 10603.91 | 39 |  | 10644.67
10:00 | 11124.88 | 49 |  | 11175.88
11:00 | 11481.24 | 0 |  | 11481.24
12:00 | 11763.91 | 0 |  | 11763.91
13:00 | 12167.45 | 0 |  | 12167.45
14:00 | 12515.21 | 0 |  | 12515.21
15:00 | 12143.82 | 15 |  | 12159.82
16:00 | 12073.12 | 10 |  | 12083.57
17:00 | 12345.47 | 22 |  | 12368.47
18:00 | 11622.3 | 0 |  | 11622.3
19:00 | 12053.38 | 0 |  | 12053.38
19:30 | 12180.63 | 0 |  | 12180.63
20:00 | 12141.89 | 0 |  | 12141.89
21:00 | 12115.45 | 0 |  | 12115.45
22:00 | 11950.58 | 0 |  | 11950.58
23:00 | 11446.58 | 0 |  | 11446.58
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 24-02-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6008 | 4803 | 10811 | DAILY GENERATION CURVE
00:30 | 5878.5 | 4713 | 10591.5
01:00 | 5749 | 4623 | 10372 | 24-02-2026
01:30 | 5635.5 | 4549.5 | 10185
02:00 | 5522 | 4476 | 9998
02:30 | 5599.5 | 4486 | 10085.5
03:00 | 5677 | 4496 | 10173
03:30 | 5947.5 | 4699 | 10646.5
04:00 | 6218 | 4902 | 11120
04:30 | 5896.5 | 4710.5 | 10607
05:00 | 5575 | 4519 | 10094
05:30 | 5342.5 | 4268 | 9610.5
06:00 | 5110 | 4017 | 9127
06:30 | 5143.545 | 3998.645 | 9142.19
07:00 | 5177.09 | 3980.29 | 9157.38
07:30 | 5347.465 | 4109.005 | 9456.47
08:00 | 5517.84 | 4237.72 | 9755.56
08:30 | 5696.93 | 4482.805 | 10179.735
09:00 | 5876.02 | 4727.89 | 10603.91
09:30 | 5943.89 | 4920.505 | 10864.395
10:00 | 6011.76 | 5113.12 | 11124.88
10:30 | 6075.82 | 5227.24 | 11303.06
11:00 | 6139.88 | 5341.36 | 11481.24
11:30 | 6178.29 | 5444.285 | 11622.575
12:00 | 6216.7 | 5547.21 | 11763.91
12:30 | 6266.925 | 5698.755 | 11965.68
13:00 | 6317.15 | 5850.3 | 12167.45
13:30 | 6513.69 | 5827.64 | 12341.33
14:00 | 6710.23 | 5804.98 | 12515.21
14:30 | 6680.275 | 5649.24 | 12329.515
15:00 | 6650.32 | 5493.5 | 12143.82
15:30 | 6674.575 | 5433.895 | 12108.47
16:00 | 6698.83 | 5374.29 | 12073.12
16:30 | 6755.52 | 5453.775 | 12209.295
17:00 | 6812.21 | 5533.26 | 12345.47
17:30 | 6677.955 | 5305.93 | 11983.885
18:00 | 6543.7 | 5078.6 | 11622.3
18:30 | 6656.95 | 5180.89 | 11837.84
19:00 | 6770.2 | 5283.18 | 12053.38
19:30 | 6732.2 | 5448.43 | 12180.63
20:00 | 6682.5 | 5459.39 | 12141.89
20:30 | 6672.8 | 5455.87 | 12128.67 |  | Executive Engineer
21:00 | 6663.1 | 5452.35 | 12115.45 |  | Network Operation Division
21:30 | 6618.45 | 5414.565 | 12033.015
22:00 | 6573.8 | 5376.78 | 11950.58
22:30 | 6345.5 | 5353.08 | 11698.58
23:00 | 6117.2 | 5329.38 | 11446.58

## En-Curve
QF-LDC-12
Date | 24-02-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3275 | 1671 | 861 | 0 | 112 | 1117 | 75 | 3562 | 0 | 17 | 118 | 0 | 0 | 3 | 0 | DAILY ENERGY CURVE
00:30 | 3201.5 | 1641.5 | 861 | 0 | 114 | 1072 | 75 | 3494 | 0 | 17 | 109.5 | 0 | 0 | 6 | 0 | 24-02-2026
01:00 | 3128 | 1612 | 861 | 0 | 116 | 1027 | 75 | 3426 | 0 | 17 | 101 | 0 | 0 | 9 | 0
01:30 | 3051.5 | 1530.5 | 861 | 0 | 115 | 1028.5 | 75 | 3393.5 | 0 | 17 | 101 | 0 | 0 | 12 | 0 | Energy Generated | 271.8088 |  | MKWHr
02:00 | 2975 | 1449 | 861 | 0 | 114 | 1030 | 75 | 3361 | 0 | 17 | 101 | 0 | 0 | 15 | 0 | Energy not Served | 0.135 |  | MKWHr
02:30 | 3000.5 | 1485 | 861 | 0 | 110 | 1027.5 | 75 | 3357.5 | 0 | 30 | 123.5 | 0 | 0 | 15.5 | 0 | Total Energy Requirement | 271.9438 |  | MKWHr
03:00 | 3026 | 1521 | 861 | 0 | 106 | 1025 | 75 | 3354 | 0 | 43 | 146 | 0 | 0 | 16 | 0
03:30 | 3134.5 | 1599 | 861 | 0 | 112 | 1072 | 75 | 3557 | 0 | 51.5 | 170 | 0 | 0 | 14.5 | 0
04:00 | 3243 | 1677 | 861 | 0 | 118 | 1119 | 75 | 3760 | 0 | 60 | 194 | 0 | 0 | 13 | 0
04:30 | 3132 | 1605.5 | 861 | 0 | 115 | 1021.5 | 75 | 3608 | 0 | 30 | 147.5 | 0 | 0 | 11.5 | 0
05:00 | 3021 | 1534 | 861 | 0 | 112 | 924 | 75 | 3456 | 0 | 0 | 101 | 0 | 0 | 10 | 0
05:30 | 2937 | 1466 | 861.5 | 0 | 107 | 873 | 75 | 3182 | 0 | 0 | 101 | 0 | 0 | 8 | 0
06:00 | 2853 | 1398 | 862 | 0 | 102 | 822 | 75 | 2908 | 0 | 0 | 101 | 0 | 0 | 6 | 0
06:30 | 2935 | 1381.5 | 861.5 | 0 | 99 | 823.5 | 75 | 2858.5 | 11.69 | 0 | 92.5 | 0 | 0 | 4 | 0
07:00 | 3017 | 1365 | 861 | 0 | 96 | 825 | 75 | 2809 | 23.38 | 0 | 84 | 0 | 0 | 2 | 0
07:30 | 3002 | 1414.5 | 850 | 0 | 97 | 928.5 | 75 | 2927.5 | 66.47 | 4.5 | 86 | 0 | 0 | 5 | 0
08:00 | 2987 | 1464 | 839 | 0 | 98 | 1032 | 75 | 3046 | 109.56 | 9 | 88 | 0 | 0 | 8 | 0
08:30 | 3088.5 | 1514.4 | 841 | 0 | 102 | 1105.87 | 75 | 3177.5 | 153.965 | 12.5 | 101 | 0 | 0 | 8 | 19.5
09:00 | 3190 | 1564.8 | 843 | 0 | 106 | 1179.74 | 75 | 3309 | 198.37 | 16 | 114 | 0 | 0 | 8 | 39
09:30 | 3175 | 1568.8 | 851.5 | 0 | 107 | 1249.245 | 75 | 3387.5 | 249.85 | 62 | 131.5 | 0 | 0 | 7 | 44
10:00 | 3160 | 1572.8 | 860 | 0 | 108 | 1318.75 | 75 | 3466 | 301.33 | 108 | 149 | 0 | 0 | 6 | 49
10:30 | 3138.5 | 1566.15 | 860 | 0 | 115 | 1322.135 | 75 | 3535 | 375.475 | 132.5 | 176.3 | 0 | 0 | 7 | 24.5
11:00 | 3117 | 1559.5 | 860 | 0 | 122 | 1325.52 | 75 | 3604 | 449.62 | 157 | 203.6 | 0 | 0 | 8 | 0
11:30 | 3117 | 1581.15 | 860.5 | 0 | 127 | 1352.27 | 75 | 3678 | 439.255 | 162 | 218.4 | 0 | 0 | 12 | 0
12:00 | 3117 | 1602.8 | 861 | 0 | 132 | 1379.02 | 75 | 3752 | 428.89 | 167 | 233.2 | 0 | 0 | 16 | 0
12:30 | 3033 | 1623.3 | 860.5 | 0 | 138 | 1420.445 | 75 | 3807 | 489.835 | 167 | 332.1 | 0 | 0 | 19.5 | 0
13:00 | 2949 | 1643.8 | 860 | 0 | 144 | 1461.87 | 75 | 3862 | 550.78 | 167 | 431 | 0 | 0 | 23 | 0
13:30 | 2959.5 | 1689.3 | 860 | 0 | 144 | 1458.505 | 75 | 3877 | 514.025 | 176 | 570.5 | 0 | 0 | 17.5 | 0
14:00 | 2970 | 1734.8 | 860 | 0 | 144 | 1455.14 | 75 | 3892 | 477.27 | 185 | 710 | 0 | 0 | 12 | 0
14:30 | 2940 | 1683.4 | 859.5 | 0 | 140 | 1457.805 | 75 | 3833.5 | 397.61 | 185 | 746.7 | 0 | 0 | 11 | 7.5
15:00 | 2910 | 1632 | 859 | 0 | 136 | 1460.47 | 75 | 3775 | 317.95 | 185 | 783.4 | 0 | 0 | 10 | 15
15:30 | 2937.5 | 1631 | 859.5 | 0 | 131 | 1453.095 | 75 | 3791 | 255.075 | 176.5 | 786.8 | 0 | 0 | 12 | 12.5
16:00 | 2965 | 1630 | 860 | 0 | 126 | 1445.72 | 75 | 3807 | 192.2 | 168 | 790.2 | 0 | 0 | 14 | 10
16:30 | 3012.5 | 1682.5 | 860 | 0 | 126 | 1450.885 | 75 | 3844 | 130.31 | 168 | 847.1 | 0 | 0 | 13 | 16
17:00 | 3060 | 1735 | 860 | 0 | 126 | 1456.05 | 75 | 3881 | 68.42 | 168 | 904 | 0 | 0 | 12 | 22
17:30 | 2821 | 1671.5 | 860.5 | 0 | 121 | 1401.325 | 75 | 3802 | 34.21 | 200 | 982.85 | 0 | 0 | 14.5 | 11
18:00 | 2582 | 1608 | 861 | 0 | 116 | 1346.6 | 75 | 3723 | 0 | 232 | 1061.7 | 0 | 0 | 17 | 0
18:30 | 2756 | 1581.5 | 860.5 | 0 | 123 | 1390.39 | 75 | 3717 | 0 | 232 | 1087.45 | 0 | 0 | 15 | 0
19:00 | 2930 | 1555 | 860 | 0 | 130 | 1434.18 | 75 | 3711 | 0 | 232 | 1113.2 | 0 | 0 | 13 | 0
19:30 | 3004 | 1648 | 860 | 0 | 134 | 1453.43 | 75 | 3762 | 0 | 188 | 1047.2 | 0 | 0 | 9 | 0
20:00 | 3073 | 1656 | 860 | 0 | 134 | 1449.39 | 75 | 3759 | 0 | 133 | 988.5 | 0 | 0 | 14 | 0
20:30 | 3155.5 | 1659.5 | 860 | 0 | 133 | 1446.87 | 75 | 3777.5 | 0 | 124 | 884.8 | 0 | 0 | 12.5 | 0
21:00 | 3238 | 1663 | 860 | 0 | 132 | 1444.35 | 75 | 3796 | 0 | 115 | 781.1 | 0 | 0 | 11 | 0
21:30 | 3220.5 | 1694 | 860 | 0 | 129 | 1446.565 | 75 | 3800 | 0 | 105 | 690.45 | 0 | 0 | 12.5 | 0
22:00 | 3203 | 1725 | 860 | 0 | 126 | 1448.78 | 75 | 3804 | 0 | 95 | 599.8 | 0 | 0 | 14 | 0
22:30 | 3158 | 1710 | 864 | 0 | 129 | 1449.58 | 75 | 3784 | 0 | 69 | 447.5 | 0 | 0 | 12.5 | 0
23:00 | 3113 | 1695 | 868 | 0 | 132 | 1450.38 | 75 | 3764 | 0 | 43 | 295.2 | 0 | 0 | 11 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 24-02-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 408 | 06:00 | 388 | 12:00 | Madunaghat | 406 | 06:00 | 396 | 13:00
Amtali | 423 | 06:00 | 411 | 13:00 | Meghnaghat | 405 | 06:00 | 389 | 12:00
Ashuganj | 410 | 18:00 | 387 | 15:00 | Payra | 423 | 06:00 | 413 | 13:00
Bhulta | 410 | 18:00 | 383 | 15:00 | Rahanpur | 417 | 06:00 | 394 | 17:00
Bibiana | 415 | 06:00 | 402 | 12:00 | Rampal | 415 | 06:00 | 397 | 12:00
BIPTC | 400 | 04:00 | 390 | 13:00
Bogura | 413 | 06:00 | 384 | 17:00
Gopalganj | 416 | 06:00 | 397 | 13:00
Kaliakoir | 406 | 01:00 | 381 | 12:00
Korerhat | 410 | 06:00 | 397 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 236 | 06:00 | 222 | 12:00 | Jhenaidah | 241 | 06:00 | 224 | 13:00
AKSML | 233 | 18:00 | 227 | 12:00 | Kachua | 236 | 18:00 | 226 | 12:00
Aminbazar | 236 | 06:00 | 223 | 12:00 | Kaliakoir | 240 | 18:00 | 223 | 12:00
Ashuganj | 235 | 03:00 | 223 | 16:00 | Keranigonj | 236 | 06:00 | 221 | 12:00
Ashuganj-400 | 235 | 18:00 | 220 | 14:00 | Khulna(S) | 244 | 07:00 | 226 | 13:00
Baghabari | 240 | 05:00 | 225 | 16:00 | Korerhat | 234 | 06:00 | 225 | 13:00
Barapukuria | 227 | 06:00 | 203 | 16:00 | Madunaghat | 232 | 06:00 | 226 | 12:00
Barapukuria-230 | 227 | 6:00 | 210 | 15:00 | Madunaghat-400 | 233 | 06:00 | 226 | 13:00
Barishal | 236 | 06:00 | 227 | 16:00 | Maniknagar | 237 | 18:00 | 223 | 12:00
Bheramara | 239 | 06:00 | 223 | 17:00 | Meghnaghat | 242 | 04:00 | 231 | 12:00
Bhulta | 237 | 18:00 | 223 | 12:00 | Meghnaghat-400 | 239 | 06:00 | 226 | 15:00
Bibiana | 239 | 06:00 | 231 | 12:00 | Mirsorai | 235 | 18:30 | 226 | 12:00
BIPTC | 242 | 06:00 | 223 | 16:00 | Rajshahi | 240 | 07:00 | 220 | 17:00
Bogura | 240 | 06:00 | 223 | 16:00 | Rampal | 239 | 06:00 | 225 | 13:00
Bogura-400 | 240 | 06:00 | 223 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Borhanuddin | 238 | 06:00 | 232 | 16:00 | Rampura | 235 | 06:00 | 220 | 15:00
BSRM | 234 | 06:00 | 225 | 12:00 | Shikalbaha | 231 | 18:00 | 225 | 12:00
Chowmuhani | N/A | N/A | N/A | N/A | Shyampur | 237 | 06:00 | 223 | 12:00
Cumilla(N) | 237 | 18:00 | 225 | 16:00 | Siddhirganj | 236 | 05:00 | 230 | 00:00
Faridpur | 234 | 06:00 | 223 | 12:00 | Sirajgonj | 244 | 06:00 | 231 | 16:00
Fenchuganj | 241 | 05:00 | 234 | 16:00 | Sreepur | 234 | 06:00 | 220 | 15:00
Feni | 236 | 06:00 | 226 | 12:00 | Tongi | 236 | 04:00 | 220 | 11:00
Ghorashal | 242 | 08:00 | 222 | 15:00
Ghorashal-230 | 234 | 06:00 | 219 | 12:00
Gopalganj | 233 | 06:00 | 223 | 13:00
GPH | 229 | 01:00 | 225 | 12:00
Haripur | 237 | 06:00 | 225 | 15:00
Hasnabad | 235 | 04:00 | 222 | 12:00
Hathazari | 231 | 18:00 | 222 | 12:00
Ishurdi | 242 | 06:00 | 226 | 16:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 05:00 | 127 | 12:00 | Magura | 138 | 05:00 | 128 | 13:00
Agargaon | 133 | 06:00 | 124 | 12:00 | Mahasthangarh | 136 | 01:00 | 124 | 17:00
Agrabad | 134 | 06:00 | 128 | 12:00 | Maijdee | 132 | 06:00 | 126 | 12:00
AKS | 132 | 03:00 | 127 | 12:00 | Manikganj | 129 | 06:00 | 118 | 12:00
Aminbazar | 138 | 06:00 | 128 | 12:00 | Maniknagar | 133 | 18:30 | 123 | 12:00
Amnura | 138 | 06:00 | 128 | 17:00 | Matarbari | 127 | 07:00 | 115 | 17:00
Ashuganj | 139 | 06:00 | 132 | 18:00 | Matuail | 134.6 | 06:00 | 128 | 09:00
Bagerhat | 137 | 06:00 | 122 | 13:00 | Metrorail_Motijheel | 133 | 18:30 | 123 | 12:00
Bajitpur | 134 | 06:00 | 124 | 16:00 | Metrorail_Uttara | 132 | 07:00 | 121 | 12:00
Bakerganj | 138 | 05:00 | 134 | 12:00 | Millgate | 132 | 06:00 | 120 | 12:00
Bakulia | 134 | 06:00 | 130 | 00:00 | Mirpur | 137 | 06:00 | 127 | 12:00
Banani | 135 | 03:00 | 126 | 13:00 | Mirzapur | 135 | 06:00 | 125 | 16:00
Bangabhaban | 132 | 06:00 | 123 | 12:00 | Mithapukur | 136 | 06:00 | 123 | 10:00
Barapukuria | 139 | 06:00 | 123 | 16:00 | MI_Cement | 136 | 18:00 | 124 | 12:00
Barguna | 138 | 07:00 | 133 | 17:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 138 | 06:00 | 131 | 13:00 | Mogbazar | 138 | 07:00 | 128 | 12:00
Barishal-230 | 137 | 06:00 | 131 | 16:00 | Mongla | 138 | 06:00 | 122 | 13:00
Baroaulia | 134 | 18:00 | 130 | 13:00 | Motijheel | 132 | 06:00 | 123 | 12:00
Baroirhat | 134 | 06:00 | 129 | 13:00 | Muktagacha | 130 | 03:00 | 115 | 16:00
Bashundhara | 136 | 06:00 | 126 | 16:00 | Munshiganj | 134 | 18:00 | 125 | 12:00
BashundharaCement | 134 | 04:00 | 127 | 17:00 | Muradnagar | 135 | 06:00 | 127 | 16:00
Beanibazar | 134 | 05:00 | 129 | 13:00 | Mymensingh | 129 | 06:00 | 112 | 16:00
Benapole | 140 | 07:00 | 116 | 13:00 | Naogaon | 140 | 01:00 | 122 | 17:00
Bhaluka | 132 | 18:30 | 120 | 13:00 | Narail | 139 | 05:00 | 126 | 13:00
Bhandaria | 134 | 06:00 | 127 | 14:00 | Narinda | 133 | 18:30 | 123 | 12:00
Bhangura | 138 | 06:00 | 128 | 17:00 | Narshingdi | 135 | 18:00 | 123 | 16:00
Bheramara | 140 | 06:00 | 132 | 16:00 | Natore | 138 | 06:00 | 127 | 17:00
Bheramara(GK) | 139 | 05:00 | 132 | 16:00 | Nawabganj | 136 | 06:00 | 126 | 12:00
Bhulta | 129 | 18:00 | 121 | 11:00 | Netrakona | 125 | 06:00 | 110 | 15:00
Bog-Sherpur | 138 | 06:00 | 126 | 10:00 | New | 135 | 18:00 | 121 | 12:00
Bogura | 138 | 06:00 | 128 | 13:00 | Niamatpur | 139 | 06:00 | 130 | 12:00
Bogura-230 | 139 | 06:00 | 128 | 16:00 | Noapara | 140 | 07:00 | 122 | 13:00
Brahmanbaria | 133 | 18:00 | 124 | 16:00 | Pabna | 139 | 02:00 | 130 | 17:00
Cantonment | 133 | 06:00 | 124 | 12:00 | Palashbari | 134 | 02:00 | 121 | 13:00
Chandina | 137 | 06:00 | 130 | 12:00 | Panchagarh | 138 | 18:30 | 123 | 13:00
Chandpur | 135 | 18:00 | 128 | 12:00 | Patiya | 134 | 06:00 | 129 | 12:00
Chandraghona | 137 | 06:00 | 132 | 12:00 | Patuakhali | 136 | 05:00 | 133 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 138 | 06:00 | 129 | 12:00 | Payra | 139 | 07:00 | 136 | 12:00
Charsaidpur | 135 | 18:00 | 126 | 15:00 | PHP | 134 | 06:00 | 128 | 12:00
Chauddagram | 134 | 05:00 | 128 | 12:00 | Postogola | 136 | 06:00 | 126 | 12:00
Chhatak | 130 | 03:00 | 124 | 12:00 | Purbachal | 136 | 06:00 | 126 | 12:00
Chowmuhani | 131 | 18:00 | 125 | 12:00 | Purbasadipur | 132 | 06:00 | 118 | 09:00
Chuadanga | 139 | 06:00 | 127 | 13:00 | Rahanpur | 140 | 06:00 | 131 | 17:00
Coxsbazar | 125 | 08:00 | 115 | 17:00 | Rahanpur-400 | 140 | 06:00 | 132 | 13:00
Cumilla(N) | 137 | 06:00 | 130 | 12:00 | Rahim | 134 | 06:00 | 127 | 13:00
Cumilla(S) | 136 | 06:00 | 122 | 10:00 | Rajbari | 135 | 06:00 | 128 | 13:00
Daganbhuiyan | 133 | 06:00 | 127 | 12:00 | Rajendrapur | 131 | 03:00 | 119 | 16:00
Daudkandi | 133 | 06:00 | 125 | 15:00 | Rajshahi | 138 | 06:00 | 127 | 17:00
DhakaUniversity | 137 | 06:00 | 127 | 12:00 | Rajshahi-230 | 138 | 03:00 | 128 | 13:00
Dhamrai | 135 | 05:00 | 126 | 12:00 | Ramganj | 132 | 18:00 | 126 | 12:00
Dhanmondi | 137 | 06:00 | 128 | 12:00 | Rampur | 134 | 05:00 | 128 | 12:00
Dohazari | 131 | 05:00 | 126 | 00:00 | Rampura | 136 | 06:00 | 126 | 12:00
Faridpur | 136 | 07:00 | 129 | 16:00 | Rangamati | 136 | 06:00 | 131 | 12:00
Fatullah | 136 | 05:00 | 125 | 11:00 | Rangpur | 136 | 18:30 | 119 | 16:00
Fenchuganj | 138 | 19:30 | 134 | 11:00 | Ruppur | 140 | 06:00 | 131 | 17:00
Feni | 132 | 18:00 | 126 | 17:00 | Saidpur | 137 | 06:00 | 118 | 16:00
Feni-230 | 133 | 06:00 | 127 | 12:00 | Satkhira | 141 | 07:00 | 123 | 13:00
Ghatail | 131 | 18:00 | 116 | 16:00 | Satmasjid | 133 | 06:00 | 124 | 13:00
Ghorashal | 139 | 05:00 | 132 | 12:00 | Savar | 140 | 18:00 | 126 | 12:00
Goalpara | 142 | 07:00 | 126 | 13:00 | SevenRings | 139 | 06:00 | 131 | 16:00
Gollamari | 140 | 06:00 | 130 | 04:00 | ShahCement | 135 | 18:00 | 126 | 15:00
Gopalganj | 138 | 06:00 | 129 | 13:00 | Shahjadpur | 140 | 05:00 | 131 | 17:00
Gopalganj-400 | 139 | 06:00 | 132 | 12:00 | Shahjibazar | 132 | 06:00 | 125 | 17:00
Gulshan | 136 | 06:00 | 127 | 11:00 | Shahmirpur | 135 | 05:00 | 130 | 12:00
Halishahar | 135 | 06:00 | 129 | 12:00 | Shariatpur | 138 | 06:00 | 130 | 13:00
Haripur | 134 | 06:00 | 127 | 12:00 | Sherpur | 127 | 19:30 | 110 | 12:00
HaripurSBU | 134 | 06:00 | 127 | 13:00 | Shikalbaha | 125 | 06:00 | 119 | 12:00
Hasnabad | 135 | 05:00 | 126 | 12:00 | Shikalbaha-230 | 136 | 06:00 | 130 | 12:00
Hathazari | 136 | 18:00 | 130 | 12:00 | Shitalakhya | 136 | 18:00 | 124 | 12:00
Hatirjheel | 135 | 03:00 | 127 | 12:00 | Sholosohor | 136 | 06:00 | 131 | 12:00
Ishurdi | 142 | 06:00 | 133 | 16:00 | Shyampur | 134 | 05:00 | 126 | 12:00
Jaldhaka | 133 | 06:00 | 118 | 09:00 | Shyampur-230 | 137 | 18:00 | 128 | 12:00
Jamalpur | 131 | 19:30 | 116 | 16:00 | Siddhirganj | 134 | 05:00 | 127 | 16:00
Jashore | 137 | 06:00 | 117 | 13:00 | Sirajganj | 135 | 01:00 | 120 | 10:00
Jhenaidah | 140 | 05:00 | 119 | 17:00 | Sonargaon | 134 | 18:00 | 125 | 17:00
Jhenaidah-230 | 141 | 06:00 | 130 | 13:00 | Sreemongol | 133 | 06:00 | 127 | 17:00
Joydebpur | 139 | 18:00 | 126 | 16:00 | Sreepur | 134 | 06:00 | 123 | 17:00
Joypurhat | 131 | 02:00 | 120 | 13:00 | Srinagar | 138 | 18:00 | 127 | 12:00
Juldah | 134 | 01:00 | 129 | 11:00 | SSM | 140 | 18:00 | 132 | 13:00
Kabirpur | 142 | 18:00 | 118 | 12:00 | Sunamganj | 127 | 06:00 | 124 | 16:00
Kachua | 139 | 17:00 | 129 | 12:00 | Sylhet | 130 | 06:00 | 125 | 17:00
Kaliakoir | 142 | 18:00 | 129 | 12:00 | Sylhet-132 | 130 | 02:00 | 127 | 12:00
Kaliganj | 140 | 04:00 | 129 | 13:00 | Tangail | 131 | 18:30 | 121 | 12:00
Kallyanpur | 138 | 06:00 | 128 | 12:00 | Taraganj | 135 | 06:00 | 119 | 16:00
Kalurghat | 136 | 06:00 | 131 | 15:00 | Tasnim | 134 | 18:00 | 125 | 17:00
Kamrangirchar | 137 | 07:00 | 125 | 16:00 | Thakurgaon | 137 | 18:30 | 120 | 16:00
Kaptai | N/A | N/A | N/A | N/A | TK | 136 | 18:00 | 131 | 12:00
Kasba | 134 | 07:00 | 126 | 16:00 | Tongi | 134 | 04:00 | 124 | 10:00
Kazla | 131 | 03:00 | 123 | 13:00 | Ullahpara | 139 | 03:00 | 126 | 16:00
Keranigonj | 137 | 06:00 | 127 | 12:00 | Ullon | 135 | 05:00 | 127 | 12:00
Khagrachori | 135 | 06:00 | 130 | 12:00 | Uttara | 138 | 18:30 | 119 | 12:00
Khulna | 139 | 06:00 | 126 | 13:00 | UttaraNew | 139 | 18:00 | 121 | 12:00
Khulna(S) | 142 | 07:00 | 127 | 13:00 | Zigatola | 138 | 18:00 | 127 | 12:00
Khulshi | 133 | 05:00 | 128 | 11:00
Kishoreganj | 133 | 04:00 | 120 | 17:00
Kodda | 139 | 18:00 | 127 | 12:00
Korerhat | 135 | 02:00 | 129 | 13:00
KSRM | 135 | 05:00 | 129 | 12:00
Kulaura | 136 | 03:00 | 132 | 12:00
Kurigram | 134 | 19:30 | 116 | 16:00
Kushtia | 136 | 06:00 | 125 | 16:00
Laksam | 134 | 18:00 | 128 | 12:00
Lakshmipur | 132 | 06:00 | 126 | 12:00
Lalbag | 137 | 18:00 | 126 | 12:00
Lalmonirhat | 132 | 06:00 | 120 | 09:00
Madanganj | 134 | 04:00 | 127 | 17:00
Madaripur | 137 | 03:00 | 132 | 13:00
Madartek | 134 | 03:00 | 126 | 12:00
Madunaghat | 136 | 06:00 | 131 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division