## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID BANGLADESH PLC
SYSTEM OPERATION DATA
Month: January 2026
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2026-01-01 |  | 2025-12-01 |  | 2025-01-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 11900.14 | 2026-01-31 | 11336.5 | 2025-12-01 | 11385.54 | 2025-01-31 | 16794 | 2025-07-23
|  |  | 19:00 Hr. |  | 18:00 Hr |  | 19:00 Hr. |  | 21:00 Hr.
2 | Minimum Generation (MW) | 6599.78 | 2026-01-01 | 6605 | 2025-12-27 | 6331.7 | 2025-01-04 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 11900.14 | 2026-01-31 | 11336.5 | 2025-12-01 | 11385.54 | 2025-01-31 | 16794 | 2025-07-23
|  |  | 19:00 Hr. |  | 18:00 Hr |  | 19:00 Hr. |  | 21:00 Hr.
4 | Maximum Day Peak Generation (MW) | 11046.28 | 2026-01-27 | 11336.5 | 2025-12-01 | 10755.81 | 2025-01-28 | 14965.88 | 2025-09-30
|  |  | 12:00 Hr. |  | 18:00 Hr |  | 12:00 Hr. |  | 12:00 Hr.
5 | Maximum Evening Peak Demand (MW) Estimated | 11980.14 | 2026-01-31 | 11336.5 | 2025-12-01 | 11385.54 | 2025-01-31 | 17200 | 2024-04-29
|  |  | 19:00 Hr. |  | 18:00 Hr |  | 19:00 Hr. |  | 21:00
6 | Average Generation (MW) at Evening Peak | 11042.1177 |  | 10803.4397 |  | 10693.0548 |  | - | -
7 | Average Generation (MW) at Day Peak | 10326.2955 |  | 9822.7461 |  | 10062.5852 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 914 | 2026-01-18 | 911 | 2025-12-18 | 933 | 2025-01-26 | 979 | 2025-09-09
|  |  | 12:00 |  | 21:30 |  | 22:30 |  | 5:00
9 | Maximum Power Import from Tripura, India (MW) | 150 | 2026-01-27 | 134 | 2025-12-17 | 135 | 2025-01-06 | 194 | 12/06/19
|  |  | 13:00 |  | 13:00 |  | ]-p0987yi7 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 937 | 2026-01-21 | - | - | 138 | 2025-01-23 | 4395 | 04/10/2022
|  |  | 19:30 Hr. |  | - |  | 19:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 10570.21 | 2026-01-21 | - | - | 10747 | 2025-01-23 | 14965 | 2024-05-16
|  |  | 19:00 Hr. |  | - |  | 19:00 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 26 | 2026-01-15 | - | - | 0 | 2025-01-01 | - | -
|  |  | 19:00 Hr. |  | - |  | 18:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 11608.6 | 2026-01-15 | - | - | 10336.5 | 2025-01-01 | - | -
|  |  | 19:00 Hr. |  |  |  | 18:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 1000 | 2026-01-29 | - | - | 90 | 2025-01-29 | - | -
|  |  | 12:00 Hr. |  |  |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 10155.9 | 2026-01-29 | - | - | 10341 | 2025-01-29 | - | -
|  |  | 12:00 Hr. |  |  |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 10 | 2026-01-19 | - | - | 0 | 2025-01-01 | - | -
|  |  | 12:00 Hr. |  |  |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 10957.77 | 2026-01-19 | - | - | 9365 | 2025-01-01 | - | -
|  |  | 12:00 Hr. |  |  |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 11 |  | - |  | 12 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 10 |  | - |  | 10 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 545.6269 |  | 681.5607 |  | 1538.3298 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 16.1913 |  | 17.5162 |  | 40.8794 |  | - | -
22 | Net Generation of BPDB (MKWH) | 529.4357 |  | 664.0444 |  | 1497.4503 |  | - | -
23 | Net Generation of IPP (MKWH) | 2271.6537 |  | 1496.5306 |  | 2109.9074 |  | - | -
23b | Net Generation by Generation Companies | 2998.9512 |  | 3235.6984 |  | 1968.7062
24 | Net Generation of REB (MKWH) | 46.5401 |  | 49.4958 |  | 63.5555 |  | - | -
25 | Net Generation of Rental Power Plant (MKWH) | 91.3657 |  | 71.649 |  | 208.7373 |  | - | -
26 | Total Net Generation (MKHWh) (Excluding Import) | 5937.9464 |  | 5517.4182 |  | 5848.3567 |  | - | -
27 | Energy Generation by Gas (MKWH) | 2908.1434 |  | 2902.0948 |  | 3127.6858 |  | - | -
28 | Energy Generation by Diesel (MKWH) | 0 |  | 0.37886 |  | 469.3291 |  | - | -
29 | Energy Generation by Furnace Oil (MKWH) | 489.8404 |  | 152.3331 |  | 426.0344 |  | - | -
30 | Energy Generation by Hydro (MKWH) | 35.0787 |  | 32.1311 |  | 3.6257 |  | - | -
31 | Energy Generation by Solar (MKWH) | 102.2478 |  | 97.514 |  | 93.1478 |  | - | -
31b | Energy Generation by Wind (MKWH) | 7.0267 |  | 2.5497 |  | 0.64176 |  | - | -
32 | Energy Generation by Coal (MKWH) | 2411.8007 |  | 2347.9329 |  | 1768.7717 |  | - | -
33 | Enegry Import from India (MKWH) | 1229.2183 |  | 1356.8575 |  | 1029.682 |  | - | -
34 | Monthly Load Factor (%) | 81.1339 |  | 81.7109 |  | 81.6792 |  | - | -

## QF-LDC-22
QF-LDC-22
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: January 2026
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 11900.14 | 2026-01-31 | 19:00 Hr.
Generation Period
| Dhaka | MW | 4317.93
| Chattogram | MW | 1192.7
| Cumilla | MW | 970
| Mymensingh | MW | 948
| Sylhet | MW | 414
a) | Total supply in East zone | MW | 7842.63
| Khulna | MW | 1305
| Barisal | MW | 323
| Rajshahi | MW | 1117.2
| Rangpur | MW | 789
b) | Total supply in West zone | MW | 3534.2
c) | Total supply in both zone ( a+b) | MW | 11376.83
Ref: | 27.21.0000.603.16.087.20.961 | Date: 16/02/2026
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month: January 2026
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Maximum power Export through EWI/ NO-1
| a) Ishurdi end | AMPS | 487 | 2026-01-31 | 14:00
|  | MW | 202
| b) Ghorashal end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
18 | Maximum power Import through EWI/ NO-1 |  |  | -
| a) Ishurdi end | AMPS | 0 | - | -
|  | MW | 0
| b) Ghorashal end | AMPS | 410 | 2026-01-31 | 14:00
|  | MW | 136
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ishurdi end | MWh | 3571.272 | 2026-01-31 | 14:00
| b) Ghorashal end | MWh | 0
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ishurdi end | MWh | 0 | -
| b) Ghorashal end | MWh | 3445.8 | 2026-01-30 | N/A
21 | Total Energy Export through EWI/ NO-1
| a) Ishurdi end | MWh | 63299.346
| b) Ghorashal end | MWh | 0
22 | Total Energy Import through EWI/ NO-1
| a) Ishurdi end | MWh | 0
| b) Ghorashal end | MWh | 61400.36
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Maximum power Export through EWI/ NO-2
| a) Sirajganj end | AMPS | 1800 | 2026-01-04
|  | MW | 680
| b) Sreepur end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
25 | Maximum power Import through EWI/ NO-2 |  | - | -
| a) Serajganj end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
| b) Sreepur | AMPS | 1810 | 2026-01-01 | 10:00
|  | MW | 718
26 | Daily Maximum Energy Export through EWI/NO-2
| a) Serajganj end | MWh | 6376 | 2026-01-31
| b) Sreepur | MWh | 0
27 | Daily Maximum Energy Import through EWI/ NO-2
| a)Serajganj end | MWh | 0 | - | -
| b) Sreepur | MWh | - | - | -
28 | Total Energy Export through EWI/ NO-2
| a)Serajganj end | MWh | 288094 | - | -
| b) Sreepur | MWh | 0 | - | -
29 | Total Energy Import through EWI/ NO-2
| a)Serajganj end | MWh | 0 | - | -
| b) Sreepur | MWh | 280112.7 | - | -
30 | Transmission loss of EWI/ NO-2 | % | 2.77 | - | -
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 2492 | 2026-01-11 | 22:00
|  | MW | 1776
| b) Aminbazar end | AMPS | 0
|  | MW | 0
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | 0
|  | MW | 0
| b) Aminbazar end | AMPS | 2487 | 2026-01-11 | 22:00
|  | MW | 1775
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 34480 | 2026-01-11 | N/A
| a) Aminbazar end | MWh | 0
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | 0 | - | N/A
| a) Aminbazar end | MWh | 34359 | 2026-01-11
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MWh | 855600
| b) Aminbazar end (ckt-1 ) | MWh | 0
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | 0
| b) Aminbazar end (ckt-2 ) | MWh | 851862
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 0.437
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: January 2026
| Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | 230/132kv Tr-03 | 2026-01-14 10:24 | 2026-01-14 13:26 | 0.12639 | T | Trapping ABB | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-1 | 2026-01-01 14:44 | 2026-01-01 16:03 | 0.054861 | T | Project work fault in Bus 1 & 2. Suspected mis operation in new bay extension part. No relay signal, only breaker trip due to BBP trip signal | 48 | 63.2 | Power interruption
Rajendrapur 132/33kV | MTR-3 | 2026-01-01 14:44 | 2026-01-01 16:06 | 0.056944 | T | Project work fault in Bus 1 & 2. Suspected mis operation in new bay extension part. No relay shown except BBP trip | 62 | 84.7333 | Power interruption
Tongi 230/132/33kV | T-1 | 2026-01-24 08:02 | 2026-01-24 16:37 | 0.35764 | T | Trip REF Opdr LV | 24 | 206 | Power interruption
Joydebpur 132/33kV | 132kV Bus | 2026-01-03 10:41 | 2026-01-03 14:09 | 0.14444 | E/O | Annual Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132 kV BUS-1 | 2026-01-10 13:10 | 2026-01-10 16:35 | 0.14236 | E/O | rajendrapur-1 Redhot Maintenance. | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132 kV BUS-2 | 2026-01-11 14:38 | 2026-01-11 16:44 | 0.0875 | E/O | Rajendrapur-1 Redhot Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV | 230 kV BUS-2 | 2026-01-14 15:14 | 2026-01-14 16:30 | 0.052778 | E/O | DS Not Closing | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 00:33 |  | Unserved Energy: |  | 353.9333
Dhaka (South) Grid Circle :
Keranigonj 230/132/33kV | TR-1 | 2026-01-06 14:22 | 2026-01-06 14:35 | 0.0090278 | T | 33kV feeder fault Siprotec 7UT612 | 31 | 6.7167 | Power interruption
Ghorashal 230kV | TARFO-2 | 2026-01-04 10:44 | 2026-01-04 17:45 | 0.29236 | E/O | Transformer-02 S/D need for 33kV side CT,CB,Red hot and system grounding maintenance work. | 60 | 421 | Power interruption
Narshingdi 132/33kV | T-2 | 2026-01-11 11:20 | 2026-01-11 13:03 | 0.071528 | E/O | oil Leakage | 0 | 0 | No interruption
Nawabganj 132/33kV | TR-1 | 2026-01-06 12:34 | 2026-01-06 14:39 | 0.086806 | E/O | OIL REFILLING | 0 | 0 | No interruption
Sonargaon 132/33kV | Bus-Coupler | 2026-01-10 13:35 | 2026-01-11 15:40 | 1899-12-31 02:05 | E/O | A bus and B bus individual | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 13:07 |  | Unserved Energy: |  | 427.7167
Chattogram Grid Circle :
Kalurghat 132/33kV | TRFO-01(506T) | 2026-01-24 06:35 | 2026-01-24 06:35 | 0 | T | RET 650 RET 670 | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-02(516T) | 2026-01-29 09:40 | 2026-01-29 09:56 | 0.011111 | T | CB open by NLDC N/A | 6.75 | 1.8 | Power interruption
Hathazari 230/132/33kV | T-02 | 2026-01-31 09:52 | 2026-01-31 14:02 | 0.17361 | E/O | PDB Demand | 0 | 0 | No interruption
Juldah 132/33kV | 133/33 KV T-2 416T | 2026-01-02 07:10 | 2026-01-02 08:28 | 0.054167 | E/O | due to intermittent flashing at R-phase CT. | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-01(506T) | 2026-01-04 10:42 | 2026-01-04 12:04 | 0.056944 | E/O | To Remove oil tank from beside the transformer | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-02(516T) | 2026-01-24 08:27 | 2026-01-24 08:31 | 0.0027778 | E/O | Emergency maint.work | 14 | 0.93333 | Power interruption
|  |  | Total : | 0.29861 |  | Unserved Energy: |  | 2.7333
Cumilla Grid Circle :
Chowmuhani 132/33kV | TR2-425T | 2026-01-04 04:38 | 2026-01-04 04:45 | 0.0048611 | T | 33 kv kabirhat fault E/F,O/C | 17 | 1.9833 | Power interruption
Chowmuhani 132/33kV | TR3-435T | 2026-01-04 04:38 | 2026-01-04 04:45 | 0.0048611 | T | 33kv kabirhat feeser fault O/C | 17 | 1.9833 | Power interruption
Cumilla(S) 132/33kV | TR-3 | 2026-01-21 08:59 | 2026-01-21 09:20 | 0.014583 | T | 33 KV PDB feeder fault(Shafiul Alam) REF-615 | 22 | 7.7 | Power interruption
Cumilla(S) 132/33kV | TR-4 | 2026-01-21 08:59 | 2026-01-21 09:27 | 0.019444 | T | 33 KV PDB feeder fault(Shafiul Alam) REF-615 | 23 | 10.7333 | Power interruption
Fenchuganj 230/132/33kV | 132 KV Bus-1 | 2026-01-12 14:54 | 2026-01-12 15:29 | 0.024306 | T | Ground Fault REB 500 | 0 | 0 | Power interruption
Fenchuganj 230/132/33kV | TR-01 | 2026-01-12 14:54 | 2026-01-12 15:35 | 0.028472 | T | 132 KV Bus -1 Fail REC 650 | 20 | 13.6667 | Power interruption
Shahjibazar 132/33kV | TR-02 | 2026-01-28 19:05 | 2026-01-28 19:20 | 0.010417 | T | Shaistaganj Feeder Flashing. Gen. Trip, Non Dir OC DMT Trip. | 8 | 2 | Power interruption
Beanibazar 132/33kV | 132 KV Transformer TR-01 | 2026-01-08 18:32 | 2026-01-08 19:28 | 0.038889 | E/O | LA Maintenance | 0 | 0 | No interruption
Chandina 132/33kV | TR-3 | 2026-01-02 16:35 | 2026-01-02 18:48 | 0.092361 | E/O | for red hot solution work in pbs cumilla-1 feeder | 0 | 0 | No interruption
Chandpur 132/33kV | 422T(T-5) | 2026-01-06 14:40 | 2026-01-08 12:10 | 1899-12-31 21:30 | E/O | PT MCB Trip | 0 | 0 | No interruption
Chandpur 132/33kV | 402T (T-01) | 2026-01-08 12:10 | 2026-01-31 08:02 | 1900-01-21 19:52 | E/O | N/A | 0 | 0 | No interruption
Chandpur 132/33kV | 422T(T-5) | 2026-01-20 17:00 | 2026-01-20 17:57 | 0.039583 | E/O | To remove the kite and kite string | 0 | 0 | No interruption
Chandpur 132/33kV | Bus-B | 2026-01-20 17:08 | 2026-01-20 17:55 | 0.032639 | E/O | To remove the kite and kite string | 0 | 0 | No interruption
Chhatak 132/33kV | Bus-B | 2026-01-06 17:16 | 2026-01-06 17:24 | 0.0055556 | E/O | Emergency shutdown required BUS-B due to kite stuck in BUS-B PT. | 0 | 0 | No interruption
Chhatak 132/33kV | T-1 | 2026-01-08 01:16 | 2026-01-08 03:16 | 0.083333 | E/O | PDB 33kV feeder maintenance work. | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 AB | 2026-01-12 14:57 | 2026-01-12 15:43 | 0.031944 | E/O | Fenchuganj grid failure | 0 | 0 | No interruption
Kulaura 132/33kV | TR-2 | 2026-01-12 14:57 | 2026-01-12 15:44 | 0.032639 | E/O | Fenchuganj grid failure | 0 | 0 | No interruption
Muradnagar 132/33kV | 132KV Transformar-01 | 2026-01-05 11:20 | 2026-01-07 18:57 | 1900-01-01 07:37 | E/O | PBS newly constructed 33 KV ss commissioning work | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2026-01-18 16:06 | 2026-01-18 16:35 | 0.020139 | E/O | Shutdown for Emergency. | 62 | 29.9667 | Power interruption
|  |  | Total : | 1900-01-26 12:36 |  | Unserved Energy: |  | 68.0333
Khulna Grid Circle :
Bakerganj 132/33kV | T1 | 2026-01-24 05:45 | 2026-01-24 06:20 | 0.024306 | T | Over Voltage Over voltage relay | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-3 | 2026-01-04 08:02 | 2026-01-04 12:02 | 0.16667 | T | 33 kV Sajjankanda wz feeder fault. The trip occurred by Earth and Over current fault of Sajjankanda feeder. 86.1 and 86.2 Relay operated. | 4 | 16 | Power interruption
Bhandaria 132/33kV | Transformer-2 | 2026-01-31 14:40 | 2026-01-31 17:11 | 0.10486 | E/O | PBS red hot maintenance | 20 | 50.3333 | Power interruption
Khulna (C) | Tr-2 415 T | 2026-01-22 16:45 | 2026-01-22 17:34 | 0.034028 | E/O | Emergency maintenance of Aux. | 0 | 0 | No interruption
|  |  | Total : | 0.32986 |  | Unserved Energy: |  | 66.3333
HVDC Grid Circle :
BIPTC | 20DF24 | 2026-01-01 22:23 | 2026-01-03 16:30 | 1899-12-31 18:07 | T | Pole discrepancy | 0 | 0 | No interruption
BIPTC | 10CF16 | 2026-01-02 07:18 | 2026-01-04 12:18 | 1900-01-01 05:00 | T | Differential relay OPTD | 0 | 0 | No interruption
BIPTC | 10CF11 | 2026-01-05 23:20 | 2026-01-06 11:27 | 0.50486 | T | Impedance 21R Trip. | 0 | 0 | No interruption
BIPTC | 20DF21 | 2026-01-10 17:30 | 2026-01-11 10:09 | 0.69375 | T | C1 unbalance 60/61 instant L1 | 0 | 0 | No interruption
BIPTC | 10CF16 | 2026-01-26 22:08 | 2026-01-26 22:08 | 0 | T | Tripped by differential protection OPTD. | 0 | 0 | No interruption
BIPTC | 20DF24 | 2026-01-03 09:22 | 2026-01-03 16:30 | 0.29722 | E/O | Corrective maintenance due to trip | 0 | 0 | No interruption
BIPTC | 10CF11 | 2026-01-06 10:14 | 2026-01-06 11:27 | 0.050694 | E/O | Shutdown is taken for emergency maintenance work | 0 | 0 | No interruption
BIPTC | 20DF21 | 2026-01-11 09:45 | 2026-01-11 10:09 | 0.016667 | E/O | Emergency maint.work | 0 | 0 | No interruption
BIPTC | 20DF31 | 2026-01-11 10:28 | 2026-01-11 15:34 | 0.2125 | E/O | Emergency maint.work | 0 | 0 | No interruption
BIPTC | 20DF13 | 2026-01-11 12:37 | 2026-01-11 13:19 | 0.029167 | E/O | None | 0 | 0 | No interruption
Baghabari 230/132kV | T-2 Bank | 2026-01-01 08:47 | 2026-01-01 16:58 | 0.34097 | E/O | T-02 Bank এর B-ফেজের Oil লিকেজ বন্ধ করার জন্য। | 0 | 0 | No interruption
Ishurdi 230/132kV | 230/132 kV T-01 | 2026-01-01 10:08 | 2026-01-01 12:47 | 0.11042 | E/O | Due to High voltage in B-Phase. | 0 | 0 | No interruption
Kushtia 132/33kV | T-1 | 2026-01-17 10:56 | 2026-01-17 11:41 | 0.03125 | E/O | Emergency maintenance | 24 | 18 | Power interruption
Shahjadpur 132/33kV | Main Bus | 2026-01-18 12:21 | 2026-01-18 13:50 | 0.061806 | E/O | Emergency Maintenance | 25 | 37.0833 | Power interruption
Shahjadpur 132/33kV | Main Bus | 2026-01-19 07:19 | 2026-01-19 09:15 | 0.080556 | E/O | Emergency Maintenance work | 20 | 38.6667 | Power interruption
|  |  | Total : | 1900-01-05 09:26 |  | Unserved Energy: |  | 93.75
Bogura Grid Circle:
Niamatpur 132/33kV | Transformer-2 (417T) | 2026-01-28 15:14 | 2026-01-28 17:18 | 0.086111 | T | OC/ Earth fault | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 230/132 KV T-01, 703T | 2026-01-25 09:32 | 2026-01-25 12:06 | 0.10694 | E/O | Maintenance | 0 | 0 | No interruption
Jaldhaka 132/33kV | 406T-1 | 2026-01-27 12:36 | 2026-01-27 14:46 | 0.090278 | E/O | Emergency observation due to oil leakage at several part of T-1 XFR. | 0 | 0 | No interruption
Joypurhat 132/33kV | Transformer T-4 (437 T) | 2026-01-07 16:30 | 2026-01-08 12:31 | 0.83403 | E/O | 132 Kv T-4 R-Phase LA Brust | 0 | 0 | No interruption
Naogaon 132/33kV | T-1 | 2026-01-10 10:50 | 2026-01-10 11:19 | 0.020139 | E/O | 132 kV Transformer-1 CB maintenance (Pole discrepancy problem) | 0 | 0 | No interruption
Panchagarh 132/33kV | T-3(A+B)(427T) | 2026-01-01 10:01 | 2026-01-01 14:22 | 0.18125 | E/O | T3 33KV Redhot Maintenance | 0 | 0 | No interruption
Saidpur 132/33kV | TR-3 (424T) | 2026-01-30 09:09 | 2026-01-30 10:01 | 0.036111 | E/O | Red hot maintenance of 33 kv golahat fedder (Nesco/Saidpur) bus isolator. | 5 | 4.3333 | Power interruption
Sirajganj 132/33kV | T4-(445) | 2026-01-19 14:21 | 2026-01-19 15:18 | 0.039583 | E/O | S/D taken by Sirajgonj PBS-2 for 33kV Economic Zone feeder BUS DS insulator replacement. | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 09:28 |  | Unserved Energy: |  | 4.3333
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 1900-02-06 12:15 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: January 2026
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Rajendrapur 132/33kV | Kodda-1 | 2026-01-01 14:44 | 2026-01-01 16:01 | 0.053472 | T | Project work fault in Bus 1 & 2. Suspected mis operation in new bay extension part. | 140 | 179.6667 | Power interruption
Bhaluka 132/33kV | Mymensingh Ckt- 01 | 2026-01-07 11:15 | 2026-01-07 17:14 | 0.24931 | E/O | CB open by NLDC | 0 | 0 | No interruption
Bhaluka 132/33kV | Mymensingh Ckt- 01 | 2026-01-08 10:32 | 2026-01-08 16:10 | 0.23472 | E/O | Load Management | 0 | 0 | No interruption
Bhaluka 132/33kV | Mymensingh Ckt- 02 | 2026-01-25 12:03 | 2026-01-25 13:44 | 0.070139 | E/O | Load management by NLDC | 0 | 0 | No interruption
Kabirpur 132/33kV | Tongi-1 | 2026-01-31 11:04 | 2026-01-31 16:38 | 0.23194 | E/O | 230/132 KV T-3 Transformer is on Shutdown at Tongi Grid S/S End | 0 | 0 | No interruption
Kabirpur 132/33kV | Tongi-2 | 2026-01-31 11:05 | 2026-01-31 16:39 | 0.23194 | E/O | 230/132 KV T-3 Transformer is on Shutdown at Tongi Grid S/S End | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Aminbazar -2 | 2026-01-09 08:43 | 2026-01-10 05:45 | 0.87639 | E/O | By NLDC | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Dhamrai-2 | 2026-01-12 08:36 | 2026-01-12 16:30 | 0.32917 | E/O | As per the instructions of NLDC. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Tongi-2 | 2026-01-12 09:53 | 2026-01-12 17:13 | 0.30556 | E/O | As per the instructions of NLDC. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Dhamrai-2 | 2026-01-13 09:09 | 2026-01-13 15:50 | 0.27847 | E/O | By NLDC | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Tangail-2 | 2026-01-16 09:41 | 2026-01-16 16:09 | 0.26944 | E/O | By NLDC | 0 | 0 | No interruption
Kishoreganj 132/33kV | Bajitpur Ckt-1 | 2026-01-03 11:01 | 2026-01-03 11:11 | 0.0069444 | E/O | By NLDC | 0 | 0 | No interruption
Kishoreganj 132/33kV | Bajitpur Ckt-2 | 2026-01-03 11:01 | 2026-01-03 11:11 | 0.0069444 | E/O | By NLDC | 0 | 0 | No interruption
Rajendrapur 132/33kV | Kodda-2 | 2026-01-10 12:09 | 2026-01-10 17:03 | 0.20417 | E/O | Sreepur end redhot problem, they taken shutdown. | 0 | 0 | No interruption
Rajendrapur 132/33kV | Kodda-1 | 2026-01-10 17:02 | 2026-01-11 13:13 | 0.84097 | E/O | Sreepur end Red Hot issue solved & Load shift from Kodda ckt to Sreepur ckt. | 0 | 0 | No interruption
Rajendrapur 132/33kV | Kodda-2 | 2026-01-11 13:12 | 2026-01-11 19:17 | 0.25347 | E/O | Sreepur Sub- Station BUS Maintenance. NB:. Kodda 2 means, Rajendrapur Sreepur CKT 1. | 0 | 0 | No interruption
Rajendrapur 132/33kV | Kodda-1 | 2026-01-11 19:16 | 2026-01-17 08:37 | 1900-01-04 13:21 | E/O | Emergency maint.work | 0 | 0 | No interruption
Rajendrapur 132/33kV | Kodda-2 | 2026-01-17 08:37 | 2026-01-17 17:27 | 0.36806 | E/O | Load shifted from Sreepur to Kodda end. | 0 | 0 | No interruption
Rajendrapur 132/33kV | Kodda-1 | 2026-01-17 17:27 | 2026-01-17 17:27 | 0 | E/O | Load shifted from kodda-1 to sreepur end. | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Valuka Ckt-2 | 2026-01-25 11:21 | 2026-01-25 13:40 | 0.096528 | E/O | Annual Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Ashuganj Ckt-1 | 2026-01-26 10:46 | 2026-01-26 17:31 | 0.28125 | E/O | S/D taken by Joydebpur Grid S/s. for Annual Maintenance. | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Ashuganj Ckt-1 | 2026-01-31 10:38 | 2026-01-31 12:06 | 0.061111 | E/O | 230 kV BUS-1 Annual Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Ashuganj Ckt-2 | 2026-01-31 12:08 | 2026-01-31 13:23 | 0.052083 | E/O | 230 kV BUS-1 Annual Maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-09 20:36 |  | Unserved Energy: |  | 179.6667
Dhaka (South) Grid Circle :
Haripur 230/132kV | Ullon (Maniknagar-2) | 2026-01-17 07:13 | 2026-01-17 12:09 | 0.20556 | T | Tripped | 0 | 0 | No interruption
Haripur 230/132kV | Ullon (Maniknagar-2) | 2026-01-23 08:50 | 2026-01-23 10:56 | 0.0875 | T | Tripped | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Sreenagar Ckt. 2 | 2026-01-14 07:33 | 2026-01-14 16:49 | 0.38611 | T | zone-01 trip | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 2 | 2026-01-22 11:47 | 2026-01-22 17:29 | 0.2375 | T | Zone-1 Tipped. | 0 | 0 | No interruption
Maniknagar 230/132kV | 230kV Siddhirganj-Maniknagar ckt-2 | 2026-01-19 17:44 | 2026-01-20 01:15 | 0.31319 | T | Tripped | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Shyampur 230kV Ckt-1 | 2026-01-01 05:07 | 2026-01-01 07:00 | 0.078472 | T | Meghnaghat -Shyampur 230kV ckt 1 Tripped. Line differential zone 1. Fault Distance: 8.1960 km | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat- Shyampur 230kv -Ckt 2 | 2026-01-02 01:01 | 2026-01-02 21:10 | 0.83958 | T | None | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Shyampur 230kV Ckt-1 | 2026-01-02 04:12 | 2026-01-02 04:24 | 0.0083333 | T | None | 290 | 58 | Power interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-2 | 2026-01-24 14:50 | 2026-01-24 15:24 | 0.023611 | T | 400 kV Madunaghat ckt- 02 Tripped. | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV Meghnaghat-2(D05) | 2026-01-01 03:54 | 2026-01-01 06:37 | 0.11319 | T | Line protection | 0 | 0 | No interruption
Srinagar 132/33kV | Keraniganj-02(Powerpac) | 2026-01-14 07:23 | 2026-01-14 08:02 | 0.027083 | T | Emergency maint.work | 0 | 0 | No interruption
Fatullah 132/33kV | 132 kV Madanganj | 2026-01-18 23:25 | 2026-01-18 23:25 | 0 | E/O | Emergency maint.work | 0 | 0 | No interruption
Haripur 230/132kV | Ullon (Maniknagar-2) | 2026-01-05 09:49 | 2026-01-05 15:50 | 0.25069 | E/O | order by NLDC | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 1 | 2026-01-05 10:33 | 2026-01-05 13:46 | 0.13403 | E/O | The rope falls on the 132kV line. | 0 | 0 | No interruption
Maniknagar 132/33kV | Narinda Ckt-2 | 2026-01-29 09:25 | 2026-01-29 15:35 | 0.25694 | E/O | PT maintenance work at Narinda end. Shut taken by Mr. Rokonul Islam, SDE, DPDC. All operation done according to instructions of NLDC. | 0 | 0 | No interruption
Siddhirganj 132/33kV | 120MW EGCB GT1 | 2026-01-06 11:29 | 2026-01-06 16:43 | 0.21806 | E/O | Maintenance Works EGCB ends | 0 | 0 | No interruption
Siddhirganj 132/33kV | 120MW EGCB GT1 | 2026-01-07 11:12 | 2026-01-07 17:04 | 0.24444 | E/O | Maintenance Works EGCB ends | 0 | 0 | No interruption
Siddhirganj 132/33kV | 120MW EGCB GT1 | 2026-01-12 14:20 | 2026-01-12 17:00 | 0.11111 | E/O | Termination kit installation | 0 | 0 | No interruption
Siddhirganj 132/33kV | 120MW EGCB GT2 | 2026-01-25 10:31 | 2026-01-25 16:41 | 0.25694 | E/O | Insulation check EGCB ends | 0 | 0 | No interruption
Sonargaon 132/33kV | Daudkandi-2 | 2026-01-28 09:00 | 2026-01-28 15:39 | 0.27708 | E/O | According to NLDC instruction. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-03 01:40 |  | Unserved Energy: |  | 58
Chattogram Grid Circle :
Dohazari 132/33kV | Dohazari-Sikalbaha ckt-1 | 2026-01-16 00:37 | 2026-01-16 05:23 | 0.19861 | T | Patiya ckt-01 ( R-Phase) CT Burst | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2026-01-06 06:53 | 2026-01-06 07:20 | 0.01875 | T | Tripped | 43 | 19.35 | Power interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2026-01-24 15:26 | 2026-01-24 15:42 | 0.011111 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Rampur 230/132/33 | Anandabazar-1 | 2026-01-10 15:20 | 2026-01-10 15:20 | 0 | T | Tripped showing REL670 relays. | 0 | 0 | No interruption
AKS 132/33kV | Bar Aulia | 2026-01-19 11:08 | 2026-01-19 13:38 | 0.10417 | E/O | Emergency maint.work | 0 | 0 | No interruption
AKS 132/33kV | Khulshi | 2026-01-19 11:52 | 2026-01-19 13:30 | 0.068056 | E/O | Emergency maint.work | 0 | 0 | No interruption
AKS 132/33kV | Bar Aulia | 2026-01-22 12:31 | 2026-01-22 16:36 | 0.17014 | E/O | Emergency maint.work | 0 | 0 | No interruption
Baroaulia 132/33kV | AKSPL | 2026-01-13 11:10 | 2026-01-13 16:11 | 0.20903 | E/O | Emergency maint.work | 0 | 0 | No interruption
Baroaulia 132/33kV | AKSPL | 2026-01-19 11:08 | 2026-01-19 13:40 | 0.10556 | E/O | Emergency maint.work | 0 | 0 | No interruption
Baroaulia 132/33kV | AKSPL | 2026-01-22 12:33 | 2026-01-22 16:35 | 0.16806 | E/O | Emergency maint.work | 0 | 0 | No interruption
Rampur 230/132/33 | Anandabazar-1 | 2026-01-10 18:20 | 2026-01-10 18:20 | 0 | E/O | Emergency maint.work | 0 | 0 | No interruption
Rampur 230/132/33 | Anandabazar-2 | 2026-01-10 19:00 | 2026-01-10 22:08 | 0.13056 | E/O | Emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 04:25 |  | Unserved Energy: |  | 19.35
Cumilla Grid Circle :
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-1 | 2026-01-12 15:15 | 2026-01-12 15:41 | 0.018056 | T | Undet Frequency Sylhet-Fenchuganj Line Trip | 40 | 17.3333 | Power interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-2 | 2026-01-12 15:15 | 2026-01-12 15:42 | 0.01875 | T | Under Frequency | 40 | 18 | Power interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-2 | 2026-01-01 20:05 | 2026-01-01 20:42 | 0.025694 | T | Tripped | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sreemongal-2 | 2026-01-01 05:58 | 2026-01-01 05:58 | 0 | T | Excessive Fog | 0 | 0 | No interruption
Kulaura 132/33kV | 132 Fenchuganj-1 | 2026-01-07 08:55 | 2026-01-07 09:38 | 0.029861 | T | None | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-Ashuganj Ckt-03 | 2026-01-01 02:41 | 2026-01-01 03:03 | 0.015278 | T | Non | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-2 | 2026-01-01 05:58 | 2026-01-01 06:24 | 0.018056 | T | distance relay Phase A | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-1 | 2026-01-12 14:57 | 2026-01-12 17:36 | 0.11042 | T | Tripped | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-2 | 2026-01-15 12:26 | 2026-01-15 13:44 | 0.054167 | E/O | Emeregency maint.work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Chowmuhuni ckt-1 | 2026-01-05 09:51 | 2026-01-05 19:03 | 0.38333 | E/O | shutdown for Chowmuhoni Grid Work | 0 | 0 | No interruption
Kulaura 132/33kV | 132 Fenchuganj-1 | 2026-01-12 14:57 | 2026-01-12 15:41 | 0.030556 | E/O | Fenchuganj grid failure | 13 | 9.5333 | Power interruption
Kulaura 132/33kV | 132 Fenchuganj-2 | 2026-01-12 14:57 | 2026-01-12 15:46 | 0.034028 | E/O | Fenchuganj grid failure | 13 | 10.6167 | Power interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-1 | 2026-01-13 14:54 | 2026-01-13 16:01 | 0.046528 | E/O | Order by NLDC. | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-2 | 2026-01-19 15:40 | 2026-01-19 16:43 | 0.04375 | E/O | Annual Maintenance at Fenchuganj End | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-1 | 2026-01-20 09:55 | 2026-01-20 12:12 | 0.095139 | E/O | NLDC | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-1 | 2026-01-21 09:01 | 2026-01-21 17:50 | 0.36736 | E/O | Ordered by NLDC | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-2 | 2026-01-25 07:44 | 2026-01-25 15:49 | 0.33681 | E/O | Order by Back Up NLDC. | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 15:04 |  | Unserved Energy: |  | 55.4833
Khulna Grid Circle :
Patuakhali 132/33kV | Barishal-Pautakhali 132kV Line | 2026-01-27 22:25 | 2026-01-27 23:00 | 0.024306 | T | Earth Fault. ( Barguna intrruption 14 MW) | 14 | 8.1667 | Power interruption
Faridpur 132/33kV | 132 KV Rajbari ckt-2 | 2026-01-19 14:28 | 2026-01-19 17:40 | 0.13333 | E/O | Circuit breaker maintenance | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-NWPGCL | 2026-01-25 13:18 | 2026-01-25 21:10 | 0.32778 | E/O | Emergency Command by ALDC Khulna | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-NWPGCL | 2026-01-26 09:21 | 2026-01-26 15:52 | 0.27153 | E/O | Instraction of ALDC Khulna. | 0 | 0 | No interruption
Rampal 400/230kV | Khulna Line-1 | 2026-01-12 09:37 | 2026-01-12 13:52 | 0.17708 | E/O | Khulna ALDC Demand (Annual Maintenance) | 0 | 0 | No interruption
Rampal 400/230kV | Gopalganj Line-1 | 2026-01-18 08:57 | 2026-01-18 16:20 | 0.30764 | E/O | Annual Maintenance | 0 | 0 | No interruption
Rampal 400/230kV | Gopalganj Line-1 Reactor | 2026-01-19 09:19 | 2026-01-19 17:05 | 0.32361 | E/O | Khulna ALDC Demand(Annual Maintenance) | 0 | 0 | No interruption
Rampal 400/230kV | Gopalganj Line-1 | 2026-01-19 09:20 | 2026-01-19 17:02 | 0.32083 | E/O | Khulna ALDC Demand(Annual Maintenance) | 0 | 0 | No interruption
Rampal 400/230kV | Gopalganj Line-1 | 2026-01-20 08:47 | 2026-01-20 16:34 | 0.32431 | E/O | Khulna ALDC Demand(Annual Maintenance) | 0 | 0 | No interruption
Rampal 400/230kV | Gopalganj Line-1 Reactor | 2026-01-20 08:47 | 2026-01-20 16:45 | 0.33194 | E/O | Khulna ALDC Demand(Annual Maintenance) | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 13:01 |  | Unserved Energy: |  | 8.1667
HVDC Grid Circle :
Jhenaidah 230/132kV | Jhenaidah (New)-Khulna (South) Ckt-1 | 2026-01-20 10:57 | 2026-01-20 11:36 | 0.027083 | T | False Operation | 0 | 0 | No interruption
Pabna 132/33kV | Pabna-Shahjadpur Line | 2026-01-18 12:07 | 2026-01-18 13:35 | 0.061111 | E/O | Emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 0.088194 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Bogura 230/132kV | Naogaon 132 KV Line-1 | 2026-01-07 16:07 | 2026-01-07 16:42 | 0.024306 | T | Unknown | 0 | 0 | No interruption
Joypurhat 132/33kV | Naogaon Ckt.-2 | 2026-01-07 10:16 | 2026-01-07 10:57 | 0.028472 | T | Protection Fault | 29 | 19.8167 | Power interruption
Panchagarh 132/33kV | 132KV Capacitor Bank | 2026-01-16 22:59 | 2026-01-16 22:59 | 0 | T | over current(O/C) | 0 | 0 | No interruption
Thakurgaon 132/33kV | Thakurgaon-EPV Ckt-2 | 2026-01-11 04:59 | 2026-01-11 05:47 | 0.033333 | T | অদ্য ১১-০১-২০২৫ ইং তারিখে ০৪:৫৯ মিনিটে গ্রিড পাওয়ার চলে যায়। এ সময় EPVTL-Thakurgaon Ckt-2 ট্রিপ করে অর্থাৎ 905B ও 902B ব্রেকার ট্রিপ করে। উল্লেখ্য যে, EPVTL-Thakurgaon Ckt-1 রি-কন্ডাক্টিং কাজের জন্য শুধু লাইন আইসোলেটর দিয়ে আগে থেকে শাট ডাউনে ছিল। | 40 | 32 | Power interruption
Bogura 132/33kV | New Bogura-1 | 2026-01-11 10:42 | 2026-01-11 12:13 | 0.063194 | E/O | Replacing SF6 pressure gauge to CB | 0 | 0 | No interruption
Bogura 230/132kV | 230KV Main 2 | 2026-01-05 15:57 | 2026-01-05 17:20 | 0.057639 | E/O | 230kv sirajganj ckt-01 main CB problem. | 0 | 0 | No interruption
Bogura 230/132kV | Bogra 132KV Line-1 | 2026-01-11 10:40 | 2026-01-11 12:13 | 0.064583 | E/O | Emergency maint.work | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-1 | 2026-01-15 10:42 | 2026-01-15 10:42 | 0 | E/O | Emergency maint.work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2026-01-01 02:55 | 2026-01-01 07:43 | 0.2 | E/O | Due to emergency voltage control | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2026-01-01 02:55 | 2026-01-01 07:43 | 0.2 | E/O | Due to emergency voltage control | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2026-01-03 01:17 | 2026-01-03 07:45 | 0.26944 | E/O | Shutdown instructed by NLDC due to emergency voltage Control . | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2026-01-03 01:17 | 2026-01-03 07:45 | 0.26944 | E/O | Shutdown instructed by NLDC due to emergency voltage Control . | 0 | 0 | No interruption
Joypurhat 132/33kV | Naogaon Ckt.-2 | 2026-01-10 09:46 | 2026-01-10 09:46 | 0 | E/O | Load shift to line ckt-1. | 0 | 0 | No interruption
Purbasadipur 132/33kV | Saidpur Line-1 | 2026-01-14 09:59 | 2026-01-14 19:31 | 0.39722 | E/O | Emergency maint.work | 0 | 0 | No interruption
Purbasadipur 132/33kV | Saidpur Line-1 | 2026-01-16 15:20 | 2026-01-16 17:28 | 0.088889 | E/O | Emergency maint.work | 0 | 0 | No interruption
Rajshahi 132/33kV | 132 kV PPP 50 Mw | 2026-01-27 10:44 | 2026-01-27 14:42 | 0.16528 | E/O | Maintenance work at PPP 50 MW switchyard . | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 20:41 |  | Unserved Energy: |  | 51.8167
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 1900-01-21 05:34 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
| Ashuganj-2 | 2024-11-13 12:06 | 2024-11-13 12:18

## QF-LDC-25
QF-LDC-25
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:January 2026
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV | 132kV Transformer-1 (405T1) | 2026-01-03 08:57 | 2026-01-03 16:54 | 7:57 | S/O | Annual maintenance | 0 | 0 | No interruption
Agargaon 230/132kV | 230kV Transformer-2 ( 715T2) | 2026-01-05 09:58 | 2026-01-05 11:36 | 1:38 | S/O | Relay Testing | 0 | 0 | No interruption
Agargaon 230/132kV | 132kV Transformer-2 (415T2) | 2026-01-05 12:00 | 2026-01-05 12:31 | 0:31 | S/O | Relay test | 0 | 0 | No interruption
Agargaon 230/132kV | 132kV Transformer-1 (405T1) | 2026-01-05 12:33 | 2026-01-05 13:22 | 0:49 | S/O | Relay test | 0 | 0 | No interruption
Agargaon 230/132kV | 230kV Transformer-1 ( 705T1) | 2026-01-05 13:49 | 2026-01-05 15:11 | 1:22 | S/O | Relay Testing | 0 | 0 | No interruption
Agargaon 230/132kV | 230kV Transformer-1 ( 705T1) | 2026-01-10 08:12 | 2026-01-10 18:22 | 10:10 | S/O | Annual Maintenance | 0 | 0 | No interruption
Agargaon 230/132kV | Auxiliary Tr-2 | 2026-01-17 07:40 | 2026-01-17 18:58 | 11:18 | S/O | Annual maintenance | 0 | 0 | No interruption
Agargaon 230/132kV | 230kV Transformer-2 ( 715T2) | 2026-01-17 07:42 | 2026-01-17 18:57 | 11:15 | S/O | Annual maintenance | 0 | 0 | No interruption
Agargaon 230/132kV | 132kV Transformer-2 (415T2) | 2026-01-24 08:30 | 2026-01-24 14:09 | 5:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | ATR-01 | 2026-01-10 09:40 | 2026-01-10 19:37 | 9:57 | S/O | Scheduled shutdown | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 230 kv Bus 01 | 2026-01-12 07:14 | 2026-01-12 09:47 | 2:33 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 230/132kv Tr-03 | 2026-01-13 08:19 | 2026-01-13 21:22 | 13:03 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | ATR-03 | 2026-01-13 09:25 | 2026-01-15 18:31 | 57:06 | S/O | Annual Maintenace | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 230 kv Bus 01 | 2026-01-13 10:06 | 2026-01-15 18:45 | 56:39 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 230/132kv Tr-01 | 2026-01-14 07:35 | 2026-01-14 18:19 | 10:44 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 230/132kv Tr-02 | 2026-01-15 07:02 | 2026-01-15 18:02 | 11:00 | S/O | CT changing | 0 | 0 | No interruption
Aminbazar 400/230/132kV | ATR-01 | 2026-01-18 08:55 | 2026-01-18 18:23 | 9:28 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 230 kv Bus 01 | 2026-01-18 10:21 | 2026-01-26 12:41 | 194:20 | S/O | DS changing | 0 | 0 | No interruption
Aminbazar 400/230/132kV | ATR-02 | 2026-01-19 08:59 | 2026-01-19 17:02 | 8:03 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | ATR-02 | 2026-01-20 08:24 | 2026-01-20 17:54 | 9:30 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 230 kv Bus 02 | 2026-01-27 10:53 | 2026-01-27 10:53 | 0:00 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV | Bus A | 2026-01-04 10:29 | 2026-01-04 16:11 | 5:42 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV | 02. Transformer- 02 | 2026-01-10 08:29 | 2026-01-10 18:11 | 9:42 | S/O | Annual maintenance | 10 | 97 | Power interruption
Bhaluka 132/33kV | 02. Transformer- 02 | 2026-01-13 09:21 | 2026-01-13 12:08 | 2:47 | S/O | Annual maintenance purpose. | 0 | 0 | No interruption
Bhaluka 132/33kV | Bus A | 2026-01-15 08:49 | 2026-01-15 13:52 | 5:03 | S/O | Annual maintenance work purpose | 0 | 0 | No interruption
Bhaluka 132/33kV | Bus B | 2026-01-15 14:14 | 2026-01-15 16:59 | 2:45 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV | 01. Transformer- 01 | 2026-01-17 08:10 | 2026-01-17 18:09 | 9:59 | S/O | Annual maintenance | 48 | 479.2 | Power interruption
Bhaluka 132/33kV | 02. Transformer- 02 | 2026-01-17 08:10 | 2026-01-17 10:18 | 2:08 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV | Bus A | 2026-01-25 11:35 | 2026-01-25 13:13 | 1:38 | S/O |  | 0 | 0 | No interruption
Dhamrai 132/33kV | Transformer-1 | 2026-01-03 09:19 | 2026-01-03 16:37 | 7:18 | S/O | Annual maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV | Transformer-1 | 2026-01-04 09:15 | 2026-01-04 16:01 | 6:46 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV | Transformer-1 | 2026-01-05 09:05 | 2026-01-05 17:03 | 7:58 | S/O | Annual maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV | Transformer-2 | 2026-01-10 09:38 | 2026-01-10 16:34 | 6:56 | S/O | Due to annual maintenance. | 0 | 0 | No interruption
Dhamrai 132/33kV | Transformer-2 | 2026-01-11 09:29 | 2026-01-11 17:08 | 7:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV | Transformer-2 | 2026-01-12 09:15 | 2026-01-12 16:55 | 7:40 | S/O | Due to annual maintenance. | 0 | 0 | No interruption
Dhamrai 132/33kV | Transformer-2 | 2026-01-14 10:42 | 2026-01-14 13:34 | 2:52 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV | Main Bus-2 | 2026-01-22 11:08 | 2026-01-22 16:07 | 4:59 | S/O | High voltage test | 0 | 0 | No interruption
Dhamrai 132/33kV | Main Bus-1 | 2026-01-22 16:14 | 2026-01-22 18:10 | 1:56 | S/O | Project work by PGCB. | 0 | 0 | No interruption
Jamalpur 132/33kV | T-2 | 2026-01-10 09:20 | 2026-01-10 11:27 | 2:07 | S/O | 132KV CT Conductor Temperature Remove Work. | 20 | 42.3333 | Power interruption
Jamalpur 132/33kV | T-3 | 2026-01-27 12:09 | 2026-01-27 13:18 | 1:09 | S/O | Project work | 0 | 0 | No interruption
Joydebpur 132/33kV | GT-3 | 2026-01-18 10:26 | 2026-01-18 12:03 | 1:37 | S/O | Oil leakage maintenance of B-Phase C.T. | 0 | 0 | No interruption
Joydebpur 132/33kV | GT-2 | 2026-01-31 15:16 | 2026-01-31 16:17 | 1:01 | S/O | OLTC Oil Centrifuged | 0 | 0 | No interruption
Kabirpur 132/33kV | XFR, T-I | 2026-01-04 09:23 | 2026-01-04 16:42 | 7:19 | S/O | Annual Maintenance Work | 25 | 182.9167 | Power interruption
Kabirpur 132/33kV | XFR, T-3 | 2026-01-04 10:04 | 2026-01-04 12:55 | 2:51 | S/O | 33 kV Section DS Maintenance Work by Dhaka PBS-01. | 48 | 136.8 | Power interruption
Kabirpur 132/33kV | XFR, T-2 | 2026-01-06 09:39 | 2026-01-06 16:56 | 7:17 | S/O | Annual maintenance | 0 | 0 | No interruption
Kabirpur 132/33kV | XFR, T-3 | 2026-01-13 09:30 | 2026-01-13 16:06 | 6:36 | S/O | Annual maintenance | 0 | 0 | No interruption
Kabirpur 132/33kV | XFR, T-2 | 2026-01-24 08:14 | 2026-01-24 18:26 | 10:12 | S/O | 33 kV Bus Maintenance Work by DPBS-1 | 55 | 561 | Power interruption
Kabirpur 132/33kV | XFR, T-I | 2026-01-24 08:17 | 2026-01-24 18:25 | 10:08 | S/O | 33 kV Bus Maintenance Work by DPBS-1 | 55 | 557.3333 | Power interruption
Kaliakoir 400/230/132kV | 400kV Bus 1 | 2026-01-01 13:05 | 2026-01-01 15:25 | 2:20 | S/O | None | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 132kV Bus 2 | 2026-01-03 13:20 | 2026-01-03 14:48 | 1:28 | S/O | Maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400/132kV TR1 | 2026-01-24 09:03 | 2026-01-24 17:37 | 8:34 | S/O | annual maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 132kV Bus 2 | 2026-01-24 14:17 | 2026-01-24 17:25 | 3:08 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 132kV Bus 2 | 2026-01-25 12:28 | 2026-01-25 17:45 | 5:17 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 132kV Bus 2 | 2026-01-26 13:41 | 2026-01-26 17:38 | 3:57 | S/O | annual maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 132kV Bus 2 | 2026-01-27 09:38 | 2026-01-27 13:13 | 3:35 | S/O | Annual maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 132kV Bus 2 | 2026-01-28 11:22 | 2026-01-28 14:48 | 3:26 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400/132kV TR2 | 2026-01-30 08:47 | 2026-01-30 17:49 | 9:02 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 132kV Bus 2 | 2026-01-30 09:03 | 2026-01-30 18:16 | 9:13 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV | GT-3 (132kV) | 2026-01-18 09:09 | 2026-01-18 17:57 | 8:48 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV | GT-1 (132kV) | 2026-01-19 09:24 | 2026-01-19 16:49 | 7:25 | S/O | DPDC 33kv bus shut down. | 0 | 0 | No interruption
Kallyanpur 132/33kV | GT-3 (132kV) | 2026-01-19 09:26 | 2026-01-19 16:52 | 7:26 | S/O | DPDC 33kv bus shut down. | 0 | 0 | No interruption
Kallyanpur 132/33kV | GT-2 (132kV) | 2026-01-21 09:29 | 2026-01-21 17:44 | 8:15 | S/O | maintenances Works | 0 | 0 | No interruption
Kallyanpur 132/33kV | GT-1 (132kV) | 2026-01-27 08:45 | 2026-01-27 17:42 | 8:57 | S/O | Ten Delta test | 0 | 0 | No interruption
Kallyanpur 132/33kV | GT-2 (132kV) | 2026-01-29 09:01 | 2026-01-31 20:22 | 59:21 | S/O | Oil centrifuging | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-2 (414T) | 2026-01-10 07:50 | 2026-01-10 15:24 | 7:34 | S/O | 33KV T-2 BUS SHUTDOWN BY BPDB | 31 | 234.5667 | Power interruption
Kishoreganj 132/33kV | Tr-1 (404T) | 2026-01-17 07:36 | 2026-01-17 09:05 | 1:29 | S/O | 33Kv bus-section-01 ds maintenance | 20.5 | 60.8167 | Power interruption
Kishoreganj 132/33kV | Tr-2 (414T) | 2026-01-17 07:36 | 2026-01-17 09:05 | 1:29 | S/O | 33Kv bus-section-01 ds maintenance | 20.5 | 60.8167 | Power interruption
Kodda 132/33kV | Tr-1 (406T) | 2026-01-26 11:44 | 2026-01-26 13:06 | 1:22 | S/O | For Relay test | 0 | 0 | No interruption
Kodda 132/33kV | Tr-3 (426T) | 2026-01-26 13:09 | 2026-01-26 13:26 | 0:17 | S/O | For Relay test | 0 | 0 | No interruption
Kodda 132/33kV | Tr-5 (446T) | 2026-01-26 13:30 | 2026-01-26 13:48 | 0:18 | S/O | Relay Testing | 0 | 0 | No interruption
Kodda 132/33kV | Tr-4 (436T) | 2026-01-26 13:57 | 2026-01-26 14:13 | 0:16 | S/O | Relay Testing | 0 | 0 | No interruption
Kodda 132/33kV | Tr-2 (416T) | 2026-01-26 14:16 | 2026-01-26 14:27 | 0:11 | S/O | Relay Testing | 0 | 0 | No interruption
Kodda 132/33kV | Tr-5 (446T) | 2026-01-31 09:15 | 2026-01-31 17:03 | 7:48 | S/O | Work by pbs | 70 | 546 | Power interruption
Kodda 132/33kV | Tr-3 (426T) | 2026-01-31 11:18 | 2026-01-31 13:35 | 2:17 | S/O | Wrk by pbs | 20 | 45.6667 | Power interruption
Kodda 132/33kV | Tr-4 (436T) | 2026-01-31 11:18 | 2026-01-31 13:36 | 2:18 | S/O | Wrk by pbs | 20 | 46 | Power interruption
Mirpur 132/33kV | T2 | 2026-01-04 09:11 | 2026-01-05 16:40 | 31:29 | S/O | HT Bushing Terminal Replacemint work. | 0 | 0 | No interruption
Mirpur 132/33kV | T1 | 2026-01-06 09:13 | 2026-01-06 17:22 | 8:09 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mirpur 132/33kV | Main Bus | 2026-01-06 09:47 | 2026-01-06 17:14 | 7:27 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mirpur 132/33kV | T1 | 2026-01-07 08:58 | 2026-01-07 17:12 | 8:14 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Mirpur 132/33kV | Reserve Bus | 2026-01-07 09:25 | 2026-01-07 17:11 | 7:46 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Mirpur 132/33kV | T2 | 2026-01-08 09:08 | 2026-01-08 16:35 | 7:27 | S/O | Annual maintenance work on 132 kV Bay equipment of T2 Xfr. | 0 | 0 | No interruption
Mirpur 132/33kV | Reserve Bus | 2026-01-08 09:26 | 2026-01-08 16:42 | 7:16 | S/O | Annual maintenance work on 132 kV Reserve Bus Bay equipment of T2 Xfr. | 0 | 0 | No interruption
Mirpur 132/33kV | T2 | 2026-01-11 08:41 | 2026-01-11 17:35 | 8:54 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mirpur 132/33kV | Main Bus | 2026-01-11 09:17 | 2026-01-11 17:34 | 8:17 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mirpur 132/33kV | Reserve Bus | 2026-01-12 09:26 | 2026-01-12 16:49 | 7:23 | S/O | 132KV Buscoupler Reserve Bus Bay Equipment Maintenance. | 0 | 0 | No interruption
Mirpur 132/33kV | Main Bus | 2026-01-13 09:47 | 2026-01-13 17:07 | 7:20 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Mirpur 132/33kV | T2 | 2026-01-14 09:05 | 2026-01-14 17:28 | 8:23 | S/O | A/M work | 0 | 0 | No interruption
Mirpur 132/33kV | Reserve Bus | 2026-01-14 09:28 | 2026-01-14 17:27 | 7:59 | S/O | 132/33 KV Transformer-2 (T2 ) maintenance work. | 0 | 0 | No interruption
Mirpur 132/33kV | Main Bus | 2026-01-19 09:22 | 2026-01-19 16:47 | 7:25 | S/O | M/B Ds of Aminbazar Ckt-2 & Uttara old ckt Annual Maintenance work. | 0 | 0 | No interruption
Mirpur 132/33kV | T2 | 2026-01-21 13:36 | 2026-01-21 14:36 | 1:00 | S/O | Relay Testing work. | 0 | 0 | No interruption
Mirpur 132/33kV | T1 | 2026-01-21 14:40 | 2026-01-21 15:32 | 0:52 | S/O | Relay test by SPMD | 0 | 0 | No interruption
Mirpur 132/33kV | Reserve Bus | 2026-01-22 08:59 | 2026-01-22 18:15 | 9:16 | S/O | AM | 0 | 0 | No interruption
Mirpur 132/33kV | Main Bus | 2026-01-26 10:11 | 2026-01-26 15:16 | 5:05 | S/O | Annual maintenance work on main bus PT. | 0 | 0 | No interruption
Mirpur 132/33kV | Main Bus | 2026-01-29 09:11 | 2026-01-29 09:11 | 0:00 | S/O | AM | 0 | 0 | No interruption
Mirzapur 132/33kV | Transformer-01(E05) | 2026-01-03 08:56 | 2026-01-03 15:02 | 6:06 | S/O | Existing LILO lINEMirzapur grid Re-conducting | 16 | 97.6 | Power interruption
Mirzapur 132/33kV | Transformer-02(E07) | 2026-01-03 08:57 | 2026-01-03 15:13 | 6:16 | S/O | Existing LILO lINEMirzapur grid Re-conducting | 9 | 56.4 | Power interruption
Mirzapur 132/33kV | Transformer-01(E05) | 2026-01-16 09:56 | 2026-01-16 16:14 | 6:18 | S/O | Exitting LILO Line Mirzapur Grid | 19 | 119.7 | Power interruption
Mirzapur 132/33kV | Transformer-02(E07) | 2026-01-16 09:56 | 2026-01-16 16:10 | 6:14 | S/O | Exitting LILO Line Mirzapur Grid | 13 | 81.0333 | Power interruption
Mirzapur 132/33kV | Transformer-01(E05) | 2026-01-17 09:36 | 2026-01-17 12:48 | 3:12 | S/O | Tangail Grid Maintenance work | 23 | 73.6 | Power interruption
Mirzapur 132/33kV | Transformer-02(E07) | 2026-01-17 09:37 | 2026-01-17 12:47 | 3:10 | S/O | Tangail Grid Maintenance work | 13 | 41.1667 | Power interruption
Mymensingh 132/33kV | Bus A | 2026-01-02 07:46 | 2026-01-02 12:30 | 4:44 | S/O | Project work. | 0 | 0 | No interruption
Mymensingh 132/33kV | Bus B | 2026-01-03 08:31 | 2026-01-03 16:06 | 7:35 | S/O | Project work. | 0 | 0 | No interruption
Mymensingh 132/33kV | Bus A | 2026-01-09 08:54 | 2026-01-09 10:26 | 1:32 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mymensingh 132/33kV | Bus B | 2026-01-10 07:42 | 2026-01-10 09:43 | 2:01 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mymensingh 132/33kV | Bus A | 2026-01-16 09:05 | 2026-01-16 10:38 | 1:33 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mymensingh 132/33kV | Bus B | 2026-01-16 11:16 | 2026-01-16 14:50 | 3:34 | S/O | Annual Maintenance | 0 | 0 | No interruption
Netrakona 132/33kV | Main Bus | 2026-01-10 09:40 | 2026-01-10 18:26 | 8:46 | S/O | A/M | 0 | 0 | No interruption
Netrakona 132/33kV | Main Bus | 2026-01-31 07:25 | 2026-01-31 11:48 | 4:23 | S/O | Project Work | 0 | 0 | No interruption
New Tongi | T1(403T) | 2026-01-08 11:05 | 2026-01-08 17:30 | 6:25 | S/O | Annual Maintanance | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-2 | 2026-01-01 12:09 | 2026-01-11 16:01 | 243:52 | S/O | Sreepur Bay extension work at busbar-01 | 0 | 0 | No interruption
Rajendrapur 132/33kV | 132 kV BUS-1 | 2026-01-01 12:14 | 2026-01-06 14:00 | 121:46 | S/O | Sreepur Bay extension work at busbar-01 | 0 | 0 | No interruption
Rajendrapur 132/33kV | 132 kV BUS-2 | 2026-01-06 14:32 | 2026-01-06 14:32 | 0:00 | S/O | Bus-1 shutdown restored and Bus-2 shutdown taken for Bus-2 extention part maintenance work. | 0 | 0 | No interruption
Satmasjid 132/33kV | 132/33 KV Transformer-1 | 2026-01-22 12:11 | 2026-01-22 13:20 | 1:09 | S/O | DPDC Maintenance Work | 0 | 0 | No interruption
Satmasjid 132/33kV | 132/33 KV Transformer-2 | 2026-01-22 13:31 | 2026-01-22 15:18 | 1:47 | S/O | DPDC Maintenance Work | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 01 | 2026-01-12 09:30 | 2026-01-12 10:50 | 1:20 | S/O | Maintenances | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 04 | 2026-01-12 11:12 | 2026-01-12 13:02 | 1:50 | S/O | maintenances Works | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 04 | 2026-01-31 10:20 | 2026-01-31 13:30 | 3:10 | S/O | maintenances Works | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132 kV BUS-1 | 2026-01-01 09:31 | 2026-01-01 14:24 | 4:53 | S/O | DS maintenance work | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2026-01-01 10:00 | 2026-01-01 11:52 | 1:52 | S/O | DS repair work. | 0 | 0 | No interruption
Sreepur 230/132/33kV | 230/132 kV T-1 | 2026-01-01 13:16 | 2026-01-01 14:02 | 0:46 | S/O | PSDC ATR-3 Installation work | 0 | 0 | No interruption
Sreepur 230/132/33kV | 230/132 kV T-1 | 2026-01-14 09:39 | 2026-01-14 16:30 | 6:51 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV | 230/132 kV T-1 | 2026-01-17 09:20 | 2026-01-17 17:22 | 8:02 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV | Auxiliary Transformer - 2 | 2026-01-18 13:34 | 2026-01-18 15:56 | 2:22 | S/O | Annual maintenance & works of Protection team for SPS | 0 | 0 | No interruption
Sreepur 230/132/33kV | 230/132 kV T-2 | 2026-01-18 13:34 | 2026-01-18 15:53 | 2:19 | S/O | Annual maintenance & works of Protection team for SPS | 0 | 0 | No interruption
Sreepur 230/132/33kV | 230/132 kV T-2 | 2026-01-19 10:10 | 2026-01-19 18:00 | 7:50 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV | 230 kV Bus-1 | 2026-01-27 10:24 | 2026-01-27 17:19 | 6:55 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV | 230 kV Bus-1 | 2026-01-31 10:24 | 2026-01-31 16:53 | 6:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132 kV BUS-2 | 2026-01-31 15:13 | 2026-01-31 17:29 | 2:16 | S/O | Annual Maintenance | 0 | 0 | No interruption
Tangail 132/33kV | Main Bus | 2026-01-17 09:26 | 2026-01-17 15:27 | 6:01 | S/O | Annual Maintenance | 100 | 601.6667 | Power interruption
Tongi 230/132/33kV | 132 kV Bus-2 | 2026-01-01 09:18 | 2026-01-01 18:51 | 9:33 | S/O | bus extension work by PSDC | 0 | 0 | No interruption
Tongi 230/132/33kV | 230 kV Bus-1 | 2026-01-01 09:58 | 2026-01-01 17:33 | 7:35 | S/O | Annual maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV | T-03 | 2026-01-01 09:58 | 2026-01-01 17:28 | 7:30 | S/O | Only HV side shutdown CB-822B open only | 0 | 0 | No interruption
Tongi 230/132/33kV | T-03 | 2026-01-02 08:20 | 2026-01-02 17:15 | 8:55 | S/O | Annual maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV | 132 kV Bus-1 | 2026-01-02 08:50 | 2026-01-02 19:30 | 10:40 | S/O | Project (To4 Trans former Installations Work) | 0 | 0 | No interruption
Tongi 230/132/33kV | T-02 | 2026-01-03 09:38 | 2026-01-03 16:43 | 7:05 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Tongi 230/132/33kV | 132 kV Bus-1 | 2026-01-04 10:58 | 2026-01-04 17:02 | 6:04 | S/O | Annual maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV | T-01 | 2026-01-05 09:34 | 2026-01-05 16:32 | 6:58 | S/O | Annual maintenace | 0 | 0 | No interruption
Tongi 230/132/33kV | T-01 | 2026-01-06 09:36 | 2026-01-06 16:50 | 7:14 | S/O | Annual maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV | 230 kV Bus-2 | 2026-01-07 09:44 | 2026-01-07 16:32 | 6:48 | S/O | Annual Maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV | T-01 | 2026-01-08 09:17 | 2026-01-08 16:15 | 6:58 | S/O | Annual maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV | T-03 | 2026-01-09 09:18 | 2026-01-09 19:52 | 10:34 | S/O | Annual maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV | T-1 | 2026-01-18 11:02 | 2026-01-18 19:31 | 8:29 | S/O | Signal shifting work | 0 | 0 | No interruption
Tongi 230/132/33kV | T-2 | 2026-01-19 11:54 | 2026-01-19 19:56 | 8:02 | S/O | Panel meter shifting | 0 | 0 | No interruption
Tongi 230/132/33kV | T-2 | 2026-01-24 17:21 | 2026-01-24 19:42 | 2:21 | S/O | Testing work | 0 | 0 | No interruption
Tongi 230/132/33kV | T-3 | 2026-01-24 19:51 | 2026-01-24 20:47 | 0:56 | S/O | Transformer Testing Work | 0 | 0 | No interruption
Tongi 230/132/33kV | T-03 | 2026-01-31 11:09 | 2026-01-31 19:47 | 8:38 | S/O | Annual maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV | 230 kV Bus-1 | 2026-01-31 11:10 | 2026-01-31 19:49 | 8:39 | S/O | Loop changing work | 0 | 0 | No interruption
|  |  | Total : | 1900-03-04 02:38 |  | Unserved Energy: |  | 4121.6167
Dhaka (South) Grid Circle :
Cantonment 132/33kV | Transformer-1 (T-1) | 2026-01-14 10:06 | 2026-01-14 16:57 | 6:51 | S/O | Transformer-1 Annual Maintenance and Testing | 0 | 0 | No interruption
Cantonment 132/33kV | Transformer-2 (T-2) | 2026-01-15 09:38 | 2026-01-15 14:53 | 5:15 | S/O | Transformer-2 Annual Maintenance and Testing | 0 | 0 | No interruption
Cantonment 132/33kV | Transformer-1 (T-1) | 2026-01-16 09:05 | 2026-01-16 17:15 | 8:10 | S/O | Transformer-1 Annual Maintenance and Testing | 0 | 0 | No interruption
Cantonment 132/33kV | Transformer-2 (T-2) | 2026-01-17 09:19 | 2026-01-17 15:44 | 6:25 | S/O | Transformer-02 due to Annual Maintenance . | 0 | 0 | No interruption
Cantonment 132/33kV | Auxiliary Transformer, AT-2 | 2026-01-17 09:25 | 2026-01-17 15:35 | 6:10 | S/O | Annual Maintenance | 0 | 0 | No interruption
Haripur 230/132kV | Auto TR-1 | 2026-01-09 10:22 | 2026-01-09 16:46 | 6:24 | S/O | Annual Maintenance | 0 | 0 | No interruption
Haripur 230/132kV | Auto TR-2 | 2026-01-09 16:49 | 2026-01-09 20:34 | 3:45 | S/O | Annunciator change | 0 | 0 | No interruption
Haripur 230/132kV | 132kV Main Bus Sec-1 | 2026-01-13 07:29 | 2026-01-13 19:13 | 11:44 | S/O | Loop replacement and clamp replacement work at 132 kV 412 MW EGCB Bay. | 0 | 0 | No interruption
Hasnabad 230/132kV | Bus-2 | 2026-01-21 07:55 | 2026-01-21 13:35 | 5:40 | S/O | annual maintenance | 0 | 0 | No interruption
Madanganj 132/33kV | GT-1 | 2026-01-17 13:10 | 2026-01-22 11:10 | 118:00 | S/O | Oil centrifuge | 0 | 0 | No interruption
Madanganj 132/33kV | GT-2 | 2026-01-25 10:04 | 2026-01-28 15:50 | 77:46 | S/O | Annual Maintenance | 0 | 0 | No interruption
Maniknagar 132/33kV | Transformer GT-1 | 2026-01-14 10:32 | 2026-01-14 12:23 | 1:51 | S/O | Oil Leakage maintenance by DPDC | 0 | 0 | No interruption
Maniknagar 132/33kV | Transformer GT-2 | 2026-01-23 23:27 | 2026-01-23 23:27 | 0:00 | S/O | DPDC 33 KV GIS SS Testing and commissioning work by DPDC PDSD Project. | 0 | 0 | No interruption
Maniknagar 230/132kV | Auto Transformer-02 (715T) | 2026-01-12 07:44 | 2026-01-19 17:32 | 177:48 | S/O | oil leakage repair | 0 | 0 | No interruption
Maniknagar 230/132kV | Auto Transformer-02 (715T) | 2026-01-28 07:30 | 2026-01-28 17:12 | 9:42 | S/O | Annual Maintenance of 230kV Siddhirganj-Maniknagar Line ckt-2 | 0 | 0 | No interruption
Maniknagar 230/132kV | Auto Transformer-01(705T) | 2026-01-29 11:25 | 2026-01-29 17:48 | 6:23 | S/O | 230kV Siddhirganj-Maniknagar ckt-1 Shutdown for Annual Maintenance. | 0 | 0 | No interruption
Meghnaghat 230/132kV | Bus1 | 2026-01-09 07:00 | 2026-01-09 18:40 | 11:40 | S/O | Maintenance work. | 0 | 0 | No interruption
Meghnaghat 400/230kV | 230kV BUS Section 01 | 2026-01-09 07:03 | 2026-01-09 19:31 | 12:28 | S/O | Instructed by NLDC | 0 | 0 | No interruption
Meghnaghat 400/230kV | ATR-1 | 2026-01-13 09:50 | 2026-01-13 15:51 | 6:01 | S/O | For annual maintenance work | 0 | 0 | No interruption
Meghnaghat 400/230kV | ATR - 2 | 2026-01-15 08:42 | 2026-01-15 14:20 | 5:38 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Meghnaghat 400/230kV | 230kV BUS Section 01 | 2026-01-16 07:35 | 2026-01-16 16:44 | 9:09 | S/O | maintenance work for meghnaghat 230kv ss. | 0 | 0 | No interruption
Narshingdi 132/33kV | T-3 | 2026-01-12 10:40 | 2026-01-12 13:45 | 3:05 | S/O | Oil leakage maintenance | 0 | 0 | No interruption
Postogola 132/33kV | GT-1 | 2026-01-18 17:08 | 2026-01-18 17:08 | 0:00 | S/O | Yearly maintenance | 0 | 0 | No interruption
Rampura 230/132kV | Auto Transformer - 03 | 2026-01-01 09:40 | 2026-01-01 14:54 | 5:14 | S/O | shutdown taken by SPMD to relay work. | 0 | 0 | No interruption
Rampura 230/132kV | Auto Transformer - 02 | 2026-01-02 07:23 | 2026-01-02 12:07 | 4:44 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampura 230/132kV | Auto Transformer - 02 | 2026-01-03 07:31 | 2026-01-03 17:38 | 10:07 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampura 230/132kV | Auto Transformer - 04 | 2026-01-06 08:18 | 2026-01-06 17:58 | 9:40 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampura 230/132kV | NLDC Trafo | 2026-01-06 08:18 | 2026-01-06 18:04 | 9:46 | S/O | Annual Maintenance on ATR-04 | 0 | 0 | No interruption
Rampura 230/132kV | Aux Transformer-01 | 2026-01-06 08:35 | 2026-01-06 17:58 | 9:23 | S/O | Annual Maintenance on ATR-04 | 0 | 0 | No interruption
Rampura 230/132kV | Auto Transformer - 03 | 2026-01-09 06:50 | 2026-01-09 16:57 | 10:07 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampura 230/132kV | Auto Transformer - 02 | 2026-01-17 07:38 | 2026-01-17 17:44 | 10:06 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampura 230/132kV | 132 kV Busbar-2 | 2026-01-17 07:40 | 2026-01-17 17:41 | 10:01 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampura 230/132kV | 230kV Busbar-1 | 2026-01-23 07:20 | 2026-01-23 12:37 | 5:17 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampura 230/132kV | 230kV Busbar-2 | 2026-01-23 14:51 | 2026-01-23 17:11 | 2:20 | S/O | Annual maintenance. | 0 | 0 | No interruption
Siddhirganj 132/33kV | T-2 | 2026-01-09 08:22 | 2026-01-09 15:37 | 7:15 | S/O | Annual maintenance | 0 | 0 | No interruption
Siddhirganj 132/33kV | 132kV Bus A | 2026-01-14 09:11 | 2026-01-14 15:40 | 6:29 | S/O | Annual maintenance work | 0 | 0 | No interruption
Siddhirganj 132/33kV | 132kV Bus B | 2026-01-15 08:48 | 2026-01-15 15:05 | 6:17 | S/O | Annual Maintenance | 0 | 0 | No interruption
Siddhirganj 230/132kV | MTR 1 | 2026-01-04 08:36 | 2026-01-04 16:53 | 8:17 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-1 | 2026-01-01 08:19 | 2026-01-01 09:46 | 1:27 | S/O | Cable heat shrink of 33KV side underground cable. | 45 | 65.25 | Power interruption
Sonargaon 132/33kV | Tr-1 | 2026-01-01 14:41 | 2026-01-01 15:47 | 1:06 | S/O | PBS 33KV side heat shrink work of underground cable | 45 | 49.5 | Power interruption
Sonargaon 132/33kV | Tr-2 | 2026-01-07 09:50 | 2026-01-07 11:30 | 1:40 | S/O | PBS underground cable maintenance | 52 | 86.6667 | Power interruption
Sonargaon 132/33kV | Tr-2 | 2026-01-09 08:08 | 2026-01-09 13:02 | 4:54 | S/O | PBS 33KV underground cable installation. | 45 | 220.5 | Power interruption
|  |  | Total : | 1900-01-25 00:05 |  | Unserved Energy: |  | 421.9167
Chattogram Grid Circle :
Agrabad 132/33kV | MTR-02 (416T) | 2026-01-26 08:00 | 2026-01-26 17:01 | 9:01 | S/O | Annual Maintenance | 0 | 0 | No interruption
Agrabad 132/33kV | MTR-01 (406T) | 2026-01-29 08:33 | 2026-01-29 16:44 | 8:11 | S/O | Annual Maintenance of MTR-01 | 0 | 0 | No interruption
Agrabad 132/33kV | Auxiliary Transformer-01 | 2026-01-29 08:40 | 2026-01-29 16:28 | 7:48 | S/O | Annual Maintenance of MTR-01 | 0 | 0 | No interruption
Bakulia 132/33kV | T-3 (422T) | 2026-01-24 07:36 | 2026-01-24 14:23 | 6:47 | S/O | Annual Maintenance | 10 | 67.8333 | Power interruption
Baroirhat 132/33kV | TR-1, 406T | 2026-01-15 11:08 | 2026-01-15 14:04 | 2:56 | S/O | Annual Maintenance | 0 | 0 | No interruption
Baroirhat 132/33kV | TR-2, 416T | 2026-01-31 07:27 | 2026-01-31 09:07 | 1:40 | S/O | Annual Maintenance | 0 | 0 | No interruption
BSRM 230/33kV | 230/33 kV Transformer-3 (125/140 MVA) | 2026-01-24 09:47 | 2026-01-28 12:52 | 99:05 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | TR-01(406T) | 2026-01-09 08:45 | 2026-01-09 08:45 | 0:00 | S/O | Bus 2 shutdown | 0 | 0 | No interruption
Chandraghona 132/33kV | TR-02(416T) | 2026-01-09 08:46 | 2026-01-09 11:48 | 3:02 | S/O | Bus 2 shutdown | 0 | 0 | No interruption
Chandraghona 132/33kV | TR-01(406T) | 2026-01-10 08:10 | 2026-01-10 10:15 | 2:05 | S/O | BPDB 33KV Bus Maintenance Work. | 17 | 35.4167 | Power interruption
Chandraghona 132/33kV | MAIN BUS-1 | 2026-01-24 08:28 | 2026-01-24 14:53 | 6:25 | S/O | Annual maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | MAIN BUS-2 | 2026-01-25 08:42 | 2026-01-25 13:46 | 5:04 | S/O | Annual maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | TR-01(406T) | 2026-01-27 08:27 | 2026-01-27 15:45 | 7:18 | S/O | None | 0 | 0 | No interruption
Chandraghona 132/33kV | TR-02(416T) | 2026-01-31 08:32 | 2026-01-31 13:59 | 5:27 | S/O | Annual maintenance | 0 | 0 | No interruption
Coxsbazar 132/33kV | 415T-T2 | 2026-01-04 08:30 | 2026-01-31 13:41 | 653:11 | S/O | Project Work | 0 | 0 | No interruption
Coxsbazar 132/33kV | 405T-T1 | 2026-01-10 07:07 | 2026-01-10 10:13 | 3:06 | S/O | 33 kv bushing to incomer-02 loop remove | 30 | 93 | Power interruption
Coxsbazar 132/33kV | T3 | 2026-01-31 05:52 | 2026-01-31 05:52 | 0:00 | S/O | Project work | 0 | 0 | No interruption
Coxsbazar 132/33kV | Main Bus | 2026-01-31 06:06 | 2026-01-31 11:05 | 4:59 | S/O | Main Bus to Tr-02 Bus DS Cable Connection. | 73 | 363.7833 | Power interruption
Dohazari 132/33kV | Power Transformer -T-1 | 2026-01-14 13:14 | 2026-01-14 15:18 | 2:04 | S/O | Due to Patiya 33 KV feeder BUS DS Redhot maintenance. | 0 | 0 | No interruption
Halishahar 132/33kV | 415T(TR-2) | 2026-01-06 08:28 | 2026-01-06 16:20 | 7:52 | S/O | Due to Transformer painting and maintenance work by ESPNER Project. | 0 | 0 | No interruption
Halishahar 132/33kV | 415T(TR-2) | 2026-01-07 08:30 | 2026-01-07 16:51 | 8:21 | S/O | Painting work at radiator of transformer | 0 | 0 | No interruption
Hathazari 230/132/33kV | 230KV MAIN BUS-01 | 2026-01-16 08:45 | 2026-01-16 17:40 | 8:55 | S/O | Project Work G2G | 0 | 0 | No interruption
Hathazari 230/132/33kV | 230KV MAIN BUS-02 | 2026-01-22 09:38 | 2026-01-22 16:15 | 6:37 | S/O | bay loop work | 0 | 0 | No interruption
Hathazari 230/132/33kV | T-01 | 2026-01-31 07:42 | 2026-01-31 14:02 | 6:20 | S/O | PBS Demand | 0 | 0 | No interruption
Khulshi 132/33kV | Main Bus | 2026-01-10 07:55 | 2026-01-10 14:19 | 6:24 | S/O | Annual maintenance | 0 | 0 | No interruption
Khulshi 132/33kV | 405T (T1) | 2026-01-29 07:46 | 2026-01-29 14:34 | 6:48 | S/O | 132/33kV TR-01 given Shutdown due to Annual maintenance work. | 0 | 0 | No interruption
Khulshi 132/33kV | 415T (T2) | 2026-01-31 08:09 | 2026-01-31 14:07 | 5:58 | S/O | Annual maintenance | 0 | 0 | No interruption
Korerhat 400/230/132kV | 400kV BUS-1 | 2026-01-16 07:19 | 2026-01-18 23:24 | 64:05 | S/O | Shout Down taken by CNTIC due to project work. | 0 | 0 | No interruption
Korerhat 400/230/132kV | 400kV BUS-2 | 2026-01-19 07:00 | 2026-01-21 13:12 | 54:12 | S/O | Busbur internal testing | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-3(7103T) | 2026-01-20 15:33 | 2026-01-20 20:05 | 4:32 | S/O | Due to project work. | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-4(7403T) | 2026-01-25 09:04 | 2026-01-25 17:23 | 8:19 | S/O | SAS witness | 0 | 0 | No interruption
Korerhat 400/230/132kV | 230kV BUS-A1 | 2026-01-25 09:11 | 2026-01-25 17:19 | 8:08 | S/O | SAS witness | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-02 | 2026-01-18 08:44 | 2026-01-18 18:04 | 9:20 | S/O | for schedule maintenance | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-01 | 2026-01-24 08:58 | 2026-01-24 17:26 | 8:28 | S/O | for DS Removal and LA Modification work on the 33KV KBIL Phase-02 Feeder | 0 | 0 | No interruption
Madunaghat 132/33kV | TR-1(507T) | 2026-01-21 09:26 | 2026-01-21 18:46 | 9:20 | S/O | Annual Maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV | TR-2(517T) | 2026-01-22 09:21 | 2026-01-22 16:47 | 7:26 | S/O |  | 0 | 0 | No interruption
Mirsorai 230/33kV | Bus-1 | 2026-01-29 10:40 | 2026-02-02 13:42 | 99:02 | S/O | Bashundhara Bus Coupling | 0 | 0 | No interruption
Shikalbaha 230/132kV | ATR 02 | 2026-01-09 08:45 | 2026-01-09 17:03 | 8:18 | S/O | None | 0 | 0 | No interruption
Shikalbaha 230/132kV | ATR 01 | 2026-01-10 07:16 | 2026-01-10 16:17 | 9:01 | S/O | Annual Maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-02-16 23:35 |  |  |  | 560.0333
Cumilla Grid Circle :
Beanibazar 132/33kV | 132 KV Transformer TR-01 | 2026-01-01 08:07 | 2026-01-01 15:24 | 7:17 | S/O | Ten dalta test | 0 | 0 | No interruption
Beanibazar 132/33kV | 132 KV Transformer TR-01 | 2026-01-04 10:12 | 2026-01-04 16:58 | 6:46 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandpur 132/33kV | Bus A | 2026-01-11 08:28 | 2026-01-11 17:53 | 9:25 | S/O | Annual maintenance | 0 | 0 | No interruption
Chandpur 132/33kV | Bus-B | 2026-01-12 07:51 | 2026-01-12 14:45 | 6:54 | S/O | Annual maintenance | 0 | 0 | No interruption
Chandpur 132/33kV | 412T (T-2) | 2026-01-31 08:05 | 2026-01-31 12:58 | 4:53 | S/O | Maintenance (CPBS-2) | 8 | 39.0667 | Power interruption
Chandpur 132/33kV | 422T(T-5) | 2026-01-31 08:05 | 2026-01-31 12:58 | 4:53 | S/O | Maintenance (CPBS-2) | 16 | 78.1333 | Power interruption
Chauddagram 132/33kV | 132 kv T-1 | 2026-01-24 09:55 | 2026-01-24 14:58 | 5:03 | S/O | Maintanence work | 0 | 0 | No interruption
Chauddagram 132/33kV | 132 kv T-2 | 2026-01-26 10:12 | 2026-01-26 15:10 | 4:58 | S/O | Cleaning purpose. | 0 | 0 | No interruption
Chhatak 132/33kV | T-3 | 2026-01-06 09:24 | 2026-01-06 12:37 | 3:13 | S/O | H.Oil Leakage Repare of T-3 132 kv GCB | 0 | 0 | No interruption
Chhatak 132/33kV | T-1 | 2026-01-08 08:18 | 2026-01-09 15:28 | 31:10 | S/O | For Tan Delta Test | 0 | 0 | No interruption
Chhatak 132/33kV | T-2 | 2026-01-08 12:46 | 2026-01-08 16:28 | 3:42 | S/O | Tan Delta Test | 0 | 0 | No interruption
Chhatak 132/33kV | T-1 | 2026-01-17 20:17 | 2026-01-17 21:19 | 1:02 | S/O | Red Hot Maintenance. | 11 | 11.3667 | Power interruption
Chhatak 132/33kV | T-2 | 2026-01-26 09:03 | 2026-01-26 14:39 | 5:36 | S/O | 33 kv bus maintenance | 24 | 134.4 | Power interruption
Chhatak 132/33kV | T-3 | 2026-01-26 09:05 | 2026-01-26 14:37 | 5:32 | S/O | 33 kv bus maintenance | 0 | 0 | No interruption
Chhatak 132/33kV | T-1 | 2026-01-26 09:05 | 2026-01-26 14:34 | 5:29 | S/O | 33 kv bus maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV ATR-03 | 2026-01-03 09:39 | 2026-01-03 13:49 | 4:10 | S/O | Annual Maintenance works | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Transformer-1 | 2026-01-29 11:14 | 2026-01-29 15:34 | 4:20 | S/O | REB 33 kv Bus Maintenance Purpose | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | AT-02 | 2026-01-01 08:45 | 2026-01-01 13:35 | 4:50 | S/O | Annual maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | AT-02 | 2026-01-04 08:31 | 2026-01-04 14:03 | 5:32 | S/O | Annual maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | 230 KV Bus-1 | 2026-01-10 08:19 | 2026-01-10 17:15 | 8:56 | S/O | Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | 230 KV Bus-1 | 2026-01-11 08:05 | 2026-01-11 15:06 | 7:01 | S/O | Annual maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | 132 KV Bus-2 | 2026-01-12 08:38 | 2026-01-12 17:30 | 8:52 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | TR-02 | 2026-01-13 09:07 | 2026-01-13 20:28 | 11:21 | S/O | 132kv Bus-02 Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | 132 KV Bus-2 | 2026-01-13 09:19 | 2026-01-13 20:21 | 11:02 | S/O | Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | AT-02 | 2026-01-13 16:21 | 2026-01-13 17:41 | 1:20 | S/O | 132kv Bus-02 Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | 230 KV Bus-2 | 2026-01-14 09:36 | 2026-01-14 19:35 | 9:59 | S/O | For Annual Maintenance. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | AT-01 | 2026-01-14 19:10 | 2026-01-14 19:26 | 0:16 | S/O | 203-89B DS problem | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | TR-01 | 2026-01-19 08:10 | 2026-01-19 17:17 | 9:07 | S/O | 132 KV BUS -1 Shutdown | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | 132 KV Bus-1 | 2026-01-19 08:35 | 2026-01-19 17:09 | 8:34 | S/O | For Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | TR-01 | 2026-01-20 08:07 | 2026-01-20 17:39 | 9:32 | S/O | 132 KV BUS -1 Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | 132 KV Bus-1 | 2026-01-20 08:09 | 2026-01-20 17:26 | 9:17 | S/O | Annual maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | AT-02 | 2026-01-20 15:03 | 2026-01-20 16:24 | 1:21 | S/O | 132kV bus-02 Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | TR-02 | 2026-01-27 07:59 | 2026-01-27 17:16 | 9:17 | S/O | 132KV Bus-02 shutdown for annual maintenance. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | 132 KV Bus-2 | 2026-01-27 08:27 | 2026-01-27 17:08 | 8:41 | S/O | For annual maintenance. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | AT-01 | 2026-01-29 10:17 | 2026-01-29 18:54 | 8:37 | S/O | Ten Delta test | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | AT-02 | 2026-01-31 08:48 | 2026-01-31 19:32 | 10:44 | S/O | Tan delta test | 0 | 0 | No interruption
Feni 132/33kV | T-1(405T) | 2026-01-23 07:41 | 2026-01-23 09:28 | 1:47 | S/O | S/D taken for 33kV Bus-1, for 33kV Sultanpur Feeder Maintenance work by BPDB | 15 | 26.75 | Power interruption
Feni 230/132kV | ATR-1 | 2026-01-10 13:21 | 2026-01-10 15:09 | 1:48 | S/O | Due to oil leakage at 33 kv neutral bushing | 0 | 0 | No interruption
Feni 230/132kV | ATR-3 | 2026-01-10 15:49 | 2026-01-10 17:02 | 1:13 | S/O | Due to oil leakage at 33kv neutral bushing | 0 | 0 | No interruption
Kachua 230/132/33kV | Main Bus-2 (132 kV) | 2026-01-03 09:10 | 2026-01-03 14:03 | 4:53 | S/O | Annual maintenance | 0 | 0 | No interruption
Kachua 230/132/33kV | TR-1 | 2026-01-19 07:50 | 2026-01-19 10:58 | 3:08 | S/O | For flood light setting. | 0 | 0 | No interruption
Kasba 132/33kV | TR-2 | 2026-01-14 11:02 | 2026-01-14 18:37 | 7:35 | S/O | AVR changed by Project. | 0 | 0 | No interruption
Kasba 132/33kV | TR-1 | 2026-01-28 11:26 | 2026-01-28 19:21 | 7:55 | S/O |  | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 AB | 2026-01-03 10:17 | 2026-01-03 16:46 | 6:29 | S/O | PBS REB-1, REB-2 feeder & 33kv bus maintenance | 18 | 116.7 | Power interruption
Kulaura 132/33kV | TR-1 AB | 2026-01-10 22:46 | 2026-01-11 00:13 | 1:27 | S/O | 33kv CT redhot maintenance. | 0 | 0 | No interruption
Lakshmipur 132/33kV | Transformer-2 | 2026-01-24 10:58 | 2026-01-24 20:29 | 9:31 | S/O | Shutdown taken for change the 33kv circuit breaker. | 0 | 0 | No interruption
Maijdee 132/33kV | TR-01 | 2026-01-06 10:13 | 2026-01-06 15:03 | 4:50 | S/O | Line parameter test for project work. | 0 | 0 | No interruption
Maijdee 132/33kV | Tr-02 | 2026-01-06 10:14 | 2026-01-06 15:05 | 4:51 | S/O | Line parameter test for project work. | 0 | 0 | No interruption
Maijdee 132/33kV | TR-01 | 2026-01-12 17:01 | 2026-01-12 17:34 | 0:33 | S/O | Due to of 33KV Subornochor feeder 33KV BUS load side DS insulator emergency maintenance. | 11 | 6.05 | Power interruption
Muradnagar 132/33kV | 132KV Transformar-02 | 2026-01-08 10:21 | 2026-01-10 18:25 | 56:04 | S/O | For PBS Project works. | 0 | 0 | No interruption
Muradnagar 132/33kV | 132KV Transformar-01 | 2026-01-13 09:20 | 2026-01-14 11:16 | 25:56 | S/O | Shutdown for 33 kv switching station connection for pbs | 0 | 0 | No interruption
Muradnagar 132/33kV | 132KV Transformar-02 | 2026-01-15 09:53 | 2026-01-25 15:51 | 245:58 | S/O | PBS Project works. | 0 | 0 | No interruption
Muradnagar 132/33kV | 132KV Transformar-01 | 2026-01-25 16:04 | 2026-01-25 19:22 | 3:18 | S/O | PBS work | 0 | 0 | No interruption
Muradnagar 132/33kV | 132KV Transformar-02 | 2026-01-25 19:54 | 2026-01-25 21:17 | 1:23 | S/O | PBS Work | 0 | 0 | No interruption
Muradnagar 132/33kV | 132KV Transformar-01 | 2026-01-31 10:02 | 2026-01-31 16:06 | 6:04 | S/O | For CNEEC 33KV CB Change. | 0 | 0 | No interruption
Ramganj 132/33kV | Transformer -02 | 2026-01-12 10:42 | 2026-01-12 14:25 | 3:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
Ramganj 132/33kV | Transformer-01 | 2026-01-12 10:42 | 2026-01-12 13:26 | 2:44 | S/O | Annual Maintenace ( SPMD) | 0 | 0 | No interruption
Ramganj 132/33kV | Transformer -02 | 2026-01-12 13:29 | 2026-01-12 14:25 | 0:56 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sunamganj 132/33kV | Tr-1 | 2026-01-10 08:11 | 2026-01-10 12:15 | 4:04 | S/O | Tan Delta Test | 3 | 12.2 | Power interruption
Sylhet (South) | Trafo-2 | 2026-01-13 14:14 | 2026-01-13 14:55 | 0:41 | S/O | 132 kv Transformer -2 is taken shutdown by simense due to replacement of 132 kv transformer -1. | 10 | 6.8333 | Power interruption
Sylhet 132/33kV | T1 | 2026-01-06 09:20 | 2026-01-06 16:25 | 7:05 | S/O | Due to Ten delta Test | 0 | 0 | No interruption
Sylhet 132/33kV | T2 | 2026-01-07 09:15 | 2026-01-07 11:56 | 2:41 | S/O | Ten Delta Test Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV | T4 | 2026-01-07 11:58 | 2026-01-07 14:30 | 2:32 | S/O | Ten-delta test | 0 | 0 | No interruption
Sylhet 132/33kV | T1 | 2026-01-17 09:36 | 2026-01-17 11:48 | 2:12 | S/O | 33KV cable test | 0 | 0 | No interruption
|  |  | Total : | 1900-01-27 08:03 |  |  |  | 431.5
Khulna Grid Circle :
Bagerhat 132/33kV | Transformer-1 (403T) | 2026-01-03 09:02 | 2026-01-03 16:09 | 7:07 | S/O | Yearly Maintenance work. | 0 | 0 | No interruption
Bagerhat 132/33kV | Transformer-2 (413 T) | 2026-01-06 09:12 | 2026-01-06 16:27 | 7:15 | S/O | Yearly maintenance | 0 | 0 | No interruption
Bagerhat 132/33kV | Transformer-3 ( 423 T) | 2026-01-07 11:47 | 2026-01-07 13:56 | 2:09 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bagerhat 132/33kV | Transformer-3 ( 423 T) | 2026-01-10 08:32 | 2026-01-10 17:21 | 8:49 | S/O | TR-03 Shutdown for Annual Maintenance Work | 0 | 0 | No interruption
Bagerhat 132/33kV | 132 kV BUS | 2026-01-24 08:33 | 2026-01-24 14:35 | 6:02 | S/O | 132KV Bus Shutdown for annual maintenance | 53 | 319.7667 | Power interruption
Bakerganj 132/33kV | T1 | 2026-01-10 07:24 | 2026-01-10 17:54 | 10:30 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barishal 132/33kV | T-2 (415T) | 2026-01-13 07:37 | 2026-01-13 09:49 | 2:12 | S/O | To remove red hot problem at 33 kv bus section D/S. | 10 | 22 | Power interruption
Barishal 132/33kV | T-1 (405T) | 2026-01-17 07:32 | 2026-01-17 16:26 | 8:54 | S/O | Annual maintenance work | 10 | 89 | Power interruption
Barishal 132/33kV | T-2 (415T) | 2026-01-24 09:20 | 2026-01-24 14:20 | 5:00 | S/O | Wzpdcl annual maintenance work | 10 | 50 | Power interruption
Barishal 132/33kV | T-1 (405T) | 2026-01-24 14:34 | 2026-01-24 17:37 | 3:03 | S/O | Maintenance work by WZPDCL. | 24 | 73.2 | Power interruption
Barishal 230/132kV | T-5 | 2026-01-01 09:35 | 2026-01-01 10:58 | 1:23 | S/O | Bus section -C and Mehendigonj feeder source DS repair by BPBS-1 | 30 | 41.5 | Power interruption
Barishal 230/132kV | T-5 | 2026-01-30 07:28 | 2026-01-30 11:05 | 3:37 | S/O | 33kv busbar maintenance | 0 | 0 | No interruption
Barishal 230/132kV | T-4 | 2026-01-30 15:14 | 2026-01-30 17:18 | 2:04 | S/O | 33kv busbar and DS maintenance | 0 | 0 | No interruption
Barishal 230/132kV | ATR-1 | 2026-01-31 15:42 | 2026-01-31 16:39 | 0:57 | S/O | Annual Maintenance | 0 | 0 | No interruption
Benapole 132/33kV | Transformer-1(406T) | 2026-01-03 08:19 | 2026-01-03 14:45 | 6:26 | S/O | PBS Annual Maintenance | 0 | 0 | No interruption
Benapole 132/33kV | Transformer-2(416T) | 2026-01-03 08:19 | 2026-01-03 14:45 | 6:26 | S/O | PBS Annual Maintenance | 45 | 289.5 | Power interruption
Bhandaria 132/33kV | Transformer-2 | 2026-01-14 10:01 | 2026-01-14 12:44 | 2:43 | S/O | G2G work | 0 | 0 | No interruption
Bhandaria 132/33kV | Transformer-1 | 2026-01-17 07:19 | 2026-01-17 17:54 | 10:35 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhandaria 132/33kV | Transformer-2 | 2026-01-17 07:19 | 2026-01-17 17:56 | 10:37 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhandaria 132/33kV | Main Bus Bar | 2026-01-17 07:26 | 2026-01-17 17:53 | 10:27 | S/O | Annual maintenance | 28 | 292.6 | Power interruption
Faridpur 132/33kV | Transformer-1 | 2026-01-10 09:06 | 2026-01-10 12:16 | 3:10 | S/O | 33 kv bus maintenance | 30 | 95 | Power interruption
Faridpur 132/33kV | Transformer-3 | 2026-01-10 10:25 | 2026-01-10 11:46 | 1:21 | S/O | Maintenance | 5 | 6.75 | Power interruption
Faridpur 132/33kV | Transformer-2 | 2026-01-10 13:11 | 2026-01-10 16:50 | 3:39 | S/O | Maintanance | 40 | 146 | Power interruption
Faridpur 132/33kV | ATR-1 | 2026-01-15 09:18 | 2026-01-15 12:04 | 2:46 | S/O | Oil Leakage Maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV | T2 | 2026-01-11 08:51 | 2026-01-11 14:12 | 5:21 | S/O | 33 kv CT oil leakage maintenance. | 0 | 0 | No interruption
Gopalganj 400/132kV | ATR-03 | 2026-01-06 11:12 | 2026-01-06 15:32 | 4:20 | S/O | Fire Fitting testing & Commissioning. | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Bus-02 | 2026-01-11 09:18 | 2026-01-12 18:01 | 32:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | ATR-04 | 2026-01-12 13:41 | 2026-01-12 14:33 | 0:52 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulna (C) | Tr-2 415 T | 2026-01-01 06:33 | 2026-01-01 18:06 | 11:33 | S/O | Piling work | 0 | 0 | No interruption
Khulna (C) | Tr-2 415 T | 2026-01-02 07:13 | 2026-01-02 18:10 | 10:57 | S/O | G TO G project work piling. | 0 | 0 | No interruption
Khulna (C) | Tr-3 405T | 2026-01-04 08:47 | 2026-01-04 10:31 | 1:44 | S/O | Oil Leakage Maintenance. | 0 | 0 | No interruption
Khulna (C) | Tr-2 415 T | 2026-01-04 10:34 | 2026-01-04 12:56 | 2:22 | S/O | Oil Leakage Maintenance. | 0 | 0 | No interruption
Khulna (C) | Tr-3 405T | 2026-01-23 07:08 | 2026-01-23 17:44 | 10:36 | S/O | 33 KV BUS conductor change. | 0 | 0 | No interruption
Khulna (C) | Tr-2 415 T | 2026-01-27 07:04 | 2026-01-27 18:41 | 11:37 | S/O | Project work | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2026-01-30 06:57 | 2026-01-30 16:42 | 9:45 | S/O | Project work | 0 | 0 | No interruption
Khulna(S) 230/132kV | TR-2 | 2026-01-17 11:21 | 2026-01-25 15:43 | 196:22 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | TR-1 | 2026-01-26 09:25 | 2026-01-28 10:58 | 49:33 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mongla 132/33kV | T-1 | 2026-01-24 08:15 | 2026-01-24 14:46 | 6:31 | S/O | Annual maintenances work | 22 | 143.3667 | Power interruption
Mongla 132/33kV | T-2 | 2026-01-24 08:16 | 2026-01-24 14:46 | 6:30 | S/O | Annual maintenances work | 0 | 0 | No interruption
Mongla 132/33kV | Main Bus | 2026-01-24 08:25 | 2026-01-24 14:40 | 6:15 | S/O | Annual maintenances work | 0 | 0 | No interruption
Narail 132/33kV | TR1 (403-T) | 2026-01-16 08:07 | 2026-01-16 12:38 | 4:31 | S/O | 33kv whole bus shutdown for annual maintenance work and shutdown taken by jpbs -2 | 18 | 81.3 | Power interruption
Narail 132/33kV | TR2 (413-T) | 2026-01-16 08:11 | 2026-01-16 12:41 | 4:30 | S/O | 33kv whole bus shutdown for annual maintenance work and shutdown taken by jpbs -2 | 18 | 81 | Power interruption
Payra 400/132/33kV | 400/132/33 kV Auto Transformer-01 | 2026-01-07 09:52 | 2026-01-07 20:00 | 10:08 | S/O | Annual Maintenance | 0 | 0 | No interruption
Payra 400/132/33kV | 400/132/33 kV Auto Transformer-02 | 2026-01-08 08:08 | 2026-01-08 16:33 | 8:25 | S/O | Annual Maintenance | 0 | 0 | No interruption
Payra 400/132/33kV | 132/33 kV Transformer-03 | 2026-01-18 08:31 | 2026-01-18 17:01 | 8:30 | S/O | Maintenance | 0 | 0 | No interruption
Payra 400/132/33kV | 132/33 kV Transformer-03 | 2026-01-19 08:11 | 2026-01-19 17:10 | 8:59 | S/O | Maintenance | 0 | 0 | No interruption
Payra 400/132/33kV | 132/33 kV Transformer-04 | 2026-01-20 08:11 | 2026-01-20 17:45 | 9:34 | S/O | Maintenance | 0 | 0 | No interruption
Payra 400/132/33kV | 400/132/33 kV Auto Transformer-01 | 2026-01-22 08:46 | 2026-01-22 16:11 | 7:25 | S/O | Maintenance | 0 | 0 | No interruption
Payra 400/132/33kV | 400/132/33 kV Auto Transformer-01 | 2026-01-26 08:36 | 2026-01-26 16:42 | 8:06 | S/O | Annual Maintenance | 0 | 0 | No interruption
Payra 400/132/33kV | 400/132/33 kV Auto Transformer-02 | 2026-01-27 07:52 | 2026-01-27 16:32 | 8:40 | S/O | Annual Maintenance | 0 | 0 | No interruption
Payra 400/132/33kV | 400/132/33 kV Auto Transformer-02 | 2026-01-28 08:29 | 2026-01-28 15:50 | 7:21 | S/O | Annual Maintenance | 0 | 0 | No interruption
Satkhira 132/33kV | Transformer-1 (T-1) | 2026-01-04 09:04 | 2026-01-04 15:18 | 6:14 | S/O | Annual maintenance work | 5 | 31.1667 | Power interruption
Satkhira 132/33kV | Transformer-1 (T-1) | 2026-01-05 11:08 | 2026-01-05 14:20 | 3:12 | S/O | Due to annual maintenance work | 5 | 16 | Power interruption
Satkhira 132/33kV | Transformer-2 (T-2) | 2026-01-05 15:05 | 2026-01-05 16:39 | 1:34 | S/O | Annual maintenance work | 0 | 0 | No interruption
Satkhira 132/33kV | Transformer-2 (T-2) | 2026-01-07 09:26 | 2026-01-07 15:25 | 5:59 | S/O | Annual maintenance work | 0 | 0 | No interruption
Shariatpur 132/33kV | T1-406T | 2026-01-30 10:47 | 2026-01-30 12:16 | 1:29 | S/O | SAS Status Indication problem maintenance | 27 | 40.05 | Power interruption
|  |  | Total : | 1900-01-23 22:50 |  | Unserved Energy : |  | 1818.2
HVDC Grid Circle
Bhangura 132/33kV | Tr-1(403T) | 2026-01-10 09:09 | 2026-01-10 16:01 | 6:52 | S/O | Annual Maintenance 33kv side | 8 | 54.9333 | Power interruption
Bhangura 132/33kV | Tr-2(413T) | 2026-01-10 09:10 | 2026-01-10 16:03 | 6:53 | S/O | Annual Maintenance 33kv side | 8 | 55.0667 | Power interruption
Bheramara(GK) 132/33kV | TR-3 | 2026-01-25 10:06 | 2026-01-25 11:39 | 1:33 | S/O | 33kV Thakur Doulatpur Raiser Maintenance due to Occured fire | 0 | 0 | No interruption
BIPTC | 400kV Bus-2 | 2026-01-07 09:23 | 2026-01-07 16:23 | 7:00 | S/O | Annual Maintenance. | 0 | 0 | No interruption
BIPTC | 230kV Bus-2 | 2026-01-08 09:34 | 2026-01-08 18:17 | 8:43 | S/O | Annual Maintenance. | 0 | 0 | No interruption
BIPTC | 11T01 | 2026-01-09 08:07 | 2026-01-09 15:24 | 7:17 | S/O | Pole-01 is in shutdown for Annual maintenance | 0 | 0 | No interruption
Chuadanga 132/33kV | 132kV Tr. T1(416T) | 2026-01-11 09:28 | 2026-01-11 15:44 | 6:16 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Chuadanga 132/33kV | 132kV Tr. T2(426T) | 2026-01-12 09:35 | 2026-01-12 15:40 | 6:05 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Chuadanga 132/33kV | 132kV Tr. T3 | 2026-01-14 09:15 | 2026-01-14 16:11 | 6:56 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Chuadanga 132/33kV | 132kV Tr. T2(426T) | 2026-01-31 08:22 | 2026-01-31 11:22 | 3:00 | S/O | 33kV Bus Maintenance. | 32 | 96 | Power interruption
Chuadanga 132/33kV | 132kV Tr. T3 | 2026-01-31 08:23 | 2026-01-31 11:24 | 3:01 | S/O | 33kV Bus Maintenance. | 32 | 96.5333 | Power interruption
Ishurdi 132/33kV | 132 kV Bus-1 | 2026-01-14 09:20 | 2026-01-14 12:14 | 2:54 | S/O | 641 DS RED Hoot maintenance | 0 | 0 | No interruption
Ishurdi 132/33kV | 132/33 kV T-1 | 2026-01-20 10:56 | 2026-01-20 12:25 | 1:29 | S/O | 33 kv bus-2 A/M work at NESCO | 10 | 14.8333 | Power interruption
Ishurdi 132/33kV | 132/33 kV T-3 | 2026-01-23 08:17 | 2026-01-23 10:23 | 2:06 | S/O | Work by Dasuria PBS at 33 kv bus-1 | 20 | 42 | Power interruption
Ishurdi 230/132kV | 230/132 kV T-01 | 2026-01-02 15:45 | 2026-01-02 17:16 | 1:31 | S/O | HT side "B" phase PT voltage test | 0 | 0 | No interruption
Ishurdi 230/132kV | 230/132 kV T-01 | 2026-01-04 09:16 | 2026-01-04 16:04 | 6:48 | S/O | r phase red hot work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230/132 kV T-02 | 2026-01-07 09:17 | 2026-01-07 17:21 | 8:04 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-2 | 2026-01-06 09:19 | 2026-01-06 16:41 | 7:22 | S/O | Annual maintenance | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-3 | 2026-01-07 09:53 | 2026-01-07 15:03 | 5:10 | S/O | Annual maintenance | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-1 | 2026-01-08 08:39 | 2026-01-08 15:50 | 7:11 | S/O | Annual maintenance | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-2 | 2026-01-17 09:00 | 2026-01-17 15:13 | 6:13 | S/O | WZPDCL Jhenaidah Annual Maintenance. | 12 | 74.6 | Power interruption
Jhenaidah 230/132kV | Transformer- 1 | 2026-01-30 07:53 | 2026-01-30 11:43 | 3:50 | S/O | Annual Maintanance | 0 | 0 | No interruption
Kushtia 132/33kV | 132 KV Bus-B | 2026-01-14 12:58 | 2026-01-14 12:58 | 0:00 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Pabna 132/33kV | T-1 | 2026-01-10 08:31 | 2026-01-10 17:25 | 8:54 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Pabna 132/33kV | T-2 | 2026-01-13 08:42 | 2026-01-13 16:34 | 7:52 | S/O | Annual Maintenance | 0 | 0 | No interruption
Pabna 132/33kV | T-3 | 2026-01-17 08:55 | 2026-01-17 16:44 | 7:49 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Pabna 132/33kV | Main Bus | 2026-01-30 05:55 | 2026-01-30 13:23 | 7:28 | S/O | Annual Maintenance | 30 | 224 | Power interruption
Ruppur 132/11kV | TR-01 | 2026-01-03 09:06 | 2026-01-03 16:43 | 7:37 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Ruppur 132/11kV | TR-01 | 2026-01-04 10:02 | 2026-01-04 15:36 | 5:34 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Ruppur 132/11kV | TR-02 | 2026-01-05 09:06 | 2026-01-05 15:08 | 6:02 | S/O | Annual maintenance work | 0 | 0 | No interruption
Ruppur 132/11kV | 132kv BUS-1 | 2026-01-17 09:07 | 2026-01-17 13:43 | 4:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Ruppur 132/11kV | 132kv BUS-2 | 2026-01-18 09:09 | 2026-01-18 12:30 | 3:21 | S/O | annual maintenance work | 0 | 0 | No interruption
Shahjadpur 132/33kV | Main Bus | 2026-01-16 08:38 | 2026-01-16 16:25 | 7:47 | S/O | Annual Maintenance | 25 | 194.5833 | Power interruption
Ullahpara 132/33kV | Power Transformer -1 | 2026-01-20 11:28 | 2026-01-20 12:44 | 1:16 | S/O | Oil Change/filling of Incomer -1 PT. | 0 | 0 | No interruption
Ullahpara 132/33kV | Power Transformer-2 | 2026-01-20 12:59 | 2026-01-20 13:48 | 0:49 | S/O | Oil Change/filling of Incomer -2 PT. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-06 17:19 |  | Unserved Energy : |  | 852.55
Bogura Grid Circle:
Barapukuria 230/132/33kV | 132 KV Bus A | 2026-01-10 10:07 | 2026-01-10 14:29 | 4:22 | S/O | Rangpur Bay bus loop upgradetion | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 230/132KV T-06, 723T | 2026-01-15 09:21 | 2026-01-15 17:19 | 7:58 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 230/132KV T-06, 723T | 2026-01-17 09:36 | 2026-01-17 17:26 | 7:50 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Transformer-3 (424T) | 2026-01-05 10:06 | 2026-01-05 16:04 | 5:58 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Transformer-3 (424T) | 2026-01-17 14:21 | 2026-01-17 17:25 | 3:04 | S/O | Maintenance Work | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Transformer-2 (414T) | 2026-01-17 14:22 | 2026-01-17 17:16 | 2:54 | S/O | Maintenance Work | 15 | 43.5 | Power interruption
Bog-Sherpur 132/33kV | Transformer-1 (404T) | 2026-01-17 14:26 | 2026-01-17 17:13 | 2:47 | S/O | Maintenance Work | 15 | 41.75 | Power interruption
Bogura 132/33kV | Transformer-4 | 2026-01-03 08:57 | 2026-01-03 16:28 | 7:31 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-4 | 2026-01-04 09:08 | 2026-01-04 14:48 | 5:40 | S/O | annual maintenance work | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-3 | 2026-01-23 08:20 | 2026-01-23 10:20 | 2:00 | S/O | maintenance work | 5 | 10 | Power interruption
Bogura 230/132kV | T-04 | 2026-01-03 09:01 | 2026-01-03 13:40 | 4:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV | T-03 | 2026-01-11 09:34 | 2026-01-11 16:48 | 7:14 | S/O | Oil Refill | 0 | 0 | No interruption
Bogura 230/132kV | T-03 | 2026-01-22 11:02 | 2026-01-22 13:13 | 2:11 | S/O | Oil leakage Maintenance | 0 | 0 | No interruption
Bogura 400/230kV | ATR-02 | 2026-01-13 14:20 | 2026-01-13 17:09 | 2:49 | S/O | maintenance work | 0 | 0 | No interruption
Bogura 400/230kV | ATR-02 | 2026-01-14 10:15 | 2026-01-14 16:52 | 6:37 | S/O | ATR-02 oil leakage maintenance.. | 0 | 0 | No interruption
Bogura 400/230kV | ATR-01 | 2026-01-15 09:35 | 2026-01-15 12:36 | 3:01 | S/O | Maintenance work | 0 | 0 | No interruption
Bogura 400/230kV | ATR-03 | 2026-01-15 13:13 | 2026-01-15 16:30 | 3:17 | S/O | Maintenance work | 0 | 0 | No interruption
Chapai 132/33kV | T-2 (415T) | 2026-01-01 09:40 | 2026-01-01 18:11 | 8:31 | S/O | T-02 CB change S/D exact time 28/12/2025 at 9:40 | 0 | 0 | No interruption
Chapai 132/33kV | T-3 (425T) | 2026-01-24 09:57 | 2026-02-01 18:30 | 200:33 | S/O | T3 -132 kv CB change | 0 | 0 | No interruption
Jaldhaka 132/33kV | 406T-1 | 2026-01-15 08:16 | 2026-01-15 11:17 | 3:01 | S/O | 132/33kV Tr-1 Shutdown due to new 33kV Feeder(Nilphamari PBS) connection on 33kV Bus section-1. | 15 | 45.25 | Power interruption
Jaldhaka 132/33kV | 406T-1 | 2026-01-17 08:16 | 2026-01-17 12:11 | 3:55 | S/O | New 33kV Feeder(Nilphamari PBS) connection on 33kV Bus section-1 | 15 | 58.75 | Power interruption
Jaldhaka 132/33kV | 416T-2 | 2026-01-24 09:28 | 2026-01-24 13:58 | 4:30 | S/O | annual maintenance of 33 KV Bus section -02 & Bus section -03 related 33 KV Feeder of NESCO & PBS | 20 | 90 | Power interruption
Joypurhat 132/33kV | Transformer T-1 (407 T) | 2026-01-21 10:13 | 2026-01-21 11:27 | 1:14 | S/O | 33kv Bushing Connector Change perpose. | 0 | 0 | No interruption
Mahasthangarh 132/33kV | 33KV Main bus T-1 | 2026-01-17 08:18 | 2026-01-17 13:05 | 4:47 | S/O | 33kv bus annual maintenance work of PBS. | 14 | 66.9667 | Power interruption
Mahasthangarh 132/33kV | 406T MTR1 | 2026-01-17 08:18 | 2026-01-17 15:45 | 7:27 | S/O | 33kv bus annual maintenance work of PBS. | 0 | 0 | Power interruption
Mahasthangarh 132/33kV | 33KV Main bus T-2 | 2026-01-17 08:20 | 2026-01-17 13:05 | 4:45 | S/O | 33kv bus annual maintenance work of PBS. | 0 | 0 | Power interruption
Mahasthangarh 132/33kV | 416T MTR 2 | 2026-01-17 08:21 | 2026-01-17 13:04 | 4:43 | S/O | 33kv bus annual maintenance work of PBS. | 0 | 0 | Power interruption
Mahasthangarh 132/33kV | 416T MTR 2 | 2026-01-17 15:47 | 2026-01-17 17:48 | 2:01 | S/O | Maintenance work done | 0 | 0 | No interruption
Naogaon 132/33kV | Main Bus | 2026-01-10 06:49 | 2026-01-10 09:12 | 2:23 | S/O | Project work | 65 | 154.9167 | Power interruption
Naogaon 132/33kV | 132kV GIS Bus B | 2026-01-29 13:17 | 2026-01-29 20:44 | 7:27 | S/O | GIS main Bus Inter lock checking. | 0 | 0 | No interruption
Naogaon 132/33kV | 132kV GIS Bus A | 2026-01-29 13:17 | 2026-01-29 20:43 | 7:26 | S/O | GIS main Bus Inter lock checking. | 0 | 0 | No interruption
Naogaon 132/33kV | 132kV GIS Bus C | 2026-01-29 13:17 | 2026-01-29 20:39 | 7:22 | S/O | GIS main Bus Inter lock checking. | 0 | 0 | No interruption
Panchagarh 132/33kV | T-1(407T) | 2026-01-21 10:13 | 2026-01-21 14:20 | 4:07 | S/O | Maintenance work(Oil Leakage of Buchholz Relay) of Transformer -01 | 0 | 0 | No interruption
Purbasadipur 132/33kV | T-1 Transformer (403T) | 2026-01-15 11:22 | 2026-01-15 16:35 | 5:13 | S/O | for new LA installing at T-1. Load served by T-4 | 0 | 0 | No interruption
Purbasadipur 132/33kV | T-3 Transformer (423T) | 2026-01-17 09:57 | 2026-01-28 17:22 | 271:25 | S/O | T3 connection work with GIS | 0 | 0 | No interruption
Purbasadipur 132/33kV | T-3 Transformer (423T) | 2026-01-31 07:55 | 2026-01-31 15:38 | 7:43 | S/O | maintenance work | 0 | 0 | No interruption
Purbasadipur 132/33kV | T-4 Transformer | 2026-01-31 16:30 | 2026-01-31 16:53 | 0:23 | S/O | maintenance work | 0 | 0 | No interruption
Rahanpur 400/132kV | AT-01 | 2026-01-02 10:40 | 2026-01-02 12:16 | 1:36 | S/O | Maintenance work | 0 | 0 | No interruption
Rahanpur 400/132kV | AT-02 | 2026-01-02 13:04 | 2026-01-02 15:00 | 1:56 | S/O | Maintenance work | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-1(405T) | 2026-01-10 07:48 | 2026-01-10 13:17 | 5:29 | S/O | Development Work | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-2(415T) | 2026-01-10 07:48 | 2026-01-10 13:34 | 5:46 | S/O | Development Work | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-3 (425T) | 2026-01-10 07:48 | 2026-01-10 13:35 | 5:47 | S/O | Development Work | 0 | 0 | No interruption
Rajshahi 132/33kV | Transfer Bus | 2026-01-10 07:56 | 2026-01-10 07:56 | 0:00 | S/O | Development Work | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-3 (425T) | 2026-01-19 08:20 | 2026-01-22 19:14 | 82:54 | S/O | Development Work | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-2(415T) | 2026-01-23 09:10 | 2026-01-28 16:54 | 127:44 | S/O | Project work | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-1(405T) | 2026-01-29 09:21 | 2026-02-01 16:50 | 79:29 | S/O | maintenance work | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-3 (425T) | 2026-01-31 08:55 | 2026-01-31 12:01 | 3:06 | S/O | None | 0 | 0 | No interruption
Rangpur 132/33kV | 132KV Bus B | 2026-01-08 09:20 | 2026-01-08 14:19 | 4:59 | S/O | Re-conducting work | 0 | 0 | No interruption
Saidpur 132/33kV | TR-2 (404T) | 2026-01-29 08:22 | 2026-01-29 14:10 | 5:48 | S/O | OLTC Oil refilling work | 0 | 0 | No interruption
Saidpur 132/33kV | TR-3 (424T) | 2026-01-29 14:18 | 2026-01-29 19:20 | 5:02 | S/O | maintenance work | 0 | 0 | No interruption
Sirajganj 132/33kV | T3-(435) | 2026-01-29 08:37 | 2026-01-29 13:27 | 4:50 | S/O | 33kV Kazipur Feeder CT shifting from the gantree structure to the new CT structure by Sirajgonj PBS-2. | 0 | 0 | No interruption
Sirajganj 132/33kV | T4-(445) | 2026-01-31 08:45 | 2026-01-31 16:53 | 8:08 | S/O | 33 kv Bay extension work | 14 | 113.8667 | Power interruption
Thakurgaon 132/33kV | T-1(422T) | 2026-01-08 10:10 | 2026-01-08 15:52 | 5:42 | S/O | Oil leakage at Bukholz | 0 | 0 | No interruption
Thakurgaon 132/33kV | T-2(412T) | 2026-01-17 08:50 | 2026-01-17 11:22 | 2:32 | S/O | 33 kV Feeder Riser Maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-02-09 05:36 |  | Unserved Energy : |  | 625
Others :Nil
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 5792:06 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:January 2026
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV | Aminbazar Ckt-2 | 2026-01-04 09:46 | 2026-01-04 14:23 | 4:37 | S/O | Relay testing | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-1 | 2026-01-04 14:40 | 2026-01-04 16:17 | 1:37 | S/O | Relay testing | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-1 | 2026-01-06 08:56 | 2026-01-06 17:56 | 9:00 | S/O | Annual Maintenance ( Deep Cleaning of Insulator) | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-1 | 2026-01-07 08:29 | 2026-01-07 17:15 | 8:46 | S/O | Annual Maintenance ( Deep Cleaning of Insulator Disc) | 0 | 0 | No interruption
Agargaon 230/132kV | Cantonment Ckt-2 | 2026-01-07 14:39 | 2026-01-07 14:55 | 0:16 | S/O | Relay Testing | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-1 | 2026-01-12 08:27 | 2026-01-12 17:59 | 9:32 | S/O | Annual maintenance | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-1 | 2026-01-13 07:32 | 2026-01-13 15:55 | 8:23 | S/O | Disc replacement | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-2 | 2026-01-14 08:55 | 2026-01-14 18:38 | 9:43 | S/O | Annual maintenance work | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-2 | 2026-01-27 08:31 | 2026-01-27 17:53 | 9:22 | S/O | Annual Maintenance. (Deep Cleaning) | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-1 | 2026-01-30 08:19 | 2026-01-30 18:40 | 10:21 | S/O | Annual Maintenance | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-1 | 2026-01-31 08:22 | 2026-01-31 21:57 | 13:35 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Meghnaghat-01 | 2026-01-01 07:17 | 2026-01-01 07:26 | 0:09 | S/O | Bay Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Keranigonj-02 | 2026-01-01 08:55 | 2026-01-01 15:01 | 6:06 | S/O | Deadline Checking and Disc Cleaning | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Gopalganj-1 | 2026-01-03 09:22 | 2026-01-03 17:09 | 7:47 | S/O | Scheduled shutdown | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Gopalganj-1 | 2026-01-04 07:43 | 2026-01-04 17:16 | 9:33 | S/O | Schedule shutdown | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Gopalganj-1 | 2026-01-05 08:51 | 2026-01-05 16:37 | 7:46 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Gopalganj-2 | 2026-01-06 08:29 | 2026-01-06 15:50 | 7:21 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kaliakoir-01 | 2026-01-07 08:28 | 2026-01-08 18:21 | 33:53 | S/O | CT Changing Works | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Gopalganj-2 | 2026-01-07 09:15 | 2026-01-07 16:09 | 6:54 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Gopalganj-2 | 2026-01-08 08:31 | 2026-01-08 17:34 | 9:03 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kaliakoir-02 | 2026-01-09 08:44 | 2026-01-10 17:53 | 33:09 | S/O | C.T. Replace work | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kaliakoir-01 | 2026-01-11 10:16 | 2026-01-13 09:19 | 47:03 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Keranigonj-01 | 2026-01-11 12:54 | 2026-01-12 17:13 | 28:19 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Keranigonj-02 | 2026-01-12 07:34 | 2026-01-12 10:27 | 2:53 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Gopalganj-1 | 2026-01-16 08:44 | 2026-01-16 21:15 | 12:31 | S/O | Deadline checking | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Keranigonj-02 | 2026-01-17 08:54 | 2026-01-17 20:52 | 11:58 | S/O | Schedule shutdown | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Manikgonj Power Plant-02 | 2026-01-26 10:15 | 2026-01-26 16:04 | 5:49 | S/O | Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Meghnaghat-02 | 2026-01-28 09:01 | 2026-01-28 17:40 | 8:39 | S/O | Disc cleaning | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kaliakoir-02 | 2026-01-29 09:11 | 2026-01-29 16:06 | 6:55 | S/O | Disc Cleaning | 0 | 0 | No interruption
Bhaluka 132/33kV | Sreepur Ckt- 01 | 2026-01-01 09:34 | 2026-01-01 12:38 | 3:04 | S/O | Shutdown taken by Shripur grid | 30 | 92 | Power interruption
Bhaluka 132/33kV | Mymensingh Ckt- 01 | 2026-01-04 09:22 | 2026-01-04 17:12 | 7:50 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Bhaluka 132/33kV | Sreepur Ckt- 01 | 2026-01-04 10:47 | 2026-01-04 16:04 | 5:17 | S/O | Annual maintenance | 15 | 79.25 | Power interruption
Bhaluka 132/33kV | Mymensingh Ckt- 01 | 2026-01-05 10:05 | 2026-01-05 17:40 | 7:35 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV | Sreepur Ckt- 01 | 2026-01-05 10:21 | 2026-01-05 20:07 | 9:46 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 01 | 2026-01-06 09:08 | 2026-01-06 17:40 | 8:32 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 02 | 2026-01-06 09:09 | 2026-01-06 17:45 | 8:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV | Sreepur Ckt- 02 | 2026-01-07 10:49 | 2026-01-07 17:05 | 6:16 | S/O | Annual maintenance | 30 | 188 | Power interruption
Bhaluka 132/33kV | Sreepur Ckt- 02 | 2026-01-08 10:30 | 2026-01-08 16:06 | 5:36 | S/O | Dead line check at sripur end. | 30 | 168 | Power interruption
Bhaluka 132/33kV | Sreepur Ckt- 01 | 2026-01-10 09:55 | 2026-01-10 18:08 | 8:13 | S/O | S/D taken by Shripur grid for annual maintenance purpose. | 0 | 0 | No interruption
Bhaluka 132/33kV | Sreepur Ckt- 01 | 2026-01-15 08:22 | 2026-01-15 15:43 | 7:21 | S/O | Annual maintenance work purpose. | 34 | 249.9 | Power interruption
Bhaluka 132/33kV | Mymensingh Ckt- 01 | 2026-01-15 12:13 | 2026-01-15 13:57 | 1:44 | S/O | Annual maintenance | 20 | 34.6667 | Power interruption
Bhaluka 132/33kV | BR Powergen Ckt- 01 | 2026-01-21 10:11 | 2026-01-21 17:16 | 7:05 | S/O | Work at BRPL end. | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 02 | 2026-01-21 10:12 | 2026-01-21 17:16 | 7:04 | S/O | Work at BRPL end. | 0 | 0 | No interruption
Bhaluka 132/33kV | Sreepur Ckt- 02 | 2026-01-25 11:14 | 2026-01-25 13:42 | 2:28 | S/O | Annual maintenance work. | 45 | 111 | Power interruption
Dhamrai 132/33kV | 132 KV Kaliakoir-Dhamrai CKT-01 | 2026-01-03 09:42 | 2026-01-03 17:18 | 7:36 | S/O | Annual maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV | 132 KV Kaliakoir-Dhamrai CKT-01 | 2026-01-04 09:35 | 2026-01-04 16:30 | 6:55 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV | 132 KV Kaliakoir-Dhamrai CKT-01 | 2026-01-05 08:22 | 2026-01-05 17:16 | 8:54 | S/O | Annual maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV | 132 KV Kaliakoir-Dhamrai CKT-01 | 2026-01-06 09:30 | 2026-01-06 16:03 | 6:33 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV | 132 KV Kaliakoir-Dhamrai CKT-02 | 2026-01-10 08:30 | 2026-01-10 16:52 | 8:22 | S/O | Due to annual maintenance. | 0 | 0 | No interruption
Dhamrai 132/33kV | 132 KV Kaliakoir-Dhamrai CKT-02 | 2026-01-11 08:50 | 2026-01-11 17:36 | 8:46 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV | 132 KV Kaliakoir-Dhamrai CKT-02 | 2026-01-12 08:22 | 2026-01-12 16:31 | 8:09 | S/O | Due to annual maintenance. | 0 | 0 | No interruption
Dhamrai 132/33kV | 132 KV Kaliakoir-Dhamrai CKT-02 | 2026-01-13 09:07 | 2026-01-13 15:51 | 6:44 | S/O | Annual maintenance | 0 | 0 | No interruption
Ghatail 132/33kV | Muktagacha-1 | 2026-01-06 09:44 | 2026-01-06 17:05 | 7:21 | S/O | dead line checking | 0 | 0 | No interruption
Ghatail 132/33kV | Muktagacha-2 | 2026-01-07 10:03 | 2026-01-07 16:49 | 6:46 | S/O | dead line checking | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-02 | 2026-01-03 08:47 | 2026-01-03 16:43 | 7:56 | S/O | 132kv bus Maintenance work purpose of Mymensingh grid substation. | 0 | 0 | No interruption
Jamalpur 132/33kV | 132KV UMPL Ckt-02 | 2026-01-07 08:22 | 2026-01-07 16:57 | 8:35 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jamalpur 132/33kV | 132KV UMPL Ckt-02 | 2026-01-08 08:59 | 2026-01-08 17:02 | 8:03 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-02 | 2026-01-08 13:12 | 2026-01-08 16:01 | 2:49 | S/O | Annual maintenance. | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-02 | 2026-01-10 07:45 | 2026-01-10 21:01 | 13:16 | S/O | G2G project work mym Grid side | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-02 | 2026-01-16 11:12 | 2026-01-16 15:23 | 4:11 | S/O | Project work at Mymensingh | 0 | 0 | No interruption
Jamalpur 132/33kV | 132KV UMPL Ckt-02 | 2026-01-31 10:40 | 2026-01-31 13:29 | 2:49 | S/O | OPGW Preform work(Tower no 06). | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-2 | 2026-01-01 08:36 | 2026-01-01 18:33 | 9:57 | S/O | OPGW Stringing work. | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-2 | 2026-01-02 07:23 | 2026-01-02 18:37 | 11:14 | S/O | OPGW wire stringing. | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-2 | 2026-01-03 07:28 | 2026-01-03 18:52 | 11:24 | S/O | OPGW wire stringing by OFCN. | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-2 | 2026-01-04 07:43 | 2026-01-04 18:54 | 11:11 | S/O | 0 | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-2 | 2026-01-05 07:11 | 2026-01-05 18:39 | 11:28 | S/O | OPGW Wire stringing | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-2 | 2026-01-06 07:33 | 2026-01-06 18:10 | 10:37 | S/O | OPGW wire stringing work by OFCN. | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-1 | 2026-01-16 06:04 | 2026-01-16 14:29 | 8:25 | S/O | Removal of PG clamp connection (Project work) | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-2 | 2026-01-16 06:04 | 2026-01-16 14:30 | 8:26 | S/O | Removal of PG clamp connection (Project work) | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-1 | 2026-01-16 14:36 | 2026-01-16 15:10 | 0:34 | S/O | NLDC | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-2 | 2026-01-16 14:36 | 2026-01-16 15:10 | 0:34 | S/O | NLDC | 0 | 0 | No interruption
Kabirpur 132/33kV | Kadda-1 | 2026-01-08 09:31 | 2026-01-08 16:53 | 7:22 | S/O | Annual maintenance | 0 | 0 | No interruption
Kabirpur 132/33kV | Kadda-2 | 2026-01-18 09:36 | 2026-01-18 15:56 | 6:20 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Kabirpur 132/33kV | Kadda-1 | 2026-01-19 09:30 | 2026-01-19 16:49 | 7:19 | S/O | Annual maintenance (deadline checking) | 0 | 0 | No interruption
Kabirpur 132/33kV | Kadda-2 | 2026-01-20 09:53 | 2026-01-20 16:35 | 6:42 | S/O | Annual Main | 0 | 0 | No interruption
Kabirpur 132/33kV | Tongi-1 | 2026-01-24 10:20 | 2026-01-24 18:38 | 8:18 | S/O | Annual Maintenance (Deadline Checking) | 0 | 0 | No interruption
Kabirpur 132/33kV | Tongi-1 | 2026-01-25 09:02 | 2026-01-25 18:36 | 9:34 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Kabirpur 132/33kV | Tongi-1 | 2026-01-27 09:29 | 2026-01-27 17:25 | 7:56 | S/O | Due to Disc change | 0 | 0 | No interruption
Kabirpur 132/33kV | Tongi-2 | 2026-01-29 09:14 | 2026-01-29 16:04 | 6:50 | S/O | Annual maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Bibiyana1 | 2026-01-01 10:22 | 2026-01-01 17:23 | 7:01 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Aminbazar -1 | 2026-01-06 08:42 | 2026-01-06 17:31 | 8:49 | S/O | Deadline checking . | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Dhamrai-1 | 2026-01-06 09:31 | 2026-01-06 16:00 | 6:29 | S/O | Deadline checking by Dhamrai End. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Aminbazar -1 | 2026-01-07 08:44 | 2026-01-08 18:21 | 33:37 | S/O | NLDC. Works for Aminbazar end. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Bibiyana1 | 2026-01-07 11:29 | 2026-01-07 17:31 | 6:02 | S/O | Dead Line checking. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Bibiyana1 | 2026-01-08 08:30 | 2026-01-08 17:03 | 8:33 | S/O | Annual maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Dhamrai-2 | 2026-01-11 08:52 | 2026-01-11 17:35 | 8:43 | S/O | NLDC. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Tongi-2 | 2026-01-11 10:44 | 2026-01-11 17:21 | 6:37 | S/O | NLDC | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Bibiyana1 | 2026-01-12 08:20 | 2026-01-12 17:01 | 8:41 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Bibiyana 2 | 2026-01-13 09:25 | 2026-01-15 17:09 | 55:44 | S/O | Disc Cleaning | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Tongi-2 | 2026-01-14 09:38 | 2026-01-15 18:12 | 32:34 | S/O | NLDC. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Summit/Kodda PS | 2026-01-17 09:26 | 2026-01-17 17:15 | 7:49 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Aminbazar -2 | 2026-01-17 10:22 | 2026-01-17 17:15 | 6:53 | S/O | Annual Maitenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Aminbazar -2 | 2026-01-18 09:22 | 2026-01-18 16:47 | 7:25 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Summit/Kodda PS | 2026-01-18 09:53 | 2026-01-18 16:44 | 6:51 | S/O | Annual Maintenance Deadline Checking & Disk Cleaning | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Tongi-2 | 2026-01-19 08:22 | 2026-01-19 16:41 | 8:19 | S/O | Annual Maintenance Disk Cleaning work | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Aminbazar -1 | 2026-01-19 08:35 | 2026-01-19 16:06 | 7:31 | S/O | Annual Maintenance Disk Cleaning work | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Aminbazar -2 | 2026-01-20 10:14 | 2026-01-20 18:08 | 7:54 | S/O | Deadline Check. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Bibiyana 2 | 2026-01-21 08:35 | 2026-01-21 17:43 | 9:08 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Bibiyana1 | 2026-01-22 08:53 | 2026-01-22 17:45 | 8:52 | S/O | Deadline check | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Kabirpur-1 | 2026-01-25 12:54 | 2026-01-25 18:30 | 5:36 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Kabirpur-2 | 2026-01-26 14:44 | 2026-01-26 16:34 | 1:50 | S/O | annual maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Dhamrai-1 | 2026-01-27 09:24 | 2026-01-27 11:44 | 2:20 | S/O | Annual maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Dhamrai-2 | 2026-01-27 11:49 | 2026-01-27 13:02 | 1:13 | S/O | Annual maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Kabirpur-1 | 2026-01-28 11:01 | 2026-01-28 13:47 | 2:46 | S/O | ‍Annual Maintenance. | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Lalbag Ckt-02 | 2026-01-03 08:40 | 2026-01-03 16:58 | 8:18 | S/O | Deadline Check | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Lalbag Ckt-02 | 2026-01-04 09:26 | 2026-01-04 16:45 | 7:19 | S/O | dead line check | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Lalbag Ckt-02 | 2026-01-05 09:01 | 2026-01-05 16:50 | 7:49 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2026-01-10 09:07 | 2026-01-10 19:04 | 9:57 | S/O | Dead line checking work. | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2026-01-11 09:01 | 2026-01-11 16:50 | 7:49 | S/O | 0 | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Aminbazar Ckt-02 | 2026-01-15 08:49 | 2026-01-15 16:45 | 7:56 | S/O | annual maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Aminbazar Ckt-02 | 2026-01-17 08:48 | 2026-01-17 16:51 | 8:03 | S/O | 0 | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2026-01-26 09:20 | 2026-01-26 16:53 | 7:33 | S/O | Tan Delta Test. | 0 | 0 | No interruption
Kodda 132/33kV | Summit 149 MW PS | 2026-01-03 10:47 | 2026-01-03 16:20 | 5:33 | S/O | Dead line check | 0 | 0 | No interruption
Kodda 132/33kV | Rajendrapur Ckt-1 | 2026-01-04 09:52 | 2026-01-04 18:34 | 8:42 | S/O | 0 | 0 | 0 | No interruption
Kodda 132/33kV | Rajendrapur Ckt-1 | 2026-01-12 09:31 | 2026-01-12 17:27 | 7:56 | S/O | Dead line checking | 0 | 0 | No interruption
Kodda 132/33kV | RPCL 100 MW PS | 2026-01-13 10:14 | 2026-01-13 13:55 | 3:41 | S/O | Maintenance Work | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Old | 2026-01-16 08:52 | 2026-01-24 15:15 | 198:23 | S/O | Upgradation work by G2G. Shifting to New Control room. | 0 | 0 | No interruption
Mirpur 132/33kV | Aminbazar-2 | 2026-01-16 09:07 | 2026-01-24 15:35 | 198:28 | S/O | Upgradation work by G2G. Shifting to New Control room. | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Old | 2026-01-24 16:33 | 2026-01-24 17:34 | 1:01 | S/O | CT Connection Check | 0 | 0 | No interruption
Mirpur 132/33kV | RPC Unit-3 | 2026-01-25 10:10 | 2026-02-01 17:01 | 174:51 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Sector-18 | 2026-01-26 09:30 | 2026-01-26 15:15 | 5:45 | S/O | Annual maintenance work on bay equipment. | 0 | 0 | No interruption
Mirpur 132/33kV | Aminbazar-1 | 2026-01-27 13:06 | 2026-02-02 17:16 | 148:10 | S/O | 0 | 0 | 0 | No interruption
Mirzapur 132/33kV | Mirzapur-Tangail-ckt-2A(E04) | 2026-01-03 08:38 | 2026-01-03 14:39 | 6:01 | S/O | Existing LILO lINEMirzapur grid Re-conducting | 0 | 0 | No interruption
Mirzapur 132/33kV | Mirzapur-Tangail-ckt-2B(E03) | 2026-01-03 08:38 | 2026-01-03 14:39 | 6:01 | S/O | Existing LILO lINEMirzapur grid Re-conducting | 25 | 150.4167 | Power interruption
Mirzapur 132/33kV | Mirzapur-Kaliakair-ckt-2A(E08) | 2026-01-03 08:39 | 2026-01-03 15:38 | 6:59 | S/O | Existing LILO lINEMirzapur grid Re-conducting | 0 | 0 | No interruption
Mirzapur 132/33kV | Mirzapur-Kaliakoir ckt-2B(E-09) | 2026-01-03 08:39 | 2026-01-03 15:38 | 6:59 | S/O | Existing LILO lINEMirzapur grid Re-conducting | 25 | 174.5833 | Power interruption
Mirzapur 132/33kV | Mirzapur-Tangail-ckt-2B(E03) | 2026-01-13 09:33 | 2026-01-13 16:16 | 6:43 | S/O | By NLDC | 0 | 0 | No interruption
Mirzapur 132/33kV | Mirzapur-Tangail-ckt-2A(E04) | 2026-01-13 09:33 | 2026-01-13 16:16 | 6:43 | S/O | By NLDC | 0 | 0 | No interruption
Mirzapur 132/33kV | Mirzapur-Tangail-ckt-2A(E04) | 2026-01-14 09:43 | 2026-01-14 14:51 | 5:08 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mirzapur 132/33kV | Mirzapur-Tangail-ckt-2B(E03) | 2026-01-14 09:43 | 2026-01-14 14:52 | 5:09 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mirzapur 132/33kV | Mirzapur-Kaliakoir ckt-2B(E-09) | 2026-01-16 09:40 | 2026-01-16 09:40 | 0:00 | S/O | Exitting LILO Line Mirzapur Grid | 0 | 0 | No interruption
Mirzapur 132/33kV | Mirzapur-Kaliakair-ckt-2A(E08) | 2026-01-16 09:40 | 2026-01-16 09:40 | 0:00 | S/O | Exitting LILO Line Mirzapur Grid | 0 | 0 | No interruption
Mirzapur 132/33kV | Mirzapur-Tangail-ckt-2A(E04) | 2026-01-16 10:00 | 2026-01-16 10:00 | 0:00 | S/O | Exitting LILO Line Mirzapur Grid | 0 | 0 | No interruption
Mirzapur 132/33kV | Mirzapur-Tangail-ckt-2B(E03) | 2026-01-16 10:00 | 2026-01-16 16:07 | 6:07 | S/O | Exitting LILO Line Mirzapur Grid | 0 | 0 | No interruption
Mirzapur 132/33kV | Mirzapur-Tangail-ckt-2B(E03) | 2026-01-17 09:36 | 2026-01-17 12:44 | 3:08 | S/O | Tangail Grid Maintenance work | 0 | 0 | No interruption
Muktagacha 132/33kV | Ghatail-1 | 2026-01-06 09:46 | 2026-01-06 17:06 | 7:20 | S/O | S/D by Ghatail S/S | 0 | 0 | No interruption
Muktagacha 132/33kV | Ghatail-2 | 2026-01-07 10:04 | 2026-01-07 16:50 | 6:46 | S/O | Annual maintenance. | 0 | 0 | No interruption
Muktagacha 132/33kV | RPCL-1 | 2026-01-20 09:03 | 2026-01-20 16:35 | 7:32 | S/O | Annual maintenance. | 0 | 0 | No interruption
Muktagacha 132/33kV | RPCL-1 | 2026-01-21 09:15 | 2026-01-21 16:41 | 7:26 | S/O | Piling work of RHD | 0 | 0 | No interruption
Muktagacha 132/33kV | RPCL-1 | 2026-01-22 09:37 | 2026-01-22 16:18 | 6:41 | S/O | Annual maintenance. | 0 | 0 | No interruption
Muktagacha 132/33kV | RPCL-1 | 2026-01-24 09:12 | 2026-01-24 17:03 | 7:51 | S/O | Piling Work of RHD | 0 | 0 | No interruption
Muktagacha 132/33kV | RPCL-1 | 2026-01-25 09:15 | 2026-01-25 15:47 | 6:32 | S/O | Annual maintenance. | 0 | 0 | No interruption
Muktagacha 132/33kV | RPCL-1 | 2026-01-26 09:17 | 2026-01-26 15:16 | 5:59 | S/O | Work by RHD | 0 | 0 | No interruption
Mymensingh 132/33kV | 50 MW Solar Plant | 2026-01-02 07:12 | 2026-01-02 12:48 | 5:36 | S/O | Project work. | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Jamalpur Ckt-2 | 2026-01-03 08:49 | 2026-01-03 16:38 | 7:49 | S/O | Project work. | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Bhaluka Ckt-1 | 2026-01-05 10:04 | 2026-01-05 17:39 | 7:35 | S/O | Dead line checking by Bhaluka Grid. | 0 | 0 | No interruption
Mymensingh 132/33kV | 50 MW Solar Plant | 2026-01-09 08:26 | 2026-01-09 10:50 | 2:24 | S/O | Annual maintenance. | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Jamalpur Ckt-2 | 2026-01-10 07:45 | 2026-01-10 20:58 | 13:13 | S/O | Annual maintenance. | 0 | 0 | No interruption
Mymensingh 132/33kV | 50 MW Solar Plant | 2026-01-16 08:38 | 2026-01-16 11:08 | 2:30 | S/O | Annual maintenance. | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Jamalpur Ckt-2 | 2026-01-16 11:13 | 2026-01-16 15:20 | 4:07 | S/O | Annual maintenance. | 0 | 0 | No interruption
Rajendrapur 132/33kV | Kodda-1 | 2026-01-03 10:25 | 2026-01-10 12:09 | 169:44 | S/O | For yearly maintenance work. | 0 | 0 | No interruption
Savar 132/33kV | 132kV Manikganj PS-Savar Ckt-1 | 2026-01-26 16:46 | 2026-01-26 17:51 | 1:05 | S/O | Scheduled work | 0 | 0 | No interruption
Savar 132/33kV | 132kV Manikganj PS-Savar Ckt-2 | 2026-01-30 07:42 | 2026-01-30 14:03 | 6:21 | S/O | maintenance work at MPGL | 0 | 0 | No interruption
Savar 132/33kV | 132kV Manikganj PS-Savar Ckt-1 | 2026-01-30 14:38 | 2026-01-30 17:26 | 2:48 | S/O | Maintenance work at Manikganj power plant | 0 | 0 | No interruption
Sherpur 132/33kV | UMPL-Sherpur Ckt-01 | 2026-01-03 08:33 | 2026-01-03 16:54 | 8:21 | S/O | Deadline checking. | 0 | 0 | No interruption
Sherpur 132/33kV | UMPL-Sherpur Ckt-01 | 2026-01-04 09:16 | 2026-01-04 16:01 | 6:45 | S/O | Annual maintenance. | 0 | 0 | No interruption
Sherpur 132/33kV | UMPL-Sherpur Ckt-02 | 2026-01-07 08:21 | 2026-01-07 16:46 | 8:25 | S/O | Annual Maintenances | 0 | 0 | No interruption
Sherpur 132/33kV | UMPL-Sherpur Ckt-02 | 2026-01-08 08:41 | 2026-01-08 16:21 | 7:40 | S/O | Annual maintenance. | 0 | 0 | No interruption
Sherpur 132/33kV | UMPL-Sherpur Ckt-02 | 2026-01-10 08:35 | 2026-01-10 16:30 | 7:55 | S/O | Annual maintenance | 0 | 0 | No interruption
Sherpur 132/33kV | UMPL-Sherpur Ckt-02 | 2026-01-11 09:57 | 2026-01-11 16:30 | 6:33 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Valuka Ckt-1 | 2026-01-01 09:36 | 2026-01-01 12:36 | 3:00 | S/O | DS Repair | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Valuka Ckt-1 | 2026-01-04 10:51 | 2026-01-04 16:02 | 5:11 | S/O | annual Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Valuka Ckt-1 | 2026-01-05 10:22 | 2026-01-05 20:05 | 9:43 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Valuka Ckt-2 | 2026-01-07 11:09 | 2026-01-07 17:03 | 5:54 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Valuka Ckt-2 | 2026-01-08 10:58 | 2026-01-08 16:04 | 5:06 | S/O | annual Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Valuka Ckt-1 | 2026-01-10 10:05 | 2026-01-10 18:07 | 8:02 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Sirajganj Ckt-2 | 2026-01-11 13:35 | 2026-01-11 17:07 | 3:32 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Valuka Ckt-1 | 2026-01-15 08:32 | 2026-01-15 15:42 | 7:10 | S/O | instructed by NLDC | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Valuka Ckt-2 | 2026-01-15 15:54 | 2026-01-15 17:56 | 2:02 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Sirajganj Ckt-1 | 2026-01-26 09:20 | 2026-01-26 18:04 | 8:44 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Sirajganj Ckt-1 | 2026-01-27 10:04 | 2026-01-27 17:18 | 7:14 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Sirajganj Ckt-1 | 2026-01-28 09:46 | 2026-01-28 17:52 | 8:06 | S/O | Annual Maintenance (Dead Line Check) | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Sirajganj Ckt-2 | 2026-01-29 10:03 | 2026-01-29 17:17 | 7:14 | S/O | Annual Maintenance (Dead Line) | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Sirajganj Ckt-2 | 2026-01-31 08:26 | 2026-01-31 17:19 | 8:53 | S/O | Annual Maintenance | 0 | 0 | No interruption
Tangail 132/33kV | RPCL-2 | 2026-01-01 09:36 | 2026-01-01 17:05 | 7:29 | S/O | Schedule S/D | 0 | 0 | No interruption
Tangail 132/33kV | Kaliakair-2 | 2026-01-03 08:43 | 2026-01-03 14:38 | 5:55 | S/O | Maintenance. | 0 | 0 | No interruption
Tangail 132/33kV | Kaliakair-1 | 2026-01-04 09:14 | 2026-01-04 17:07 | 7:53 | S/O | Annual Maintenance | 0 | 0 | No interruption
Tangail 132/33kV | Kaliakair-1 | 2026-01-05 09:25 | 2026-01-05 16:41 | 7:16 | S/O | Schedule S/D for Deadline Checking. | 0 | 0 | No interruption
Tangail 132/33kV | Kaliakair-2 | 2026-01-13 09:30 | 2026-01-14 14:52 | 29:22 | S/O | Annual Maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Ghorashal Ckt-1 | 2026-01-02 08:05 | 2026-01-18 13:19 | 389:14 | S/O | Ghorashal end side work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kaliakoir Ckt | 2026-01-10 09:02 | 2026-01-10 17:46 | 8:44 | S/O | Annual maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kaliakoir Ckt | 2026-01-11 10:44 | 2026-01-11 17:17 | 6:33 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kaliakoir Ckt | 2026-01-12 09:29 | 2026-01-12 17:14 | 7:45 | S/O | Maintenance. | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kaliakoir Ckt | 2026-01-14 09:35 | 2026-01-14 15:42 | 6:07 | S/O | Annual maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Ghorashal Ckt-2 | 2026-01-14 11:25 | 2026-01-14 18:27 | 7:02 | S/O | Shutdown taken by NLDC | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kaliakoir Ckt | 2026-01-15 09:09 | 2026-01-15 18:13 | 9:04 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kaliakoir Ckt | 2026-01-19 08:24 | 2026-01-19 16:42 | 8:18 | S/O | Shutdown taken by kalaikair ss | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Ghorashal Ckt-2 | 2026-01-19 11:18 | 2026-01-19 12:35 | 1:17 | S/O | Shutdown taken by Ghorashal ss | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Tongi 80 MW PS | 2026-01-19 11:31 | 2026-01-19 20:25 | 8:54 | S/O | Kabirpur panel instillation | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Dhaka Metro Rail Ckt | 2026-01-19 11:31 | 2026-01-19 16:15 | 4:44 | S/O | Kabirpur Panel installation | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Summit PS(Kodda) | 2026-01-20 09:45 | 2026-01-20 17:10 | 7:25 | S/O | Maintenance. | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Ghorashal Ckt-2 | 2026-01-20 17:13 | 2026-01-20 17:25 | 0:12 | S/O | Shutdown taken by NLDC | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Summit PS(Kodda) | 2026-01-21 10:05 | 2026-01-21 17:10 | 7:05 | S/O | Annual maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Summit PS(Kodda) | 2026-01-22 09:47 | 2026-01-22 17:52 | 8:05 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2026-01-24 10:19 | 2026-01-24 18:35 | 8:16 | S/O | Maintenance. | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2026-01-25 09:03 | 2026-01-25 17:36 | 8:33 | S/O | Shutdown taken by Kabirpur | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2026-01-26 11:10 | 2026-01-26 17:33 | 6:23 | S/O | Maintenance. | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2026-01-27 09:31 | 2026-01-27 17:25 | 7:54 | S/O | Annual maintenance works | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Summit PS(Kodda) | 2026-01-27 11:37 | 2026-01-27 21:14 | 9:37 | S/O | Fitting changing work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2026-01-28 08:46 | 2026-01-28 14:47 | 6:01 | S/O | Shutdown taken by Kabirpur | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2026-01-28 14:48 | 2026-01-28 17:50 | 3:02 | S/O | Annual maintenance by kabirpur grid | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2026-01-29 09:20 | 2026-01-29 16:03 | 6:43 | S/O | Shutdown taken by kabirpur ss | 0 | 0 | No interruption
|  |  | Total : | 1900-04-27 16:34 |  | Unserved Energy: |  | 1247.8167
Dhaka (South) Grid Circle :
Bhulta 400/230kV | Ghorashal-01 | 2026-01-11 09:30 | 2026-01-11 17:52 | 8:22 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Bhulta 400/230kV | Ghorashal-02 | 2026-01-14 07:48 | 2026-01-14 17:22 | 9:34 | S/O | Maintenance work | 0 | 0 | No interruption
Bhulta 400/230kV | Ashuganj-01 | 2026-01-18 09:03 | 2026-01-18 18:03 | 9:00 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Bhulta 400/230kV | Ashuganj-01 | 2026-01-19 07:25 | 2026-01-19 16:11 | 8:46 | S/O | Dead Line Checking. | 0 | 0 | No interruption
Bhulta 400/230kV | Ashuganj-01 | 2026-01-20 07:12 | 2026-01-20 17:28 | 10:16 | S/O | Maintenance work | 0 | 0 | No interruption
Bhulta 400/230kV | Ashuganj-01 | 2026-01-21 09:04 | 2026-01-21 19:28 | 10:24 | S/O | Maintenance work | 0 | 0 | No interruption
Bhulta 400/230kV | Ashuganj-02 | 2026-01-24 08:24 | 2026-01-24 17:30 | 9:06 | S/O | Annual maintenance work | 0 | 0 | No interruption
Bhulta 400/230kV | Ashuganj-02 | 2026-01-25 08:28 | 2026-01-25 16:33 | 8:05 | S/O | Maintenance work | 0 | 0 | No interruption
Bhulta 400/230kV | Ashuganj-02 | 2026-01-26 08:42 | 2026-01-26 18:32 | 9:50 | S/O | Maintenance work | 0 | 0 | No interruption
Bhulta 400/230kV | Ashuganj-02 | 2026-01-27 08:37 | 2026-01-27 18:36 | 9:59 | S/O | Dead Line Checking | 0 | 0 | No interruption
Fatullah 132/33kV | 132 kV Shyampur-1 | 2026-01-06 10:09 | 2026-01-06 19:41 | 9:32 | S/O | Maintenance work | 0 | 0 | No interruption
Fatullah 132/33kV | 132 kV Hasnabad | 2026-01-18 08:32 | 2026-01-18 23:25 | 14:53 | S/O | Shutdown For Annual Maintenance | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi Circuit-2 | 2026-01-06 12:10 | 2026-01-06 12:10 | 0:00 | S/O | Maintenance | 0 | 0 | No interruption
Gulshan 132/33kV | Rampura-2 | 2026-01-01 09:01 | 2026-01-01 16:08 | 7:07 | S/O | Maintenance work | 0 | 0 | No interruption
Haripur 230/132kV | Sonargaon 2 | 2026-01-02 08:49 | 2026-01-02 16:25 | 7:36 | S/O | Annual Deadline checking. | 0 | 0 | No interruption
Haripur 230/132kV | Madanganj-1 | 2026-01-03 10:19 | 2026-01-03 16:53 | 6:34 | S/O | Annual Maintenance | 0 | 0 | No interruption
Haripur 230/132kV | Madanganj-2 | 2026-01-05 09:40 | 2026-01-05 16:27 | 6:47 | S/O | Annual Maintenace | 0 | 0 | No interruption
Haripur 230/132kV | Siddhirganj-1 | 2026-01-07 08:22 | 2026-01-07 16:55 | 8:33 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Haripur 230/132kV | Meghnaghat-2 | 2026-01-08 07:25 | 2026-01-11 00:07 | 64:42 | S/O | MK box changing work. | 0 | 0 | No interruption
Haripur 230/132kV | Madanganj-1 | 2026-01-11 11:15 | 2026-01-11 15:18 | 4:03 | S/O | Annunciator Replacement Work. | 0 | 0 | No interruption
Haripur 230/132kV | HPL-1 | 2026-01-12 11:20 | 2026-01-13 11:00 | 23:40 | S/O | For HPL end. | 0 | 0 | No interruption
Haripur 230/132kV | Madanganj-2 | 2026-01-12 11:49 | 2026-01-12 14:00 | 2:11 | S/O | Annunciator replacement. | 0 | 0 | No interruption
Haripur 230/132kV | EGCB 412MW | 2026-01-13 07:15 | 2026-01-13 18:24 | 11:09 | S/O | Loop replacement and clamp replacement work. | 0 | 0 | No interruption
Haripur 230/132kV | Meghnaghat-1 | 2026-01-15 06:36 | 2026-01-15 17:30 | 10:54 | S/O | For other end. | 0 | 0 | No interruption
Haripur 230/132kV | Meghnaghat-1 | 2026-01-16 06:47 | 2026-01-16 17:15 | 10:28 | S/O | For other end. | 0 | 0 | No interruption
Haripur 230/132kV | Meghnaghat-1 | 2026-01-17 08:18 | 2026-01-17 14:15 | 5:57 | S/O | Annual Maintenance | 0 | 0 | No interruption
Haripur 230/132kV | Meghnaghat-2 | 2026-01-17 14:25 | 2026-01-17 16:29 | 2:04 | S/O | Maintenance work | 0 | 0 | No interruption
Hasnabad 132/33kV | Fatulla (Pre-Brahmongaon) | 2026-01-18 08:35 | 2026-01-18 23:21 | 14:46 | S/O | Deadline checking | 0 | 0 | No interruption
Hasnabad 230/132kV | Shyampur-Hasnabad Ckt-1 | 2026-01-06 08:25 | 2026-01-06 18:08 | 9:43 | S/O | Annual maintenance | 0 | 0 | No interruption
Hasnabad 230/132kV | Shyampur-APR-Hasnabad Ckt-2 | 2026-01-07 07:31 | 2026-01-07 15:34 | 8:03 | S/O | Annual Maintenance | 0 | 0 | No interruption
Hasnabad 230/132kV | Hasnabad-Keraniganj Ckt-1 | 2026-01-11 08:15 | 2026-01-11 12:20 | 4:05 | S/O | Deadline checking | 0 | 0 | No interruption
Hasnabad 230/132kV | Hasnabad-Keraniganj Ckt-2 | 2026-01-11 12:29 | 2026-01-11 16:31 | 4:02 | S/O | dead line checking. | 0 | 0 | No interruption
Hasnabad 230/132kV | Hasnabad-Keraniganj Ckt-1 | 2026-01-16 08:17 | 2026-01-16 15:10 | 6:53 | S/O | 132 kv shitolakhha line maintenance work | 0 | 0 | No interruption
Hasnabad 230/132kV | Hasnabad-Keraniganj Ckt-1 | 2026-01-18 08:40 | 2026-01-18 16:24 | 7:44 | S/O | Hasnabad-Keraniganj 230KV circuit shutdown has been requested from Hasnabad 132KV substation for work on Hasnabad-Fatullah 132KV line. | 0 | 0 | No interruption
Hasnabad 230/132kV | Hasnabad-Keraniganj Ckt-2 | 2026-01-27 07:53 | 2026-01-27 22:24 | 14:31 | S/O | Relay Replacement Work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Aminbazar Ckt. 2 | 2026-01-01 08:56 | 2026-01-01 15:02 | 6:06 | S/O | Annual maintenance work | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Lalbagh Ckt. 3 | 2026-01-03 11:55 | 2026-01-03 15:26 | 3:31 | S/O | Line material checking for project work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Sreenagar Ckt. 1 | 2026-01-10 10:33 | 2026-01-10 13:45 | 3:12 | S/O | As instruction of NLDC. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Hasnabad Ckt. 1 | 2026-01-11 08:13 | 2026-01-12 07:14 | 23:01 | S/O | Annual Maintenance work at Hasnabad end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Hasnabad Ckt. 2 | 2026-01-11 12:13 | 2026-01-12 07:13 | 19:00 | S/O | Shutdown taken by NLDC | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Aminbazar Ckt. 1 | 2026-01-11 12:24 | 2026-01-12 17:21 | 28:57 | S/O | Annual Maintenance work at Aminbazar End. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Aminbazar Ckt. 2 | 2026-01-12 07:35 | 2026-01-12 10:31 | 2:56 | S/O | Maintenance work at Aminbazar end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 2 | 2026-01-12 08:47 | 2026-01-12 08:58 | 0:11 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 1 | 2026-01-12 08:59 | 2026-01-12 16:42 | 7:43 | S/O | Annual work at Hasnabad end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 2 | 2026-01-12 10:17 | 2026-01-12 16:42 | 6:25 | S/O | Maintenance work at Hasnabad ss end | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Hasnabad Ckt. 1 | 2026-01-12 10:31 | 2026-01-12 12:37 | 2:06 | S/O | Maintenance work | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Hasnabad Ckt. 2 | 2026-01-12 12:00 | 2026-01-12 12:07 | 0:07 | S/O | Maintenance work | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Aminbazar Ckt. 2 | 2026-01-12 12:07 | 2026-01-12 17:19 | 5:12 | S/O | Maintenance work | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Sreenagar Ckt. 2 | 2026-01-13 07:30 | 2026-01-13 17:10 | 9:40 | S/O | Dead line checking | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 1 | 2026-01-13 07:52 | 2026-01-13 16:07 | 8:15 | S/O | Dead line checking | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 2 | 2026-01-13 10:03 | 2026-01-13 16:08 | 6:05 | S/O | Deadline Checking | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Sreenagar Ckt. 2 | 2026-01-14 09:09 | 2026-01-14 16:49 | 7:40 | S/O | Deadline checking at Sreenagar end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Hasnabad Ckt. 1 | 2026-01-16 08:14 | 2026-01-16 15:10 | 6:56 | S/O | Deadline chekcing from Hasnabad end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Aminbazar Ckt. 2 | 2026-01-17 08:53 | 2026-01-17 20:44 | 11:51 | S/O | CT maintenance work at aminbazar end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Hasnabad Ckt. 1 | 2026-01-18 08:39 | 2026-01-18 16:23 | 7:44 | S/O | Maintenance work at Hasnabad end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 1 | 2026-01-19 09:53 | 2026-01-19 14:27 | 4:34 | S/O | Dead line checking at Hasnabad end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 2 | 2026-01-19 10:02 | 2026-01-19 14:28 | 4:26 | S/O | Dead line checking at Hasnabad end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 2 | 2026-01-19 10:02 | 2026-01-19 14:28 | 4:26 | S/O | Dead line checking at Hasnabad end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 2 | 2026-01-20 08:39 | 2026-01-20 18:09 | 9:30 | S/O | Dead line checking by Keraniganj grid. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Sreenagar Ckt. 1 | 2026-01-20 08:47 | 2026-01-20 16:34 | 7:47 | S/O | Dead line checking by Keraniganj grid. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Nawabganj Ckt. 2 | 2026-01-21 08:18 | 2026-01-21 18:39 | 10:21 | S/O | Deadline checked at both end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Nawabganj Ckt. 1 | 2026-01-22 08:47 | 2026-01-22 17:46 | 8:59 | S/O | Deadline Checking | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Kamrangirchar Ckt, | 2026-01-23 07:44 | 2026-01-23 14:38 | 6:54 | S/O | Annual maintenance & deadline checking at Keraniganj end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Lalbagh Ckt. 3 | 2026-01-24 07:18 | 2026-01-24 14:34 | 7:16 | S/O | Annual maintenance and deadline checking. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Hasnabad Ckt. 2 | 2026-01-27 07:51 | 2026-01-27 22:24 | 14:33 | S/O | SPMD work at Hasnabad end. | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Haripur 132 kv Ckt-1 | 2026-01-03 10:16 | 2026-01-03 16:52 | 6:36 | S/O | Annual maintenance | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Haripur 132 kv Ckt-2 | 2026-01-05 09:33 | 2026-01-05 16:27 | 6:54 | S/O | Annual maintenance | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Shitalakhya 132 kv Ckt | 2026-01-11 09:15 | 2026-01-11 16:59 | 7:44 | S/O | Annual Maintenance | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Munshiganj 132 kv Ckt-1 | 2026-01-13 07:20 | 2026-01-13 11:57 | 4:37 | S/O | Annual Maintenance | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Munshiganj 132 kv Ckt-2 | 2026-01-13 12:09 | 2026-01-13 16:50 | 4:41 | S/O | Annual Maintenance | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Munshiganj 132 kv Ckt-1 | 2026-01-15 08:54 | 2026-01-15 14:39 | 5:45 | S/O | Annual Maintenance | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Munshiganj 132 kv Ckt-2 | 2026-01-15 14:47 | 2026-01-15 17:20 | 2:33 | S/O | Annual Maintenance | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Munshiganj 132 kv Ckt-2 | 2026-01-28 08:44 | 2026-01-28 14:45 | 6:01 | S/O | Maintenance work | 0 | 0 | No interruption
Maniknagar 132/33kV | Narinda Ckt-1 | 2026-01-03 09:29 | 2026-01-03 16:05 | 6:36 | S/O | PT oil leakage repair (Blue phase) | 0 | 0 | No interruption
Maniknagar 132/33kV | Kazla Ckt -1 | 2026-01-04 11:23 | 2026-01-04 15:20 | 3:57 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Maniknagar 230/132kV | 230kV Siddhirganj-Maniknagar ckt-1 | 2026-01-26 07:14 | 2026-01-26 17:26 | 10:12 | S/O | Dead line checking. | 0 | 0 | No interruption
Meghnaghat 230/132kV | Meghnaghat-Haripur-02 | 2026-01-08 08:00 | 2026-01-11 00:07 | 64:07 | S/O | Clam connector assembly work | 0 | 0 | No interruption
Meghnaghat 230/132kV | Meghnaghat-Comilla-01 | 2026-01-17 09:58 | 2026-01-17 19:41 | 9:43 | S/O | As per request of NLDC | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2026-01-01 07:19 | 2026-01-01 18:02 | 10:43 | S/O | 400 kV Aminbazar ckt- 02 shutdown instructed by NLDC. | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Shyampur 230kV Ckt-1 | 2026-01-01 13:20 | 2026-01-01 17:45 | 4:25 | S/O | Maintanance work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2026-01-02 08:43 | 2026-01-02 16:40 | 7:57 | S/O | Requested by Aminbazar | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Shyampur 230kV Ckt-1 | 2026-01-03 07:23 | 2026-01-03 16:50 | 9:27 | S/O | Maintenance purpose | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat- Shyampur 230kv -Ckt 2 | 2026-01-09 07:50 | 2026-01-09 17:52 | 10:02 | S/O | Instructed by NLDC | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Shyampur 230kV Ckt-1 | 2026-01-10 07:43 | 2026-01-10 14:58 | 7:15 | S/O | Maintenance work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-1 | 2026-01-17 09:49 | 2026-01-17 17:39 | 7:50 | S/O | for maintenance work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-2 | 2026-01-19 08:33 | 2026-01-21 15:48 | 55:15 | S/O | maintenance work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-1 | 2026-01-23 07:00 | 2026-01-23 17:55 | 10:55 | S/O | project work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2026-01-25 08:50 | 2026-01-25 17:13 | 8:23 | S/O | 400 kV Aminbazar ckt- 02 shutdown instructed by NLDC. Munshiganj SS will do their annual maintenance work. | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-1 | 2026-01-26 08:54 | 2026-01-26 17:55 | 9:01 | S/O | maintenance work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-1 | 2026-01-27 08:52 | 2026-01-27 17:08 | 8:16 | S/O | Dead line checking | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Shyampur 230kV Ckt-1 | 2026-01-28 09:08 | 2026-01-28 15:20 | 6:12 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2026-01-28 09:10 | 2026-01-28 17:40 | 8:30 | S/O | None | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2026-01-29 09:13 | 2026-01-29 17:19 | 8:06 | S/O | Annual Maintenace work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat- Shyampur 230kv -Ckt 2 | 2026-01-29 09:45 | 2026-01-29 13:25 | 3:40 | S/O | Maintenance work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Shyampur 230kV Ckt-1 | 2026-01-30 07:42 | 2026-01-30 16:24 | 8:42 | S/O | Maintenance work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2026-01-30 08:35 | 2026-01-30 16:11 | 7:36 | S/O | Maintenance work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat- Shyampur 230kv -Ckt 2 | 2026-01-31 07:32 | 2026-01-31 17:15 | 9:43 | S/O | For annual maintenance. | 0 | 0 | No interruption
Mogbazar 132/33kV | Rampura 2 | 2026-01-14 07:28 | 2026-01-14 07:28 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
Mogbazar 132/33kV | Rampura 1 | 2026-01-21 09:05 | 2026-01-21 15:42 | 6:37 | S/O | annaual maintance | 0 | 0 | No interruption
Munshiganj 132/33kV | Madanganj- Munshiganj Ckt-1 | 2026-01-13 07:20 | 2026-01-13 11:58 | 4:38 | S/O | Annual maintenance | 0 | 0 | No interruption
Munshiganj 132/33kV | Madanganj- Munshiganj- Ckt-2 | 2026-01-13 12:09 | 2026-01-13 16:56 | 4:47 | S/O | Annual maintenance | 0 | 0 | No interruption
Munshiganj 132/33kV | Madanganj- Munshiganj Ckt-1 | 2026-01-15 07:54 | 2026-01-15 14:42 | 6:48 | S/O | Deadline check | 0 | 0 | No interruption
Munshiganj 132/33kV | Madanganj- Munshiganj- Ckt-2 | 2026-01-15 14:47 | 2026-01-15 17:22 | 2:35 | S/O | Dead line Checking | 0 | 0 | No interruption
Munshiganj 132/33kV | Madanganj- Munshiganj- Ckt-2 | 2026-01-28 08:44 | 2026-01-28 14:49 | 6:05 | S/O | Insulator Replacement | 0 | 0 | No interruption
Narshingdi 132/33kV | Brahmanbaria-01 | 2026-01-13 09:01 | 2026-01-13 16:05 | 7:04 | S/O | For annual maintenance Work. | 0 | 0 | No interruption
Narshingdi 132/33kV | Brahmanbaria-02 | 2026-01-15 08:32 | 2026-01-15 15:43 | 7:11 | S/O | Annual maintenance | 0 | 0 | No interruption
Narshingdi 132/33kV | Brahmanbaria-02 | 2026-01-17 08:40 | 2026-01-17 16:04 | 7:24 | S/O | Annual maintenance | 0 | 0 | No interruption
Nawabganj 132/33kV | Keraniganj-2 | 2026-01-21 08:17 | 2026-01-21 18:40 | 10:23 | S/O | For Deadline Checking(Annual Maintenance) | 0 | 0 | No interruption
Nawabganj 132/33kV | Keraniganj-1 | 2026-01-22 08:46 | 2026-01-22 17:47 | 9:01 | S/O | For deadline chekiang | 0 | 0 | No interruption
Postogola 132/33kV | Hasnabad Circuit-1 | 2026-01-18 16:53 | 2026-01-18 16:53 | 0:00 | S/O | Yearly maintenance | 0 | 0 | No interruption
Rampura 230/132kV | Gulshan Ckt-02 | 2026-01-01 08:52 | 2026-01-01 16:08 | 7:16 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampura 230/132kV | Madertek-01 | 2026-01-01 09:45 | 2026-01-01 16:02 | 6:17 | S/O | shutdown taken by NLDC to Madertek end SS works. | 0 | 0 | No interruption
Rampura 230/132kV | Ullon-01 | 2026-01-11 09:21 | 2026-01-11 17:01 | 7:40 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampura 230/132kV | Ullon-02 | 2026-01-14 07:26 | 2026-01-14 15:53 | 8:27 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampura 230/132kV | Moghbazar-01 | 2026-01-18 07:39 | 2026-01-18 15:57 | 8:18 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Rampura 230/132kV | Moghbazar-01 | 2026-01-19 07:10 | 2026-01-19 17:05 | 9:55 | S/O | Annual Maintenance and Line PT(Y) Phase Replacement. | 0 | 0 | No interruption
Rampura 230/132kV | Moghbazar-01 | 2026-01-21 09:22 | 2026-01-21 15:42 | 6:20 | S/O | Order by NLDC | 0 | 0 | No interruption
Rampura 230/132kV | Ullon-02 | 2026-01-22 09:16 | 2026-01-22 14:46 | 5:30 | S/O | Order by NLDC | 0 | 0 | No interruption
Rampura 230/132kV | Madertek-01 | 2026-01-25 07:28 | 2026-01-25 17:40 | 10:12 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampura 230/132kV | Madertek-02 | 2026-01-28 08:25 | 2026-01-28 14:55 | 6:30 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV Meghnaghat-1(D06) | 2026-01-01 13:30 | 2026-01-01 17:46 | 4:16 | S/O | Disc Cleaning | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV Meghnaghat-2(D05) | 2026-01-02 07:20 | 2026-01-02 21:11 | 13:51 | S/O | Disc Cleaning at Tower No 22 & 23 | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV Meghnaghat-1(D06) | 2026-01-03 07:42 | 2026-01-03 16:50 | 9:08 | S/O | Dead Line Checking & Disc Cleaning of Tower no#23 | 0 | 0 | No interruption
Shyampur 230/132kV | 132 kV Shyampur old-2(E10) | 2026-01-05 09:35 | 2026-01-05 12:57 | 3:22 | S/O | Annual maintenance at 132kV Shyampur SS DPDC end. | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV Hasnabad-1(D02) | 2026-01-06 08:24 | 2026-01-06 18:07 | 9:43 | S/O | Deadline checking and annual maintenance | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV APR (D04) | 2026-01-07 07:31 | 2026-01-07 15:35 | 8:04 | S/O | for Dead Line checking | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV Meghnaghat-2(D05) | 2026-01-09 07:48 | 2026-01-09 17:52 | 10:04 | S/O | Deadline checking | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV Meghnaghat-1(D06) | 2026-01-10 07:44 | 2026-01-10 14:59 | 7:15 | S/O | Deadline checking. | 0 | 0 | No interruption
Shyampur 230/132kV | 132 kV Shyampur old-2(E10) | 2026-01-19 09:23 | 2026-01-19 20:01 | 10:38 | S/O | Project work of DPDC. | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV Meghnaghat-1(D06) | 2026-01-28 09:13 | 2026-01-28 15:19 | 6:06 | S/O | Annual maintenane work at Meghnaghat SS and insulator disc cleaning at tower no 22 an 23. | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV Meghnaghat-2(D05) | 2026-01-29 09:38 | 2026-01-29 13:25 | 3:47 | S/O | Annual maintenance at Meghnaghat substation. | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV Meghnaghat-1(D06) | 2026-01-30 07:42 | 2026-01-30 16:24 | 8:42 | S/O | Insulator disc change tower no: 22 & 23 | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV Meghnaghat-2(D05) | 2026-01-31 07:34 | 2026-01-31 17:15 | 9:41 | S/O | Changing of Insulator Disc at Tower no. 22 & 23 (Top phase = all set & Middle phase = all set | 0 | 0 | No interruption
Siddhirganj 132/33kV | 132kV MTR 1 | 2026-01-04 08:33 | 2026-01-04 16:55 | 8:22 | S/O | Annual Maintenance | 0 | 0 | No interruption
Siddhirganj 132/33kV | 132kV MTR 2 | 2026-01-06 08:54 | 2026-01-06 15:47 | 6:53 | S/O | Annual Maintenance Works | 0 | 0 | No interruption
Siddhirganj 132/33kV | Ullon 1 | 2026-01-06 09:23 | 2026-01-06 18:12 | 8:49 | S/O | Maintenance work by NLDC | 0 | 0 | No interruption
Siddhirganj 132/33kV | Haripur 1 | 2026-01-07 08:24 | 2026-01-07 16:55 | 8:31 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Siddhirganj 132/33kV | Haripur 2 | 2026-01-10 08:52 | 2026-01-10 15:34 | 6:42 | S/O | Annual Maintenance | 0 | 0 | No interruption
Siddhirganj 230/132kV | 335MW EGCB 1 | 2026-01-02 00:10 | 2026-01-02 19:15 | 19:05 | S/O | emergency maintence work perform by egcb side | 0 | 0 | No interruption
Siddhirganj 230/132kV | 335MW EGCB 1 | 2026-01-05 09:55 | 2026-01-05 17:37 | 7:42 | S/O | EMERGENCY MAINTENANCE WORK | 0 | 0 | No interruption
Siddhirganj 230/132kV | 335MW EGCB 2 | 2026-01-05 17:45 | 2026-01-05 19:29 | 1:44 | S/O | emergency maintence maintenance work | 0 | 0 | No interruption
Siddhirganj 230/132kV | Maniknagar 2 | 2026-01-19 18:35 | 2026-01-20 01:13 | 6:38 | S/O | Replace LA | 0 | 0 | No interruption
Siddhirganj 230/132kV | Maniknagar 1 | 2026-01-26 07:14 | 2026-01-26 19:25 | 12:11 | S/O | Annual maintenance work | 0 | 0 | No interruption
Siddhirganj 230/132kV | Maniknagar 2 | 2026-01-28 07:32 | 2026-01-28 17:10 | 9:38 | S/O | Annual maintenance | 0 | 0 | No interruption
Sonargaon 132/33kV | Haripur-2 | 2026-01-02 08:51 | 2026-01-02 16:24 | 7:33 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Sonargaon 132/33kV | Daudkandi-01 | 2026-01-13 09:04 | 2026-01-13 16:10 | 7:06 | S/O | Annual maintenance | 0 | 0 | No interruption
Sonargaon 132/33kV | Daudkandi-01 | 2026-01-14 09:05 | 2026-01-14 16:34 | 7:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sonargaon 132/33kV | OPML(IEL-1) | 2026-01-14 09:29 | 2026-01-14 16:31 | 7:02 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sonargaon 132/33kV | Daudkandi-01 | 2026-01-15 08:35 | 2026-01-15 15:47 | 7:12 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sonargaon 132/33kV | OPSL(IEL-2) | 2026-01-16 09:06 | 2026-01-16 16:14 | 7:08 | S/O | Annual maintenance work | 0 | 0 | No interruption
Sonargaon 132/33kV | Daudkandi-01 | 2026-01-17 08:22 | 2026-01-17 15:02 | 6:40 | S/O | Annual maintenance on Sonargaon to Daudkandi line by Siddhirgonj 132/33KV grid Substation | 0 | 0 | No interruption
Sonargaon 132/33kV | Daudkandi-2 | 2026-01-18 08:34 | 2026-01-18 16:58 | 8:24 | S/O | Annual maintenance | 0 | 0 | No interruption
Sonargaon 132/33kV | Daudkandi-2 | 2026-01-19 08:23 | 2026-01-19 15:32 | 7:09 | S/O | Annual maintenance deadline checking &Bay maintenance.. | 0 | 0 | No interruption
Sonargaon 132/33kV | Daudkandi-2 | 2026-01-20 09:05 | 2026-01-20 16:46 | 7:41 | S/O | Annual Maintenance | 0 | 0 | No interruption
Srinagar 132/33kV | Keraniganj-01 | 2026-01-10 10:48 | 2026-01-10 13:45 | 2:57 | S/O | Purpose OPGW wire cutting. | 0 | 0 | No interruption
Srinagar 132/33kV | Keraniganj-02(Powerpac) | 2026-01-13 07:28 | 2026-01-13 17:09 | 9:41 | S/O | Dead Line Checking. | 0 | 0 | No interruption
Srinagar 132/33kV | Keraniganj-02(Powerpac) | 2026-01-14 08:03 | 2026-01-14 08:03 | 0:00 | S/O | Annual Deadline Checking. | 0 | 0 | No interruption
Srinagar 132/33kV | Keraniganj-01 | 2026-01-20 08:44 | 2026-01-20 16:34 | 7:50 | S/O | Dead Line Checking. | 0 | 0 | No interruption
|  |  | Total : | 1900-02-25 21:49 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
AKS 132/33kV | Khulshi | 2026-01-10 07:47 | 2026-01-10 14:52 | 7:05 | S/O | Annual maintenance work of Khulshi Grid and Khulshi to AKSPL line. | 0 | 0 | No interruption
AKS 132/33kV | Khulshi | 2026-01-13 08:21 | 2026-01-13 15:25 | 7:04 | S/O | Khulshi to AKSPL 132 KV Line Checking & Annual Maintenance. | 0 | 0 | No interruption
AKS 132/33kV | Bar Aulia | 2026-01-13 11:08 | 2026-01-13 16:13 | 5:05 | S/O | Baraulia 132 KV Line Shutdown due to Baraulia 132/33 KV Sub-station Annual Maintenance. | 0 | 0 | No interruption
AKS 132/33kV | Khulshi | 2026-01-14 09:30 | 2026-01-14 15:27 | 5:57 | S/O | Khulshi to AKSPL 132 Kv line Checking and Annual Maintenance. | 0 | 0 | No interruption
AKS 132/33kV | Bar Aulia | 2026-01-17 08:30 | 2026-01-17 15:49 | 7:19 | S/O | AKSPL to Baraulia Deadline Checking | 0 | 0 | No interruption
Bakulia 132/33kV | Bakalia-Kulshi Ckt | 2026-01-10 07:56 | 2026-01-10 15:02 | 7:06 | S/O | Annual maintanance | 0 | 0 | No interruption
Bakulia 132/33kV | Bakalia-Modern Ckt | 2026-01-10 07:56 | 2026-01-10 15:08 | 7:12 | S/O | Annual maintanance | 0 | 0 | No interruption
Bakulia 132/33kV | Bakalia-Modern Ckt | 2026-01-25 08:22 | 2026-01-25 14:56 | 6:34 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bakulia 132/33kV | Bakalia-Modern Ckt | 2026-01-26 08:51 | 2026-01-26 14:48 | 5:57 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bakulia 132/33kV | Bakalia-Modern Ckt | 2026-01-27 07:55 | 2026-01-27 15:58 | 8:03 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bakulia 132/33kV | Bakalia-Sikalbaha Ckt-01 | 2026-01-31 08:26 | 2026-01-31 14:06 | 5:40 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Baroaulia 132/33kV | Kulshi | 2026-01-10 07:14 | 2026-01-10 14:18 | 7:04 | S/O | Annual maintence of Bay Equipment at KHULSHI end. | 0 | 0 | No interruption
Baroaulia 132/33kV | AKSPL | 2026-01-11 12:06 | 2026-01-11 15:51 | 3:45 | S/O | Braulia AKSPL line CVT Y-phase loop change at AKSPL S/S | 0 | 0 | No interruption
Baroaulia 132/33kV | AKSPL | 2026-01-17 08:34 | 2026-01-17 15:47 | 7:13 | S/O | Annual Maintenance for Dead line check Baraulia to AKSPL line. | 0 | 0 | No interruption
Baroaulia 132/33kV | Hat-1 | 2026-01-28 09:43 | 2026-01-28 14:37 | 4:54 | S/O | Annual maintanance | 0 | 0 | No interruption
Baroaulia 132/33kV | Hat-2 | 2026-01-29 10:08 | 2026-01-29 14:17 | 4:09 | S/O | Annual Maintenance | 0 | 0 | No interruption
Baroirhat 132/33kV | Hat-1 | 2026-01-11 06:56 | 2026-01-11 19:09 | 12:13 | S/O | Annual Maintenance | 0 | 0 | No interruption
Baroirhat 132/33kV | Hat-2 | 2026-01-11 06:57 | 2026-01-11 20:07 | 13:10 | S/O | Annual Maintenance | 0 | 0 | No interruption
Baroirhat 132/33kV | PHP | 2026-01-12 08:11 | 2026-01-12 18:28 | 10:17 | S/O | None | 0 | 0 | No interruption
Baroirhat 132/33kV | Feni-1 | 2026-01-13 09:05 | 2026-01-13 14:46 | 5:41 | S/O | Annual Maintenance | 0 | 0 | No interruption
Baroirhat 132/33kV | Feni-1 | 2026-01-14 09:07 | 2026-01-14 16:28 | 7:21 | S/O | Annual Maintenance | 0 | 0 | No interruption
BSRM 230/33kV | GPH Ispat Ckt. -01 | 2026-01-10 09:20 | 2026-01-10 15:13 | 5:53 | S/O | Annual Maintenance | 0 | 0 | No interruption
BSRM 230/33kV | GPH Ispat Ckt. -01 | 2026-01-11 10:04 | 2026-01-11 16:25 | 6:21 | S/O | Annual Maintenance | 0 | 0 | No interruption
BSRM 230/33kV | GPH Ispat Ckt. -01 | 2026-01-12 09:27 | 2026-01-12 15:33 | 6:06 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Madunaghat Ckt-01 | 2026-01-13 09:22 | 2026-01-13 17:00 | 7:38 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Kaptai Ckt-01 | 2026-01-27 09:30 | 2026-01-27 18:09 | 8:39 | S/O | Requirement of kaptai power house | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Kaptai Ckt-02 | 2026-01-27 09:30 | 2026-01-27 18:13 | 8:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Kaptai Ckt-01 | 2026-01-29 10:04 | 2026-01-29 18:36 | 8:32 | S/O | Kaptai Power House Maintenance Work | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Kaptai Ckt-02 | 2026-01-29 10:10 | 2026-01-29 18:39 | 8:29 | S/O | Kaptai Power House Maintenance Work. | 0 | 0 | No interruption
Coxsbazar 132/33kV | Doh-Cox Ckt-1 | 2026-01-01 15:40 | 2026-01-01 17:41 | 2:01 | S/O | Maintenance | 0 | 0 | No interruption
Coxsbazar 132/33kV | Doh-Cox Ckt-1 | 2026-01-03 09:00 | 2026-01-03 11:30 | 2:30 | S/O | Maintenance | 0 | 0 | No interruption
Coxsbazar 132/33kV | Doh-Cox Ckt-1 | 2026-01-03 14:55 | 2026-01-03 16:35 | 1:40 | S/O | Maintenance | 0 | 0 | No interruption
Coxsbazar 132/33kV | Doh-Cox Ckt-1 | 2026-01-04 14:42 | 2026-01-04 16:21 | 1:39 | S/O | Annual Maintenance of Doh-Cox Ckt-1 Dohajari site. | 0 | 0 | No interruption
Coxsbazar 132/33kV | Doh-Cox Ckt-1 | 2026-01-05 08:56 | 2026-01-05 11:32 | 2:36 | S/O | Annual Maintenance of Doh- Cox Ckt-1 Dohazari Side. | 0 | 0 | No interruption
Coxsbazar 132/33kV | Doh-Cox Ckt-1 | 2026-01-05 15:12 | 2026-01-05 17:03 | 1:51 | S/O | Annual maintenance | 0 | 0 | No interruption
Coxsbazar 132/33kV | Doh-Cox Ckt-1 | 2026-01-06 09:30 | 2026-01-06 15:42 | 6:12 | S/O | Annual maintenance | 0 | 0 | No interruption
Coxsbazar 132/33kV | Doh-Cox Ckt-1 | 2026-01-07 09:12 | 2026-01-07 15:53 | 6:41 | S/O | Doh-Cox Ckt-1 Annual Maintenance (Cox’s Bazar side) | 0 | 0 | No interruption
Coxsbazar 132/33kV | Doh-Cox Ckt-1 | 2026-01-08 09:34 | 2026-01-08 15:02 | 5:28 | S/O | Annual maintenance | 0 | 0 | No interruption
Coxsbazar 132/33kV | Doh-Cox Ckt-1 | 2026-01-11 10:28 | 2026-01-11 17:33 | 7:05 | S/O | Annual maitenance. | 0 | 0 | No interruption
Coxsbazar 132/33kV | Doh-Cox Ckt-1 | 2026-01-13 08:43 | 2026-01-13 17:22 | 8:39 | S/O | Annual maintenance | 0 | 0 | No interruption
Coxsbazar 132/33kV | Doh-Cox Ckt-1 | 2026-01-14 08:33 | 2026-01-14 16:19 | 7:46 | S/O | Annual maintenance | 0 | 0 | No interruption
Coxsbazar 132/33kV | Doh-Cox Ckt-1 | 2026-01-15 08:18 | 2026-01-15 17:43 | 9:25 | S/O | Annual Maintenance Doh-Cox Ckt-1 | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2026-01-01 09:35 | 2026-01-01 17:40 | 8:05 | S/O | Annual Maintenance | 10 | 80.8333 | Power interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2026-01-03 09:04 | 2026-01-03 16:35 | 7:31 | S/O | Annual Maintenance | 10 | 75.1667 | Power interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2026-01-04 09:47 | 2026-01-04 16:18 | 6:31 | S/O | Annual Maintenance | 12 | 78.2 | Power interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2026-01-05 08:57 | 2026-01-05 17:02 | 8:05 | S/O | Annual maintenance. | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2026-01-06 09:35 | 2026-01-06 10:35 | 1:00 | S/O | Annual maintenance. | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2026-01-06 14:21 | 2026-01-06 15:40 | 1:19 | S/O | Annual maintenance. | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2026-01-07 09:13 | 2026-01-07 10:30 | 1:17 | S/O | Annual maintenance | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2026-01-07 14:24 | 2026-01-07 15:52 | 1:28 | S/O | Annual maintenance | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2026-01-08 09:35 | 2026-01-08 10:51 | 1:16 | S/O | Annual maintenance | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2026-01-08 13:38 | 2026-01-08 15:01 | 1:23 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2026-01-11 10:28 | 2026-01-11 10:48 | 0:20 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2026-01-11 16:18 | 2026-01-11 17:34 | 1:16 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2026-01-12 08:47 | 2026-01-12 16:33 | 7:46 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2026-01-13 08:45 | 2026-01-13 17:21 | 8:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2026-01-14 08:34 | 2026-01-14 16:17 | 7:43 | S/O | Annual maintenance. | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2026-01-15 08:20 | 2026-01-15 17:41 | 9:21 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Sikalbaha ckt-1 | 2026-01-19 11:19 | 2026-01-19 13:53 | 2:34 | S/O | Loop connection work from Line DS to newly installed CT (R-phase). | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Sikalbaha ckt-1 | 2026-01-27 10:11 | 2026-01-27 11:50 | 1:39 | S/O | Line Parameter Test (SPMD) | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Sikalbaha ckt-2 | 2026-01-27 11:52 | 2026-01-27 15:16 | 3:24 | S/O | Line Parameter Test (SPMD) | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Sikalbaha ckt-2 | 2026-01-31 15:06 | 2026-01-31 17:20 | 2:14 | S/O | Due to Disks change | 0 | 0 | No interruption
GPH 230/33kV | BSRM CKT-1 | 2026-01-10 09:27 | 2026-01-10 15:12 | 5:45 | S/O | shedule shutdown | 0 | 0 | No interruption
GPH 230/33kV | BSRM CKT-1 | 2026-01-11 10:05 | 2026-01-11 16:24 | 6:19 | S/O | Annual Maintenance | 0 | 0 | No interruption
GPH 230/33kV | BSRM CKT-1 | 2026-01-12 09:08 | 2026-01-12 15:32 | 6:24 | S/O | Annual maintenance | 0 | 0 | No interruption
GPH 230/33kV | HATHAZARI | 2026-01-13 09:32 | 2026-01-13 14:52 | 5:20 | S/O | Annual maintenance | 0 | 0 | No interruption
GPH 230/33kV | HATHAZARI | 2026-01-14 09:00 | 2026-01-14 14:54 | 5:54 | S/O | annual maintenance | 0 | 0 | No interruption
GPH 230/33kV | HATHAZARI | 2026-01-15 11:50 | 2026-01-15 17:37 | 5:47 | S/O | for hatazari | 0 | 0 | No interruption
GPH 230/33kV | HATHAZARI | 2026-01-22 08:46 | 2026-01-22 16:16 | 7:30 | S/O | Maintenance Works in Hathazari | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Khulshi-Ckt.-3 | 2026-01-10 07:09 | 2026-01-10 16:48 | 9:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroiarhat-01 | 2026-01-11 06:58 | 2026-01-11 19:45 | 12:47 | S/O | Project work | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroiarhat-02 | 2026-01-11 06:58 | 2026-01-11 20:20 | 13:22 | S/O | Project work | 0 | 0 | No interruption
Hathazari 230/132/33kV | Madunaghat GIS-01 | 2026-01-17 08:02 | 2026-01-17 17:17 | 9:15 | S/O | Annual Maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV | AKSML-02 | 2026-01-17 09:44 | 2026-01-17 17:19 | 7:35 | S/O | dead line check | 0 | 0 | No interruption
Hathazari 230/132/33kV | GPH-01 | 2026-01-22 08:58 | 2026-01-22 16:15 | 7:17 | S/O | Bay loop work | 0 | 0 | No interruption
Hathazari 230/132/33kV | Shikolbaha-02 | 2026-01-22 09:30 | 2026-01-22 16:15 | 6:45 | S/O | Bay loop work | 0 | 0 | No interruption
Hathazari 230/132/33kV | Madunaghat GIS-01 | 2026-01-24 10:08 | 2026-01-24 15:02 | 4:54 | S/O | Annual dead line Check | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroaulia-01 | 2026-01-28 10:00 | 2026-01-28 14:35 | 4:35 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-Madunaghat CKT-2 | 2026-01-07 07:58 | 2026-01-07 15:30 | 7:32 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-AKSPL Line | 2026-01-13 08:18 | 2026-01-13 15:21 | 7:03 | S/O | Annual maintenance (Deadline checking) | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-AKSPL Line | 2026-01-14 09:33 | 2026-01-14 15:31 | 5:58 | S/O | Annual Maintenance(Deadline Checking) | 0 | 0 | No interruption
Korerhat 400/230/132kV | Meghnaghat-1 | 2026-01-23 07:00 | 2026-01-23 17:56 | 10:56 | S/O | For project work. | 0 | 0 | No interruption
Korerhat 400/230/132kV | Chowmuhani-04 | 2026-01-25 08:55 | 2026-01-25 17:44 | 8:49 | S/O | SAS witness | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Kulshi-1 | 2026-01-08 07:52 | 2026-01-11 16:03 | 80:11 | S/O | Annual Maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Chandraghona-1 | 2026-01-13 09:23 | 2026-01-13 17:00 | 7:37 | S/O | insulator disk change. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Hathazari-1 | 2026-01-17 07:54 | 2026-01-17 17:16 | 9:22 | S/O | Annual Maintenance | 0 | 0 | No interruption
Madunaghat 400/230kV | Madunaghat-Meghnaghat 400kV Ckt.-2 | 2026-01-19 11:31 | 2026-01-21 15:00 | 51:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
Madunaghat 400/230kV | Madunaghat-Hathazari 230kV Ckt.-2 | 2026-01-22 09:22 | 2026-01-22 16:13 | 6:51 | S/O | Annual maintenance | 0 | 0 | No interruption
Madunaghat 400/230kV | Madunaghat-Shikalbaha 230kV Ckt.-1 | 2026-01-23 09:58 | 2026-01-23 15:43 | 5:45 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Madunaghat 400/230kV | Madunaghat-Hathazari 230kV Ckt.-1 | 2026-01-24 09:57 | 2026-01-24 15:01 | 5:04 | S/O | Annual Maintenance | 0 | 0 | No interruption
Madunaghat 400/230kV | Madunaghat-Hathazari 230kV Ckt.-1 | 2026-01-25 09:29 | 2026-01-25 17:07 | 7:38 | S/O | Annual Maintenance | 0 | 0 | No interruption
Madunaghat 400/230kV | Madunaghat-Hathazari 230kV Ckt.-2 | 2026-01-26 09:17 | 2026-01-26 15:21 | 6:04 | S/O | Annual maintenance | 0 | 0 | No interruption
Madunaghat 400/230kV | Madunaghat-Shikalbaha 230kV Ckt.-2 | 2026-01-30 09:05 | 2026-01-30 15:00 | 5:55 | S/O | Annual maintenance | 0 | 0 | No interruption
Mirsorai 230/33kV | BSRM-1 | 2026-01-22 08:50 | 2026-01-22 08:50 | 0:00 | S/O | Project Work | 0 | 0 | No interruption
Mirsorai 230/33kV | EGCB 75MW Solar Power Station | 2026-01-30 18:15 | 2026-01-31 07:49 | 13:34 | S/O | Bashundhara Bus Coupling | 0 | 0 | No interruption
Patiya 132/33kV | Patiya-Dohazari Ckt-01 | 2026-01-27 10:12 | 2026-01-27 11:50 | 1:38 | S/O | Line parameter test | 0 | 0 | No interruption
Patiya 132/33kV | Patiya-Dohazari Ckt-02 | 2026-01-27 11:53 | 2026-01-27 15:15 | 3:22 | S/O | Line parameter test | 0 | 0 | No interruption
Patiya 132/33kV | Sikalbaha-Patiya Ckt-02 | 2026-01-27 15:22 | 2026-01-27 17:12 | 1:50 | S/O | Line parameter test | 0 | 0 | No interruption
Patiya 132/33kV | Sikalbaha-Patiya Ckt-01 | 2026-01-29 08:28 | 2026-01-29 18:34 | 10:06 | S/O | Line work | 0 | 0 | No interruption
Rampur 230/132/33 | Khulshi-1 | 2026-01-10 07:04 | 2026-01-10 15:19 | 8:15 | S/O | annual maintenance of kulshi grid | 0 | 0 | No interruption
Rampur 230/132/33 | Khulshi-2 | 2026-01-10 07:05 | 2026-01-10 15:19 | 8:14 | S/O | annual maintenance of kulshi grid | 0 | 0 | No interruption
Rangamati 132/33kV | Chandraghona Ckt-01 | 2026-01-11 09:20 | 2026-01-11 15:25 | 6:05 | S/O | Right Of Way | 0 | 0 | No interruption
Rangamati 132/33kV | Chandraghona Ckt-02 | 2026-01-12 08:21 | 2026-01-12 17:02 | 8:41 | S/O | Annual ROW. | 0 | 0 | No interruption
Rangamati 132/33kV | Khagrachari Ckt-01 | 2026-01-13 08:58 | 2026-01-13 15:51 | 6:53 | S/O | For Row maintenance | 0 | 0 | No interruption
Rangamati 132/33kV | Khagrachari Ckt-02 | 2026-01-14 08:57 | 2026-01-14 08:57 | 0:00 | S/O | Line Row Checking | 9 | 0 | No interruption
Shahmirpur 132/33kV | Sikalbaha-1 | 2026-01-28 10:40 | 2026-01-28 15:05 | 4:25 | S/O | annual maintenance | 0 | 0 | No interruption
Shikalbaha 230/132kV | Hathazari-02 | 2026-01-30 09:04 | 2026-01-30 15:00 | 5:56 | S/O | Annual maintenance | 0 | 0 | No interruption
Sholosohor 132/33kV | Sholoshahar-Khulshi Ckt-1 | 2026-01-05 07:46 | 2026-01-05 14:35 | 6:49 | S/O | Deadline checking by Khulshi Grid | 0 | 0 | No interruption
|  |  | Total : | 1900-01-31 18:41 |  | Unserved Energy: |  | 234.2
Cumilla Grid Circle :
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-1 | 2026-01-03 09:07 | 2026-01-03 17:05 | 7:58 | S/O | 33kv bus 1 & 2 maintenance | 44 | 350.5333 | Power interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-2 | 2026-01-03 09:08 | 2026-01-03 17:10 | 8:02 | S/O | 33kv bus 1 & 2 maintenance | 0 | 0 | No interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-1 | 2026-01-24 07:41 | 2026-01-24 10:04 | 2:23 | S/O | OPGW project work | 32 | 76.2667 | Power interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-2 | 2026-01-24 07:42 | 2026-01-24 10:08 | 2:26 | S/O | OPGW project work | 0 | 0 | No interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-1 | 2026-01-26 07:07 | 2026-01-26 09:14 | 2:07 | S/O | OPGW project work | 32 | 67.7333 | Power interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-2 | 2026-01-26 07:12 | 2026-01-26 09:16 | 2:04 | S/O | OPGW project work | 0 | 0 | No interruption
Bibiana 400/230kV | Bibi-Shahzi Ckt-II | 2026-01-27 08:50 | 2026-01-27 18:32 | 9:42 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV | Bibi-Shahzi Ckt-I | 2026-01-28 09:29 | 2026-01-28 17:12 | 7:43 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV | Bibi-Shahzi Ckt-I | 2026-01-29 09:15 | 2026-01-29 17:29 | 8:14 | S/O | AM | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-1 | 2026-01-01 09:15 | 2026-01-01 14:53 | 5:38 | S/O | AM | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-2 | 2026-01-01 09:32 | 2026-01-01 17:53 | 8:21 | S/O | AM | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-2 | 2026-01-03 09:12 | 2026-01-03 16:13 | 7:01 | S/O | AM | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-2 | 2026-01-04 08:48 | 2026-01-04 15:45 | 6:57 | S/O | AM | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-2 | 2026-01-05 08:44 | 2026-01-05 16:42 | 7:58 | S/O | AM | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-2 | 2026-01-06 08:52 | 2026-01-06 16:44 | 7:52 | S/O | AM | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-2 | 2026-01-07 08:40 | 2026-01-07 16:31 | 7:51 | S/O | AM | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-1 | 2026-01-11 09:23 | 2026-01-11 16:04 | 6:41 | S/O | None | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-1 | 2026-01-12 08:40 | 2026-01-12 16:22 | 7:42 | S/O | ANNUAL MAINTENANCE | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-1 | 2026-01-13 09:00 | 2026-01-13 16:04 | 7:04 | S/O | ANNUAL MAINTENANCE | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-2 | 2026-01-14 08:42 | 2026-01-14 14:42 | 6:00 | S/O | ANNUAL MAINTENANCE | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-2 | 2026-01-15 08:34 | 2026-01-17 07:34 | 47:00 | S/O | annual maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-2 | 2026-01-17 08:43 | 2026-01-17 16:04 | 7:21 | S/O | annual maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-2 | 2026-01-18 08:36 | 2026-01-18 16:01 | 7:25 | S/O | ANNUAL MAINTENANCE | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-1 | 2026-01-27 09:00 | 2026-01-27 14:57 | 5:57 | S/O | Maintenance work | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-1 | 2026-01-31 08:38 | 2026-01-31 17:03 | 8:25 | S/O | Maintenance work | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-1 | 2026-01-31 08:54 | 2026-01-31 13:00 | 4:06 | S/O | Maintenance work | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Kachua Ckt-2 | 2026-01-14 08:35 | 2026-01-14 16:05 | 7:30 | S/O | Line checking and maintenance. | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Kachua Ckt-2 | 2026-01-15 07:57 | 2026-01-15 15:09 | 7:12 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Kachua Ckt-2 | 2026-01-17 09:08 | 2026-01-17 14:03 | 4:55 | S/O | Maintenance work | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Desh Energy Ckt-1 | 2026-01-20 08:20 | 2026-01-20 16:45 | 8:25 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Desh Energy Ckt-1 | 2026-01-21 07:42 | 2026-01-21 11:49 | 4:07 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Desh Energy Ckt-2 | 2026-01-27 08:22 | 2026-01-27 17:20 | 8:58 | S/O | For Annual Maintenance work. | 0 | 0 | No interruption
Chandpur 132/33kV | 33 kV T-2 section | 2026-01-31 08:05 | 2026-01-31 12:58 | 4:53 | S/O | Maintenance (CPBS-2) | 8 | 39.0667 | Power interruption
Chandpur 132/33kV | 33 kV T-5 section | 2026-01-31 08:05 | 2026-01-31 12:58 | 4:53 | S/O | Maintenance (CPBS-2) | 16 | 78.1333 | Power interruption
Chauddagram 132/33kV | Feni-2 | 2026-01-07 08:24 | 2026-01-07 16:22 | 7:58 | S/O | Yearly Maintenanc. | 0 | 0 | No interruption
Chauddagram 132/33kV | Feni-2 | 2026-01-08 08:56 | 2026-01-08 16:21 | 7:25 | S/O | Yearly maintenance | 0 | 0 | No interruption
Chhatak 132/33kV | Sylhet 01 | 2026-01-01 07:34 | 2026-01-01 16:55 | 9:21 | S/O | Dead Line Cheacking | 0 | 0 | No interruption
Chhatak 132/33kV | Sylhet 01 | 2026-01-03 08:57 | 2026-01-03 16:11 | 7:14 | S/O | dead line cheacking | 0 | 0 | No interruption
Chhatak 132/33kV | Sylhet 02 | 2026-01-10 09:29 | 2026-01-10 18:38 | 9:09 | S/O | For Dead Line Checking. | 0 | 0 | No interruption
Chhatak 132/33kV | Sylhet 02 | 2026-01-12 06:43 | 2026-01-12 17:38 | 10:55 | S/O | Dead Line Checking | 0 | 0 | No interruption
Chhatak 132/33kV | Sylhet 02 | 2026-01-13 08:56 | 2026-01-13 17:48 | 8:52 | S/O | Dead Line Cheacking. | 6 | 53.2 | Power interruption
Chhatak 132/33kV | Sylhet 01 | 2026-01-14 09:11 | 2026-01-14 15:15 | 6:04 | S/O | Shutdown for deadline checking | 0 | 0 | No interruption
Chhatak 132/33kV | Sylhet 02 | 2026-01-15 07:33 | 2026-01-15 13:59 | 6:26 | S/O | Shutdown for deadline checking | 7 | 45.0333 | Power interruption
Chowmuhani 132/33kV | Feni line-01 | 2026-01-01 09:18 | 2026-01-01 17:17 | 7:59 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chowmuhani 132/33kV | Feni line-01 | 2026-01-03 09:00 | 2026-01-03 16:28 | 7:28 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Chowmuhani 132/33kV | Feni line-01 | 2026-01-05 09:52 | 2026-01-05 19:03 | 9:11 | S/O | Chowmuhani - Daganbhuiyan ckt-1 OPGW replacement . | 0 | 0 | No interruption
Chowmuhani 132/33kV | Ramganj line-01 | 2026-01-20 10:08 | 2026-01-20 10:08 | 0:00 | S/O | 132/33 kV Chowmuhani AIS Substation with new panels and integrating them into the SAS. | 0 | 0 | No interruption
Chowmuhani 132/33kV | Feni line-01 | 2026-01-28 14:39 | 2026-01-28 17:33 | 2:54 | S/O | Request by Daganbhuiyan Grid | 0 | 0 | No interruption
Chowmuhani 132/33kV | Feni line-02 | 2026-01-28 14:59 | 2026-01-28 17:41 | 2:42 | S/O | Request by Daganbhuiyan Grid | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 132KV Cumilla(N)-Kachua Ckt-1 | 2026-01-10 08:53 | 2026-01-10 15:30 | 6:37 | S/O | Annual maintenance | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Cumilla North-1 | 2026-01-08 12:53 | 2026-01-08 15:37 | 2:44 | S/O | Annual Maintenance | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Tripura Ckt-2 | 2026-01-18 09:48 | 2026-01-18 15:57 | 6:09 | S/O | Annual Bay maintenance | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Cumilla North-2 | 2026-01-21 08:48 | 2026-01-21 17:11 | 8:23 | S/O | Annual maintenance. | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Cumilla North-1 | 2026-01-24 07:46 | 2026-01-24 13:39 | 5:53 | S/O | Annual Maintenance | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Cumilla North-3 | 2026-01-28 08:11 | 2026-01-28 17:18 | 9:07 | S/O | Annual Maintenance | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Cumilla North-2 | 2026-01-29 08:25 | 2026-01-29 23:46 | 15:21 | S/O | Annual maintenance. | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Cumilla North-3 | 2026-01-31 08:46 | 2026-01-31 17:05 | 8:19 | S/O | Annual Maintenance | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Chowmuhuni ckt-1 | 2026-01-01 09:14 | 2026-01-01 17:39 | 8:25 | S/O | Deadline Checkout | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Chowmuhuni ckt-1 | 2026-01-03 09:02 | 2026-01-03 16:28 | 7:26 | S/O | Deadline Check | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Feni Ckt-1 | 2026-01-04 08:55 | 2026-01-04 15:43 | 6:48 | S/O | Deadline check | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Feni Ckt-2 | 2026-01-22 08:32 | 2026-01-28 13:38 | 149:06 | S/O | Deadline Checking | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Feni Ckt-1 | 2026-01-28 10:22 | 2026-01-28 14:27 | 4:05 | S/O | Parameter test | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Chowmuhuni ckt-1 | 2026-01-28 14:38 | 2026-01-28 17:35 | 2:57 | S/O | Project work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Chowmuhani Ckt-2 | 2026-01-28 14:58 | 2026-01-28 17:45 | 2:47 | S/O | Project work | 0 | 0 | No interruption
Daudkandi 132/33kV | Sonargaon-1 | 2026-01-13 09:05 | 2026-01-13 16:11 | 7:06 | S/O | Annual Maintenance | 0 | 0 | No interruption
Daudkandi 132/33kV | Sonargaon-1 | 2026-01-14 09:06 | 2026-01-14 16:32 | 7:26 | S/O | Shutdown for annual maintenance work. | 0 | 0 | No interruption
Daudkandi 132/33kV | Sonargaon-1 | 2026-01-15 08:32 | 2026-01-15 15:45 | 7:13 | S/O | Maintenance work at Sonargaon Substation | 0 | 0 | No interruption
Daudkandi 132/33kV | Sonargaon-1 | 2026-01-17 08:21 | 2026-01-17 15:04 | 6:43 | S/O | Maintenance work at Sonargaon Substation side | 0 | 0 | No interruption
Daudkandi 132/33kV | Sonargaon-2 | 2026-01-18 08:22 | 2026-01-18 17:00 | 8:38 | S/O | Maintenance work at Sonargaon SS side | 0 | 0 | No interruption
Daudkandi 132/33kV | Sonargaon-2 | 2026-01-19 08:22 | 2026-01-19 15:32 | 7:10 | S/O | Annual maintenance | 0 | 0 | No interruption
Daudkandi 132/33kV | Cumilla(N)-1 | 2026-01-21 08:44 | 2026-01-21 15:30 | 6:46 | S/O | Muradnagar-1 Line shutdown for Annual Maintenance work | 0 | 0 | No interruption
Daudkandi 132/33kV | Cumilla(N)-2 | 2026-01-22 08:41 | 2026-01-22 16:14 | 7:33 | S/O | Annual Maintenance | 0 | 0 | No interruption
Daudkandi 132/33kV | Cumilla(N)-1 | 2026-01-24 09:01 | 2026-01-24 15:25 | 6:24 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Daudkandi 132/33kV | Cumilla(N)-2 | 2026-01-26 09:06 | 2026-01-26 15:10 | 6:04 | S/O | Dead line checking | 0 | 0 | No interruption
Daudkandi 132/33kV | Sonargaon-2 | 2026-01-28 08:41 | 2026-01-28 15:37 | 6:56 | S/O | 132 KV Sonargaon-2 Line Shutdown for annual maintenance work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sylhet-2 | 2026-01-03 09:12 | 2026-01-03 17:00 | 7:48 | S/O | Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Bibiyana-1 | 2026-01-05 07:51 | 2026-01-05 17:50 | 9:59 | S/O | Deadline checking. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Bibiyana-2 | 2026-01-05 18:08 | 2026-01-05 19:14 | 1:06 | S/O | maintenace work of Bibiyana grid end | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Bibiyana-1 | 2026-01-06 08:41 | 2026-01-06 17:55 | 9:14 | S/O | deadline cheaking | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Bibiyana-2 | 2026-01-07 07:48 | 2026-01-07 17:45 | 9:57 | S/O | Deadline Checking | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Bibiyana-2 | 2026-01-08 07:38 | 2026-01-08 18:04 | 10:26 | S/O | Deadline Checking | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-3 | 2026-01-10 13:43 | 2026-01-10 20:31 | 6:48 | S/O | OFCN Work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-3 | 2026-01-11 09:26 | 2026-01-11 18:49 | 9:23 | S/O | OPGW work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-3 | 2026-01-12 09:22 | 2026-01-12 18:56 | 9:34 | S/O | OFCN Work. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-3 | 2026-01-13 08:45 | 2026-01-13 18:41 | 9:56 | S/O | OPCN Work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-1 | 2026-01-13 10:03 | 2026-01-13 16:39 | 6:36 | S/O | 132kv Bus-02 Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sreemongal-1 | 2026-01-13 14:54 | 2026-01-13 16:00 | 1:06 | S/O | Annual maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-2 | 2026-01-13 16:48 | 2026-01-13 18:13 | 1:25 | S/O | 132kv Bus-02 Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Bibiyana-2 | 2026-01-17 07:41 | 2026-01-17 17:35 | 9:54 | S/O | Deadline Checking. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Bibiyana-2 | 2026-01-18 07:42 | 2026-01-18 16:29 | 8:47 | S/O | Deadline Cheacking | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Kulaura-1 | 2026-01-19 09:08 | 2026-01-19 10:27 | 1:19 | S/O | Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Kulaura-2 | 2026-01-19 10:30 | 2026-01-19 15:19 | 4:49 | S/O | Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sreemongal-2 | 2026-01-19 15:42 | 2026-01-19 16:40 | 0:58 | S/O | Annual maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sreemongal-1 | 2026-01-20 09:44 | 2026-01-20 12:13 | 2:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-3 | 2026-01-20 10:52 | 2026-01-20 12:49 | 1:57 | S/O | Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-2 | 2026-01-20 12:53 | 2026-01-20 15:29 | 2:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-1 | 2026-01-20 15:37 | 2026-01-20 17:13 | 1:36 | S/O | 132kV BUS-01 Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sreemongal-1 | 2026-01-21 09:02 | 2026-01-21 17:36 | 8:34 | S/O | For deadline checking. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-3 | 2026-01-23 07:17 | 2026-01-23 21:31 | 14:14 | S/O | Fechuganj Power Station work & OFCN Work(For OPGW upgradation ) | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sreemongal-1 | 2026-01-23 08:22 | 2026-01-23 16:23 | 8:01 | S/O | For deadline checking. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-1 | 2026-01-23 15:20 | 2026-01-23 19:49 | 4:29 | S/O | Fenchuganj 90MW power station end work. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-2 | 2026-01-23 15:20 | 2026-01-23 20:39 | 5:19 | S/O | Fenchuganj 90MW power station end work. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sylhet-2 | 2026-01-24 07:42 | 2026-01-24 09:53 | 2:11 | S/O | For OPGW upgradation work. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sreemongal-2 | 2026-01-24 08:18 | 2026-01-24 16:32 | 8:14 | S/O | Deadline Checking. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sreemongal-2 | 2026-01-25 07:44 | 2026-01-25 15:48 | 8:04 | S/O | Deadline Checking | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sylhet-2 | 2026-01-26 07:15 | 2026-01-26 09:11 | 1:56 | S/O | Sylhet south SS end loop connection between two ckt by OFCN | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-3 | 2026-01-26 10:31 | 2026-01-26 20:49 | 10:18 | S/O | OPGW upgradation work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-3 | 2026-01-27 09:25 | 2026-01-27 15:30 | 6:05 | S/O | loop connect to sylhet ckt 1 | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-2 | 2026-01-28 08:57 | 2026-01-28 16:41 | 7:44 | S/O | For deadline checking | 0 | 0 | No interruption
Feni 132/33kV | Feni Ckt-1 | 2026-01-05 09:26 | 2026-01-05 16:18 | 6:52 | S/O | S/D Taken for AMS=2025-26 (Bay) | 0 | 0 | No interruption
Feni 132/33kV | Feni Ckt-2 | 2026-01-06 09:05 | 2026-01-06 15:30 | 6:25 | S/O | for annual maintenance. | 0 | 0 | No interruption
Feni 132/33kV | Feni Ckt-4 | 2026-01-07 08:56 | 2026-01-07 15:42 | 6:46 | S/O | For annual maintenance | 0 | 0 | No interruption
Feni 132/33kV | Feni Ckt-4 | 2026-01-08 08:54 | 2026-01-08 16:14 | 7:20 | S/O | Deadline Check | 0 | 0 | No interruption
Feni 132/33kV | PHP (ISML) Ckt | 2026-01-12 08:34 | 2026-01-12 18:45 | 10:11 | S/O | Annual maintenance work | 0 | 0 | No interruption
Feni 132/33kV | Barayerhat Ckt | 2026-01-13 09:20 | 2026-01-13 14:45 | 5:25 | S/O | S/D taken for AMS-2025-26 | 0 | 0 | No interruption
Feni 132/33kV | Barayerhat Ckt | 2026-01-14 09:09 | 2026-01-14 16:28 | 7:19 | S/O | For Annual maintenance | 0 | 0 | No interruption
Feni 132/33kV | PHP (ISML) Ckt | 2026-01-15 08:24 | 2026-01-15 16:10 | 7:46 | S/O | For Annual Maintenance Deadline Checking | 0 | 0 | No interruption
Feni 230/132kV | Dagonbhuyan-1 | 2026-01-04 09:00 | 2026-01-04 15:42 | 6:42 | S/O | Annual Deadline checking 2025_2026 | 0 | 0 | No interruption
Feni 230/132kV | Feni-2 | 2026-01-06 09:06 | 2026-01-06 15:29 | 6:23 | S/O | Feni 132kv end annual maintenance. | 0 | 0 | No interruption
Feni 230/132kV | Chauddagram-2 | 2026-01-07 08:25 | 2026-01-07 16:21 | 7:56 | S/O | Annual maintenance chauddagram end | 0 | 0 | No interruption
Feni 230/132kV | Feni-4 | 2026-01-07 08:57 | 2026-01-07 15:41 | 6:44 | S/O | feni end Annual maintenance | 0 | 0 | No interruption
Feni 230/132kV | Feni-4 | 2026-01-08 08:57 | 2026-01-08 16:13 | 7:16 | S/O | Annual maintenance | 0 | 0 | No interruption
Feni 230/132kV | Chauddagram-2 | 2026-01-08 08:58 | 2026-01-08 16:21 | 7:23 | S/O | Annual maintenance | 0 | 0 | No interruption
Feni 230/132kV | Feni-3 | 2026-01-20 11:10 | 2026-01-20 19:55 | 8:45 | S/O | circuit breaker work | 0 | 0 | No interruption
Feni 230/132kV | Korarhat-1 | 2026-01-21 09:33 | 2026-01-21 14:41 | 5:08 | S/O | 230 kv korerhat ckt-1 s/d due to project work | 0 | 0 | No interruption
Feni 230/132kV | Dagonbhuyan-2 | 2026-01-22 08:33 | 2026-01-28 13:38 | 149:05 | S/O | Shutdown due to annual deadline checking | 0 | 0 | No interruption
Feni 230/132kV | Cumilla(North)-1 | 2026-01-22 09:41 | 2026-01-28 15:31 | 149:50 | S/O | Shutdown due to annual deadline checking | 0 | 0 | No interruption
Feni 230/132kV | Dagonbhuyan-1 | 2026-01-28 10:15 | 2026-01-28 14:28 | 4:13 | S/O | Line parameter test | 0 | 0 | No interruption
Feni 230/132kV | Cumilla(North)-2 | 2026-01-29 08:43 | 2026-01-29 15:07 | 6:24 | S/O | For disc cleaning works | 0 | 0 | No interruption
Kachua 230/132/33kV | Cumilla North CKT | 2026-01-08 08:00 | 2026-01-08 16:02 | 8:02 | S/O | For annual maintenance work. | 0 | 0 | No interruption
Kachua 230/132/33kV | Cumilla North CKT | 2026-01-10 08:52 | 2026-01-10 15:30 | 6:38 | S/O | Annual maintenance | 0 | 0 | No interruption
Kachua 230/132/33kV | Cumilla North CKT | 2026-01-11 08:30 | 2026-01-11 15:05 | 6:35 | S/O | for annual maintenance work. | 0 | 0 | No interruption
Kachua 230/132/33kV | Chandpur CKT-2 | 2026-01-14 08:28 | 2026-01-14 16:08 | 7:40 | S/O | Annual maintenance | 0 | 0 | No interruption
Kachua 230/132/33kV | Chandpur CKT-2 | 2026-01-15 07:50 | 2026-01-15 15:09 | 7:19 | S/O | for maintenance work. | 0 | 0 | No interruption
Kachua 230/132/33kV | Chandpur CKT-2 | 2026-01-17 09:02 | 2026-01-17 13:58 | 4:56 | S/O | Annual maintenance | 0 | 0 | No interruption
Kachua 230/132/33kV | Laksam CKT-1 | 2026-01-26 12:02 | 2026-01-26 16:04 | 4:02 | S/O | Project Work | 0 | 0 | No interruption
Kachua 230/132/33kV | Laksam CKT-2 | 2026-01-26 14:45 | 2026-01-26 17:01 | 2:16 | S/O | Project Work | 0 | 0 | No interruption
Kasba 132/33kV | Muradnagar-Kasba Ckt-1 | 2026-01-02 08:51 | 2026-01-02 15:00 | 6:09 | S/O | Remove birds net, kites and others obstacles by Project | 0 | 0 | No interruption
Kasba 132/33kV | Muradnagar-Kasba Ckt-2 | 2026-01-03 09:00 | 2026-01-03 14:44 | 5:44 | S/O | Remove bird nest kites and other obstacles | 0 | 0 | No interruption
Kasba 132/33kV | Muradnagar-Kasba Ckt-1 | 2026-01-28 12:14 | 2026-01-28 14:03 | 1:49 | S/O | check phase sequence | 0 | 0 | No interruption
Kulaura 132/33kV | 132 Fenchuganj-1 | 2026-01-12 09:05 | 2026-01-12 12:48 | 3:43 | S/O | Fenchuganj Grid Annual maintenance. | 0 | 0 | No interruption
Kulaura 132/33kV | 132 Fenchuganj-2 | 2026-01-12 12:56 | 2026-01-12 13:40 | 0:44 | S/O | Fenchuganj grid annual maintenance | 0 | 0 | No interruption
Kulaura 132/33kV | 132 Fenchuganj-1 | 2026-01-19 09:01 | 2026-01-19 10:30 | 1:29 | S/O | Fenchuganj ckt-1 shutdown for maintenance by NLDC AE | 0 | 0 | No interruption
Kulaura 132/33kV | 132 Fenchuganj-2 | 2026-01-19 10:31 | 2026-01-19 15:22 | 4:51 | S/O | Fenchuganj ckt-2 shutdown for maintenance by NLDC AE | 0 | 0 | No interruption
Lakshmipur 132/33kV | Lakshmipur-Chowmuhani Circuit 1 | 2026-01-06 10:51 | 2026-01-06 14:35 | 3:44 | S/O | Line Parameter Measurement | 0 | 0 | No interruption
Maijdee 132/33kV | Chowmuhoni-Maijdee ckt -01 | 2026-01-06 10:15 | 2026-01-06 14:54 | 4:39 | S/O | Line parameter test for project work. | 0 | 0 | No interruption
Maijdee 132/33kV | Chowmuhoni-Maijdee ckt -02 | 2026-01-06 10:37 | 2026-01-06 14:58 | 4:21 | S/O | Line parameter test for project work. | 0 | 0 | No interruption
Muradnagar 132/33kV | 132 KV Muradnagar- Kosba Ckt-01 | 2026-01-02 08:58 | 2026-01-02 14:58 | 6:00 | S/O | project work | 0 | 0 | No interruption
Muradnagar 132/33kV | 132 KV Muradnagar- Kosba Ckt-02 | 2026-01-03 08:56 | 2026-01-03 14:43 | 5:47 | S/O | Remove bird nest and other obstacles | 0 | 0 | No interruption
Muradnagar 132/33kV | 132 KV Muradnagar- Cumilla(N) Ckt-01 | 2026-01-09 08:51 | 2026-01-09 12:08 | 3:17 | S/O | Maintenance period | 0 | 0 | No interruption
Muradnagar 132/33kV | 132 KV Muradnagar- Cumilla(N) Ckt-02 | 2026-01-09 12:09 | 2026-01-09 14:53 | 2:44 | S/O | Maintenance work | 0 | 0 | No interruption
Muradnagar 132/33kV | 132 KV Muradnagar- Cumilla(N) Ckt-01 | 2026-01-19 09:53 | 2026-01-19 15:49 | 5:56 | S/O | maintenance work | 0 | 0 | No interruption
Muradnagar 132/33kV | 132 KV Muradnagar- Cumilla(N) Ckt-01 | 2026-01-20 09:40 | 2026-01-20 15:23 | 5:43 | S/O | Maintenance Work | 0 | 0 | No interruption
Muradnagar 132/33kV | 132 KV Muradnagar- Daudkandi Ckt-01 | 2026-01-21 08:45 | 2026-01-21 15:29 | 6:44 | S/O | deadline check | 0 | 0 | No interruption
Muradnagar 132/33kV | 132 KV Muradnagar- Cumilla(N) Ckt-02 | 2026-01-21 09:04 | 2026-01-21 17:42 | 8:38 | S/O | Deadline check | 0 | 0 | No interruption
Muradnagar 132/33kV | 132 KV Muradnagar- Daudkandi Ckt-02 | 2026-01-22 08:42 | 2026-01-22 16:13 | 7:31 | S/O | Deadline Check | 0 | 0 | No interruption
Muradnagar 132/33kV | 132 KV Muradnagar- Cumilla(N) Ckt-01 | 2026-01-22 09:41 | 2026-01-22 12:46 | 3:05 | S/O | Deadline Check | 0 | 0 | No interruption
Muradnagar 132/33kV | 132 KV Muradnagar- Cumilla(N) Ckt-02 | 2026-01-22 12:47 | 2026-01-22 14:31 | 1:44 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Muradnagar 132/33kV | 132 KV Muradnagar- Daudkandi Ckt-01 | 2026-01-24 09:02 | 2026-01-24 15:25 | 6:23 | S/O | Maintenance work | 0 | 0 | No interruption
Muradnagar 132/33kV | 132 KV Muradnagar- Daudkandi Ckt-02 | 2026-01-26 09:26 | 2026-01-26 15:10 | 5:44 | S/O | Line checking | 0 | 0 | No interruption
Muradnagar 132/33kV | 132 KV Muradnagar- Kosba Ckt-01 | 2026-01-28 12:10 | 2026-01-28 14:02 | 1:52 | S/O | Maintenance Work | 0 | 0 | No interruption
Ramganj 132/33kV | Ramgonj-Desh Energy Ckt-02 | 2026-01-12 08:29 | 2026-01-12 15:47 | 7:18 | S/O | Annual Maintenance | 0 | 0 | No interruption
Ramganj 132/33kV | Ramgonj-Desh Energy Ckt-02 | 2026-01-20 08:34 | 2026-01-20 15:16 | 6:42 | S/O | IVT Replacement Work (B phase) . | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-01 | 2026-01-01 09:08 | 2026-01-01 14:54 | 5:46 | S/O | Shutdown for annual maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-02 | 2026-01-03 09:13 | 2026-01-03 15:46 | 6:33 | S/O | Shutdown for annual maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-02 | 2026-01-04 08:47 | 2026-01-04 15:46 | 6:59 | S/O | Annaul Maintenance. | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-02 | 2026-01-05 08:43 | 2026-01-05 16:34 | 7:51 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-02 | 2026-01-06 08:50 | 2026-01-06 16:44 | 7:54 | S/O | Annaul Maintenance. | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-02 | 2026-01-07 08:41 | 2026-01-07 16:32 | 7:51 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-2 | 2026-01-12 13:15 | 2026-01-12 17:36 | 4:21 | S/O | For Bus maintenance at Fen SS. | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-1 | 2026-01-23 08:21 | 2026-01-23 16:25 | 8:04 | S/O | For maintenance work at Fenchuganj SS. | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-2 | 2026-01-24 08:16 | 2026-01-24 16:33 | 8:17 | S/O | Dead Line checking at Fenchuganj End. | 0 | 0 | No interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-1 | 2026-01-03 09:12 | 2026-01-03 17:02 | 7:50 | S/O | For Fenchugonj grid schedule shutdown. | 0 | 0 | No interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-2 | 2026-01-03 09:13 | 2026-01-03 17:02 | 7:49 | S/O | For Fenchugonj grid schedule shutdown. | 0 | 0 | No interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-1 | 2026-01-24 07:41 | 2026-01-26 09:14 | 49:33 | S/O | opgw change work. | 0 | 0 | No interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-2 | 2026-01-24 07:41 | 2026-01-24 11:40 | 3:59 | S/O | opgw change work | 0 | 0 | No interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-2 | 2026-01-26 07:12 | 2026-01-26 09:14 | 2:02 | S/O | OFCN works | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2026-01-01 07:33 | 2026-01-01 16:50 | 9:17 | S/O | Dead Line Checking | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2026-01-03 09:00 | 2026-01-03 16:09 | 7:09 | S/O | Dead line checking | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2026-01-04 09:02 | 2026-01-04 18:50 | 9:48 | S/O | SD by GIS Project SAE ZIarul Islam | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Sylhet (S) Ckt | 2026-01-05 08:24 | 2026-01-05 10:42 | 2:18 | S/O | GIS Project work Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-2 | 2026-01-10 09:49 | 2026-01-10 18:37 | 8:48 | S/O | dead line checking | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2026-01-10 09:55 | 2026-01-10 19:25 | 9:30 | S/O | OPGW change | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2026-01-11 09:28 | 2026-01-11 19:58 | 10:30 | S/O | CB Open Request by NLDC AE Desk | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-2 | 2026-01-12 06:48 | 2026-01-12 17:37 | 10:49 | S/O | Sylhet-Chatak CKT-2 SD due to CB pole Replace at Chatak Grid SS Direction by NLDC (01713201801). | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2026-01-12 08:51 | 2026-01-12 19:00 | 10:09 | S/O | Operation Direction by NlDC AE Desk | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-2 | 2026-01-13 08:57 | 2026-01-13 17:53 | 8:56 | S/O | Deadline Checking Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2026-01-13 09:19 | 2026-01-13 18:01 | 8:42 | S/O | OPGW Change purpose. | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2026-01-14 07:07 | 2026-01-14 18:21 | 11:14 | S/O | OPGW change | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2026-01-14 09:13 | 2026-01-14 15:13 | 6:00 | S/O | Dead Line Checking Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2026-01-15 06:42 | 2026-01-15 19:10 | 12:28 | S/O | Due to OPGW Replace work CB Open direction by NLDC (AE Desk) | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2026-01-16 07:35 | 2026-01-16 18:48 | 11:13 | S/O | OPGW change | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2026-01-18 07:30 | 2026-01-18 18:35 | 11:05 | S/O | OPGW Replacement | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2026-01-19 07:21 | 2026-01-19 19:59 | 12:38 | S/O | OPGW wire change | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2026-01-20 09:28 | 2026-01-20 19:40 | 10:12 | S/O | OPGW change Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2026-01-21 07:29 | 2026-01-21 14:37 | 7:08 | S/O | OPGW Replace | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2026-01-21 07:29 | 2026-01-21 14:37 | 7:08 | S/O | OPGW Replace | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2026-01-23 07:16 | 2026-01-23 21:32 | 14:16 | S/O | Looping for Fenchuganj ckt-3 to 90 MW PS ckt. | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Sylhet (S) Ckt | 2026-01-24 12:02 | 2026-01-24 19:20 | 7:18 | S/O | OPGW Replacement work by OFCN. | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Sylhet (S) Ckt | 2026-01-25 08:21 | 2026-01-25 17:28 | 9:07 | S/O | SD Request by SDE Mojaffor , OFCEN, Due to OPGW Replace. | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2026-01-26 10:26 | 2026-01-26 20:35 | 10:09 | S/O | OPGW change Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2026-01-27 09:25 | 2026-01-27 15:36 | 6:11 | S/O | 90 MW PS CKT Loop Connection | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2026-01-29 08:39 | 2026-01-29 18:21 | 9:42 | S/O | Dead Line Checking Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Sylhet (S) Ckt | 2026-01-31 09:05 | 2026-01-31 16:23 | 7:18 | S/O | Dead Line checking purpose, shutdown taken by AE, Sylhet S/S | 0 | 0 | No interruption
|  |  | Total : | 1900-03-18 05:01 |  | Unserved Energy: |  | 709.9667
Khulna Grid Circle :
Amtali 400/132kV | Amtali - RNPL 400 kV Ckt - 2 | 2026-01-22 19:49 | 2026-01-22 21:50 | 2:01 | S/O | Annual Maintenance Purpose | 0 | 0 | No interruption
Amtali 400/132kV | Amtali - RNPL 400 kV Ckt - 1 | 2026-01-22 21:16 | 2026-01-22 21:16 | 0:00 | S/O | Protection Relay Maintenance | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Mongla 2 | 2026-01-07 09:43 | 2026-01-07 15:55 | 6:12 | S/O | Annual maintenance | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Mongla 2 | 2026-01-08 09:27 | 2026-01-08 15:56 | 6:29 | S/O | Yearly maintenance | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Goalpara Line | 2026-01-13 08:39 | 2026-01-13 16:50 | 8:11 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Goalpara Line | 2026-01-14 08:21 | 2026-01-14 16:40 | 8:19 | S/O | Annual maintenance | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Goalpara Line | 2026-01-15 08:16 | 2026-01-15 16:03 | 7:47 | S/O | 132kv Goalpara Line Annual Maintenance from Goalpara End | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2026-01-17 07:21 | 2026-01-17 18:12 | 10:51 | S/O | Bus Shut down at Bhandaria S/S. | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Orion P/S Line | 2026-01-17 08:43 | 2026-01-17 16:11 | 7:28 | S/O | Yearly maintenance work by Goalpara Grid S/S. | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Orion P/S Line | 2026-01-18 08:28 | 2026-01-18 16:09 | 7:41 | S/O | Annual maintenance | 0 | 0 | No interruption
Bakerganj 132/33kV | 132 kV Bakerganj Patuakhali Ckt | 2026-01-10 07:25 | 2026-01-10 17:54 | 10:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bakerganj 132/33kV | 132 kV Bakerganj Barguna Ckt | 2026-01-10 07:25 | 2026-01-10 18:08 | 10:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barguna 132/33kV | Barguna-Bakergonj 132kv line | 2026-01-10 07:21 | 2026-01-10 18:08 | 10:47 | S/O | Patuakhali- Barishal North 230kv Line project Work. | 12 | 129.4 | Power interruption
Barishal 132/33kV | 132kv Bhandaria ckt | 2026-01-17 07:25 | 2026-01-17 17:32 | 10:07 | S/O | Annual busber maintenance | 0 | 0 | No interruption
Barishal 132/33kV | 132kv Bhandaria ckt | 2026-01-17 17:35 | 2026-01-17 17:52 | 0:17 | S/O | Shutdown by ALDC | 0 | 0 | No interruption
Barishal 230/132kV | Bhola Ckt-1 | 2026-01-10 07:41 | 2026-01-10 17:23 | 9:42 | S/O | annual mainntenance | 0 | 0 | No interruption
Barishal 230/132kV | Bhola Ckt-1 | 2026-01-11 08:03 | 2026-01-11 17:25 | 9:22 | S/O | Annual maintenance | 0 | 0 | No interruption
Barishal 230/132kV | Bhola Ckt-1 | 2026-01-12 08:15 | 2026-01-12 17:33 | 9:18 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barishal 230/132kV | Bhola Ckt-2 | 2026-01-13 07:57 | 2026-01-13 17:02 | 9:05 | S/O | Annual maintenance | 0 | 0 | No interruption
Barishal 230/132kV | Bhola Ckt-2 | 2026-01-14 08:27 | 2026-01-14 16:55 | 8:28 | S/O | annual maintenance | 0 | 0 | No interruption
Barishal 230/132kV | Bhola Ckt-2 | 2026-01-15 07:34 | 2026-01-15 16:24 | 8:50 | S/O | Annual Maintenance | 0 | 0 | No interruption
Benapole 132/33kV | Jashore-2 | 2026-01-01 08:49 | 2026-01-01 16:02 | 7:13 | S/O | annual maintenance work. | 0 | 0 | No interruption
Bhandaria 132/33kV | Barishal (L4) | 2026-01-17 07:26 | 2026-01-17 17:53 | 10:27 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhandaria 132/33kV | Bagerhat (L3) | 2026-01-17 07:45 | 2026-01-17 18:12 | 10:27 | S/O | Annual maintenance | 26 | 271.7 | Power interruption
Faridpur 132/33kV | 132 KV Rajbari ckt-2 | 2026-01-17 08:50 | 2026-01-17 20:58 | 12:08 | S/O | Annual maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | 132 KV Gopalganj (400kv) ckt-1 | 2026-01-24 09:11 | 2026-01-24 15:54 | 6:43 | S/O | Annual maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | 132 KV Gopalganj (400kv) ckt-2 | 2026-01-24 09:13 | 2026-01-24 15:55 | 6:42 | S/O | Annual maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | 132 KV Gopalganj (400kv) ckt-1 | 2026-01-25 08:58 | 2026-01-25 17:20 | 8:22 | S/O | Annual Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | 132 KV Gopalganj (400kv) ckt-2 | 2026-01-25 08:58 | 2026-01-25 17:21 | 8:23 | S/O | Annual Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | 132 KV Gopalganj (400kv) ckt-1 | 2026-01-26 09:04 | 2026-01-26 16:29 | 7:25 | S/O | Annual maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | 132 KV Gopalganj (400kv) ckt-2 | 2026-01-26 09:05 | 2026-01-26 16:29 | 7:24 | S/O | Annual maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | 132 KV Gopalganj (400kv) ckt-1 | 2026-01-27 09:35 | 2026-01-27 15:39 | 6:04 | S/O | Annual Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | 132 KV Gopalganj (400kv) ckt-2 | 2026-01-27 09:35 | 2026-01-27 15:39 | 6:04 | S/O | Annual Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-1 | 2026-01-28 09:01 | 2026-01-28 15:16 | 6:15 | S/O | Annual Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-2 | 2026-01-29 09:03 | 2026-01-29 12:45 | 3:42 | S/O | Maintenance at Gopalganj 400kV SS end. | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Khulna Central-1 | 2026-01-03 10:09 | 2026-01-03 14:57 | 4:48 | S/O | Annual Maintenance | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Khulna Central-1 | 2026-01-04 10:45 | 2026-01-04 15:46 | 5:01 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-NWPGCL | 2026-01-05 09:27 | 2026-01-05 15:50 | 6:23 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Bagerhat | 2026-01-13 09:03 | 2026-01-13 16:50 | 7:47 | S/O | Annual maintenance | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Bagerhat | 2026-01-14 08:23 | 2026-01-14 16:32 | 8:09 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Bagerhat | 2026-01-15 08:17 | 2026-01-15 16:02 | 7:45 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Orion | 2026-01-19 09:01 | 2026-01-19 16:39 | 7:38 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Orion | 2026-01-20 09:26 | 2026-01-20 14:41 | 5:15 | S/O | Annual Maintenence works. | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Bagerhat | 2026-01-24 08:36 | 2026-01-24 14:33 | 5:57 | S/O | For annual Maintenance work | 0 | 0 | No interruption
Gollamari 132/33kV | E01 Gollamari-Gopalgonj Line - 1 | 2026-01-28 08:47 | 2026-01-28 16:57 | 8:10 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Gollamari 132/33kV | E07 Gollamari-Gopalgonj Line - 2 | 2026-01-28 08:47 | 2026-01-28 17:00 | 8:13 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Gollamari 132/33kV | E03 Gollamari-Khulna(S) Line-1 | 2026-01-31 08:18 | 2026-01-31 08:18 | 0:00 | S/O | None | 0 | 0 | No interruption
Gollamari 132/33kV | E05 Gollamari-Khulna(S) Line-2 | 2026-01-31 11:47 | 2026-01-31 11:47 | 0:00 | S/O | OPGW Change. | 0 | 0 | No interruption
Gopalganj 132/33kV | Modhumoti 100MW PS | 2026-01-13 08:28 | 2026-01-13 17:08 | 8:40 | S/O | Yearly maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV | Modhumoti 100MW PS | 2026-01-14 08:24 | 2026-01-14 16:45 | 8:21 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV | Gallamari-1 | 2026-01-28 08:48 | 2026-01-28 16:59 | 8:11 | S/O | Annual maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV | Gallamari-2 | 2026-01-28 08:48 | 2026-01-28 17:03 | 8:15 | S/O | Annual maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Amtoli Ckt-1 | 2026-01-01 08:39 | 2026-01-01 17:22 | 8:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Amtoli Ckt-1 | 2026-01-02 08:36 | 2026-01-02 17:31 | 8:55 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Amtoli Ckt-2 | 2026-01-03 08:42 | 2026-01-03 17:18 | 8:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Aminbazar Ckt-1 | 2026-01-03 09:23 | 2026-01-03 17:07 | 7:44 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Aminbazar Ckt-1 | 2026-01-04 07:45 | 2026-01-04 17:15 | 9:30 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Amtoli Ckt-2 | 2026-01-04 08:40 | 2026-01-04 17:03 | 8:23 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Amtoli Ckt-2 | 2026-01-05 08:19 | 2026-01-05 17:01 | 8:42 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Aminbazar Ckt-1 | 2026-01-05 08:52 | 2026-01-05 16:35 | 7:43 | S/O | Annual | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Amtoli Ckt-2 | 2026-01-06 09:28 | 2026-01-06 17:06 | 7:38 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Aminbazar Ckt-2 | 2026-01-06 09:28 | 2026-01-06 17:06 | 7:38 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Amtoli Ckt-2 | 2026-01-07 08:21 | 2026-01-07 16:45 | 8:24 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Aminbazar Ckt-2 | 2026-01-07 09:31 | 2026-01-07 16:09 | 6:38 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Aminbazar Ckt-2 | 2026-01-08 08:31 | 2026-01-08 17:46 | 9:15 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Amtoli Ckt-2 | 2026-01-08 09:21 | 2026-01-08 17:33 | 8:12 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Amtoli Ckt-2 | 2026-01-10 09:30 | 2026-01-10 17:42 | 8:12 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Amtoli Ckt-2 | 2026-01-15 09:17 | 2026-01-15 12:14 | 2:57 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Amtoli Ckt-1 | 2026-01-16 07:50 | 2026-01-16 16:30 | 8:40 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Aminbazar Ckt-1 | 2026-01-16 08:47 | 2026-01-16 21:14 | 12:27 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Amtoli Ckt-1 | 2026-01-17 09:24 | 2026-01-17 17:00 | 7:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2026-01-17 09:40 | 2026-01-17 16:39 | 6:59 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Aminbazar Ckt-2 | 2026-01-17 09:42 | 2026-01-17 15:38 | 5:56 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rampal Ckt-1 | 2026-01-18 08:48 | 2026-01-18 16:21 | 7:33 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Amtoli Ckt-1 | 2026-01-18 09:07 | 2026-01-18 16:16 | 7:09 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rampal Ckt-1 | 2026-01-19 09:18 | 2026-01-19 17:02 | 7:44 | S/O | Annual maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rampal Ckt-1 | 2026-01-20 08:46 | 2026-01-20 16:35 | 7:49 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-3 | 2026-01-20 09:19 | 2026-01-20 16:41 | 7:22 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-4 | 2026-01-20 09:27 | 2026-01-20 16:44 | 7:17 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-3 | 2026-01-21 08:42 | 2026-01-21 17:16 | 8:34 | S/O | Annual Maintenance at Madaripur SS End | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-4 | 2026-01-21 08:44 | 2026-01-21 17:16 | 8:32 | S/O | Annual Maintenance at Madaripur SS end. | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rampal Ckt-1 | 2026-01-21 09:38 | 2026-01-21 16:41 | 7:03 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rampal Ckt-2 | 2026-01-22 07:56 | 2026-01-22 16:52 | 8:56 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-3 | 2026-01-22 08:45 | 2026-01-22 17:16 | 8:31 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-4 | 2026-01-22 08:49 | 2026-01-22 17:23 | 8:34 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rampal Ckt-2 | 2026-01-23 08:27 | 2026-01-23 16:29 | 8:02 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-3 | 2026-01-23 10:27 | 2026-01-23 15:24 | 4:57 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-4 | 2026-01-23 10:30 | 2026-01-23 15:24 | 4:54 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rampal Ckt-2 | 2026-01-24 08:53 | 2026-01-24 17:00 | 8:07 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Faridpur Ckt-1 | 2026-01-24 09:12 | 2026-01-24 15:53 | 6:41 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Faridpur Ckt-2 | 2026-01-24 09:13 | 2026-01-24 15:54 | 6:41 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rampal Ckt-2 | 2026-01-25 08:34 | 2026-01-25 17:03 | 8:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Faridpur Ckt-1 | 2026-01-25 08:57 | 2026-01-25 17:18 | 8:21 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Faridpur Ckt-2 | 2026-01-25 08:58 | 2026-01-25 17:20 | 8:22 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Faridpur Ckt-1 | 2026-01-26 09:05 | 2026-01-26 16:28 | 7:23 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Faridpur Ckt-2 | 2026-01-26 09:05 | 2026-01-26 16:29 | 7:24 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Faridpur Ckt-1 | 2026-01-27 09:35 | 2026-01-27 15:38 | 6:03 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Faridpur Ckt-2 | 2026-01-27 09:35 | 2026-01-27 15:39 | 6:04 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Faridpur CKT-01 | 2026-01-28 09:00 | 2026-01-28 15:16 | 6:16 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Faridpur CKT-02 | 2026-01-29 09:03 | 2026-01-29 12:32 | 3:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulna (C) | 132kV Central-Goalpara-1 | 2026-01-03 10:10 | 2026-01-03 14:56 | 4:46 | S/O | Annual maintenance | 0 | 0 | No interruption
Khulna (C) | 132kV Central-Noapara-1 | 2026-01-20 10:09 | 2026-01-20 11:38 | 1:29 | S/O | For Kite removal | 0 | 0 | No interruption
Khulna (C) | North-WestCkt-1 | 2026-01-24 09:34 | 2026-01-24 16:42 | 7:08 | S/O | S/D by ALDC | 0 | 0 | No interruption
Khulna (C) | North- West Ckt-2 | 2026-01-25 09:22 | 2026-01-25 12:58 | 3:36 | S/O | NW circuit shutdown taken By NW substation side. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Jhenaidah Ckt-1 | 2026-01-03 08:38 | 2026-01-03 15:33 | 6:55 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Jhenaidah Ckt-1 | 2026-01-04 08:23 | 2026-01-04 18:23 | 10:00 | S/O | Yearly Maintenance Work. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Jhenaidah Ckt-1 | 2026-01-05 08:55 | 2026-01-05 13:50 | 4:55 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | Jhenaidah Ckt-2 | 2026-01-06 08:39 | 2026-01-06 17:46 | 9:07 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | Jhenaidah Ckt-2 | 2026-01-07 08:42 | 2026-01-07 17:03 | 8:21 | S/O | None | 0 | 0 | No interruption
Khulna(S) 230/132kV | Jhenaidah Ckt-2 | 2026-01-08 08:42 | 2026-01-08 12:41 | 3:59 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Rampal Ckt-1 | 2026-01-10 09:34 | 2026-01-10 14:24 | 4:50 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Rampal Ckt-1 | 2026-01-11 09:21 | 2026-01-11 16:17 | 6:56 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | Rampal Ckt-1 | 2026-01-12 09:37 | 2026-01-12 13:52 | 4:15 | S/O | Yearly Maintenance Work. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Rampal Ckt-2 | 2026-01-13 09:12 | 2026-01-13 16:04 | 6:52 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | Rampal Ckt-2 | 2026-01-14 09:19 | 2026-01-14 12:33 | 3:14 | S/O | Yearly Maintenance Work. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Rampal Ckt-2 | 2026-01-15 08:54 | 2026-01-15 14:07 | 5:13 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-1 | 2026-01-16 09:10 | 2026-01-16 12:00 | 2:50 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | Gallamari Ckt-1 | 2026-01-31 08:18 | 2026-02-01 23:49 | 39:31 | S/O | OPGW Work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Gallamari Ckt-2 | 2026-01-31 11:48 | 2026-02-01 23:48 | 36:00 | S/O | OPGW Work | 0 | 0 | No interruption
Madaripur 132/33kV | Gopaganj North CKT-03 | 2026-01-20 09:17 | 2026-01-20 16:42 | 7:25 | S/O | Annual maintenance | 0 | 0 | No interruption
Madaripur 132/33kV | Gopaganj North CKT-04 | 2026-01-20 09:17 | 2026-01-20 16:44 | 7:27 | S/O | Annual maintenance | 0 | 0 | No interruption
Madaripur 132/33kV | Gopaganj North CKT-03 | 2026-01-21 08:41 | 2026-01-21 17:17 | 8:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Madaripur 132/33kV | Gopaganj North CKT-04 | 2026-01-21 08:41 | 2026-01-21 17:17 | 8:36 | S/O | Annual maintenance | 0 | 0 | No interruption
Madaripur 132/33kV | Gopaganj North CKT-03 | 2026-01-22 08:45 | 2026-01-22 17:21 | 8:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Madaripur 132/33kV | Gopaganj North CKT-04 | 2026-01-22 08:45 | 2026-01-22 17:22 | 8:37 | S/O | Annual Maintenance | 0 | 0 | No interruption
Madaripur 132/33kV | Gopaganj North CKT-04 | 2026-01-22 08:45 | 2026-01-22 17:22 | 8:37 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mongla 132/33kV | Bagerhat-Mongla Line-2 | 2026-01-07 09:43 | 2026-01-07 15:56 | 6:13 | S/O | Annual maintenances | 0 | 0 | No interruption
Mongla 132/33kV | Bagerhat-Mongla Line-2 | 2026-01-08 09:27 | 2026-01-24 15:59 | 390:32 | S/O | Annual maintenances | 0 | 0 | No interruption
Mongla 132/33kV | 100MW ERBL Solar PS | 2026-01-24 08:24 | 2026-01-24 14:42 | 6:18 | S/O | Annual maintenances work | 0 | 0 | No interruption
Mongla 132/33kV | Bagerhat-Mongla Line-1 | 2026-01-24 08:24 | 2026-01-24 14:40 | 6:16 | S/O | Annual maintenances work | 0 | 0 | No interruption
Narail 132/33kV | Magura 1 | 2026-01-06 08:34 | 2026-01-06 16:06 | 7:32 | S/O | Annual maintenance | 0 | 0 | No interruption
Narail 132/33kV | Magura 1 | 2026-01-07 08:34 | 2026-01-07 15:55 | 7:21 | S/O | Annual Maintenance | 0 | 0 | No interruption
Narail 132/33kV | Magura 1 | 2026-01-08 08:09 | 2026-01-08 16:15 | 8:06 | S/O | For Annual maintenance work. | 0 | 0 | No interruption
Narail 132/33kV | Magura 2 | 2026-01-10 08:30 | 2026-01-10 16:10 | 7:40 | S/O | Annual Maintenance | 0 | 0 | No interruption
Narail 132/33kV | Magura 2 | 2026-01-11 08:19 | 2026-01-11 16:15 | 7:56 | S/O | Annual Maintenance work purpose. | 0 | 0 | No interruption
Narail 132/33kV | Magura 2 | 2026-01-12 08:30 | 2026-01-12 15:24 | 6:54 | S/O | 132 kV Magura 2 Scheduled S/D due to Annual Maintenance work purpose | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 1 | 2026-01-20 10:08 | 2026-01-20 11:39 | 1:31 | S/O | Annual Maintenance | 0 | 0 | No interruption
Patuakhali 132/33kV | PAYRA-PATUAKHALI CKT-2 | 2026-01-09 09:11 | 2026-01-13 17:41 | 104:30 | S/O | Project Work | 0 | 0 | No interruption
Patuakhali 132/33kV | Barishal-Pautakhali 132kV Line | 2026-01-10 07:35 | 2026-01-10 17:44 | 10:09 | S/O | Project work | 0 | 0 | No interruption
Patuakhali 132/33kV | PAYRA-PATUAKHALI CKT-1 | 2026-01-10 08:21 | 2026-01-10 17:19 | 8:58 | S/O | Project work | 27 | 242.1 | Power interruption
Patuakhali 132/33kV | PAYRA-PATUAKHALI CKT-1 | 2026-01-19 07:54 | 2026-01-26 17:18 | 177:24 | S/O | Annual Maintenance-2026 | 0 | 0 | No interruption
Patuakhali 132/33kV | PAYRA-PATUAKHALI CKT-2 | 2026-01-27 08:16 | 2026-01-30 17:55 | 81:39 | S/O | Payra ckt 2 bay shift work ( G2G) | 0 | 0 | No interruption
Payra 400/132/33kV | Payra -Payra PGCB Grid 400kV Line 01 | 2026-01-07 09:52 | 2026-01-07 20:00 | 10:08 | S/O | Annual Maintenance | 0 | 0 | No interruption
Payra 400/132/33kV | Payra -Payra PGCB Grid 400kV Line 02 | 2026-01-08 08:08 | 2026-01-08 16:33 | 8:25 | S/O | Annual Maintenance | 0 | 0 | No interruption
Payra 400/132/33kV | Payra Patuakhali Line-02 | 2026-01-09 09:13 | 2026-01-13 17:41 | 104:28 | S/O | Annual Maintenance | 0 | 0 | No interruption
Payra 400/132/33kV | Payra Patuakhali Line-01 | 2026-01-10 07:59 | 2026-01-10 17:18 | 9:19 | S/O | Annual Maintenance | 0 | 0 | No interruption
Payra 400/132/33kV | Payra Patuakhali Line-01 | 2026-01-19 07:47 | 2026-01-26 17:17 | 177:30 | S/O | Maintenance | 0 | 0 | No interruption
Payra 400/132/33kV | Payra Patuakhali Line-02 | 2026-01-27 08:18 | 2026-01-30 17:54 | 81:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rajbari 132/33kV | Faridpur - 2 | 2026-01-17 08:50 | 2026-01-17 20:59 | 12:09 | S/O | Annual maintenance | 0 | 0 | No interruption
Rampal 400/230kV | Khulna Line-1 | 2026-01-11 09:22 | 2026-01-11 16:20 | 6:58 | S/O | Khulna ALDC Demand Annual Maintenance | 0 | 0 | No interruption
Rampal 400/230kV | Khulna Line-2 | 2026-01-13 09:12 | 2026-01-13 16:05 | 6:53 | S/O | Khulna ALDC Requirement. | 0 | 0 | No interruption
Rampal 400/230kV | Khulna Line-2 | 2026-01-14 09:20 | 2026-01-14 12:33 | 3:13 | S/O | Khulna ALDC Requirement | 0 | 0 | No interruption
Rampal 400/230kV | Khulna Line-2 | 2026-01-15 08:54 | 2026-01-15 14:06 | 5:12 | S/O | Scheduled Shutdown For khulna ALDC | 0 | 0 | No interruption
Rampal 400/230kV | Gopalganj Line-1 | 2026-01-21 09:39 | 2026-01-21 16:41 | 7:02 | S/O | Khulna ALDC Required. | 0 | 0 | No interruption
Rampal 400/230kV | Gopalganj Line-2 | 2026-01-22 07:56 | 2026-01-22 16:53 | 8:57 | S/O | Khulna Aldc Requirement. | 0 | 0 | No interruption
Rampal 400/230kV | Gopalganj Line-2 | 2026-01-23 09:28 | 2026-01-23 16:28 | 7:00 | S/O | Yearly Maintenance By Khulna ALDC | 0 | 0 | No interruption
Rampal 400/230kV | Gopalganj Line-2 Reactor | 2026-01-24 08:50 | 2026-01-24 17:02 | 8:12 | S/O | Maintenance work at Khulna-ALDC. | 0 | 0 | No interruption
Rampal 400/230kV | Gopalganj Line-2 | 2026-01-24 08:53 | 2026-01-24 17:01 | 8:08 | S/O | Maintenance work at Khulna-ALDC. | 0 | 0 | No interruption
Rampal 400/230kV | Gopalganj Line-2 | 2026-01-25 08:35 | 2026-01-25 17:03 | 8:28 | S/O | NLDC requirement. | 0 | 0 | No interruption
Satkhira 132/33kV | Khulna South-1 (L-1) | 2026-01-16 09:09 | 2026-01-16 12:01 | 2:52 | S/O | Due to Satkhira monirampur 132 kv line charging | 0 | 0 | No interruption
|  |  | Total : | 1900-04-04 06:24 |  | Unserved Energy: |  | 643.2
HVDC Grid Circle :
Baghabari 230/132kV | Baghabari- Sirajgonj-2 | 2026-01-01 09:51 | 2026-01-01 17:35 | 7:44 | S/O | সিরাজগঞ্জ পান্তে কাজ করার জন্য। | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari-Roppur 230kV Ckt-2 | 2026-01-12 08:52 | 2026-01-12 16:59 | 8:07 | S/O | Annual Maintenance | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari-Roppur 230kV Ckt-1 | 2026-01-23 06:09 | 2026-01-23 15:28 | 9:19 | S/O | Project Work Shutdown | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari-Roppur 230kV Ckt-2 | 2026-01-23 06:18 | 2026-01-23 12:48 | 6:30 | S/O | Project Work Shutdown | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari-Roppur 230kV Ckt-1 | 2026-01-24 06:21 | 2026-01-24 12:04 | 5:43 | S/O | Temporary cradle | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari-Roppur 230kV Ckt-2 | 2026-01-24 06:22 | 2026-01-24 11:41 | 5:19 | S/O | Temporary cradle | 0 | 0 | No interruption
Bhangura 132/33kV | Bhangura-Bhagabari ckt-1 | 2026-01-17 15:12 | 2026-01-17 15:56 | 0:44 | S/O | For Bhagabari PDB work | 16 | 11.7333 | Power interruption
BIPTC | 20DF24 | 2026-01-01 10:42 | 2026-01-01 11:32 | 0:50 | S/O | Corrective maintenance | 0 | 0 | No interruption
BIPTC | 10CF16 | 2026-01-01 11:06 | 2026-01-01 13:28 | 2:22 | S/O | for corrective maintenance | 0 | 0 | No interruption
BIPTC | Rajshahi-1 | 2026-01-03 08:43 | 2026-01-03 16:38 | 7:55 | S/O | Annual maintenance | 0 | 0 | No interruption
BIPTC | Rajshahi-1 | 2026-01-04 09:29 | 2026-01-04 16:17 | 6:48 | S/O | Shutdown has been taken from Rajshahi end. | 0 | 0 | No interruption
BIPTC | Rajshahi-1 | 2026-01-05 08:52 | 2026-01-05 16:21 | 7:29 | S/O | Shutdown is taken from Rajshahi end | 0 | 0 | No interruption
BIPTC | Rajshahi-2 | 2026-01-08 08:52 | 2026-01-08 16:32 | 7:40 | S/O | Annual maintenance | 0 | 0 | No interruption
BIPTC | Rajshahi-2 | 2026-01-10 09:13 | 2026-01-10 17:24 | 8:11 | S/O | Shutdown has been taken from Rajshahi end. | 0 | 0 | No interruption
BIPTC | Rajshahi-2 | 2026-01-11 08:45 | 2026-01-11 17:35 | 8:50 | S/O | Annual Maintenance | 0 | 0 | No interruption
BIPTC | 20DF32 | 2026-01-12 10:03 | 2026-01-12 13:15 | 3:12 | S/O | Annual Maintenance | 0 | 0 | No interruption
BIPTC | Rajshahi-2 | 2026-01-12 11:06 | 2026-01-12 15:42 | 4:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
BIPTC | 20DF41 | 2026-01-13 10:28 | 2026-01-13 13:31 | 3:03 | S/O | Shutdown is taken for annual maintenance | 0 | 0 | No interruption
BIPTC | 20DF42 | 2026-01-14 09:49 | 2026-01-14 13:52 | 4:03 | S/O | Shutdown is taken for annual maintenance | 0 | 0 | No interruption
BIPTC | 20DF43 | 2026-01-15 09:44 | 2026-01-15 12:39 | 2:55 | S/O | For Annual Maintenance | 0 | 0 | No interruption
BIPTC | Baharampur-1 | 2026-01-17 09:02 | 2026-01-17 16:04 | 7:02 | S/O | Annual Maintenance. | 0 | 0 | No interruption
BIPTC | Baharampur-1 | 2026-01-18 08:55 | 2026-01-18 16:37 | 7:42 | S/O | Annual Maintenance | 0 | 0 | No interruption
BIPTC | Baharampur-2 | 2026-01-20 09:51 | 2026-01-20 16:29 | 6:38 | S/O | Annual Maintenance | 0 | 0 | No interruption
BIPTC | Baharampur-2 | 2026-01-21 09:05 | 2026-01-21 16:49 | 7:44 | S/O | Annual Maintenance | 0 | 0 | No interruption
BIPTC | Baharampur-3 | 2026-01-24 08:46 | 2026-01-24 20:41 | 11:55 | S/O | Annual maintenance | 0 | 0 | No interruption
BIPTC | Baharampur-3 | 2026-01-25 08:21 | 2026-01-25 15:27 | 7:06 | S/O | Annual Maintenance | 0 | 0 | No interruption
BIPTC | Baharampur-4 | 2026-01-27 09:41 | 2026-01-27 16:24 | 6:43 | S/O | Annual Maintenance. | 0 | 0 | No interruption
BIPTC | Baharampur-4 | 2026-01-28 08:42 | 2026-01-28 15:51 | 7:09 | S/O | Annual Maintenance | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Pabna | 2026-01-30 05:55 | 2026-01-30 16:51 | 10:56 | S/O | Pabna Bus Maintenance | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 2 | 2026-01-06 12:12 | 2026-01-06 12:12 | 0:00 | S/O | Annual maintenance | 0 | 0 | No interruption
Jashore 132/33kV | BEN-2 | 2026-01-01 08:53 | 2026-01-01 16:00 | 7:07 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jashore 132/33kV | JH-2(L1) | 2026-01-14 07:13 | 2026-01-15 19:21 | 36:08 | S/O | shutdown is taken by g2g project | 0 | 0 | No interruption
Jashore 132/33kV | JH-1(L2) | 2026-01-14 07:13 | 2026-01-15 19:19 | 36:06 | S/O | shutdown is taken by g2g project | 0 | 0 | No interruption
Jashore 132/33kV | JH-1(L2) | 2026-01-30 06:51 | 2026-01-31 16:45 | 33:54 | S/O | Annual maintenance | 0 | 0 | No interruption
Jashore 132/33kV | JH-2(L1) | 2026-01-30 06:51 | 2026-01-31 16:45 | 33:54 | S/O | Annual maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-Khulna (South) Ckt-1 | 2026-01-03 08:37 | 2026-01-03 15:29 | 6:52 | S/O | A/M | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-Khulna (South) Ckt-1 | 2026-01-04 08:23 | 2026-01-04 18:22 | 9:59 | S/O | annual maintanance | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-Khulna (South) Ckt-1 | 2026-01-05 08:55 | 2026-01-05 13:55 | 5:00 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-Khulna (South) Ckt-2 | 2026-01-06 08:38 | 2026-01-06 17:47 | 9:09 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-Khulna (South) Ckt-2 | 2026-01-07 08:40 | 2026-01-07 17:05 | 8:25 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-Khulna (South) Ckt-2 | 2026-01-08 08:42 | 2026-01-08 12:43 | 4:01 | S/O | annual Maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Jashore Ckt-1 | 2026-01-14 07:14 | 2026-01-15 19:19 | 36:05 | S/O | Shutdown for kaliganj grid line work | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Jashore Ckt-2 | 2026-01-14 07:14 | 2026-01-15 19:20 | 36:06 | S/O | Shutdown for Kaliganj grid line work | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Jashore Ckt-1 | 2026-01-30 06:52 | 2026-01-31 16:41 | 33:49 | S/O | As per order of ALDC | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Jashore Ckt-2 | 2026-01-30 06:52 | 2026-01-31 16:43 | 33:51 | S/O | As per order of ALDC | 0 | 0 | No interruption
Magura 132/33kV | Narail Ckt. - 1 | 2026-01-06 08:36 | 2026-01-06 16:05 | 7:29 | S/O | For Annual Maintenance. | 0 | 0 | No interruption
Magura 132/33kV | Narail Ckt. - 1 | 2026-01-07 08:35 | 2026-01-07 15:54 | 7:19 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Magura 132/33kV | Narail Ckt. - 1 | 2026-01-08 08:08 | 2026-01-08 16:15 | 8:07 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Magura 132/33kV | Narail Ckt. - 2 | 2026-01-10 08:30 | 2026-01-10 16:09 | 7:39 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Magura 132/33kV | Narail Ckt. - 2 | 2026-01-11 08:20 | 2026-01-11 16:15 | 7:55 | S/O | For Annual Maintenance. | 0 | 0 | No interruption
Magura 132/33kV | Narail Ckt. - 2 | 2026-01-12 08:30 | 2026-01-12 15:23 | 6:53 | S/O | Annual maintenance | 0 | 0 | No interruption
Pabna 132/33kV | Pabna-Shahjadpur Line | 2026-01-03 08:40 | 2026-01-03 17:25 | 8:45 | S/O | Annual maintenance | 0 | 0 | No interruption
Pabna 132/33kV | Pabna-Shahjadpur Line | 2026-01-16 08:39 | 2026-01-16 16:25 | 7:46 | S/O | Annual maintenance | 0 | 0 | No interruption
Shahjadpur 132/33kV | 132 KV Shahjadpur-Pabna | 2026-01-03 08:39 | 2026-01-03 17:23 | 8:44 | S/O | annual maintenance | 0 | 0 | No interruption
Shahjadpur 132/33kV | 132 KV Shahjadpur-Sirajgonj | 2026-01-06 09:35 | 2026-01-06 21:11 | 11:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shahjadpur 132/33kV | 132 KV Shahjadpur-Sirajgonj | 2026-01-12 09:51 | 2026-01-12 15:04 | 5:13 | S/O | Maintenance work | 0 | 0 | No interruption
Shahjadpur 132/33kV | 132 KV Shahjadpur-Pabna | 2026-01-30 05:56 | 2026-01-30 13:30 | 7:34 | S/O | AM | 0 | 0 | No interruption
Ullahpara 132/33kV | Shahjadpur Ckt | 2026-01-06 09:35 | 2026-01-06 21:10 | 11:35 | S/O | Annual Maintenance work to Shahjadpur end. | 0 | 0 | No interruption
Ullahpara 132/33kV | Shahjadpur Ckt | 2026-01-12 09:50 | 2026-01-12 15:05 | 5:15 | S/O | Annual Maintenance | 0 | 0 | No interruption
Ullahpara 132/33kV | 132 KV Sirajgonj Ckt-1 | 2026-01-13 08:28 | 2026-01-13 17:29 | 9:01 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Ullahpara 132/33kV | 132 KV Sirajgonj Ckt-1 | 2026-01-14 08:37 | 2026-01-14 15:36 | 6:59 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Ullahpara 132/33kV | 132 KV Sirajgonj Ckt-1 | 2026-01-15 08:23 | 2026-01-15 14:39 | 6:16 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Ullahpara 132/33kV | 132 KV Sirajgonj Ckt-2 | 2026-01-19 09:35 | 2026-01-19 15:37 | 6:02 | S/O | Annual maintenance Work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-26 06:49 |  | Unserved Energy: |  | 11.7333
Bogura Grid Circle :
Barapukuria 230/132/33kV | Saidpur 132 KV Ckt1 | 2026-01-02 08:47 | 2026-01-02 12:41 | 3:54 | S/O | project work | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Saidpur 132 KV Ckt2 | 2026-01-02 08:48 | 2026-01-02 12:42 | 3:54 | S/O | project work | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Rangpur 132 KV Ckt1 | 2026-01-04 08:41 | 2026-01-04 17:20 | 8:39 | S/O | Project work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV | PS 230 KV Ckt1 | 2026-01-18 09:58 | 2026-01-18 16:05 | 6:07 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Rangpur 132 KV Ckt1 | 2026-01-25 08:57 | 2026-01-25 12:25 | 3:28 | S/O | Project work G to G | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Rangpur 132 KV Ckt2 | 2026-01-25 08:58 | 2026-01-25 12:27 | 3:29 | S/O | Project work G to G | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Bogura 230 KV Ckt2 | 2026-01-26 11:17 | 2026-01-26 17:35 | 6:18 | S/O | Project work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Bogura 230 KV Ckt2 | 2026-01-27 08:36 | 2026-01-27 15:33 | 6:57 | S/O | Project work | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Bogura 230 KV Ckt1 | 2026-01-29 08:35 | 2026-01-29 17:17 | 8:42 | S/O | Conductor restringing work. | 0 | 0 | No interruption
Bogura 132/33kV | Mahasthangarh-2 | 2026-01-01 09:46 | 2026-01-01 16:12 | 6:26 | S/O | ALDC shutdown. | 0 | 0 | No interruption
Bogura 132/33kV | New Bogura-1 | 2026-01-07 09:30 | 2026-01-07 13:59 | 4:29 | S/O | Annual maintenance. | 0 | 0 | No interruption
Bogura 132/33kV | New Bogura-2 | 2026-01-08 09:38 | 2026-01-08 14:48 | 5:10 | S/O | Annual /maintenance | 0 | 0 | No interruption
Bogura 132/33kV | New Bogura-2 | 2026-01-21 09:33 | 2026-01-21 17:25 | 7:52 | S/O | Relay Change work of 230/132kV Sub-Station side. | 0 | 0 | No interruption
Bogura 230/132kV | Serajganj Line-1 | 2026-01-04 08:59 | 2026-01-05 17:20 | 32:21 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Bogura 230/132kV | Serajganj Line-1 | 2026-01-06 09:05 | 2026-01-06 19:28 | 10:23 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV | Bogra 132KV Line-1 | 2026-01-07 09:29 | 2026-01-07 13:59 | 4:30 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV | Bogra 132KV Line-2 | 2026-01-08 09:38 | 2026-01-08 15:01 | 5:23 | S/O | annual Maintenance work | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-2 | 2026-01-10 06:50 | 2026-01-10 14:36 | 7:46 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-1 | 2026-01-10 09:09 | 2026-01-11 15:28 | 30:19 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV | Bogra 132KV Line-2 | 2026-01-21 09:32 | 2026-01-21 17:24 | 7:52 | S/O | Relay Replacement | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2026-01-04 08:43 | 2026-01-04 16:29 | 7:46 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2026-01-04 08:43 | 2026-01-04 16:29 | 7:46 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2026-01-05 08:40 | 2026-01-05 16:39 | 7:59 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2026-01-05 08:40 | 2026-01-05 16:39 | 7:59 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2026-01-06 10:53 | 2026-01-06 16:49 | 5:56 | S/O | Kaliakoir ckt-01 shutdown due to annual maintenance | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2026-01-07 10:03 | 2026-01-07 17:08 | 7:05 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2026-01-10 10:19 | 2026-01-10 20:16 | 9:57 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2026-01-10 10:20 | 2026-01-10 20:16 | 9:56 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2026-01-11 09:44 | 2026-01-11 17:21 | 7:37 | S/O | Annual maintenance | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2026-01-11 09:44 | 2026-01-11 17:21 | 7:37 | S/O | Annual maintenance | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Rahanpur 400 KV CKT-01 | 2026-01-17 08:20 | 2026-01-17 17:10 | 8:50 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Rahanpur 400 KV CKT-01 | 2026-01-18 08:20 | 2026-01-18 17:25 | 9:05 | S/O | Annual maintenance | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Rahanpur 400 KV CKT-01 | 2026-01-19 08:35 | 2026-01-19 16:15 | 7:40 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Rahanpur 400 KV CKT-02 | 2026-01-20 08:52 | 2026-01-20 16:55 | 8:03 | S/O | Annual maintenance. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Rahanpur 400 KV CKT-02 | 2026-01-21 08:36 | 2026-01-21 17:01 | 8:25 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Rahanpur 400 KV CKT-02 | 2026-01-22 08:27 | 2026-01-22 15:31 | 7:04 | S/O | Annual maintenance work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Baropukuria 230 KV Ckt-2 | 2026-01-26 08:46 | 2026-01-26 17:35 | 8:49 | S/O | Project work at Barapukuria site on the line | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Baropukuria 230 KV Ckt-2 | 2026-01-27 08:36 | 2026-01-27 15:36 | 7:00 | S/O | Barapukuria ckt- 02 has been shutdown due to project (G2G) work on the line at the Barapukuria site. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Baropukuria 230 KV Ckt-1 | 2026-01-29 08:38 | 2026-01-29 17:15 | 8:37 | S/O | Barapukuria ckt- 01 has been shutdown due to project (G2G) work on the line at the Barapukuria site. | 0 | 0 | No interruption
Kurigram 132/33kV | 132 Kv Rangpur-kurigram Ckt | 2026-01-05 09:04 | 2026-01-06 17:18 | 32:14 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kurigram 132/33kV | 132 Kv Rangpur-kurigram Ckt | 2026-01-08 10:05 | 2026-01-08 13:26 | 3:21 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kurigram 132/33kV | 132 Kv Rangpur-kurigram Ckt | 2026-01-10 09:43 | 2026-01-10 17:18 | 7:35 | S/O | annual maintance | 0 | 0 | No interruption
Kurigram 132/33kV | 132 Kv Rangpur-kurigram Ckt | 2026-01-11 09:30 | 2026-01-11 16:46 | 7:16 | S/O | annual maintenance | 0 | 0 | No interruption
Kurigram 132/33kV | 132 Kv Rangpur-kurigram Ckt | 2026-01-12 16:18 | 2026-01-12 19:22 | 3:04 | S/O | Annual maintenance | 0 | 0 | No interruption
Kurigram 132/33kV | 132 Kv Rangpur-kurigram Ckt | 2026-01-14 10:45 | 2026-01-14 18:41 | 7:56 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kurigram 132/33kV | 132 Kv Rangpur-kurigram Ckt | 2026-01-15 09:10 | 2026-01-15 17:23 | 8:13 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kurigram 132/33kV | 132 Kv Rangpur-kurigram Ckt | 2026-01-18 12:28 | 2026-01-18 14:42 | 2:14 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mahasthangarh 132/33kV | Mahasthangarh-Bogura Ckt-2 | 2026-01-01 09:45 | 2026-01-01 16:12 | 6:27 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Niamatpur Ckt-1 | 2026-01-06 12:30 | 2026-01-06 19:15 | 6:45 | S/O | Project work. | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Niamatpur Ckt-1 | 2026-01-09 08:55 | 2026-01-13 19:52 | 106:57 | S/O | Project work. | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-SPPP Ckt-1 | 2026-01-10 06:49 | 2026-01-10 06:49 | 0:00 | S/O | Project work. | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Bogura Ckt-2 | 2026-01-10 06:49 | 2026-01-10 14:38 | 7:49 | S/O | Project work | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Bogura Ckt-1 | 2026-01-11 14:53 | 2026-01-15 10:55 | 92:02 | S/O | Project work. | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Joypurhat Ckt-1 | 2026-01-11 15:30 | 2026-01-11 18:43 | 3:13 | S/O | Project work for parameter test by SPMD. | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Joypurhat Ckt-1 | 2026-01-15 10:22 | 2026-01-15 10:32 | 0:10 | S/O | Project work. | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Niamatpur Ckt-2 | 2026-01-29 13:17 | 2026-01-29 20:39 | 7:22 | S/O | GIS main Bus inter lock checking. | 0 | 0 | No interruption
Natore 132/33kV | Rajshahi-2 | 2026-01-23 08:43 | 2026-01-23 18:47 | 10:04 | S/O | Shutdown taken from rajshahi 132/33 kV Grid. | 0 | 0 | No interruption
Natore 132/33kV | Rajshahi-2 | 2026-01-24 08:17 | 2026-01-24 10:36 | 2:19 | S/O | Annual Maintenance | 0 | 0 | No interruption
Natore 132/33kV | Rajshahi-2 | 2026-01-29 09:22 | 2026-01-30 11:43 | 26:21 | S/O | Annual Maintenance | 0 | 0 | No interruption
Natore 132/33kV | Rajshahi-2 | 2026-01-30 11:50 | 2026-01-30 11:57 | 0:07 | S/O | In order to AlDC bogura | 0 | 0 | No interruption
Natore 132/33kV | Rajshahi-1 | 2026-01-30 12:06 | 2026-01-30 17:48 | 5:42 | S/O | In order to AlDC bogura . | 0 | 0 | No interruption
Niamatpur 132/33kV | 132 kV Naogaon ckt-1 | 2026-01-06 12:26 | 2026-01-06 19:15 | 6:49 | S/O | (Project Work) As per the instruction of Bogura ALDC. | 0 | 0 | No interruption
Niamatpur 132/33kV | 132 kV Naogaon ckt-1 | 2026-01-09 08:46 | 2026-01-13 19:52 | 107:06 | S/O | Annual Maintenance | 0 | 0 | No interruption
Niamatpur 132/33kV | 132 kV Naogaon ckt-2 | 2026-01-12 11:40 | 2026-01-12 17:01 | 5:21 | S/O | As per instruction of ALDC Bogura. | 0 | 0 | No interruption
Niamatpur 132/33kV | 132 kV Naogaon ckt-2 | 2026-01-13 17:02 | 2026-01-13 19:52 | 2:50 | S/O | as per instruction of ALDC, Bogura | 0 | 0 | No interruption
Niamatpur 132/33kV | 132 kV Naogaon ckt-2 | 2026-01-21 09:16 | 2026-01-21 14:26 | 5:10 | S/O | Project work | 0 | 0 | No interruption
Niamatpur 132/33kV | 132 kV Naogaon ckt-1 | 2026-01-29 16:25 | 2026-01-29 18:25 | 2:00 | S/O | As per instruction of ALDC, Bogura | 0 | 0 | No interruption
Purbasadipur 132/33kV | Saidpur Line-2 | 2026-01-08 11:40 | 2026-01-08 11:40 | 0:00 | S/O | EEGBPS project shutdown for equipment dismentale for GIS connection. No loadshed because Load served by GIS to AIS connection. | 0 | 0 | No interruption
Purbasadipur 132/33kV | Saidpur Line-1 | 2026-01-11 09:15 | 2026-01-11 20:45 | 11:30 | S/O | Annual Maintenance | 0 | 0 | No interruption
Purbasadipur 132/33kV | Saidpur Line-1 | 2026-01-15 09:15 | 2026-01-16 00:37 | 15:22 | S/O | CB problem at Saidpur end | 0 | 0 | No interruption
Purbasadipur 132/33kV | Thakurgaon Line-2 | 2026-01-19 07:52 | 2026-01-19 10:19 | 2:27 | S/O | Annual Maintenance | 0 | 0 | No interruption
Purbasadipur 132/33kV | Thakurgaon Line-1 | 2026-01-31 13:03 | 2026-01-31 19:08 | 6:05 | S/O | DFDR test | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Bogura 400 KV Line Ckt-01 | 2026-01-17 08:21 | 2026-01-17 17:10 | 8:49 | S/O | Annual maintenance | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Bogura 400 KV Line Ckt-01 | 2026-01-18 08:21 | 2026-01-18 17:25 | 9:04 | S/O | Due to Annual maintenance work. | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Bogura 400 KV Line Ckt-01 | 2026-01-19 08:38 | 2026-01-19 16:15 | 7:37 | S/O | Annual maintenance work | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Bogura 400 KV Line Ckt-02 | 2026-01-20 08:52 | 2026-01-20 16:55 | 8:03 | S/O | Annual maintenance work | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Bogura 400 KV Line Ckt-02 | 2026-01-21 08:36 | 2026-01-21 17:01 | 8:25 | S/O | For annual maintenance | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Bogura 400 KV Line Ckt-02 | 2026-01-22 08:29 | 2026-01-22 15:30 | 7:01 | S/O | For Annual maintenance | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Monakasha 400KV Line ckt-01 | 2026-01-24 10:21 | 2026-01-24 17:06 | 6:45 | S/O | Annual maintenance | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Monakasha 400KV Line ckt-01 | 2026-01-25 08:36 | 2026-01-25 16:31 | 7:55 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Monakasha 400KV Line ckt-02 | 2026-01-26 08:32 | 2026-01-26 16:24 | 7:52 | S/O | Due to maintenance work. | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Monakasha 400KV Line ckt-02 | 2026-01-27 09:00 | 2026-01-27 16:56 | 7:56 | S/O | Annual maintenance work | 0 | 0 | No interruption
Rajshahi 132/33kV | 132 kV Natore-1 | 2026-01-10 07:51 | 2026-01-10 13:15 | 5:24 | S/O | Development Work | 0 | 0 | No interruption
Rajshahi 132/33kV | 132 kV Natore-2 | 2026-01-10 07:52 | 2026-01-10 13:52 | 6:00 | S/O | Development Work | 0 | 0 | No interruption
Rajshahi 132/33kV | 132 kV PPP 50 Mw | 2026-01-10 07:54 | 2026-01-10 14:03 | 6:09 | S/O | Development Work | 0 | 0 | No interruption
Rajshahi 132/33kV | 132 kV Raj(new)-1 | 2026-01-10 07:56 | 2026-01-10 13:30 | 5:34 | S/O | Development Work | 0 | 0 | No interruption
Rajshahi 132/33kV | 132 kV Raj(new)-2 | 2026-01-10 07:56 | 2026-01-10 13:42 | 5:46 | S/O | Development Work | 0 | 0 | No interruption
Rajshahi 132/33kV | 132 kV Raj(new)-2 | 2026-01-11 08:52 | 2026-01-14 19:31 | 82:39 | S/O | Project work | 0 | 0 | No interruption
Rajshahi 132/33kV | 132 kV Raj(new)-1 | 2026-01-15 09:03 | 2026-01-18 16:11 | 79:08 | S/O | DS,ES changing work by Project. | 0 | 0 | No interruption
Rajshahi 132/33kV | 132 kV Natore-2 | 2026-01-23 08:43 | 2026-01-30 11:57 | 171:14 | S/O | Project work | 0 | 0 | No interruption
Rajshahi 132/33kV | 132 kV PPP 50 Mw | 2026-01-29 16:30 | 2026-01-29 16:59 | 0:29 | S/O | S/D taken by SPMD | 0 | 0 | No interruption
Rajshahi 132/33kV | 132 kV Natore-1 | 2026-01-30 12:08 | 2026-01-30 12:08 | 0:00 | S/O | Project work | 0 | 0 | No interruption
Rajshahi 230/132/33kV | 230 Kv BIPTC Ckt-01 | 2026-01-03 08:29 | 2026-01-03 16:36 | 8:07 | S/O | A/M | 0 | 0 | No interruption
Rajshahi 230/132/33kV | 230 Kv BIPTC Ckt-01 | 2026-01-04 09:17 | 2026-01-04 16:18 | 7:01 | S/O | A/M | 0 | 0 | No interruption
Rajshahi 230/132/33kV | 230 Kv BIPTC Ckt-01 | 2026-01-05 08:16 | 2026-01-05 16:22 | 8:06 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Rajshahi 230/132/33kV | 230 Kv BIPTC Ckt-02 | 2026-01-08 08:30 | 2026-01-08 15:52 | 7:22 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Rajshahi 230/132/33kV | 230 Kv BIPTC Ckt-02 | 2026-01-10 09:01 | 2026-01-10 17:24 | 8:23 | S/O | Annual maintenance | 0 | 0 | No interruption
Rajshahi 230/132/33kV | 230 Kv BIPTC Ckt-02 | 2026-01-11 08:28 | 2026-01-11 17:35 | 9:07 | S/O | A/M | 0 | 0 | No interruption
Rajshahi 230/132/33kV | 230 Kv BIPTC Ckt-02 | 2026-01-12 11:02 | 2026-01-12 15:41 | 4:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Barapukuria-1 | 2026-01-04 08:38 | 2026-01-04 17:22 | 8:44 | S/O | None Re-Conductor Ing work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Kurigram | 2026-01-05 09:05 | 2026-01-12 19:18 | 178:13 | S/O | gantry piling work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-GTPS | 2026-01-08 09:25 | 2026-01-08 18:10 | 8:45 | S/O | Re-conducting work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Lalmonirhat | 2026-01-13 08:51 | 2026-01-13 20:00 | 11:09 | S/O | Grantly piling | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Taraganj-1 | 2026-01-13 09:25 | 2026-01-24 14:05 | 268:40 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Kurigram | 2026-01-14 10:44 | 2026-01-14 18:40 | 7:56 | S/O | G2G Project works | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Kurigram | 2026-01-15 09:18 | 2026-01-18 14:40 | 77:22 | S/O | Piling Work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Taraganj-2 | 2026-01-18 08:26 | 2026-01-18 17:58 | 9:32 | S/O | Annual Maintenance ⛑. | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Taraganj-2 | 2026-01-19 08:27 | 2026-01-19 17:14 | 8:47 | S/O | Annual Maintenance ⛑. | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Taraganj-2 | 2026-01-20 08:36 | 2026-01-20 16:38 | 8:02 | S/O | Instruction of ALDC Bogura | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Lalmonirhat | 2026-01-21 09:54 | 2026-01-23 16:49 | 54:55 | S/O | Piling Work | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Baropukuria CKT-01 | 2026-01-02 08:45 | 2026-01-02 12:42 | 3:57 | S/O | Annual Maintenance | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Baropukuria CKT-02 | 2026-01-02 08:46 | 2026-01-02 12:44 | 3:58 | S/O | Annual Maintenance | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Purbosadipur CKT-02 | 2026-01-08 11:40 | 2026-01-08 16:44 | 5:04 | S/O | By the instructions of ALDC, Bogura | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Purbosadipur CKT-01 | 2026-01-11 09:08 | 2026-01-16 17:28 | 128:20 | S/O | Annual maintenance | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Taraganj CKT-02 | 2026-01-13 08:49 | 2026-01-13 16:46 | 7:57 | S/O | Annual maintenance | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Taraganj CKT-02 | 2026-01-14 09:23 | 2026-01-14 17:05 | 7:42 | S/O | Annual maintainance | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Taraganj CKT-02 | 2026-01-15 08:43 | 2026-01-15 15:35 | 6:52 | S/O | Annual maintainance | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Taraganj CKT-01 | 2026-01-18 08:25 | 2026-01-18 17:34 | 9:09 | S/O | Annual maintenance | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Taraganj CKT-01 | 2026-01-19 08:28 | 2026-01-19 16:55 | 8:27 | S/O | Annual maintenance | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Taraganj CKT-01 | 2026-01-20 08:36 | 2026-01-20 15:49 | 7:13 | S/O | Annual maintenance | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Purbosadipur CKT-02 | 2026-01-24 08:49 | 2026-01-24 15:28 | 6:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Purbosadipur CKT-02 | 2026-01-25 08:39 | 2026-01-25 16:45 | 8:06 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sirajganj 132/33kV | Ullapara -1 | 2026-01-13 08:27 | 2026-01-13 17:27 | 9:00 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Sirajganj 132/33kV | Ullapara -1 | 2026-01-14 08:35 | 2026-01-14 15:37 | 7:02 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sirajganj 132/33kV | Ullapara -1 | 2026-01-15 08:30 | 2026-01-15 14:39 | 6:09 | S/O | S/D Taken by Ullapara S/S. | 0 | 0 | No interruption
Sirajganj 132/33kV | Ullapara -1 | 2026-01-15 08:30 | 2026-01-15 14:39 | 6:09 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Sirajganj 132/33kV | Ullapara -2 | 2026-01-17 08:41 | 2026-01-17 17:03 | 8:22 | S/O | Annual maintenance. | 0 | 0 | No interruption
Sirajganj 132/33kV | Ullapara -2 | 2026-01-18 09:19 | 2026-01-18 16:37 | 7:18 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sirajganj 132/33kV | Ullapara -2 | 2026-01-19 09:34 | 2026-01-19 15:38 | 6:04 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sirajgonj 230 | Baghabari -02 | 2026-01-01 09:50 | 2026-01-01 17:38 | 7:48 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sirajgonj 230 | SNWPCL (Unit-04) | 2026-01-17 07:58 | 2026-01-17 18:12 | 10:14 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Sirajgonj 230 | SNWPCL (Unit-04) | 2026-01-18 08:32 | 2026-01-18 17:20 | 8:48 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Sirajgonj 230 | Sreepur-01 | 2026-01-26 09:02 | 2026-01-26 18:04 | 9:02 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Sirajgonj 230 | Sreepur-01 | 2026-01-28 09:34 | 2026-01-28 17:53 | 8:19 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sirajgonj 230 | Sreepur-02 | 2026-01-29 09:19 | 2026-01-29 17:16 | 7:57 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Taraganj 132/33kV | Taraganj-Saidpur CKT-02 | 2026-01-13 08:50 | 2026-01-13 16:45 | 7:55 | S/O | Annual Maintenance | 0 | 0 | No interruption
Taraganj 132/33kV | Taraganj-Rangpur CKT-01 | 2026-01-13 09:25 | 2026-01-13 19:40 | 10:15 | S/O | Annual Maintenance | 0 | 0 | No interruption
Taraganj 132/33kV | Taraganj-Saidpur CKT-02 | 2026-01-14 09:25 | 2026-01-14 17:08 | 7:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
Taraganj 132/33kV | Taraganj-Rangpur CKT-01 | 2026-01-14 09:45 | 2026-01-15 17:42 | 31:57 | S/O | Annual Maintenance | 0 | 0 | No interruption
Taraganj 132/33kV | Taraganj-Saidpur CKT-02 | 2026-01-15 08:44 | 2026-01-15 15:34 | 6:50 | S/O | Annual Maintenance | 0 | 0 | No interruption
Taraganj 132/33kV | Taraganj-Saidpur CKT-01 | 2026-01-18 08:22 | 2026-01-18 17:34 | 9:12 | S/O | Annual maintenance | 0 | 0 | No interruption
Taraganj 132/33kV | Taraganj-Rangpur CKT-02 | 2026-01-18 08:24 | 2026-01-18 17:59 | 9:35 | S/O | Annual maintenance | 0 | 0 | No interruption
Taraganj 132/33kV | Taraganj-Rangpur CKT-02 | 2026-01-19 08:26 | 2026-01-19 17:16 | 8:50 | S/O | Annual Maintenance | 0 | 0 | No interruption
Taraganj 132/33kV | Taraganj-Saidpur CKT-01 | 2026-01-19 08:26 | 2026-01-19 16:55 | 8:29 | S/O | deadline checking | 0 | 0 | No interruption
Taraganj 132/33kV | Taraganj-Saidpur CKT-01 | 2026-01-20 08:36 | 2026-01-20 15:49 | 7:13 | S/O | For annual maintenance | 0 | 0 | No interruption
Taraganj 132/33kV | Taraganj-Rangpur CKT-02 | 2026-01-20 08:38 | 2026-01-20 16:39 | 8:01 | S/O | For annual maintenance | 0 | 0 | No interruption
Taraganj 132/33kV | Taraganj-Rangpur CKT-01 | 2026-01-22 09:07 | 2026-01-22 19:00 | 9:53 | S/O | Annual Maintenance | 0 | 0 | No interruption
Taraganj 132/33kV | Taraganj-Rangpur CKT-01 | 2026-01-23 10:31 | 2026-01-23 15:48 | 5:17 | S/O | Due to ALDC information. | 0 | 0 | No interruption
Taraganj 132/33kV | Taraganj-Rangpur CKT-01 | 2026-01-24 13:45 | 2026-01-24 14:04 | 0:19 | S/O | ordered by ALDC Bogura | 0 | 0 | No interruption
Thakurgaon 132/33kV | Thakurgaon-EPV Ckt-1 | 2026-01-05 08:22 | 2026-01-05 10:43 | 2:21 | S/O | EPVTL-Thakurgaon 01 Ckt. Reconductoring under KEC International Limited, India. | 0 | 0 | No interruption
Thakurgaon 132/33kV | Thakurgaon-EPV Ckt-1 | 2026-01-05 11:35 | 2026-01-17 18:46 | 295:11 | S/O | Reconductoring works | 0 | 0 | No interruption
Thakurgaon 132/33kV | Thakurgaon-EPV Ckt-2 | 2026-01-18 14:54 | 2026-01-18 21:10 | 6:16 | S/O | STEGEP Project Reconductoring work | 0 | 0 | No interruption
Thakurgaon 132/33kV | Thakurgaon-EPV Ckt-1 | 2026-01-18 21:25 | 2026-01-19 11:05 | 13:40 | S/O | Temperature Rise at Thakurgaon-EPV Ckt-1 R-Phase LA. Need to Maintenance | 0 | 0 | No interruption
Thakurgaon 132/33kV | Thakurgaon-EPV Ckt-2 | 2026-01-19 11:07 | 2026-02-06 17:19 | 438:12 | S/O | FOR RECONDUCTOING WORK | 0 | 0 | No interruption
|  |  | Total : | 1900-05-11 00:26 |  | Unserved Energy: |  | 0
Others :Nil
No interruption
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1901-06-25 03:44 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:January 2026
| Area | Previous Month (December' 2025) |  |  |  | Current Month (January '2026)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 15 | 14 | 353 | 382 | 5 | 26 | 349 | 380
2 | Dhaka (South) Grid Circle. | 16 | 20 | 185 | 221 | 12 | 13 | 200 | 225
3 | Chattogram Grid Circle. | 7 | 6 | 114 | 127 | 6 | 12 | 147 | 165
4 | Cumilla Grid Circle. | 10 | 16 | 240 | 266 | 15 | 21 | 204 | 240
5 | Khulna Grid Circle. | 9 | 9 | 212 | 230 | 3 | 11 | 216 | 230
6 | HVDC Grid Circle | 4 | 2 | 110 | 116 | 6 | 11 | 98 | 115
7 | Bogura Grid Circle. | 7 | 122 | 245 | 374 | 5 | 19 | 208 | 232
8 | Others
9 | Total | 68 | 189 | 1459 | 1716 | 52 | 113 | 1422 | 1587
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month: January 2026
| Area | Previous Month (December' 2025) |  |  |  | Current Month (January '2026)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 54.75 | - | 1075.13 | 1129.88 | 533.6 | - | 5369.44 | 5903.04
2 | Dhaka (South) Grid Circle. | 311.87 | 448.35 | 932.5 | 1692.72 | 64.72 | 421 | 421.92 | 907.64
3 | Chattogram Grid Circle. | 20.37 | 4.9 | 35.2 | 60.47 | 21.15 | 0.93 | 794.23 | 816.31
4 | Cumilla Grid Circle. | 40.2 | 56 | 1477.6 | 1573.8 | 73.4 | 50.12 | 1141.47 | 1264.99
5 | Khulna Grid Circle. | 40.67 | - | 3282.87 | 3323.54 | 24.17 | 50.33 | 2461.4 | 2535.9
6 | HVDC Grid Circle | - | - | 813.95 | 813.95 | - | 93.75 | 864.28 | 958.03
7 | Bogura Grid Circle. | 98.02 | 122.33 | 836.98 | 1057.33 | 51.82 | 4.33 | 625 | 681.15
8 | Others | bar: Energy unserved ( MWH ) due to T to Energy unserved ( MWH ) due to Total
9 | Total | 565.88 | 631.58 | 8454.23 | 9651.69 | 768.86 | 620.46 | 11677.74 | 13067.06
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-29
QF-LDC-29
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:January 2026
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 3 | 20 | 23 | - | - | 23 | 4475.55
2 | Dhaka (South) | 5031.6 | 2 | 4 | 6 | 1 |  | 5 | 849.63
3 | Chattogram | 2042 | 2 | 4 | 6 | 2 |  | 4 | 562.76
4 | Khulna | 2434 | 2 | 17 | 19 |  |  | 19 | 1884.53
5 | HVDC | 5954.3 | 3 | 9 | 12 | - | 1 | 11 | 946.3
6 | Bogura | 3145.6 | 1 | 9 | 10 |  | 1 | 9 | 629.33
7 | Cumilla | 2981 | 9 | 9 | 18 | 6 | 5 | 7 | 499.54
8 | Others | - | - | - | - | - | - | - | -
| Total | 30390.1 | [6 empty] | 9847.64
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.99%
4 | Khulna | 99.99%
5 | HVDC | 99.99%
6 | Bogura | 99.99%
7 | Cumilla | 99.99% | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:January 2026
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 1 | 9 | 10 |  | - | 10 | 1427.48
2 | Dhaka (South) | 990.29 | - | 1 | - | 1 | 1 | - | - | 58
3 | Chattogram | 917 | - | 1 | 3 | 4 | 1 | - | 3 | 253.55
4 | Khulna | 1238.4 | - | 1 | 3 | 4 | - | 1 | 3 | 651.37
5 | HVDC | 1325 | - | - | 1 | 1 | - | 1 |  | 11.7333
6 | Bogura | 1803.3 | - | 2 |  | 2 | - | - | 2 | 51.82
7 | Cumilla | 1648.16 | - | 4 | 7 | 11 | 2 | 2 | 7 | 765.45
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 3219.4033
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.99%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 100%
6 | Bogura | 99.99%
7 | Cumilla | 99.99% | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:January 2026
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2026-01-01 | 6 | - | 1 | 00:04 min | - | - |  |  | 1 | 0:44
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-32
QF-LDC-32
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:January 2026
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Rajendrapur 132/33kV | 2 | 0.11181 | 147.93
Tongi 230/132/33kV | 1 | 0.35764 | 206
Rajendrapur 132/33kV | 1 | 1:17 | 179.6667
Bhaluka 132/33kV | 2 | 19:41 | 576.2
Jamalpur 132/33kV | 1 | 0.088194 | 42.3333
Kabirpur 132/33kV | 4 | 30:30 | 1438.05
Kishoreganj 132/33kV | 3 | 10:32 | 356.2
Kodda 132/33kV | 3 | 12:23 | 637.67
Mirzapur 132/33kV | 6 | 31:16 | 469.5
Tangail 132/33kV | 1 | 6:01 | 601.6667
Bhaluka 132/33kV | 7 | 1899-12-31 07:46 | 922.82
Mirzapur 132/33kV | 2 | 13:00 | 325
Keranigonj 230/132/33kV | 1 | 0:13 | 6.7167
Ghorashal 230kV | 1 | 7:01 | 421
Meghnaghat 400/230kV | 1 | 0:12 | 58
Sonargaon 132/33kV | 4 | 9:07 | 421.92
Kalurghat 132/33kV | 1 | 0.011111 | 1.8
Kalurghat 132/33kV | 1 | 0.0027778 | 0.93333
Juldah 132/33kV | 1 | 0:27 | 19.35
Bakulia 132/33kV | 1 | 6:47 | 67.8333
Chandraghona 132/33kV | 1 | 2:05 | 35.4167
Coxsbazar 132/33kV | 2 | 8:05 | 456.78
Dohazari 132/33kV | 3 | 22:07 | 234.2
Chowmuhani 132/33kV | 2 | 0:14 | 3.97
Cumilla(S) 132/33kV | 2 | 0:49 | 18.43
Fenchuganj 230/132/33kV | 1 | 0:41 | 13.6667
Shahjibazar 132/33kV | 1 | 0:15 | 2
Shahjibazar 132/33kV | 1 | 0:29 | 29.9667
Beanibazar 132/33kV | 2 | 0:53 | 35.33
Kulaura 132/33kV | 2 | 1:33 | 20.15
Chandpur 132/33kV | 2 | 0.40694 | 117.2
Chhatak 132/33kV | 2 | 0.27639 | 145.77
Feni 132/33kV | 1 | 0.074306 | 26.75
Kulaura 132/33kV | 1 | 6:29 | 116.7
Maijdee 132/33kV | 1 | 0:33 | 6.05
Sunamganj 132/33kV | 1 | 4:04 | 12.2
Sylhet (South) | 1 | 0:41 | 6.8333
Beanibazar 132/33kV | 3 | 12:28 | 494.53
Chandpur 132/33kV | 2 | 9:46 | 117.2
Chhatak 132/33kV | 2 | 15:18 | 98.23
Rajbari 132/33kV | 1 | 4:00 | 16
Bhandaria 132/33kV | 1 | 2:31 | 50.3333
Patuakhali 132/33kV | 1 | 0:35 | 8.17
Bagerhat 132/33kV | 1 | 6:02 | 319.7667
Barishal 132/33kV | 4 | 19:19 | 234.2
Barishal 230/132kV | 1 | 1:23 | 41.5
Benapole 132/33kV | 1 | 6:26 | 289.5
Bhandaria 132/33kV | 1 | 10:27 | 292.6
Faridpur 132/33kV | 3 | 8:10 | 247.75
Mongla 132/33kV | 1 | 6:31 | 143.3667
Narail 132/33kV | 2 | 9:01 | 162.3
Satkhira 132/33kV | 2 | 9:26 | 47.17
Shariatpur 132/33kV | 1 | 1:29 | 40.05
Barguna 132/33kV | 1 | 10:47 | 129.4
Bhandaria 132/33kV | 1 | 10:27 | 271.7
Patuakhali 132/33kV | 1 | 8:58 | 242.1
Kushtia 132/33kV | 1 | 0:45 | 18
Shahjadpur 132/33kV | 2 | 3:25 | 75.75
Bhangura 132/33kV | 2 | 13:45 | 110
Chuadanga 132/33kV | 2 | 6:01 | 192.53
Ishurdi 132/33kV | 1 | 1:29 | 14.8333
Ishurdi 132/33kV | 1 | 2:06 | 42
Jhenaidah 132/33kV | 1 | 6:13 | 74.6
Pabna 132/33kV | 1 | 7:28 | 224
Shahjadpur 132/33kV | 1 | 7:47 | 194.5833
Bhangura 132/33kV | 1 | 0:44 | 11.7333
Saidpur 132/33kV | 1 | 0:52 | 4.3333
Joypurhat 132/33kV | 1 | 0:41 | 19.8167
Panchagarh 132/33kV | 1 | 0:00 | 0
Thakurgaon 132/33kV | 1 | 0:48 | 32
Bog-Sherpur 132/33kV | 2 | 5:41 | 85.25
Bogura 132/33kV | 1 | 2:00 | 10
Jaldhaka 132/33kV | 3 | 11:26 | 194
Mahasthangarh 132/33kV | 1 | 4:47 | 66.9667
Naogaon 132/33kV | 1 | 2:23 | 154.9167
Sirajganj 132/33kV | 1 | 8:08 | 113.8667
| 126 | 438:52 | 13067.05
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: January-2026
Sl No. | Sub-station | Load (MW) | Date & Time
1 | AKS | 15 | 2026-01-21 21:00
2 | AKSML | 147 | 2026-01-18 08:00
3 | Aftabnagar | 30 | 2026-01-16 13:00
4 | Agargaon | 94 | 2026-01-16 13:00
5 | Agrabad | 52 | 2026-01-29 11:00
6 | Amnura | 46 | 2026-01-13 13:00
7 | Ashuganj | 77 | 2026-01-23 13:00
8 | BSRM | 210 | 2026-01-07 02:00
9 | Bagerhat | 75 | 2026-01-24 18:30
10 | Bajitpur | 75 | 2026-01-17 18:30
11 | Bakerganj | 0 | 2026-01-01 00:00
12 | Bakulia | 89 | 2026-01-10 13:00
13 | Banani | 41 | 2026-01-27 13:00
14 | Bangabhaban | 12 | 2026-01-29 13:00
15 | Barapukuria | 62 | 2026-01-30 09:00
16 | Barguna | 20 | 2026-01-10 19:30
17 | Barishal | 95 | 2026-01-02 13:00
18 | Barishal-230 | 93 | 2026-01-31 10:00
19 | Baroaulia | 66 | 2026-01-06 18:00
20 | Baroirhat | 64 | 2026-01-01 13:00
21 | Bashundhara | 169 | 2026-01-27 13:00
22 | BashundharaCement | 10 | 2026-01-04 18:00
23 | Beanibazar | 68 | 2026-01-21 13:00
24 | Benapole | 74 | 2026-01-17 09:00
25 | Bhaluka | 146 | 2026-01-10 19:00
26 | Bhandaria | 52 | 2026-01-17 18:30
27 | Bhangura | 44 | 2026-01-20 21:00
28 | Bheramara(GK) | 45 | 2026-01-04 18:00
29 | Bhulta | 210 | 2026-01-07 16:00
30 | Bog-Sherpur | 60 | 2026-01-12 18:30
31 | Bogura | 127 | 2026-01-31 19:00
32 | Borhanuddin | 68 | 2026-01-03 19:00
33 | Brahmanbaria | 104 | 2026-01-16 13:00
34 | Cantonment | 92 | 2026-01-05 13:00
35 | Chandina | 23 | 2026-01-16 13:00
36 | Chandpur | 66 | 2026-01-09 13:00
37 | Chandraghona | 29 | 2026-01-21 18:00
38 | Chapai | 60 | 2026-01-31 13:00
39 | Charsaidpur | 46 | 2026-01-01 15:00
40 | Chauddagram | 61 | 2026-01-23 13:00
41 | Chhatak | 33 | 2026-01-17 18:00
42 | Chowmuhani | 129 | 2026-01-06 13:00
43 | Chuadanga | 85 | 2026-01-16 13:00
44 | Coxsbazar | 120 | 2026-01-31 14:00
45 | Cumilla(N) | 127 | 2026-01-18 18:00
46 | Cumilla(S) | 146 | 2026-01-27 14:00
47 | Daganbhuiyan | 0 | 2026-01-01 00:00
48 | Daudkandi | 126 | 2026-01-29 19:00
49 | DhakaUniversity | 70 | 2026-01-27 13:00
50 | Dhamrai | 112 | 2026-01-31 18:00
51 | Dhanmondi | 87 | 2026-01-21 13:00
52 | Dohazari | 83 | 2026-01-24 20:00
53 | Faridpur | 145 | 2026-01-10 18:30
54 | Fatullah | 96 | 2026-01-13 12:00
55 | Fenchuganj | 37 | 2026-01-13 10:00
56 | Feni | 89 | 2026-01-09 13:00
57 | GPH | 100 | 2026-01-19 10:00
58 | Ghatail | 76 | 2026-01-10 18:00
59 | Ghorashal | 0 | 2026-01-01 00:00
60 | Ghorashal-230 | 97 | 2026-01-18 19:00
61 | Goalpara | 33 | 2026-01-09 13:00
62 | Gollamari | 92 | 2026-01-18 13:00
63 | Gopalganj | 84.2 | 2026-01-06 18:00
64 | Gulshan | 80 | 2026-01-21 13:00
65 | Halishahar | 74.5 | 2026-01-27 15:00
66 | HaripurSBU | 134 | 2026-01-20 12:00
67 | Hasnabad | 98 | 2026-01-04 13:00
68 | Hathazari | 75 | 2026-01-31 18:00
69 | Hatirjheel | 32 | 2026-01-28 14:00
70 | Ishurdi | 60 | 2026-01-03 18:00
71 | Jaldhaka | 60 | 2026-01-06 18:00
72 | Jamalpur | 100 | 2026-01-13 08:00
73 | Jashore | 124 | 2026-01-16 13:00
74 | Jhenaidah | 108 | 2026-01-19 08:00
75 | Joydebpur | 118 | 2026-01-19 19:00
76 | Joypurhat | 49 | 2026-01-31 09:00
77 | Juldah | 18 | 2026-01-21 11:00
78 | KSRM | 48 | 2026-01-07 19:00
79 | Kabirpur | 221 | 2026-01-29 18:00
80 | Kachua | 68 | 2026-01-12 23:00
81 | Kallyanpur | 99 | 2026-01-18 17:00
82 | Kalurghat | 44 | 2026-01-22 00:00
83 | Kamrangirchar | 72 | 2026-01-28 13:00
84 | Kaptai | N/A | N/A
85 | Kasba | 30 | 2026-01-16 13:00
86 | Kazla | 105 | 2026-01-24 13:00
87 | Keranigonj | 79 | 2026-01-19 13:00
88 | Khagrachori | 30 | 2026-01-24 18:30
89 | Khulna | 58 | 2026-01-31 13:00
90 | Khulshi | 175 | 2026-01-28 18:30
91 | Kishoreganj | 114 | 2026-01-17 18:30
92 | Kodda | 279 | 2026-01-29 18:00
93 | Kulaura | 37 | 2026-01-03 18:00
94 | Kurigram | 64 | 2026-01-30 08:00
95 | Kushtia | 128 | 2026-01-12 13:00
96 | Laksam | 24 | 2026-01-09 22:00
97 | Lakshmipur | 27 | 2026-01-01 15:00
98 | Lalbag | 72 | 2026-01-29 13:00
99 | Lalmonirhat | 52 | 2026-01-30 08:00
100 | MI_Cement | 18.7 | 2026-01-06 03:00
101 | Madanganj | 51 | 2026-01-10 01:00
102 | Madaripur | 92 | 2026-01-09 13:00
103 | Madartek | 70 | 2026-01-16 13:00
104 | Madunaghat | 95 | 2026-01-06 00:00
105 | Magura | 63 | 2026-01-31 18:30
106 | Mahasthangarh | 58 | 2026-01-14 18:00
107 | Maijdee | 43 | 2026-01-12 18:30
108 | Manikganj | 107 | 2026-01-07 18:30
109 | Maniknagar | 54 | 2026-01-14 13:00
110 | Matarbari | 82 | 2026-01-07 05:00
111 | Matuail | 58 | 2026-01-22 12:00
112 | Metrorail_Motijheel | 80 | 2026-01-07 03:00
113 | Metrorail_Uttara | 8 | 2026-01-01 09:00
114 | Millgate | 85 | 2026-01-29 12:00
115 | Mirpur | 120 | 2026-01-21 14:00
116 | Mirsorai | 45 | 2026-01-15 04:00
117 | Mirzapur | 45 | 2026-01-24 12:00
118 | Mithapukur | 78 | 2026-01-11 19:00
119 | Modern | N/A | N/A
120 | Mogbazar | 66.8 | 2026-01-29 13:00
121 | Mongla | 43 | 2026-01-11 14:00
122 | Motijheel | 38 | 2026-01-26 13:00
123 | Muktagacha | 39 | 2026-01-23 13:00
124 | Munshiganj | 84 | 2026-01-02 13:00
125 | Muradnagar | 27 | 2026-01-26 21:00
126 | Mymensingh | 180 | 2026-01-27 13:00
127 | Naogaon | 113 | 2026-01-31 09:00
128 | Narail | 51 | 2026-01-14 18:30
129 | Narinda | 62 | 2026-01-13 13:00
130 | Narshingdi | 149 | 2026-01-26 20:00
131 | Natore | 117 | 2026-01-31 13:00
132 | Nawabganj | 59.8 | 2026-01-14 20:00
133 | Netrakona | 131 | 2026-01-16 18:00
134 | New | 76 | 2026-01-25 12:00
135 | Niamatpur | 95 | 2026-01-27 09:00
136 | Noapara | 52 | 2026-01-17 13:00
137 | PHP | 9 | 2026-01-08 05:00
138 | Pabna | 81 | 2026-01-06 18:00
139 | Palashbari | 104 | 2026-01-31 18:00
140 | Panchagarh | 49 | 2026-01-07 18:00
141 | Patiya | 9 | 2026-01-30 13:00
142 | Patuakhali | 56.7 | 2026-01-10 18:30
143 | Payra | 46 | 2026-01-18 11:00
144 | Postogola | 44 | 2026-01-08 14:00
145 | Purbachal | 26 | 2026-01-29 18:00
146 | Purbasadipur | 126 | 2026-01-09 13:00
147 | Rahanpur | 27 | 2026-01-30 12:00
148 | Rahim | 57 | 2026-01-22 10:00
149 | Rajbari | 64 | 2026-01-06 18:00
150 | Rajendrapur | 125 | 2026-01-05 18:00
151 | Rajshahi | 82 | 2026-01-30 13:00
152 | Rajshahi-230 | 106 | 2026-01-10 13:00
153 | Ramganj | 100 | 2026-01-06 13:00
154 | Rampur | 40 | 2026-01-31 14:00
155 | Rangamati | 15 | 2026-01-28 18:00
156 | Rangpur | 124 | 2026-01-09 13:00
157 | Ruppur | 3 | 2026-01-26 15:00
158 | SSM | 13 | 2026-01-19 00:00
159 | Saidpur | 99 | 2026-01-27 09:00
160 | Satkhira | 107 | 2026-01-18 08:00
161 | Satmasjid | 87 | 2026-01-29 13:00
162 | Savar | 194 | 2026-01-12 12:00
163 | SevenRings | 23.03 | 2026-01-20 15:00
164 | ShahCement | 118 | 2026-01-15 07:00
165 | Shahjadpur | 61 | 2026-01-14 18:00
166 | Shahjibazar | 108 | 2026-01-30 19:30
167 | Shahmirpur | 44 | 2026-01-31 18:00
168 | Shariatpur | 70 | 2026-01-30 13:00
169 | Sherpur | 138 | 2026-01-30 19:00
170 | Shikalbaha | 28.5 | 2026-01-20 18:30
171 | Shitalakhya | 71.3 | 2026-01-29 13:00
172 | Sholosohor | 40 | 2026-01-22 12:00
173 | Shyampur | 164 | 2026-01-14 12:00
174 | Siddhirganj | 117 | 2026-01-28 12:00
175 | Sirajganj | 92 | 2026-01-19 18:00
176 | Sonargaon | 147 | 2026-01-19 18:00
177 | Sreemongol | 62 | 2026-01-19 18:30
178 | Sreepur | 105 | 2026-01-25 18:30
179 | Srinagar | 38.94 | 2026-01-09 13:00
180 | Sunamganj | 48 | 2026-01-29 19:00
181 | Sylhet | 44 | 2026-01-09 13:00
182 | Sylhet-132 | 99 | 2026-01-06 13:00
183 | TK | 20 | 2026-01-04 18:00
184 | Tangail | 154 | 2026-01-17 19:00
185 | Taraganj | 25 | 2026-01-25 18:00
186 | Tasnim | 38 | 2026-01-15 07:00
187 | Thakurgaon | 83 | 2026-01-04 18:00
188 | Tongi | 141 | 2026-01-31 13:00
189 | Ullahpara | 32 | 2026-01-05 13:00
190 | Ullon | 59 | 2026-01-02 13:00
191 | Uttara | 71 | 2026-01-18 11:00
192 | UttaraNew | 65 | 2026-01-06 23:00
193 | Zigatola | 80 | 2026-01-09 13:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID BANGLADESH PLC. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: January 2026
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 4417.76 | 2026-01-27 | 12:00
Chattogram | 1312 | 2026-01-29 | 18:30
Cumilla | 1083 | 2026-01-23 | 13:00
Mymensingh | 971 | 2026-01-17 | 19:00
Sylhet | 448 | 2026-01-17 | 18:00
Khulna | 1362.6 | 2026-01-10 | 18:30
Barishal | 342.5 | 2026-01-10 | 19:30
Rajshahi | 1069.4 | 2026-01-12 | 18:30
Rangpur | 803 | 2026-01-08 | 18:30
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: January-2026
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar | 400 | 426 | 2026-01-03 03:00 | 383 | 2026-01-07 12:00
2 | Amtali | 400 | 428 | 2026-01-25 13:00 | 412 | 2026-01-21 12:00
3 | Ashuganj | 400 | N/A | N/A | N/A | N/A
4 | Bhulta | 400 | 409 | 2026-01-04 04:00 | 372 | 2026-01-27 12:00
5 | Bibiana | 400 | 425 | 2026-01-16 13:00 | 381 | 2026-01-07 12:00
6 | BIPTC | 400 | 410 | 2026-01-01 04:00 | 385 | 2026-01-18 10:00
7 | Bogura | 400 | 421 | 2026-01-04 04:00 | 383 | 2026-01-12 13:00
8 | Gopalganj | 400 | 426 | 2026-01-06 05:00 | 396 | 2026-01-07 12:00
9 | Kaliakoir | 400 | 425 | 2026-01-07 05:00 | 373 | 2026-01-07 12:00
10 | Korerhat | 400 | 428 | 2026-01-09 06:00 | 400 | 2026-01-07 12:00
11 | Madunaghat | 400 | 424 | 2026-01-19 05:00 | 398 | 2026-01-18 15:00
12 | Meghnaghat | 400 | 431 | 2026-01-17 03:00 | 391 | 2026-01-07 12:00
13 | Payra | 400 | 429 | 2026-01-17 05:00 | 411 | 2026-01-06 13:00
14 | Rahanpur | 400 | 424 | 2026-01-04 04:00 | 395 | 2026-01-12 12:00
15 | Rampal | 400 | 421 | 2026-01-05 04:00 | 395 | 2026-01-07 12:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon | 230 | 249 | 2026-01-12 04:00 | 218 | 2026-01-07 12:00
2 | AKSML | 230 | 244.6 | 2026-01-04 06:00 | 228 | 2026-01-07 12:00
3 | Aminbazar | 230 | 248 | 2026-01-10 04:00 | 220 | 2026-01-07 12:00
4 | Ashuganj | 230 | 243 | 2026-01-20 23:00 | 223 | 2026-01-12 12:00
5 | Ashuganj-400 | 230 | N/A | N/A | N/A | N/A
6 | Baghabari | 230 | 244 | 2026-01-04 06:00 | 223 | 2026-01-12 12:00
7 | Barapukuria | 230 | 239 | 2026-01-20 19:00 | 204 | 2026-01-11 08:00
8 | Barapukuria-230 | 230 | N/A | N/A | N/A | N/A
9 | Barishal | 230 | 242 | 2026-01-03 04:00 | 227 | 2026-01-12 12:00
10 | Bheramara | 230 | 244 | 2026-01-05 04:00 | 221 | 2026-01-03 12:00
11 | Bhulta | 230 | 246 | 2026-01-03 04:00 | 222 | 2026-01-07 12:00
12 | Bibiana | 230 | 251 | 2026-01-07 04:00 | 226 | 2026-01-07 12:00
13 | BIPTC | 230 | 246 | 2026-01-31 04:00 | 221 | 2026-01-09 13:00
14 | Bogura | 230 | 247 | 2026-01-19 22:00 | 225 | 2026-01-05 13:00
15 | Bogura-400 | 230 | 246 | 2026-01-04 04:00 | 223 | 2026-01-12 13:00
16 | Borhanuddin | 230 | 243 | 2026-01-01 04:00 | 234 | 2026-01-07 12:00
17 | BSRM | 230 | 246 | 2026-01-04 05:00 | 227 | 2026-01-07 12:00
18 | Chowmuhani | 230 | N/A | N/A | N/A | N/A
19 | Cumilla(N) | 230 | 242 | 2026-01-02 04:00 | 225 | 2026-01-07 13:00
20 | Faridpur | 230 | 241 | 2026-01-01 05:00 | 225 | 2026-01-07 12:00
21 | Fenchuganj | 230 | 249 | 2026-01-05 05:00 | 232 | 2026-01-07 12:00
22 | Feni | 230 | 246 | 2026-01-03 03:00 | 226 | 2026-01-07 12:00
23 | Ghorashal | 230 | 248 | 2026-01-04 04:00 | 225 | 2026-01-12 13:00
24 | Ghorashal-230 | 230 | 244 | 2026-01-05 04:00 | 209 | 2026-01-15 12:00
25 | Gopalganj | 230 | 240 | 2026-01-06 02:00 | 223 | 2026-01-07 12:00
26 | GPH | 230 | 243 | 2026-01-03 03:00 | 223 | 2026-01-19 01:00
27 | Haripur | 230 | 246 | 2026-01-17 02:00 | 221 | 2026-01-07 12:00
28 | Hasnabad | 230 | 246 | 2026-01-03 06:00 | 219 | 2026-01-07 12:00
29 | Hathazari | 230 | 241 | 2026-01-29 18:30 | 224 | 2026-01-07 12:00
30 | Ishurdi | 230 | 246 | 2026-01-05 04:00 | 224 | 2026-01-09 13:00
31 | Jhenaidah | 230 | 246 | 2026-01-05 05:00 | 220 | 2026-01-05 13:00
32 | Kachua | 230 | 244 | 2026-01-04 04:00 | 227 | 2026-01-14 12:00
33 | Kaliakoir | 230 | 247 | 2026-01-01 03:00 | 218 | 2026-01-07 12:00
34 | Keranigonj | 230 | 248 | 2026-01-12 05:00 | 218 | 2026-01-07 12:00
35 | Khulna(S) | 230 | 249 | 2026-01-05 05:00 | 226 | 2026-01-10 13:00
36 | Korerhat | 230 | 246 | 2026-01-02 04:00 | 227 | 2026-01-07 12:00
37 | Madunaghat | 230 | 247 | 2026-01-12 19:30 | 228 | 2026-01-18 16:00
38 | Madunaghat-400 | 230 | 241 | 2026-01-02 03:00 | 228 | 2026-01-18 16:00
39 | Maniknagar | 230 | 244 | 2026-01-02 06:00 | 220 | 2026-01-07 12:00
40 | Meghnaghat | 230 | 250 | 2026-01-17 03:00 | 226 | 2026-01-07 12:00
41 | Meghnaghat-400 | 230 | 244 | 2026-01-01 03:00 | 211 | 2026-01-07 12:00
42 | Mirsorai | 230 | 246 | 2026-01-02 04:00 | 227 | 2026-01-08 00:00
43 | Rajshahi | 230 | 243 | 2026-01-03 05:00 | 218 | 2026-01-10 13:00
44 | Rampal | 230 | 249 | 2026-01-06 02:00 | 214 | 2026-01-21 19:00
45 | Rampur | 230 | N/A | N/A | N/A | N/A
46 | Rampura | 230 | 246 | 2026-01-04 04:00 | 221 | 2026-01-07 12:00
47 | Shikalbaha | 230 | 241 | 2026-01-29 17:00 | 224 | 2026-01-14 09:00
48 | Shyampur | 230 | 245 | 2026-01-01 05:00 | 219 | 2026-01-07 12:00
49 | Siddhirganj | 230 | 245 | 2026-01-02 04:00 | 222 | 2026-01-07 13:00
50 | Sirajgonj | 230 | 249 | 2026-01-04 04:00 | 224 | 2026-01-15 18:00
51 | Sreepur | 230 | 241 | 2026-01-20 23:00 | 218 | 2026-01-13 12:00
52 | Tongi | 230 | 247 | 2026-01-16 13:00 | 217 | 2026-01-07 10:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar | 132 | 138 | 2026-01-01 04:00 | 121 | 2026-01-27 12:00
2 | Agargaon | 132 | 142 | 2026-01-12 04:00 | 123 | 2026-01-07 12:00
3 | Agrabad | 132 | 140 | 2026-01-01 03:00 | 130 | 2026-01-19 12:00
4 | AKS | 132 | 137 | 2026-01-02 01:00 | 129 | 2026-01-18 16:00
5 | Aminbazar | 132 | 142 | 2026-01-19 00:00 | 124 | 2026-01-07 12:00
6 | Amnura | 132 | 140 | 2026-01-04 02:00 | 126 | 2026-01-10 12:00
7 | Ashuganj | 132 | 144 | 2026-01-02 04:00 | 133 | 2026-01-08 17:00
8 | Bagerhat | 132 | 138 | 2026-01-20 18:30 | 119 | 2026-01-14 12:00
9 | Bajitpur | 132 | 139 | 2026-01-03 11:00 | 124 | 2026-01-31 14:00
10 | Bakerganj | 132 | 142 | 2026-01-21 12:00 | 130 | 2026-01-22 06:00
11 | Bakulia | 132 | 141 | 2026-01-24 08:00 | 130 | 2026-01-26 02:00
12 | Banani | 132 | 138 | 2026-01-01 02:00 | 121 | 2026-01-27 12:00
13 | Bangabhaban | 132 | 142 | 2026-01-02 06:00 | 123 | 2026-01-13 12:00
14 | Barapukuria | 132 | 142 | 2026-01-18 23:00 | 122 | 2026-01-15 12:00
0 | Barguna | 132 | 142 | 2026-01-21 12:00 | 129 | 2026-01-22 08:00
16 | Barishal | 132 | 142 | 2026-01-01 06:00 | 132 | 2026-01-07 14:00
17 | Barishal-230 | 132 | 142 | 2026-01-01 03:00 | 132 | 2026-01-15 12:00
18 | Baroaulia | 132 | 141 | 2026-01-05 03:00 | 132 | 2026-01-18 13:00
19 | Baroirhat | 132 | 140 | 2026-01-02 04:00 | 127 | 2026-01-11 12:00
20 | Bashundhara | 132 | 138 | 2026-01-01 03:00 | 121 | 2026-01-27 12:00
21 | BashundharaCement | 132 | 139 | 2026-01-02 04:00 | 125 | 2026-01-16
22 | Beanibazar | 132 | 138 | 2026-01-01 06:00 | 121 | 2026-01-12 16:00
23 | Benapole | 132 | 138 | 2026-01-05 03:00 | 113 | 2026-01-05 13:00
24 | Bhaluka | 132 | 137 | 2026-01-01 15:00 | 117 | 2026-01-11 08:00
25 | Bhandaria | 132 | 141 | 2026-01-04 04:00 | 130 | 2026-01-14 12:00
26 | Bhangura | 132 | 142 | 2026-01-06 05:00 | 129 | 2026-01-12 12:00
27 | Bheramara | 132 | 143 | 2026-01-05 04:00 | 128 | 2026-01-01 12:00
28 | Bheramara(GK) | 132 | 143 | 2026-01-05 04:00 | 128 | 2026-01-01 12:00
29 | Bhulta | 132 | 136 | 2026-01-16 13:00 | 121 | 2026-01-07 12:00
30 | Bog-Sherpur | 132 | 141 | 2026-01-04 05:00 | 126 | 2026-01-12 12:00
31 | Bogura | 132 | 140 | 2026-01-01 04:00 | 127 | 2026-01-11 13:00
32 | Bogura-230 | 132 | 141 | 2026-01-06 05:00 | 127 | 2026-01-11 08:00
33 | Brahmanbaria | 132 | 139 | 2026-01-03 18:00 | 122 | 2026-01-12 16:00
34 | Cantonment | 132 | 141 | 2026-01-01 04:00 | 123 | 2026-01-07 12:00
35 | Chandina | 132 | 143 | 2026-01-01 03:00 | 130 | 2026-01-07 12:00
36 | Chandpur | 132 | 142 | 2026-01-02 03:00 | 130 | 2026-01-05 13:00
37 | Chandraghona | 132 | 141 | 2026-01-02 04:00 | 132 | 2026-01-19 12:00
39 | Chapai | 132 | 141 | 2026-01-05 05:00 | 130 | 2026-01-12 12:00
40 | Charsaidpur | 132 | 141 | 2026-01-03 06:00 | 126 | 2026-01-07 12:00
41 | Chauddagram | 132 | 141 | 2026-01-02 03:00 | 129 | 2026-01-07 12:00
42 | Chhatak | 132 | 137 | 2026-01-03 02:00 | 120 | 2026-01-13 12:00
43 | Chowmuhani | 132 | 138 | 2026-01-02 05:00 | 128 | 2026-01-05 12:00
44 | Chuadanga | 132 | 142 | 2026-01-01 04:00 | 122 | 2026-01-04 13:00
45 | Coxsbazar | 132 | 132 | 2026-01-03 02:00 | 117 | 2026-01-01 12:00
46 | Cumilla(N) | 132 | 143 | 2026-01-02 06:00 | 129 | 2026-01-07 12:00
47 | Cumilla(S) | 132 | 143 | 2026-01-01 02:00 | 119 | 2026-01-18 10:00
48 | Daganbhuiyan | 132 | 139 | 2026-01-01 03:00 | 127 | 2026-01-07 12:00
49 | Daudkandi | 132 | 140 | 2026-01-04 02:00 | 121 | 2026-01-11 12:00
50 | DhakaUniversity | 132 | 139 | 2026-01-01 04:00 | 121 | 2026-01-27 12:00
51 | Dhamrai | 132 | 140 | 2026-01-01 01:00 | 121 | 2026-01-07 09:00
52 | Dhanmondi | 132 | 142 | 2026-01-02 05:00 | 127.6 | 2026-01-27 12:00
53 | Dohazari | 132 | 139 | 2026-01-31 06:00 | 125 | 2026-01-19 13:00
54 | Faridpur | 132 | 141 | 2026-01-05 04:00 | 128 | 2026-01-24 12:00
55 | Fatullah | 132 | 142 | 2026-01-01 05:00 | 120 | 2026-01-07 12:00
56 | Fenchuganj | 132 | 145 | 2026-01-06 03:00 | 129 | 2026-01-12 16:00
57 | Feni | 132 | 138 | 2026-01-02 04:00 | 126 | 2026-01-07 12:00
58 | Feni-230 | 132 | 140 | 2026-01-16 02:00 | 127 | 2026-01-07 12:00
59 | Ghatail | 132 | 135 | 2026-01-02 06:00 | 118 | 2026-01-22 11:00
60 | Ghorashal | 132 | 139 | 2026-01-03 06:00 | 119 | 2026-01-07 11:00
61 | Goalpara | 132 | 140 | 2026-01-03 03:00 | 122 | 2026-01-31 12:00
62 | Gollamari | 132 | 139 | 2026-01-01 04:00 | 125 | 2026-01-14 13:00
63 | Gopalganj | 132 | 142 | 2026-01-01 05:00 | 121 | 2026-01-14 05:00
64 | Gopalganj-400 | 132 | 145 | 2026-01-04 04:00 | 124 | 2026-01-23 21:00
65 | Gulshan | 132 | 137 | 2026-01-01 06:00 | 121 | 2026-01-07 12:00
66 | Halishahar | 132 | 142 | 2026-01-29 18:00 | 132 | 2026-01-07 12:00
67 | Haripur | 132 | 141 | 2026-01-01 05:00 | 126 | 2026-01-27 12:00
68 | HaripurSBU | 132 | 141 | 2026-01-01 05:00 | 127 | 2026-01-07 12:00
69 | Hasnabad | 132 | 141 | 2026-01-21 02:00 | 124 | 2026-01-08 12:00
70 | Hathazari | 132 | 141 | 2026-01-03 05:00 | 131 | 2026-01-30 12:30
71 | Hatirjheel | 132 | 139 | 2026-01-01 05:00 | 122 | 2026-01-07 12:00
72 | Ishurdi | 132 | 144 | 2026-01-04 04:00 | 131 | 2026-01-01 12:00
73 | Jaldhaka | 132 | 136 | 2026-01-19 20:00 | 118 | 2026-01-04 18:00
74 | Jamalpur | 132 | 137 | 2026-01-05 10:00 | 108 | 2026-01-30 01:00
75 | Jashore | 132 | 139 | 2026-01-08 03:00 | 114 | 2026-01-31 12:00
76 | Jhenaidah | 132 | 142 | 2026-01-03 04:00 | 109 | 2026-01-08 18:30
77 | Jhenaidah-230 | 132 | 143 | 2026-01-05 04:00 | 123 | 2026-01-14 13:00
78 | Joydebpur | 132 | 137 | 2026-01-02 05:00 | 115 | 2026-01-05 12:00
79 | Joypurhat | 132 | 137 | 2026-01-05 02:00 | 123 | 2026-01-11 08:00
80 | Juldah | 132 | 142 | 2026-01-29 19:30 | 132 | 2026-01-07 12:00
81 | Kabirpur | 132 | 141 | 2026-01-01 03:00 | 117 | 2026-01-14 12:00
82 | Kachua | 132 | 143 | 2026-01-01 02:00 | 130 | 2026-01-05 13:00
83 | Kaliakoir | 132 | 144 | 2026-01-06 04:00 | 124 | 2026-01-07 09:00
84 | Kaliganj | 132 | N/A | N/A | N/A | N/A
85 | Kallyanpur | 132 | 141 | 2026-01-03 03:00 | 124 | 2026-01-07 12:00
86 | Kalurghat | 132 | 141 | 2026-01-03 03:00 | 133 | 2026-01-05 18:00
87 | Kamrangirchar | 132 | 140 | 2026-01-01 01:00 | 121 | 2026-01-07 12:00
88 | Kaptai | 132 | N/A | N/A | N/A | N/A
89 | Kasba | 132 | 142 | 2026-01-01 03:00 | 128 | 2026-01-07 12:00
90 | Kazla | 132 | 142 | 2026-01-03 04:00 | 122 | 2026-01-13 13:00
91 | Keranigonj | 132 | 140 | 2026-01-01 02:00 | 121 | 2026-01-07 12:00
92 | Khagrachori | 132 | 140 | 2026-01-02 03:00 | 131 | 2026-01-13 13:00
93 | Khulna | 132 | 139 | 2026-01-01 04:00 | 121 | 2026-01-31 12:00
94 | Khulna(S) | 132 | 140 | 2026-01-05 04:00 | 124 | 2026-01-31 12:00
95 | Khulshi | 132 | 139 | 2026-01-03 07:00 | 127 | 2026-01-18 10:00
96 | Kishoreganj | 132 | 136 | 2026-01-02 05:00 | 122 | 2026-01-31 14:00
97 | Kodda | 132 | 140 | 2026-01-21 18:00 | 120 | 2026-01-01 12:00
98 | KSRM | 132 | 141 | 2026-01-26 19:30 | 132 | 2026-01-08 12:00
99 | Kulaura | 132 | 142 | 2026-01-01 03:00 | 127 | 2026-01-12 16:00
100 | Kurigram | 132 | 136 | 2026-01-18 23:00 | 116 | 2026-01-11 08:00
101 | Kushtia | 132 | 141 | 2026-01-16 04:00 | 119 | 2026-01-08 18:30
102 | Laksam | 132 | 143 | 2026-01-01 02:00 | 130 | 2026-01-05 13:00
103 | Lakshmipur | 132 | 138 | 2026-01-02 03:00 | 127 | 2026-01-07 12:00
104 | Lalbag | 132 | 140 | 2026-01-01 06:00 | 122 | 2026-01-12 14:00
105 | Lalmonirhat | 132 | 135 | 2026-01-18 22:00 | 118 | 2026-01-03 18:00
106 | Madanganj | 132 | 140 | 2026-01-02 06:00 | 129 | 2026-01-14 16:00
107 | Madaripur | 132 | 143 | 2026-01-02 04:00 | 134 | 2026-01-06 13:00
108 | Madartek | 132 | 137 | 2026-01-01 02:00 | 121 | 2026-01-07 12:00
109 | Madunaghat | 132 | 141 | 2026-01-01 05:00 | 132 | 2026-01-18 11:00
110 | Magura | 132 | 141 | 2026-01-06 05:00 | 122 | 2026-01-10 13:00
111 | Mahasthangarh | 132 | 139 | 2026-01-04 05:00 | 125 | 2026-01-11 08:00
112 | Maijdee | 132 | 139 | 2026-01-04 02:00 | 127 | 2026-01-07 12:00
113 | Manikganj | 132 | 137 | 2026-01-01 02:00 | 116 | 2026-01-14 15:00
114 | Maniknagar | 132 | 142 | 2026-01-02 05:00 | 123 | 2026-01-13 13:00
115 | Matarbari | 132 | 139 | 2026-01-26 18:00 | 112 | 2026-01-04 13:00
116 | Matuail | 132 | 141.31 | 2026-01-03 06:00 | 115 | 2026-01-11 00:00
117 | Metrorail_Motijheel | 132 | 142 | 2026-01-02 05:00 | 123 | 2026-01-13 13:00
118 | Metrorail_Uttara | 132 | 141 | 2026-01-03 03:00 | 121 | 2026-01-27 12:00
119 | Millgate | 132 | 141 | 2026-01-03 04:00 | 113 | 2026-01-14 22:00
120 | Mirpur | 132 | 141 | 2026-01-19 22:00 | 123 | 2026-01-07 12:00
121 | Mirzapur | 132 | 140 | 2026-01-01 04:00 | 124 | 2026-01-07 12:00
122 | Mithapukur | 132 | 139 | 2026-01-18 18:00 | 122 | 2026-01-03 18:00
123 | MI_Cement | 132 | 139.3 | 2026-01-03 05:00 | 120 | 2026-01-07 12:00
124 | Modern | 132 | N/A | N/A | N/A | N/A
125 | Mogbazar | 132 | 139 | 2026-01-01 03:00 | 123 | 2026-01-19 06:00
126 | Mongla | 132 | 138 | 2026-01-01 03:00 | 119 | 2026-01-14 13:00
127 | Motijheel | 132 | 142 | 2026-01-02 06:00 | 123 | 2026-01-13 12:00
128 | Muktagacha | 132 | 138 | 2026-01-06 10:00 | 114 | 2026-01-30 01:00
129 | Munshiganj | 132 | 140 | 2026-01-02 06:00 | 125 | 2026-01-07 12:00
130 | Muradnagar | 132 | 142 | 2026-01-01 03:00 | 127 | 2026-01-11 12:00
131 | Mymensingh | 132 | 138 | 2026-01-06 10:00 | 114 | 2026-01-28 14:00
132 | Naogaon | 132 | 142 | 2026-01-30 20:00 | 122 | 2026-01-12 13:00
133 | Narail | 132 | 142 | 2026-01-01 03:00 | 122 | 2026-01-07 13:00
134 | Narinda | 132 | N/A | 2026-01-01 00:00 | N/A | N/A
135 | Narshingdi | 132 | 140 | 2026-01-03 22:00 | 114 | 2026-01-12 13:00
136 | Natore | 132 | 140 | 2026-01-21 18:30 | 127 | 2026-01-11 13:00
137 | Nawabganj | 132 | 140 | 2026-01-01 02:00 | 121 | 2026-01-07 12:00
139 | Netrakona | 132 | 131 | 2026-01-01 01:00 | 106 | 2026-01-31 14:00
140 | New Tongi | 132 | 141 | 2026-01-09 14:00 | 120 | 2026-01-10 12:00
141 | Niamatpur | 132 | 141 | 2026-01-04 06:00 | 130 | 2026-01-12 12:00
142 | Noapara | 132 | 139 | 2026-01-07 04:00 | 116 | 2026-01-01 13:00
143 | Pabna | 132 | 142 | 2026-01-05 04:00 | 127 | 2026-01-04 13:00
144 | Palashbari | 132 | 137 | 2026-01-17 19:30 | 121 | 2026-01-11 08:00
145 | Panchagarh | 132 | 141 | 2026-01-12 19:00 | 123 | 2026-01-01 08:00
146 | Patiya | 132 | 141 | 2026-01-26 19:30 | 131 | 2026-01-19 12:00
147 | Patuakhali | 132 | 141 | 2026-01-23 16:00 | 132 | 2026-01-10 19:00
148 | Payra | 132 | 143 | 2026-01-24 05:00 | 129 | 2026-01-22 10:00
149 | PHP | 132 | 140 | 2026-01-01 04:00 | 127 | 2026-01-11 13:00
150 | Postogola | 132 | 140 | 2026-01-01 04:00 | 122 | 2026-01-07 12:00
151 | Purbachal | 132 | 139 | 2026-01-01 03:00 | 121 | 2026-01-27 12:00
152 | Purbasadipur | 132 | 139 | 2026-01-12 19:00 | 117 | 2026-01-08 08:00
153 | Rahanpur | 132 | 142 | 2026-01-06 03:00 | 132 | 2026-01-12 13:00
154 | Rahanpur-400 | 132 | 142 | 2026-01-02 04:00 | 132 | 2026-01-12 12:00
155 | Rahim | 132 | 140 | 2026-01-02 03:00 | 126 | 2026-01-07 12:00
156 | Rajbari | 132 | 140 | 2026-01-03 05:00 | 128 | 2026-01-27 11:00
157 | Rajendrapur | 132 | 139 | 2026-01-01 03:00 | 117 | 2026-01-01 12:00
158 | Rajshahi | 132 | 140 | 2026-01-06 06:00 | 126 | 2026-01-11 12:00
159 | Rajshahi-230 | 132 | 140 | 2026-01-03 05:00 | 125 | 2026-01-10 12:00
160 | Ramganj | 132 | 139 | 2026-01-01 06:00 | 128 | 2026-01-05 13:00
161 | Rampur | 132 | 140 | 2026-01-02 02:00 | 130 | 2026-01-19 12:00
162 | Rampura | 132 | 138 | 2026-01-07 18:00 | 122 | 2026-01-07 11:00
163 | Rangamati | 132 | 140 | 2026-01-01 03:00 | 130 | 2026-01-02 07:00
164 | Rangpur | 132 | 140 | 2026-01-19 20:00 | 125 | 2026-01-31 08:00
165 | Ruppur | 132 | 140 | 2026-01-19 20:00 | 130 | 2026-01-01 12:00
166 | Saidpur | 132 | 139 | 2026-01-19 19:30 | 120 | 2026-01-12 08:00
167 | Satkhira | 132 | 138 | 2026-01-01 02:00 | 121 | 2026-01-15 13:00
168 | Satmasjid | 132 | 141 | 2026-01-04 04:00 | 122 | 2026-01-15 13:00
169 | Savar | 132 | 142 | 2026-01-19 22:00 | 122 | 2026-01-07 12:00
170 | SevenRings | 132 | 139 | 2026-01-01 05:00 | 119 | 2026-01-07 12:00
171 | ShahCement | 132 | 141 | 2026-01-03 06:00 | 126 | 2026-01-07 12:00
172 | Shahjadpur | 132 | 145 | 2026-01-05 04:00 | 133 | 2026-01-11 12:00
173 | Shahjibazar | 132 | 139 | 2026-01-03 06:00 | 121 | 2026-01-12 16:00
174 | Shahmirpur | 132 | 142 | 2026-01-29 18:00 | 132 | 2026-01-13 08:00
175 | Shariatpur | 132 | 143 | 2026-01-01 02:00 | 133 | 2026-01-07 13:00
176 | Sherpur | 132 | 135 | 2026-01-06 10:00 | 103 | 2026-01-30 01:00
177 | Shikalbaha | 132 | 130 | 2026-01-02 03:00 | 121 | 2026-01-19 12:00
178 | Shikalbaha-230 | 132 | 143 | 2026-01-29 18:00 | 122 | 2026-01-19 12:00
179 | Shitalakhya | 132 | 139.3 | 2026-01-03 05:00 | 120 | 2026-01-07 12:00
180 | Sholosohor | 132 | 141 | 2026-01-03 03:00 | 132 | 2026-01-18 16:00
181 | Shyampur | 132 | 140 | 2026-01-16 18:30 | 125 | 2026-01-07 12:00
182 | Shyampur-230 | 132 | 142 | 2026-01-01 05:00 | 126 | 2026-01-07 12:00
183 | Siddhirganj | 132 | 141 | 2026-01-02 06:00 | 127 | 2026-01-07 13:00
184 | Sirajganj | 132 | 140 | 2026-01-08 04:00 | 123 | 2026-01-06 12:00
185 | Sonargaon | 132 | 140 | 2026-01-02 03:00 | 116 | 2026-01-11 07:00
186 | Sreemongol | 132 | 139 | 2026-01-01 03:00 | 120 | 2026-01-12 16:00
187 | Sreepur | 132 | 141 | 2026-01-01 02:00 | 121 | 2026-01-11 08:00
188 | Srinagar | 132 | 140 | 2026-01-03 03:00 | 121 | 2026-01-07 12:00
189 | SSM | 132 | 143 | 2026-01-21 22:00 | 133 | 2026-01-10 08:00
190 | Sunamganj | 132 | 136 | 2026-01-01 04:00 | 116 | 2026-01-17 16:00
191 | Sylhet | 132 | 138 | 2026-01-01 03:00 | 122 | 2026-01-13 13:00
192 | Sylhet-132 | 132 | 138 | 2026-01-01 02:00 | 123 | 2026-01-12 16:00
193 | Tangail | 132 | 135 | 2026-01-01 05:00 | 120 | 2026-01-07 09:00
194 | Taraganj | 132 | 138 | 2026-01-19 20:00 | 120 | 2026-01-08 08:00
195 | Tasnim | 132 | 141 | 2026-01-08 02:00 | 123 | 2026-01-10 16:00
196 | Thakurgaon | 132 | 142 | 2026-01-12 19:00 | 121 | 2026-01-08 08:00
197 | TK | 132 | 141 | 2026-01-03 05:00 | 132 | 2026-01-19 12:00
198 | Tongi | 132 | 142 | 2026-01-03 04:00 | 120 | 2026-01-12 12:00
199 | Ullahpara | 132 | 148 | 2026-01-22 06:00 | 124 | 2026-01-06 12:00
200 | Ullon | 132 | 137 | 2026-01-01 02:00 | 121 | 2026-01-27 12:00
201 | Uttara | 132 | 141 | 2026-01-03 04:00 | 118 | 2026-01-14 12:00
202 | UttaraNew | 132 | 141 | 2026-01-03 03:00 | 121 | 2026-01-27 12:00
203 | Zigatola | 132 | 140 | 2026-01-01 03:00 | 120 | 2026-01-12 13:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-36
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month: January 2026
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Aminbazar 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 13-01-2026 | 13:00 | 365 | 114 | 73.5363
Aminbazar 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 10-01-2026 | 13:00 | 385 | 144 | 79.0478
Aminbazar 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 520 | 10-01-2026 | 13:00 | 385 | 144 | 79.0478
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 325 | 01-01-2026 | 00:00 | 0 | 0 | 0
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 03-01-2026 | 12:00 | 297 | 109 | 60.8404
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 03-01-2026 | 12:00 | 297 | 109 | 60.8404
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | 520 | 24-01-2026 | 04:00 | 242 | 29 | 46.8714
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | 520 | 07-01-2026 | 08:00 | 87 | 25 | 17.4078
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 750 | 14-01-2026 | 13:00 | 431 | 36 | 57.6668
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 750 | 15-01-2026 | 14:00 | 415 | 18 | 55.3854
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 750 | 14-01-2026 | 13:00 | 431 | 36 | 57.6668
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | 325 | 07-01-2026 | 18:30 | 106 | 58 | 37.1786
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | 325 | 07-01-2026 | 18:30 | 106 | 58 | 37.1786
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | 325 | 07-01-2026 | 18:30 | 106 | 58 | 37.1786
Gopalganj 400/230kV Grid Sub-Station | ATR-04 | 400/230 | 750 | 24-01-2026 | 16:00 | 85 | 145 | 22.4103
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 520 | 01-01-2026 | 12:00 | 102 | 12 | 19.7507
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 520 | 10-01-2026 | 12:00 | 202 | 68 | 40.9882
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 325 | 19-01-2026 | 08:00 | 292 | 80 | 93.1571
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 325 | 19-01-2026 | 08:00 | 292 | 80 | 93.1571
Madunaghat 400/230kV Grid Sub-Station | ATR-1 7006T | 400/230 | 750 | 19-01-2026 | 01:00 | 320 | 19 | 42.7418
Madunaghat 400/230kV Grid Sub-Station | ATR-2 7106T | 400/230 | 750 | 19-01-2026 | 01:00 | 320 | 19 | 42.7418
Madunaghat 400/230kV Grid Sub-Station | ATR-3 7206T | 400/230 | 750 | 19-01-2026 | 01:00 | 320 | 19 | 42.7418
Meghnaghat 400/230kV Grid Sub-Station | ATR-1 | 400/230 | 750 | 15-01-2026 | 12:00 | 377 | 10 | 50.2843
Meghnaghat 400/230kV Grid Sub-Station | ATR-2 | 400/230 | 750 | 13-01-2026 | 11:00 | 441 | 31 | 58.9451
Meghnaghat 400/230kV Grid Sub-Station | ATR-3 | 400/230 | 750 | 13-01-2026 | 11:00 | 445 | 35 | 59.5166
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | 520 | 09-01-2026 | 09:00 | 302 | 2 | 58.0782
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | 520 | 23-01-2026 | 08:00 | 272 | 1 | 52.308
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | 325 | 08-01-2026 | 13:00 | 69 | 11 | 21.4989
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | 325 | 07-01-2026 | 20:00 | 83 | 10 | 25.7232
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 520 | 31-01-2026 | 08:00 | 102 | 20 | 19.9889
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 520 | 02-01-2026 | 12:00 | 140 | 24 | 27.3158
Koerhat 400/230kV Grid Sub-Station | ATR-3 (7103T) | 400/230 | 1000 | 25-01-2026 | 17:00 | 378 | 61 | 38.289
Koerhat 400/230kV Grid Sub-Station | ATR-4 (7403T) | 400/230 | 1000 | 02-01-2026 | 13:00 | 277 | 19 | 27.7651
Koerhat 400/230kV Grid Sub-Station | ATR-2 (7203T) | 400/132 | 325
Koerhat 400/230kV Grid Sub-Station | ATR-3 (7303T) | 400/132 | 325
Mirsharai 400/230 kV Grid Sub-Station | ATR-1 | 400/230 | 1000
Mirsharai 400/230 kV Grid Sub-Station | ATR-2 | 400/230 | 1000
Ashuganj 400/230 kV GIS Grid Sub-Station | Interbus-1 | 400/230 | 325
Ashuganj 400/230 kV GIS Grid Sub-Station | Interbus-2 | 400/230 | 325
Amtali 400/132kV Grid Sub-Station
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 300 | 17-01-2026 | 13:00 | 234 | 68 | 81.2267
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 300 | 05-01-2026 | 14:00 | 242 | 57 | 82.8741
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 225 | 03-01-2026 | 12:00 | 174 | 32 | 83.2263
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 225 | 14-01-2026 | 12:00 | 182 | 12 | 83.2263
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 225 | 03-01-2026 | 12:00 | 174 | 32 | 83.2263
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 300 | 21-01-2026 | 10:00 | 235 | 60 | 80.8462
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 300 | 03-01-2026 | 18:30 | 230 | 70 | 80.1388
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 300 | 02-01-2026 | 18:30 | 206 | 24 | 69.1311
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 225 | 08-01-2026 | 19:00 | 118 | 19 | 53.1199
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 225 | 15-01-2026 | 17:00 | 106 | 6 | 47.1865
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 225 | 06-01-2026 | 05:00 | 141 | 60 | 68.1045
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 300 | 04-01-2026 | 09:00 | 130 | 47 | 46.0784
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 06-01-2026 | 13:00 | 106 | 7 | 35.4103
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 31-01-2026 | 16:00 | 115 | 0.2 | 38.3334
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | 225 | 03-01-2026 | 18:00 | 154 | 25 | 69.3405
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | 225 | 10-01-2026 | 18:00 | 110 | 17 | 49.4693
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 225 | 06-01-2026 | 18:30 | 147 | 12 | 65.5507
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 225 | 06-01-2026 | 18:30 | 147 | 12 | 65.5507
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 300 | 06-01-2026 | 18:30 | 197 | 23 | 66.1127
Bogura 230/132kV Grid Sub-Station | T-04 | 230/132 | 300 | 06-01-2026 | 18:30 | 197 | 23 | 66.1127
Naogaon 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 |  |  |  |  | 0
Naogaon 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 |  |  |  |  | 0
Naogaon 230/132kV Grid Sub-Station | ATR-3 | 230/132 | 300 |  |  |  |  | 0
Purbasadipur 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 31-01-2026 | 18:00 | 150 | 98 | 59.7253
Purbasadipur 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 12-01-2026 | 16:00 | 213 | 94 | 77.6066
Purbasadipur 230/132kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 01-01-2026 | 00:00 | 0 | 0 | 0
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-01 | 230/132 | 225 | 01-01-2026 | 00:00 | 0 | 0 | 0
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 | 230/132 | 225 | 27-01-2026 | 10:00 | 99 | 22 | 45.0733
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-03 | 230/132 | 225 | 27-01-2026 | 10:00 | 117 | 33 | 54.0288
Chowmohani 230/132 kV Grid Sub-Station | ATR-1 | 230/132 | 350 | 27-01-2026 | 10:00 | 107 | 24 | 31.331
Chowmohani 230/132 kV Grid Sub-Station | ATR-2 | 230/132 | 350 | 03-01-2026 | 12:00 | 104 | 44 | 32.2642
Chowmohani 230/132 kV Grid Sub-Station | ATR-3 | 230/132 | 350 | 03-01-2026 | 12:00 | 104 | 44 | 32.2642
Fenchuganj 230/132/33kV Grid Sub-Station | AT-01 | 230/132 | 300 | 03-01-2026 | 12:00 | 104 | 44 | 37.6416
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 300 | 06-01-2026 | 18:00 | 77 | 33 | 27.9245
Feni 230/132 kV GIS Grid Sub-Station | ATR-1 | 230/132 | 300 | 01-01-2026 | 00:00 | 0 | 0 | 0
Feni 230/132 kV GIS Grid Sub-Station | ATR-2 | 230/132 | 300 | 06-01-2026 | 18:00 | 77 | 33 | 27.9245
Feni 230/132 kV GIS Grid Sub-Station | ATR-3 | 230/132 | 300 | 06-01-2026 | 18:00 | 77 | 33 | 27.9245
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 125 | 03-01-2026 | 18:00 | 137 | 63 | 120.633
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 125 | 03-01-2026 | 18:00 | 137 | 63 | 120.633
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 225 | 01-01-2026 | 00:00 | 0 | 0 | 0
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 225 | 09-01-2026 | 13:00 | 191 | 50 | 87.7494
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 225 | 09-01-2026 | 13:00 | 191 | 50 | 87.7494
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 225 | 21-01-2026 | 00:00 | 0 | 0 | 0
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 225 | 19-01-2026 | 13:00 | 172 | 52 | 79.8616
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 225 | 19-01-2026 | 13:00 | 172 | 52 | 79.8616
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 150 | 01-01-2026 | 00:00 | 0 | 0 | 0
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 150 | 23-01-2026 | 21:00 | 169 | 7 | 112.7633
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 150 | 15-01-2026 | 18:30 | 144 | 20 | 96.9215
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 150 | 18-01-2026 | 08:00 | 194 | 23 | 130.2391
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 225 | 19-01-2026 | 18:00 | 106 | 20 | 47.9424
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 225 | 19-01-2026 | 18:00 | 106 | 20 | 47.9424
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 225 | 19-01-2026 | 18:00 | 106 | 20 | 47.9424
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | 300 | 13-01-2026 | 13:00 | 249 | 119 | 91.9915
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | 300 | 29-01-2026 | 13:00 | 225 | 87 | 80.4114
Kaliakoir 230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 300 | 03-01-2026 | 20:00 | 110 | 13 | 36.9218
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 03-01-2026 | 20:00 | 110 | 13 | 36.9218
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 01-01-2026 | 00:00 | 1 | 0 | 0.33333
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 01-01-2026 | 00:00 | 0 | 0 | 0
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | 225 | 09-01-2026 | 13:00 | 274 | 7 | 121.8175
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | 225 | 17-01-2026 | 13:00 | 275 | 17 | 122.4555
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | 300 | 17-01-2026 | 13:00 | 275 | 17 | 91.8417
Madunaghat 230/132/33kV Grid Sub-Station | ATR-1(705T) | 230/132 | 300 | 09-01-2026 | 12:00 | 203 | 125 | 79.4663
Madunaghat 230/132/33kV Grid Sub-Station | ATR-2(715T) | 230/132 | 300 | 10-01-2026 | 12:00 | 209 | 119 | 80.1679
Madunaghat 230/132/33kV Grid Sub-Station | ATR-3(725T) | 230/132 | 300 | 07-01-2026 | 13:00 | 82 | 35 | 29.7191
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 300 | 07-01-2026 | 13:00 | 82 | 35 | 29.7191
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 300 | 27-01-2026 | 09:00 | 125 | 53 | 45.2573
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | 300 | 27-01-2026 | 09:00 | 125 | 53 | 45.2573
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | 300 | 18-01-2026 | 14:00 | 261 | 65 | 89.6574
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 300 | 14-01-2026 | 13:00 | 259 | 61 | 88.6955
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 300 | 31-01-2026 | 18:00 | 215 | 25 | 72.1495
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 230/132 | 450 | 09-01-2026 | 13:00 | 274 | 7 | 60.9088
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 LT | 230/132 | 450 | 17-01-2026 | 13:00 | 275 | 17 | 61.2278
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 LT | 230/132 | 450 | 17-01-2026 | 13:00 | 275 | 17 | 61.2278
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 300 | 09-01-2026 | 12:00 | 203 | 125 | 79.4663
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 300 | 10-01-2026 | 12:00 | 209 | 119 | 80.1679
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 300 | 07-01-2026 | 13:00 | 82 | 35 | 29.7191
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 300 | 07-01-2026 | 13:00 | 82 | 35 | 29.7191
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 300 | 27-01-2026 | 09:00 | 125 | 53 | 45.2573
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 300 | 27-01-2026 | 09:00 | 125 | 53 | 45.2573
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 300 | 18-01-2026 | 14:00 | 261 | 65 | 89.6574
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 300 | 14-01-2026 | 13:00 | 259 | 61 | 88.6955
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 225 | 31-01-2026 | 18:00 | 215 | 25 | 96.1994
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 225 | 08-01-2026 | 15:00 | 200 | 25 | 89.5806
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 225 | 08-01-2026 | 15:00 | 200 | 25 | 89.5806
Tongi 230/132/33kV Grid Sub-Station | T-04 | 230/132 | 450 |  |  |  |  | 0
Bhulta 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 300 | 13-01-2026 | 11:15 | 171 | 59 | 60.2974
Bhulta 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 300 |  |  |  |  | 0
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF_LDC_37
|  |  |  | POWER GRID BANGLADESH PLC. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID BANGLADESH PLC. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[5 empty] | Report on load shedding | [12 empty] | Report on load shedding
Month: January-2026 |  |  |  | (For Evening Peak) | [10 empty] | Month: January-2026 |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur
2025-01-01 | 10592.22 | 10592.22 | 0 | 18:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-01-01 | 9683.67 | 9683.67 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-01-02 | 9605.14 | 9605.14 | 0 | 20:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-01-02 | 9664.78 | 9664.78 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-01-03 | 10806.5 | 10806.5 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-01-03 | 9522.76 | 9522.76 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-01-04 | 11000.55 | 11000.55 | 0 | 19:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-01-04 | 10067.54 | 10067.54 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-01-05 | 11058 | 11058 | 0 | 18:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-01-05 | 10297.08 | 10297.08 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-01-06 | 11123.27 | 11123.27 | 0 | 19:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-01-06 | 10551.06 | 10551.06 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-01-07 | 11209.54 | 11209.54 | 0 | 19:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-01-07 | 10359.07 | 10359.07 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-01-08 | 11311.4 | 11311.4 | 0 | 19:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-01-08 | 10353.14 | 10353.14 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-01-09 | 9897.93 | 9897.93 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-01-09 | 9699.26 | 9699.26 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-01-10 | 11120 | 11120 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-01-10 | 9471.25 | 9471.25 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0
2025-01-11 | 11379.07 | 11379.07 | 0 | 19:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-01-11 | 10487.28 | 10487.28 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-01-12 | 11430.48 | 11430.48 | 0 | 19:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-01-12 | 10496.66 | 10496.66 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-01-13 | 11531.7 | 11531.7 | 0 | 19:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-01-13 | 10458.54 | 10458.54 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-01-14 | 11624.56 | 11624.56 | 0 | 19:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-01-14 | 10668.45 | 10732.45 | 61 | 12:00 Hr. | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | -
2025-01-15 | 11608.6 | 11635.6 | 26 | 19:00 Hr. | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | - | 2025-01-15 | 10647.58 | 10647.58 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-01-16 | 10026.79 | 10026.79 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-01-16 | 9774.45 | 9774.45 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-01-17 | 11360.99 | 11360.99 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-01-17 | 9662.54 | 9662.54 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-01-18 | 11433.7 | 11433.7 | 0 | 20:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-01-18 | 10799.57 | 10799.57 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-01-19 | 11418.3 | 11418.3 | 0 | 19:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-01-19 | 10957.77 | 10967.77 | 10 | 12:00 Hr. | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-01-20 | 10932 | 11498 | 542 | 19:30 Hr. | 180 | 0 | 0 | 100 | 0 | 110 | 10 | 120 | 22 | - | 2025-01-20 | 10711.21 | 10711.21 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-01-21 | 10570.21 | 11549.21 | 937 | 19:30 Hr. | 300 | 70 | 70 | 110 | 15 | 160 | 40 | 117 | 55 | - | 2025-01-21 | 10710.19 | 11124.19 | 396 | 12:00 Hr. | 185 | 0 | 25 | 55 | 0 | 60 | 5 | 46 | 20 | -
2025-01-22 | 11351.7 | 11550.7 | 190 | 19:30 Hr. | 0 | 0 | 20 | 65 | 0 | 55 | 0 | 40 | 10 | - | 2025-01-22 | 10836.13 | 11153.13 | 303 | 12:00 Hr. | 95 | 20 | 0 | 32 | 0 | 75 | 7 | 50 | 24 | -
2025-01-23 | 10164.3 | 10164.3 | 0 | 19:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-01-23 | 10167.95 | 10167.95 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-01-24 | 11342.7 | 11548.97 | 151 | 20:00 Hr. | 0 | 0 | 0 | 31 | 0 | 70 | 0 | 40 | 10 | - | 2025-01-24 | 10272.22 | 10272.22 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-01-25 | 11186.91 | 11699.91 | 491 | 19:00 Hr. | 110 | 0 | 10 | 45 | 0 | 160 | 0 | 95 | 71 | - | 2025-01-25 | 10679.94 | 11203.94 | 501 | 12:00 Hr. | 176 | 0 | 30 | 98 | 35 | 62 | 0 | 54 | 46 | -
2025-01-26 | 10959.19 | 11700.19 | 709 | 19:00 Hr. | 0 | 66 | 82 | 118 | 60 | 164 | 34 | 73 | 112 | - | 2025-01-26 | 10237.36 | 11151.36 | 875 | 12:00 Hr. | 250 | 85 | 80 | 130 | 35 | 150 | 30 | 80 | 35 | -
2025-01-27 | 11154.97 | 11599.97 | 426 | 19:30 Hr. | 56 | 0 | 10 | 100 | 0 | 150 | 20 | 60 | 30 | - | 2025-01-27 | 11046.28 | 11254.28 | 199 | 12:00 Hr. | 50 | 25 | 14 | 45 | 20 | 45 | 0 | 0 | 0 | -
2025-01-28 | 11159 | 11679 | 498 | 18:00 Hr. | 115 | 0 | 8 | 56 | 31 | 137 | 36 | 65 | 50 | - | 2025-01-28 | 10751.14 | 11304.14 | 529 | 12:00 Hr. | 200 | 10 | 20 | 40 | 20 | 150 | 10 | 50 | 29 | -
2025-01-29 | 11504.39 | 11801.39 | 284 | 19:00 Hr. | 74 | 0 | 10 | 50 | 10 | 80 | 20 | 20 | 20 | - | 2025-01-29 | 10155.9 | 11200.9 | 1000 | 12:00 Hr. | 310 | 80 | 140 | 140 | 53 | 158 | 15 | 64 | 40 | -
2025-01-30 | 10541.4 | 10541.4 | 0 | 19:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-01-30 | 10722.21 | 10722.21 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-01-31 | 11900.14 | 11980.14 | 77 | 19:00 Hr. | 22 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | - | 2025-01-31 | 10202.18 | 10274.18 | 69 | 12:00 Hr. | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
[16 empty] | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: January 2026
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 11900.14 | 2026-01-31 | 19:00 Hr.
2 | Maximum Day Peak Genaration | MW | 11046.28 | 2026-01-27 | 12:00 Hr.
3 | Maximum Evening Peak Demand | MW | 11980.14 | 2026-01-31 | 19:00 Hr.
4 | Minimum Generation | MW | 6599.78 | 2026-01-01 | 05:00 Hr.
5 | Average of the daily evening peak Genaration | MW | 11042.1177 | - | -
6 | Average of the daily day peak Genaration | MW | 10326.2955 | - | -
7 | Maximum load shed (Evening Peak) | MW | 937 | 2025-01-21 | 19:30 Hr.
8 | Minimum load shed | MW | 26 | 2025-01-15 | 19:00 Hr.
9 | Total nos. of load shed days | Day | 11 | - | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 139.7097 | - | -
11 | Total Generation | MkWh | 7183.356 | - | -
12 | Total Generation by BPDB | MkWh | 545.6269 | % of total Gen. | 7.596%
13 | Total Generation by IPP | MkWh | 2271.6537 | '' | 31.62%
14 | A) Total Generation by Generation Companies | MkWh | 2998.9512 | '' | 41.75%
| B) Total Generation by REB | MkWh | 46.5401 | " | 0.6479%
| C) Total Generation by RENTAL | MkWh | 91.3657 | " | 1.272%
| D) Total Imported from India (BIPTC) | MkWh | 486.3709 | " | 6.771%
| E) Total Imported from Tripura, India (A.C) | MkWh | 75.9053 | " | 1.057%
| F) Total Imported from Nepal | MkWh | 0 | " | 0%
| E) Total Imported from India (Adani Power Jharkhanda Ltd) | MkWh | 666.9421 | " | 9.285%
15 | Fuel wise Generation.
| A) Gas | MkWh | 2908.1434 | % of total Gen. | 40.48%
| B) Oil | MkWh | 489.8404 | '' | 6.819%
| C) Hydro | MkWh | 35.0787 | '' | 0.4883%
| D) Solar | MkWh | 102.2478 | '' | 1.423%
| E) Coal | MkWh | 2411.8007 | '' | 33.57%
| F) BIPTC (Import from India) | MkWh | 486.3709 | '' | 6.771%
| G) A.C (Import from Tripura, India) | MkWh | 75.9053 | '' | 1.057%
| H) Total Imported from Nepal | MkWh | 0 | '' | 0%
| I) Adani (Import from India) | MkWh | 666.9421 | '' | 9.285%
| J) Wind | MkWh | 7.0267 | '' | 0.09782%
16 | Maximun of the daily total Generation . | MkWh | 245.8073 | 2026-01-27
17 | Monthly Load factor | % | 81.1339 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 43801.6752 | - | -
| A) Gas | M.Taka | 10225.6127 | - | -
| B) Coal | M.Taka | 15826.1994 | - | -
| C) HFO | M.Taka | 8762.5469 | - | -
| D) HSD | M.Taka | 0 | - | -
| E) Hydro | M.Taka | 3.5079 | - | -
| F) Solar | M.Taka | 1606.8375 | - | -
| G) Total Import | M.Taka | 7273.6078 | - | -
| H) Wind | M.Taka | 103.3631 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1733.3536 | 2026-01-20
| A) Gas | M.Taka | 367.6949 | 2026-01-30
| B) Coal | M.Taka | 574.7816 | 2026-01-08
| C) HFO | M.Taka | 654.0816 | 2026-01-20
| D) HSD | M.Taka | 0 | 2026-01-01 | -
| E) Hydro | M.Taka | 0.20696 | 2026-01-23 | -
| F) Solar | M.Taka | 63.6356 | 2026-01-28 | -
| G) Total Import | M.Taka | 315.2441 | 2026-01-14
| H) Wind | M.Taka | 8.6636 | 2026-01-26
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 5.9068
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 6.0279
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 97.2 | 31/1/2026 | 06:00
b) | Actual | FT (MSL) | 95.1 | 31/1/2026 | 06:00
22 | Peak Genaration of January 2025 | MW | 11385.54 | 2025-01-31 | 19:00 Hr.
23 | Peak Demand of January 2025 | MW | 11385.54 | 2025-01-31 | 19:00 Hr.
24 | Maximum peak Generation recorded upto 31/01/2026 | MW | 16794 | 2025-07-23 | 21:00
25 | Maximum peak Demand recorded upto 31/01/2026 | MW | 16794 | 2025-07-23 | 21:00
26 | Maximum load shed recorded upto 31/01/2026 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## FGMO Weekly
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status | [49 empty] | SR at 50 Hz (MW)
SL | Plant Name | Owner | Fuel | Installed capacity (MW) | Capability Status of Last Week | 29.01.2026 | 22.01.2026 | 15.01.2026 | 08.01.2026 | 01.01.2026 | 25.12.2025 | 18.12.2025 | 11.12.2025 | 04.12.2025 | 27.11.2025 | 20.11.2025 | 13.11.2025 | 06.11.2025 | 30.10.2025 | 23.10.2025 | 16.10.2025 | 09.10.2025 | 02.10.2025 | 25.09.2025 | 18.09.2025 | 11.09.2025 | 04.09.2025 | 28.08.2025 | 21.08.2025 | 14.08.2025 | 07.08.2025 | 31.07.2025 | 24.07.2025 | 17.07.2025 | 10.07.2025 | 03.07.2025 | 26.06.2025 | 19.06.2025 | 12.06.2025 | 05.06.2025 | 29.05.2025 | 22.05.2025 | 15.05.2025 | 08.05.2025 | 01.05.2025 | 24.04.2025 | 17.04.2025 | 10.04.2025 | 03.04.2025 | 27.03.2025 | 20.03.2025 | 13.03.2025 | 06.03.2025 | 27.02.2025 | 20.02.2025 | 13.02.2025 | 06.02.2025 | 30.01.2025 | 23.01.2025 | 16.01.2025 | 09.01.2025 | 02.01.2025 | 28.11.2024 | 21.11.2024 | 14.11.2024 | 07.11.2024 | 31.10.2024 | 24.10.2024 | 17.10.2024 | 10.10.2024 | 03.10.2024 | 26.09.2024 | 19.09.2024 | 05.09.2024 | 12.09.2024 | 29.08.2024 | 22.08.2024 | 15.08.2024 | 08.08.2024 | 01.08.2024 | 25.07.2024 | 18.07.2024 | 11.07.2024 | 04.07.2024 | 27.06.2024 | 20.06.2024 | 13.06.2024 | 06.06.2024 | 30.05.2024 | 22.05.2024 | 16.05.2024 | 09.05.2024 | 02.05.2024 | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | Gas | 341 | Capable | 30 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | Gas | 414 | Capable | 40 |  |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | Gas | 220 | Capable | [24 empty] | 20 | 20 | [7 empty] | 20 | [41 empty] | 20 | [7 empty] | 20 | 20 | 20 | 20
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | Gas | 220 | Capable | [5 empty] | 20 | 20 | [18 empty] | 20 | [5 empty] | 20 | 20 | 20 | 20 | [40 empty] | 20 |  | 15 | 15 |  | 15 |  |  |  | 20 | 20 | 20 | 20
5 | Meghnaghat CCPP(Summit) | IPP | Gas | 305 | Capable | [15 empty] | 7 | 7 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 10 | 10 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 15 | 30 | [7 empty] | 35 | [6 empty] | 25 | 15 | 15 | 15 | 15 | 30 | 30 | 30 |  |  |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
6 | Ashuganj 450 MW CCPP(North) | APSCL | Gas | 360 | Capable | [56 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 |  |  | 30 | 30 | 30 |  |  |  | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
7 | Ashuganj 225 MW CCPP | APSCL | Gas | 221 | Capable |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | [11 empty] | 15 | 15 | 15 | 15 | [15 empty] | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
8 | Bheramara 410 MW CCPP | NWPGCL | Gas | 410 | Capable | [25 empty] | 45 | [47 empty] | 40 | [6 empty] | 30 |  |  |  | 30 | 30 | 30 | 30 | 30
9 | Haripur 412 MW CCPP | EGCB | Gas | 412 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
10 | Fenchugonj CCPP Phase-1 | BPDB | Gas | 97 | Capable | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [24 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
11 | Chandpur 150 MW CCPP | BPDB | Gas | 163 | Capable
12 | Siddhirganj 2x120 MW GTPP | EGCB | Gas | 210 | Capable
13 | Shikalbaha 225 MW CCPP | BPDB | Gas | 225 | Capable
14 | Shikalbaha Peaking GT | BPDB | Gas | 150 | Capable
15 | Shahjibazar 330 MW CCPP | BPDB | Gas | 330 | Capable | [49 empty] | 40 | [20 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 |  |  |  | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
16 | Ashuganj 450 MW CCPP(South) | APSCL | Gas | 360 | Capable | [46 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
17 | Fenchugonj CCPP Phase-2 | BPDB | Gas | 104 | Capable | [23 empty] | 2 |  |  | 2 | 2 | [18 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
18 | Bhola 225 MW CCPP | BPDB | Gas | 194 | Capable | [28 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | Gas | 365 | Capable
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | Gas | 210 | Capable |  | 20 | 20 | 20 | 20 |  |  | 20 | 20 | 20 |  |  |  | 20 | [10 empty] | 20 | 16 | [7 empty] | 20 | 20 | [38 empty] | 20 | [6 empty] | 15 | [6 empty] | 15 | 20 | 20 | 20
21 | Siddhirganj 335 MW CCPP | EGCB | Gas | 335 | Capable | [34 empty] | 30 | 30 | 30 | 30 |  | 30 | 30
22 | Bibiyana-III 400 MW CCPP | BPDB | Gas | 400 | Capable | [9 empty] | 30 | 30 | 30 | 30 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 |  |  |  |  | 35 | 35 | 35 | 35 | 35 | [14 empty] | 35 | 35 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
23 | Sylhet 225 MW CCPP | BPDB | Gas | 231 | Capable
24 | RPCL 210 MW CCPP | IPP | Gas | 210 | Capable but not tested recently
25 | a) Baghabari 71 MW GTPP | BPDB | Gas | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | Gas | 100 | Not Capable but feasible
26 | Karnaphuli Hydro PP Unit: 1 | BPDB | Hydro | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | Hydro | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | Hydro | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | Hydro | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | Hydro | 50 | Not Capable but feasible
27 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | Gas | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | Gas | 410 | Not Capable but feasible
28 | Bibiyana South 400 MW CCPP | BPDB | Gas | 400 | Capable | [54 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
29 | Barapukuria 275 MW TPP Unit-3 | BPDB | Coal | 274 | Not Capable but feasible
16 | Payra 1320 MW Unit-1 & 2 | BCPCL | Coal | 1244 | Capable | 30 | 30 | 30 | 30 | 60 | 60 | 60 | 60 | 60 |  |  |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | [7 empty] | 20 | 20
31 | Kushiara 163 MW CCPP (KP) | IPP | Gas | 163 | Capable | 16 | 16 | 16 | 16 | [6 empty] | 16 | 16 | 30 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  | 16 | 16 | 16 | 16 | 10 | 10 | 10 | 10 | 10
32 | Bhola Nutan Bidyut | IPP | Gas | 220 | Capable
33 | Haripur 360MW CCPP(HPL) | IPP | Gas | 360 | Not Capable but feasible
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | Gas | 450 | Not Capable but feasible
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | Coal | 1150 | Capable | [23 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30
36 | Anwara 300 MW PP (United) | IPP | HFO | 300 | Capable
37 | Chandpur 200MW (Desh energy) | IPP | HFO | 200 | Capable
38 | Meghnaghat 104 MW PP (OPCL) | IPP | HFO | 104 | Capable
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | HFO | 105 | Capable
40 | Gazipur 100 MW PP | IPP | HFO | 105 | Capable
41 | United Payra Power Ltd. | IPP | HFO | 150 | Capable
42 | Madhumati 100 MW PP | IPP | HFO | 100 | Capable
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | HFO | 105 | Capable
44 | Karnaphuli Power Ltd. | IPP | HFO | 110 | Capable
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | HFO | 300 | Capable
46 | Madanganj-55 MW PP(Summit) | IPP | HFO | 55 | Capable
47 | Kodda 149 MW PP Unit-1 (Summit) | IPP | HFO | 149 | Capable
48 | Feni Lanka Power | IPP | HFO | 114 | Capable
49 | Barisal 110 MW PP (Summit) | IPP | HFO | 110 | Capable
50 | Manikganj 162 MW (MPGL) | IPP | HFO | 162 | Capable
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | HFO | 55 | Capable
52 | Zodiac 54 MW | IPP | HFO | 54 | Capable
53 | Anlima Energy Ltd | IPP | HFO | 116 | Capable
54 | Thakurgaon 115 MW (EPV) | IPP | HFO | 115 | Capable
55 | Confidence Unit-2 Bogura | IPP | HFO | 113 | Capable
56 | Confidence Unit-1 Bogura | IPP | HFO | 113 | Capable
57 | Kamalaghat 54 MW Banco Energy | IPP | HFO | 54 | Capable
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | HFO | 55 | Capable
59 | Kodda 150 MW (BR Power) | IPP | HFO | 149 | Capable
60 | Chandpur 115 MW (Doreen) | IPP | HFO | 115 | Capable
61 | Kanchan Purbachal Power Ltd | IPP | HFO | 55 | Capable
62 | Chattogram SS Power U- 1 & 2 | Private | Coal | 1224 | Capable | 33 | 66 | 66 | 66 | 66 | 66 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 66 | 66
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | Coal | 1436 | Capable | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  | 50 | 50 | 50 | 50 | 20 | 20 | 40 | 20 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | Coal | 1234 | Capable | 25 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 50 | 50 | 50 | 50
65 | Barishal 307 MW PP (BEPCL) | Private | Coal | 307 | Capable | 30 | 30 | 30 | [11 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
66 | Unique Meghnaghat Power Ltd(UMPL) | IPP | Gas | 584 | [12 empty] | 24 | 24 | 24 |  |  |  |  | 50 | 24 | 24 | 50
67 | Meghnaghat CCPP Unit 2 (Summit) | [5 empty] | 50 | 50 | 50 | 50 | 50 | 50
| Payra 1320 MW Unit-2 | BCPCL |  | 622 | Capable | [38 empty] | 20 | 20
| Shahjibazar GTPP Unit 8 & 9 | BPDB |  | 70 | Capable
| Shajibazar 100 MW PP | BPDB |  | 100 | Not Capable but feasible
| Khulna 225 MW CCPP | NWPGCL |  | 230 | Capable but not tested recently
Total Installed capacity | [5 empty] | 20506 | 20506 | 20506 | 20506 | 20506 | 20506 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19339 | 19339 | 19339 | 19339 | 19339 | 19339 | 19339 | 19739 | 19739 | 19739 | 19739 | 14388 | 14388 | 14388 | 14388 | 14388 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity | [5 empty] | 4146 | 5722 | 6660 | 6754 | 7086 | 6756 | 5564 | 5851 | 5937 | 5232 | 5185 | 3503 | 3503 | 6403 | 6525 | 5821 | 6221 | 6871 | 7523 | 8031 | 7313 | 7523 | 6939 | 8121 | 8527 | 9061 | 8099 | 8099 | 7580 | 8537 | 6163 | 6795 | 6632 | 2862 | 3135 | 2325 | 2165 | 2165 | 2525 | 2855 | 2325 | 1595 | 1635 | 1072 | 1812 | 1432 | 1464 | 1064 | 592 | 1332 | 1282 | 1682 | 1302 | 1302 | 1685 | 1685 | 1315 | 1813 | 2027 | 1475 | 1475 | 1092 | 1124 | 744 | 712 | 712 | 1802 | 1492 | 1152 | 1492 | 2442 | 2442 | 2036 | 2956 | 2416 | 2476 | 1836 | 1696 | 1696 | 1876 | 3336 | 1196 | 1196 | 1796 | 3416 | 3436 | 3076 | 3038 | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve | [5 empty] | 256 | 359 | 399 | 429 | 443 | 398 | 365 | 358 | 358 | 328 | 324 | 228 | 228 | 351 | 372 | 349 | 379 | 427 | 477 | 471 | 451 | 477 | 427 | 459 | 452 | 503 | 386 | 404 | 382 | 452 | 356 | 424 | 408 | 262 | 288 | 218 | 193 | 193 | 202 | 232 | 212 | 152 | 137 | 92 | 172 | 142 | 144 | 109 | 67 | 137 | 132 | 167 | 137 | 137 | 162 | 162 | 122 | 160 | 179 | 132 | 132 | 107 | 109 | 79 | 77 | 77 | 172 | 137 | 107 | 137 | 217 | 217 | 186 | 271 | 216 | 226 | 156 | 141 | 156 | 171 | 291 | 111 | 111 | 161 | 311 | 316 | 276 | 269 | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO | [5 empty] | 10 | 11 | 12 | 12 | 11 | 10 | 10 | 9 | 9 | 9 | 9 | 7 | 7 | 9 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 12 | 14 | 13 | 15 | 12 | 12 | 12 | 13 | 11 | 14 | 13 | 11 | 12 | 9 | 9 | 9 | 10 | 11 | 9 | 7 | 7 | 5 | 7 | 6 | 7 | 6 | 3 | 5 | 5 | 6 | 5 | 5 | 6 | 6 | 5 | 6 | 8 | 5 | 5 | 4 | 5 | 4 | 3 | 3 | 6 | 5 | 4 | 5 | 8 | 8 | 8 | 11 | 9 | 10 | 7 | 7 | 7 | 7 | 12 | 5 | 5 | 7 | 12 | 12 | 11 | 11 | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list | [5 empty] | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 68 | 68 | 68 | 68 | 64 | 64 | 64 | 64 | 64 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list | [5 empty] | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 74 | 74 | 74 | 74 | 70 | 70 | 70 | 70 | 70 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable | [5 empty] | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 63 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 63 | 63 | 63 | 61 | 61 | 61 | 61 | 62 | 62 | 62 | 62 | 58 | 58 | 58 | 58 | 58 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible | [5 empty] | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant

## FGMO
Power Grid Bangladesh PLC.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: January 2026
SL | Plant Name | Owner | Fuel | Installed capacity | FGMO Status
|  |  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | Gas | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | Gas | 414 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [12 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | Gas | 220
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | Gas | 220
5 | Meghnaghat CCPP(Summit) | IPP | Gas | 305
6 | Ashuganj 450 MW CCPP(North) | APSCL | Gas | 360 | [6 empty] | √ | √ | [5 empty] | √ | √ |  | √ |  |  |  | √ | √ |  | √ |  | √ |  | √ | √ | √ | √
7 | Ashuganj 225 MW CCPP | APSCL | Gas | 221 | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √
8 | Bheramara 410 MW CCPP | NWPGCL | Gas | 410 |  |  |  |  | √ | √
9 | Haripur 412 MW CCPP | EGCB | Gas | 412 | √ |  |  |  |  | √ | √ | √ | √ | √ | √ | √
10 | Fenchugonj CCPP Phase-1 | BPDB | Gas | 97
11 | Chandpur 150 MW CCPP | BPDB | Gas | 163
12 | Siddhirganj 2x120 MW GTPP | EGCB | Gas | 210
13 | Shikalbaha 225 MW CCPP | BPDB | Gas | 225
14 | Shikalbaha Peaking GT | BPDB | Gas | 150
15 | Shahjibazar 330 MW CCPP | BPDB | Gas | 330
16 | Ashuganj 450 MW CCPP(South) | APSCL | Gas | 360
17 | Fenchugonj CCPP Phase-2 | BPDB | Gas | 104
18 | Bhola 225 MW CCPP | BPDB | Gas | 194
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | Gas | 365
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | Gas | 210 |  | √ | √ | √ | √ |  | √ |  |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
21 | Siddhirganj 335 MW CCPP | EGCB | Gas | 335
22 | Bibiyana-III 400 MW CCPP | BPDB | Gas | 400
23 | Sylhet 225 MW CCPP | BPDB | Gas | 231
24 | RPCL 210 MW CCPP | IPP | Gas | 210
25 | a) Baghabari 71 MW GTPP | BPDB | Gas | 71
| b) Baghabari 100 MW GTPP | BPDB | Gas | 100
26 | Karnaphuli Hydro PP Unit: 1 | BPDB | Hydro | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | Hydro | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | Hydro | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | Hydro | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | Hydro | 50
27 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | Gas | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | Gas | 410
28 | Bibiyana South 400 MW CCPP | BPDB | Gas | 400
29 | Barapukuria 275 MW TPP Unit-3 | BPDB | Coal | 274
30 | Payra 1320 MW Unit-1 & 2 | BCPCL | Coal | 1244 | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ |  | √ |  | √ | √ | √ | √
31 | Kushiara 163 MW CCPP (KP) | IPP | Gas | 163 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
32 | Bhola Nutan Bidyut | IPP | Gas | 220
33 | Haripur 360MW CCPP(HPL) | IPP | Gas | 360
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | Gas | 450
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | Coal | 1150
36 | Anwara 300 MW PP (United) | IPP | HFO | 300
37 | Chandpur 200MW (Desh energy) | IPP | HFO | 200 | [8 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
38 | Meghnaghat 104 MW PP (OPCL) | IPP | HFO | 104
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | HFO | 105
40 | Gazipur 100 MW PP | IPP | HFO | 105
41 | United Payra Power Ltd. | IPP | HFO | 150
42 | Madhumati 100 MW PP | IPP | HFO | 100
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | HFO | 105
44 | Karnaphuli Power Ltd. | IPP | HFO | 110 | [26 empty] | √ | √ | √ | √ | √
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | HFO | 300
46 | Madanganj-55 MW PP(Summit) | IPP | HFO | 55
47 | Kodda 150 MW PP BRPL | IPP | HFO | 149
48 | Feni Lanka Power | IPP | HFO | 114 | [26 empty] | √ | √ | √ | √ | √
49 | Barisal 110 MW PP (Summit) | IPP | HFO | 110
50 | Manikganj 162 MW (MPGL) | IPP | HFO | 162 | [8 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | HFO | 55
52 | Jodiac Power | IPP | HFO | 54
53 | Anlima Energy Ltd | IPP | HFO | 116
54 | Thakurgaon 115 MW (EPV) | IPP | HFO | 115
55 | Confidence Unit-2 Bogura | IPP | HFO | 113
56 | Confidence Unit-1 Bogura | IPP | HFO | 113
57 | Kamalaghat 54 MW Banco Energy | IPP | HFO | 54 | [8 empty] | √ | √ | √
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | HFO | 55
59 | Kodda 150 MW (BR Power) | IPP | HFO | 149
60 | Chandpur 115 MW (Doreen) | IPP | HFO | 115 | [26 empty] | √ | √ | √ | √ | √
61 | Kanchan Purbachal Power Ltd | IPP | HFO | 55
62 | Chattogram SS Power U- 1 & 2 | Private | Coal | 1224 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | Coal | 1436 | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | Coal | 1234 | √ | √ | √ | √ | √ |  |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
65 | Barishal 307 MW PP (BEPCL) | Private | Coal | 307 |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
66 | Unique Meghnaghat Power Limited (UMPL) | IPP | Gas | 584 | [17 empty] | √
67 | Meghnaghat CCPP(Summit)-2 | IPP | Gas/HSD | 583 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  |  | √
| JERA Meghnaghat Power Limited | IPP | Gas | 718
| United Payra Power Ltd. | IPP |  | 150
| Mirsharai 150 MW | IPP | HFO/Gas | 150 | [26 empty] | √ | √ | √ | √ | √
Jangalia 52 MW PP (Lakdanavi)
| Ashuganj 420 MW CCPP(East) | APSCL |  | 400 |  | √ |  |  | √ | √ | √ | √
| Ashuganj 55 MW PP (Precision) | QRPP |  | 55
| Bagura 113 MW PP (Confidence)-2 | IPP |  | 113
| Energypac Power Venture Thakurgaon Ltd. | IPP |  | 115
| Chandpur 150 MW CCPP | BPDB |  | 163
| Khulna 225 MW CCPP | NWPGCL |  | 230
| Shahjibazar GTPP Unit 8 & 9 | BPDB |  | 70
| Shajibazar 100 MW PP | BPDB |  | 100
| Payra 1320 MW Unit-1 | BCPCL |  | 622