## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 01-03-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-02-2026 | during | 01-03-2026 | during | 01-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 344 | 319 | 412 | 412 | 412 | 412 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 310 | 335 | 335 | 335 | 335
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 16 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 7 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23 | 20 | 33.75 | 33.75 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 20 | 22 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 8 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 45 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 52 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 25 | 17 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 53 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 350 | 400 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 355 | 405 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 90 | 160 | 160 | 160 | 160 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1544 | 1781 | 5946.97 | 5915.97 | 3207.05 | 3212.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 39 | 32 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 95 | 80 | 75 | 75 | 75 | 75 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 150 | 146 | 150 | 150 | 150 | 150 | ps availability is less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 32 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 64 | 64 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 48 | 17 | 68 | 68 | 68 | 68 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 0 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 6 | 29 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.73 | 0 | 3.28 | 0 | 3.28 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 36 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1150 | 1166 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 2 | 0 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 680 | 770 | 920 | 1030 | 920 | 1030 | ps availability is less
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2214.73 | 2308 | 3745.14 | 3864.86 | 3228.78 | 3332.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 190 | 200 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 290 | 330 | 353.35 | 353.35 | 353.35 | 353.35 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 318.81 | 318.81 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 280 | 350 | 393 | 393 | 393 | 393
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 5 | 5 | 55 | 55 | 5 | 5 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 42 | 42 | 42 | 42 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 99 | 106 | 163 | 163 | 110 | 110 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 17 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 124 | 126 | 84 | 80 | 84 | 80 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 32 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1121 | 1237 | 2741.51 | 2682.51 | 1943.55 | 1884.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-02-2026 | during | 01-03-2026 | during | 01-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 18 | 20 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 78 | 60 | 80 | 60 | 80 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 98 | 70 | 115 | 70 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | Annual Maintenance on going
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 146 | 219 | 366.1 | 429 | 155.1 | 218
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 42 | 42 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 53 | 53 | 30 | 30 | ps availability is less
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 159 | 153 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 25 | 70 | 40 | 40 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 41 | 40 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 98 | 100 | 100 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 20 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 354 | 352 | 385 | 385 | 385 | 385 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1118 | 1115 | 1282 | 1282 | 1166 | 1166
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 877 | 877 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 252 | 238 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 93 | 0 | 91 | 0 | 91 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 816 | 1100 | 0 | 0 | 1148.28 | 1148.28
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2038 | 2215 | 2365 | 2274 | 2546.38 | 2455.38
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 122 | 125 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 445 | 610 | 622 | 622 | 622 | 622 | Unit-1 under maint
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 15 | 15 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 240 | 277 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.65 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2700.36 | 1027.65 | 1232 | 1540 | 1539 | 1405 | 1404
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 52.81 | 0 | 50 | 0 | 50 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown As Per PGB PLC's Requirements.
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 202 | 190 | 220 | 220 | 220 | 220
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 403 | 414 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 32 | 32 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.34 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1121.46 | 1453.58 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 53.13 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 111 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1948.74 | 2057.58 | 3137.37 | 2920.87 | 2592.37 | 2375.87
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 66 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.3 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 178 | 0 | 181.91 | 0 | 181.91 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 214.3 | 116 | 479.11 | 262 | 445.11 | 228
System Total |  |  |  |  | 28823.2 | 28385.703 | 11372.42 | 12280.58 | 21603.2 | 21170.21 | 16689.34 | 16276.35
Forecast Scenario (01-03-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11070 |  | 0 |  | 11070
|  |  |  | 1:00 | 10540 |  | 0 |  | 10540
|  |  |  | 2:00 | 10250 |  | 0 |  | 10250
|  |  |  | 3:00 | 10280 |  | 0 |  | 10280
|  |  |  | 4:00 | 11220 |  | 0 |  | 11220
|  |  |  | 5:00 | 10320 |  | 0 |  | 10320
|  |  |  | 6:00 | 9320 |  | 0 |  | 9320
|  |  |  | 7:00 | 9410 |  | 0 |  | 9410
|  |  |  | 8:00 | 10140 |  | 0 |  | 10140
|  |  |  | 9:00 | 11050 |  | 0 |  | 11050
|  |  |  | 10:00 | 11550 |  | 0 |  | 11550
|  |  |  | 11:00 | 11790 |  | 0 |  | 11790
|  |  |  | 12:00 | 12260 |  | 0 |  | 12260
|  |  |  | 13:00 | 12680 |  | 0 |  | 12680
|  |  |  | 14:00 | 12880 |  | 0 |  | 12880
|  |  |  | 15:00 | 12650 |  | 0 |  | 12650
|  |  |  | 16:00 | 12590 |  | 0 |  | 12590
|  |  |  | 17:00 | 12810 |  | 0 |  | 12810
|  |  |  | 18:00 | 12370 |  | 0 |  | 12370
|  |  |  | 18:30 | 12400 |  | 0 |  | 12400
|  |  |  | 19:00 | 12510 |  | 0 |  | 12510
|  |  |  | 19:30 | 12630 |  | 0 |  | 12630
|  |  |  | 20:00 | 12560 |  | 0 |  | 12560
|  |  |  | 21:00 | 12560 |  | 0 |  | 12560
|  |  |  | 22:00 | 12420 |  | 0 |  | 12420
|  |  |  | 23:00 | 11830 |  | 0 |  | 11830
Probable Maximum Temperature: |  |  | 31.80°C
Probable Maximum Demand at Day Peak: |  |  | 12260.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12630.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12630.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 277.06 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:52 hrs on 01-03-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 28-02-2026 | [28 empty] | Date: | 28-02-2026 | [28 empty] | Date: | 28-02-2026 | [28 empty] | Date: | 28-02-2026 | [28 empty] | Date: | 28-02-2026 | [17 empty] | Date: | 28-02-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 270 | 0 | 0 | 0 | 17 | 13.5 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 42 | 625 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1047 | 0 | 0 | 0 | 250 | 295 | 0 | 51 | 0 | 195 | 0 | 0 | 105 | 0 | 0 | 20 | 0 | 110 | 0 | 0 | 0 | 315 | 0 | 358 | 41 | 30 | 152 | 0 | 20 | 0 | 41 | 30 | 25 | 0 | 100 | 0 | 45 | 8 | 18 | 0 | 0 | 6 | 5591.5 | 877 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 975 | 0 | 0 | 0 | 1003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 123 | 220 | 0 | 0 | 545 | 0 | 4775 | 10366.5 | 91.8
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 270 | 0 | 0 | 0 | 17 | 13.5 | 22 | 0 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 42 | 625 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 860 | 0 | 0 | 0 | 260 | 305 | 0 | 51 | 0 | 201 | 0 | 0 | 105 | 0 | 0 | 20 | 0 | 88 | 0 | 0 | 0 | 310 | 0 | 340 | 41 | 30 | 138 | 0 | 17 | 0 | 41 | 30 | 23 | 0 | 100 | 0 | 45 | 8 | 18 | 0 | 0 | 6 | 5357.5 | 877 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 902 | 0 | 0 | 0 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 122 | 220 | 0 | 0 | 410 | 0 | 4418 | 9775.5 | 91.79
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 13.5 | 22 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 42 | 625 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 855 | 0 | 0 | 0 | 280 | 305 | 0 | 51 | 0 | 196 | 0 | 0 | 105 | 0 | 0 | 20 | 0 | 100 | 0 | 0 | 0 | 305 | 0 | 338 | 41 | 30 | 139 | 0 | 17 | 0 | 41 | 30 | 24 | 0 | 100 | 0 | 45 | 8 | 21 | 0 | 0 | 6 | 5216.5 | 877 | 218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 910 | 0 | 0 | 0 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 122 | 220 | 0 | 0 | 350 | 0 | 4290 | 9506.5 | 91.78
03:00 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 250 | 0 | 0 | 0 | 35 | 13.5 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 42 | 625 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 855 | 0 | 0 | 0 | 280 | 290 | 0 | 51 | 0 | 194 | 0 | 0 | 105 | 0 | 0 | 8 | 0 | 98 | 0 | 0 | 0 | 310 | 0 | 326 | 42 | 30 | 136 | 0 | 17 | 0 | 41 | 30 | 23 | 0 | 100 | 0 | 96 | 56 | 21 | 0 | 0 | 6 | 5309.5 | 878 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 904 | 0 | 0 | 0 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 122 | 200 | 0 | 0 | 350 | 0 | 4333 | 9642.5 | 91.77
04:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 300 | 0 | 0 | 0 | 52 | 13.5 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 42 | 625 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 1081 | 0 | 0 | 0 | 310 | 310 | 0 | 51 | 0 | 191 | 0 | 0 | 107 | 0 | 0 | 14 | 0 | 100 | 0 | 0 | 0 | 300 | 0 | 355 | 41 | 30 | 150 | 0 | 17 | 0 | 41 | 30 | 25 | 0 | 100 | 0 | 98 | 56 | 21 | 0 | 0 | 6 | 5842.5 | 877 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 0 | 0 | 0 | 1056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 122 | 200 | 0 | 0 | 407 | 0 | 4774 | 10616.5 | 91.76
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 13.5 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 5 | 520 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 990 | 0 | 0 | 0 | 315 | 345 | 0 | 5 | 0 | 205 | 0 | 0 | 107 | 0 | 0 | 14 | 0 | 96 | 0 | 0 | 0 | 300 | 0 | 350 | 41 | 30 | 148 | 0 | 17 | 0 | 5 | 30 | 25 | 0 | 100 | 0 | 68 | 8 | 23 | 0 | 0 | 0 | 5284.5 | 877 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 0 | 0 | 0 | 893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 110 | 200 | 0 | 0 | 390 | 0 | 4323 | 9607.5 | 91.75
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 13.5 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 5 | 520 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 250 | 290 | 0 | 5 | 0 | 193 | 0 | 0 | 50 | 0 | 0 | 14 | 0 | 88 | 0 | 0 | 0 | 295 | 0 | 324 | 41 | 30 | 138 | 0 | 17 | 0 | 5 | 30 | 24 | 0 | 100 | 0 | 35 | 8 | 23 | 0 | 0 | 0 | 4714.5 | 877 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 0 | 0 | 0 | 829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 100 | 200 | 0 | 0 | 280 | 0 | 3903 | 8617.5 | 91.74
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 280 | 0 | 0 | 2 | 0 | 13.5 | 22 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27 | 75 | 0 | 5 | 520 | 0 | 0 | 0 | 0 | 0 | 111 | 0 | 0 | 0 | 865 | 2 | 0 | 0 | 250 | 290 | 0 | 5 | 0 | 209 | 0 | 0 | 50 | 0 | 0 | 14 | 0 | 88 | 0 | 2 | 0 | 290 | 0 | 352 | 41 | 30 | 139 | 1 | 17 | 0 | 5 | 30 | 24 | 0 | 100 | 0 | 35 | 8 | 23 | 0 | 0 | 0 | 4896.77 | 795 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 779 | 0 | 0 | 0 | 830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.65 | 6 | 0 | 0 | 3.09 | 0 | 0 | 130 | 0 | 0 | 0 | 414 | 0 | 0.27 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.2 | 8 | 0.04 | 0 | 184 | 100 | 200 | 0 | 0 | 280 | 0 | 3964.25 | 8861.02 | 91.73
08:00 | 0 | 12 | 25 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 300 | 0 | 0 | 9 | 0 | 20 | 22 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 1.09 | 75 | 0 | 9 | 520 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 850 | 6 | 0 | 0 | 340 | 315 | 0 | 21 | 0 | 200 | 0 | 0 | 104 | 0 | 0 | 14 | 0 | 88 | 0 | 23 | 0 | 300 | 0 | 364 | 41 | 30 | 157 | 3 | 17 | 0 | 44 | 30 | 24 | 0 | 100 | 0 | 48 | 56 | 21 | 1 | 0 | 0 | 5447.09 | 688 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 780 | 0 | 0 | 0 | 830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.96 | 32 | 0 | 0 | 14.27 | 0 | 0 | 194 | 0 | 0 | 0 | 414 | 0 | 1.41 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 1.1 | 42 | 0.16 | 0 | 177 | 128 | 220 | 0 | 0 | 280 | 0 | 4112.9 | 9559.99 | 91.72
09:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 300 | 0 | 0 | 19 | 17 | 23 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 2.06 | 75 | 0 | 7 | 625 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 945 | 12 | 0 | 0 | 295 | 300 | 0 | 51 | 0 | 192 | 0 | 0 | 104 | 0 | 0 | 14 | 0 | 106 | 0 | 42 | 0 | 300 | 0 | 361 | 41 | 30 | 162 | 5 | 17 | 0 | 44 | 30 | 25 | 0 | 100 | 0 | 65 | 56 | 21 | 1 | 0 | 0 | 5723.06 | 861 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 785 | 0 | 0 | 0 | 968.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.56 | 62 | 0 | 0 | 29.82 | 0 | 0 | 206 | 0 | 0 | 0 | 403 | 0 | 2.89 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 2.8 | 88 | 0.33 | 0 | 239 | 128 | 220 | 0 | 0 | 306 | 0 | 4662.08 | 10385.14 | 91.71
10:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 300 | 0 | 0 | 26 | 35 | 23 | 21 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 2.77 | 75 | 0 | 7 | 575 | 0 | 0 | 3 | 0 | 0 | 150 | 0 | 0 | 0 | 952 | 16 | 0 | 0 | 280 | 310 | 0 | 51 | 0 | 205 | 0 | 0 | 100 | 0 | 0 | 14 | 0 | 112 | 0 | 56 | 0 | 305 | 0 | 363 | 42 | 30 | 162 | 8 | 17 | 0 | 44 | 30 | 25 | 0 | 100 | 0 | 68 | 58 | 21 | 2 | 0 | 0 | 5743.77 | 878 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 766 | 0 | 0 | 0 | 965.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.05 | 86 | 0 | 0 | 42.13 | 0 | 0 | 208 | 0 | 0 | 0 | 414 | 0 | 4.13 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 3.9 | 130 | 0.49 | 0 | 244 | 128 | 220 | 0 | 0 | 364 | 0 | 4852.73 | 10596.5 | 91.7
11:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 300 | 0 | 0 | 29 | 35 | 23 | 21 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 7 | 12 | 3.23 | 75 | 0 | 6 | 660 | 0 | 0 | 36 | 1 | 0 | 100 | 0 | 0 | 0 | 997 | 19 | 0 | 0 | 280 | 310 | 0 | 51 | 3 | 199 | 0 | 0 | 99 | 0 | 0 | 14 | 0 | 124 | 0 | 65 | 0 | 310 | 0 | 354 | 42 | 30 | 162 | 10 | 17 | 0 | 44 | 30 | 23 | 0 | 100 | 0 | 69 | 58 | 18 | 2 | 0 | 0 | 5939.23 | 878 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 781 | 0 | 0 | 0 | 1052.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.42 | 102 | 0 | 0 | 51.73 | 0 | 0 | 204 | 0 | 0 | 0 | 414 | 0 | 5.02 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 4.4 | 163 | 0.61 | 0 | 243 | 125 | 220 | 0 | 0 | 405 | 0 | 5067.35 | 11006.58 | 91.69
12:00 | 0 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 300 | 0 | 0 | 32 | 35 | 23 | 20 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 12 | 12 | 3.73 | 95 | 0 | 6 | 680 | 0 | 0 | 39 | 0 | 0 | 150 | 0 | 0 | 0 | 1150 | 19 | 0 | 0 | 280 | 290 | 0 | 51 | 5 | 190 | 0 | 0 | 99 | 0 | 0 | 14 | 0 | 124 | 0 | 68 | 0 | 310 | 0 | 354 | 42 | 30 | 159 | 10 | 17 | 0 | 41 | 30 | 25 | 0 | 100 | 0 | 68 | 58 | 18 | 2 | 0 | 0 | 6143.73 | 877 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 816 | 0 | 0 | 0 | 1121.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.81 | 111 | 0 | 0 | 53.13 | 0 | 0 | 202 | 0 | 0 | 0 | 403 | 0 | 5.34 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 5.3 | 178 | 0.65 | 0 | 240 | 122 | 220 | 0 | 0 | 445 | 0 | 5228.69 | 11372.42 | 91.69
13:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 300 | 0 | 0 | 32 | 52 | 23 | 20 | 0 | 350 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 0 | 0 | 12 | 1.14 | 80 | 0 | 10 | 830 | 0 | 0 | 39 | 0 | 0 | 148 | 0 | 0 | 0 | 1132 | 19 | 0 | 0 | 280 | 290 | 0 | 51 | 5 | 192 | 0 | 0 | 99 | 0 | 0 | 14 | 0 | 122 | 0 | 66 | 0 | 305 | 0 | 354 | 42 | 30 | 155 | 11 | 17 | 0 | 16 | 25 | 23 | 0 | 98 | 0 | 69 | 58 | 15 | 2 | 0 | 3 | 6245.14 | 877 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 948 | 0 | 0 | 0 | 1126.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.72 | 111 | 0 | 0 | 53.76 | 0 | 0 | 200 | 0 | 0 | 0 | 414 | 0 | 5.31 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 5 | 173 | 0.62 | 0 | 241 | 122 | 220 | 0 | 0 | 495 | 0 | 5412.01 | 11657.15 | 91.68
14:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 250 | 0 | 0 | 28 | 70 | 23 | 20 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 12 | 2.99 | 80 | 0 | 8 | 1030 | 0 | 0 | 45 | 0 | 0 | 146 | 0 | 0 | 0 | 1157 | 17 | 0 | 0 | 280 | 310 | 0 | 51 | 5 | 197 | 0 | 0 | 98 | 0 | 0 | 14 | 0 | 144 | 0 | 57 | 0 | 315 | 0 | 349 | 42 | 30 | 156 | 9 | 17 | 0 | 16 | 25 | 23 | 0 | 98 | 0 | 69 | 58 | 15 | 2 | 0 | 6 | 6459.99 | 878 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 1033 | 0 | 0 | 0 | 1126.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.97 | 95 | 0 | 0 | 47.16 | 0 | 0 | 200 | 0 | 0 | 0 | 366 | 0 | 4.87 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 5 | 146 | 0.54 | 0 | 243 | 122 | 220 | 0 | 0 | 551 | 0 | 5441.31 | 11901.3 | 91.68
15:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 0 | 0 | 71 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 250 | 0 | 0 | 23 | 70 | 23 | 20 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 12 | 2.21 | 80 | 0 | 6 | 930 | 0 | 0 | 50 | 0 | 0 | 147 | 0 | 0 | 0 | 1166 | 13 | 0 | 0 | 320 | 295 | 0 | 51 | 5 | 194 | 0 | 0 | 97 | 0 | 0 | 14 | 0 | 140 | 0 | 44 | 0 | 315 | 0 | 335 | 42 | 30 | 155 | 6 | 17 | 0 | 32 | 0 | 70 | 0 | 98 | 0 | 69 | 57 | 10 | 1 | 0 | 6 | 6397.21 | 878 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 1047 | 0 | 0 | 0 | 1128.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.32 | 75 | 0 | 0 | 35.53 | 0 | 0 | 200 | 0 | 0 | 0 | 347 | 0 | 3.91 | 0 | 0 | 0 | 20 | 15 | 0 | 0 | 0 | 1.8 | 100 | 0.44 | 0 | 241 | 122 | 220 | 0 | 0 | 590 | 0 | 5366.16 | 11763.37 | 91.67
16:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 88 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 250 | 0 | 0 | 15 | 90 | 23 | 20 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 12 | 1.26 | 80 | 0 | 13 | 920 | 0 | 0 | 50 | 0 | 0 | 146 | 0 | 0 | 0 | 1169 | 8 | 0 | 0 | 325 | 315 | 0 | 51 | 5 | 209 | 0 | 0 | 97 | 0 | 0 | 14 | 0 | 126 | 0 | 25 | 0 | 310 | 0 | 337 | 42 | 30 | 155 | 3 | 17 | 0 | 40 | 0 | 70 | 0 | 96 | 0 | 69 | 57 | 12 | 1 | 0 | 6 | 6534.26 | 878 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 1055 | 0 | 0 | 0 | 1122.85 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 20.56 | 47 | 0 | 0 | 24.28 | 0 | 0 | 198 | 0 | 0 | 0 | 388 | 0 | 2.42 | 0 | 0 | 35 | 12 | 34 | 0 | 0 | 0 | 1.8 | 65 | 0.28 | 0 | 246 | 122 | 220 | 0 | 0 | 600 | 0 | 5358.19 | 11892.45 | 91.67
17:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 11 | 0 | 89 | 15 | 30 | 0 | 0 | 40 | 0 | 0 | 0 | 395 | 0 | 0 | 250 | 0 | 0 | 5 | 108 | 24 | 20 | 0 | 430 | 0 | 0 | 0 | 0 | 2 | 34 | 0 | 0 | 0 | 12 | 0.43 | 80 | 0 | 22 | 850 | 0 | 0 | 50 | 0 | 12 | 146 | 0 | 0 | 0 | 1177 | 3 | 0 | 0 | 393 | 350 | 0 | 51 | 5 | 208 | 0 | 6 | 97 | 1 | 0 | 14 | 0 | 124 | 0 | 9 | 0 | 305 | 0 | 337 | 42 | 30 | 156 | 1 | 17 | 0 | 41 | 0 | 70 | 0 | 97 | 0 | 69 | 58 | 12 | 0 | 0 | 3 | 6701.43 | 878 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 1114 | 0 | 0 | 0 | 1225.75 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 6.63 | 16 | 0 | 0 | 7.24 | 0 | 0 | 197 | 0 | 0 | 0 | 414 | 0 | 0.75 | 0 | 0 | 50 | 4 | 52 | 0 | 0 | 0 | 0.3 | 22 | 0.1 | 0 | 246 | 122 | 220 | 0 | 0 | 600 | 0 | 5438.27 | 12139.7 | 91.66
18:00 | 0 | 48 | 33 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 32.6 | 0 | 101 | 15 | 60 | 0 | 3 | 72 | 0 | 0 | 0 | 455 | 0 | 0 | 250 | 0 | 0 | 0 | 108 | 14 | 20 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 36 | 0 | 80 | 0 | 26 | 850 | 0 | 0 | 33 | 0 | 58 | 146 | 0 | 0 | 0 | 1095 | 0 | 0 | 0 | 250 | 330 | 0 | 20 | 5 | 170 | 0 | 26 | 50 | 24 | 0 | 14 | 0 | 120 | 0 | 0 | 0 | 310 | 0 | 322 | 42 | 30 | 157 | 0 | 17 | 0 | 41 | 0 | 68 | 0 | 98 | 11 | 97 | 76 | 12 | 0 | 0 | 6 | 6533.6 | 878 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1123 | 0 | 0 | 0 | 1267.01 | 0 | 0 | 0 | 35 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 110 | 220 | 0 | 0 | 590 | 0 | 5418.51 | 11952.11 | 91.65
19:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 21.8 | 0 | 71 | 15 | 45 | 0 | 17 | 53 | 0 | 0 | 0 | 350 | 0 | 0 | 328 | 0 | 0 | 0 | 108 | 20 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 36 | 0 | 80 | 0 | 30 | 775 | 0 | 0 | 32 | 0 | 50 | 146 | 0 | 0 | 0 | 1161 | 0 | 0 | 0 | 350 | 325 | 0 | 36 | 5 | 208 | 0 | 35 | 100 | 34 | 0 | 20 | 0 | 126 | 0 | 0 | 0 | 295 | 0 | 350 | 42 | 30 | 146 | 0 | 17 | 0 | 44 | 0 | 70 | 0 | 98 | 17 | 98 | 78 | 20 | 0 | 0 | 6 | 6711.8 | 877 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1066 | 0 | 0 | 0 | 1435.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 125 | 220 | 0 | 0 | 595 | 0 | 5543.26 | 12255.06 | 91.64
19:30 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 16 | 0 | 52 | 7 | 45 | 0 | 17 | 53 | 0 | 0 | 0 | 405 | 0 | 0 | 310 | 0 | 0 | 0 | 90 | 20 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 36 | 0 | 80 | 0 | 29 | 770 | 0 | 0 | 32 | 0 | 32 | 146 | 0 | 0 | 0 | 1166 | 0 | 0 | 0 | 350 | 330 | 0 | 51 | 5 | 200 | 0 | 32 | 106 | 17 | 0 | 20 | 0 | 126 | 0 | 0 | 0 | 310 | 0 | 352 | 42 | 30 | 153 | 0 | 20 | 0 | 40 | 0 | 70 | 0 | 98 | 17 | 98 | 78 | 20 | 0 | 0 | 6 | 6660 | 877 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 1453.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 50 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 125 | 220 | 0 | 0 | 610 | 0 | 5620.58 | 12280.58
20:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 16 | 0 | 58 | 0 | 45 | 0 | 17 | 52 | 0 | 0 | 0 | 400 | 0 | 0 | 300 | 0 | 0 | 0 | 90 | 20 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 36 | 0 | 80 | 0 | 36 | 775 | 0 | 0 | 33 | 0 | 33 | 151 | 0 | 0 | 0 | 1163 | 0 | 0 | 0 | 325 | 330 | 0 | 51 | 5 | 193 | 0 | 32 | 102 | 17 | 0 | 20 | 0 | 124 | 0 | 0 | 0 | 305 | 0 | 354 | 42 | 30 | 156 | 0 | 20 | 0 | 41 | 0 | 72 | 0 | 99 | 17 | 98 | 78 | 20 | 0 | 0 | 6 | 6626 | 877 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1111 | 0 | 0 | 0 | 1457.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 123 | 220 | 0 | 0 | 620 | 0 | 5631.36 | 12257.36 | 91.63
21:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 16.4 | 0 | 52 | 0 | 15 | 0 | 17 | 50 | 0 | 0 | 0 | 405 | 0 | 0 | 300 | 0 | 0 | 0 | 90 | 20 | 22 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 80 | 0 | 33 | 715 | 0 | 0 | 33 | 0 | 33 | 151 | 0 | 0 | 0 | 1170 | 0 | 0 | 0 | 300 | 315 | 0 | 51 | 5 | 197 | 0 | 32 | 103 | 16 | 0 | 20 | 0 | 128 | 0 | 0 | 0 | 305 | 0 | 354 | 42 | 30 | 159 | 0 | 20 | 0 | 41 | 0 | 71 | 0 | 98 | 17 | 88 | 88 | 20 | 0 | 0 | 6 | 6515.4 | 877 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1124 | 0 | 0 | 0 | 1456.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 123 | 220 | 0 | 0 | 610 | 0 | 5640.83 | 12156.23 | 91.62
22:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 16.8 | 0 | 52 | 0 | 15 | 0 | 17 | 51 | 0 | 0 | 0 | 410 | 0 | 0 | 290 | 0 | 0 | 0 | 90 | 20 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 80 | 0 | 33 | 720 | 0 | 0 | 33 | 0 | 33 | 151 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 300 | 305 | 0 | 51 | 0 | 198 | 0 | 33 | 104 | 17 | 0 | 20 | 0 | 132 | 0 | 0 | 0 | 300 | 0 | 354 | 42 | 30 | 160 | 0 | 20 | 0 | 41 | 0 | 70 | 0 | 98 | 17 | 88 | 88 | 20 | 0 | 0 | 6 | 6480.8 | 883 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1129 | 0 | 0 | 0 | 1458.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 394 | 0 | 0 | 0 | 0 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 123 | 220 | 0 | 0 | 622 | 0 | 5640.95 | 12121.75 | 91.61
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 270 | 0 | 0 | 0 | 52 | 19 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 27 | 720 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1161 | 0 | 0 | 0 | 300 | 300 | 0 | 51 | 0 | 196 | 0 | 0 | 105 | 0 | 0 | 20 | 0 | 132 | 0 | 0 | 0 | 300 | 0 | 353 | 42 | 30 | 154 | 0 | 20 | 0 | 41 | 0 | 71 | 0 | 99 | 0 | 58 | 49 | 16 | 0 | 0 | 6 | 6008 | 884 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1117 | 0 | 0 | 0 | 1455.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 123 | 220 | 0 | 0 | 622 | 0 | 5484.97 | 11492.97 | 91.6
Total KWH | 0 | 406080 | 410491 | 0 | 0 | 0 | 0 | 0 | 7956000 | 0 | 0 | 130572 | 0 | 1115568 | 88320 | 225065 | 0 | 85370 | 349920 | 0 | 0 | 0 | 8808060 | 0 | 0 | 6741721 | 0 | 0 | 219885 | 1219200 | 456000 | 502920 | 0 | 9032727.27 | 0 | 0 | 0 | 0 | 2880 | 429749 | 0 | 0 | 20160 | 272640 | 21848 | 1951580 | 0 | 552960 | 17309090.91 | 0 | 0 | 521760 | 17382.6 | 272654 | 3370705 | 0 | 0 | 0 | 25123634 | 130950 | 0 | 0 | 7331800 | 7860500 | 0 | 1108238 | 63940 | 5192000 | 0 | 202560 | 2355851 | 138240 | 0 | 365330 | 0 | 2673600 | 0 | 461882 | 0 | 7379000 | 0 | 8558000 | 985000 | 723840 | 3667664 | 65372 | 417888 | 0 | 836160 | 422496 | 979000 | 0 | 2385870 | 92880 | 1677600 | 1221600 | 415680 | 13800 | 0 | 96480 | 145438163.78 | 20850909 | 5837472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 645840 | 23069090 | 0 | 0 | 0 | 26657408 | 0 | 0 | 0 | 27744 | 67776 | 0 | 17072 | 0 | 0 | 351336 | 760250 | 0 | 0 | 366000 | 0 | 0 | 4701027 | 0 | 0 | 0 | 9337163 | 0 | 35940 | 0 | 0 | 394720 | 199455 | 444336 | 0 | 0 | 0 | 31474.92 | 1123200 | 4231 | 0 | 5651000 | 2898000 | 5229300 | 0 | 0 | 11812363.64 | 0 | 120513107.56 | 265951271.34

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 28-02-2026
Power Supply Scenario
| Day Peak Generation |  |  | 11372.42 | MW | 12:00 Hr. | Energy Generated |  |  | 265.9513 |  | MKWHr.
| Day Peak Demand |  |  | 11372.42 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 12280.58 | MW | 19:30 Hr. | Energy Demand |  |  | 265.9513 |  | MKWHr.
| Evening Peak Demand |  |  | 12280.58 | MW | 19:30 Hr. | Maximum Temperature |  |  | 32.4 |  | °C
| Minimum Generation of the Day |  |  | 8617.5 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 850.79 |  | MMCFD
| Maximum Generation of the Day |  |  | 12280.58 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 5.4886 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.4974 | 0 | 4.0306 | 0 | 0 | 0.21988 | 0 | 0 | 37.7479 | Gas | 116.4723 | Gas | 401181069.0459
| Chattogram Zone |  |  | 3.9237 | 42.4327 | 1.5343 | 0 | 1.9516 | 0.1528 | 0 | 0.00288 | 49.998 | Coal | 82.9652 | Coal | 539598186.1335
| Cumilla Zone |  |  | 24.2777 | 0 | 0.3408 | 0 | 0 | 0.46188 | 2.6736 | 0 | 27.7539 | HFO | 9.9459 | HFO | 168251286.02
| Mymensingh Zone |  |  | 0.41568 | 0 | 3.0886 | 0 | 0 | 0.0138 | 0 | 0 | 3.518 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.3549 | 0 | 0 | 0 | 0 | 0.065372 | 0 | 0 | 26.4203 | Hydro | 1.9516 | Hydro | 195158
| Khulna Zone |  |  | 5.8375 | 23.0691 | 0 | 0 | 0 | 0.64584 | 20.8509 | 0 | 50.4033 | Solar | 4.4315 | Solar | 69405771.754
| Barishal Zone |  |  | 8.1273 | 17.4634 | 0 | 0 | 0 | 0.004231 | 0 | 0 | 25.5949 | Import | 50.1819 | Import | 281024523.18
| Rajshahi Zone |  |  | 14.0382 | 0 | 0.11259 | 0 | 0 | 1.5135 | 26.6574 | 0 | 42.3217 | Wind | 0.00288 | Wind | 42364.8
| Rangpur Zone |  |  | 0 | 0 | 0.83906 | 0 | 0 | 1.3541 | 0 | 0 | 2.1932
| Total |  |  | 116.4723 | 82.9652 | 9.9459 | 0 | 1.9516 | 4.4315 | 50.1819 | 0.00288 | 265.9513
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 401181069.0459 |  | Hydro | 195158
|  |  |  | Coal | 539598186.1335 |  | Solar | 69405771.754
|  |  |  | HFO | 168251286.02 |  | Import | 281024523.18
|  |  |  | HSD | 0 |  | Wind | 42364.8
[5 empty] | Total: | 145,96,98,358 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.8509 | Peak Hr Flow | 877.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 32460002.07 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.6574 | Peak Hr Flow | 1453.58 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1899 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.6736 | Peak Hr Flow | 126.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2070 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.1819 | Peak Hr Flow | 2456.58 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4643
|  |  |  | Chattogram |  | 0 |  | 1225
|  |  |  | Cumilla |  | 0 |  | 1038
|  |  |  | Mymensingh |  | 0 |  | 1016
|  |  |  | Sylhet |  | 0 |  | 419
|  |  |  | Khulna |  | 0 |  | 1357
|  |  |  | Barishal |  | 0 |  | 362
|  |  |  | Rajshahi |  | 0 |  | 1138
|  |  |  | Rangpur |  | 0 |  | 713
|  |  |  | Total |  | 0 |  | 11911
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:37 |  | Chowmuhani-Feni 132 kV Ckt-2 Forced S/D from Daganbhuiyan 132/33kV end Due to Chowmuhoni
Grid Working
| 08:53 | 12:22 | Faridpur 132/33kV S/S 230kV Faridpur-Gopalganj CKT-2 Scheduled S/D Due to 118 no tower
maintenance work
| 08:54 | 12:21 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-02 Scheduled S/D
| 09:18 | 14:08 | Shariatpur 132/33kV S/S T1-406T LT Scheduled S/D Due to Incomer -1 ,Source side Red Hot
Maintenance Work.
| 09:19 | 14:09 | Shariatpur 132/33kV S/S T1-406T HT Scheduled S/D Due to Incomer -1 ,Source side Red Hot
Maintenance Work.
| 09:22 | 15:02 | Kallyanpur-Lalbag 132kV Ckt-2 Scheduled S/D from Kallyanpur 132/33kV end Due to
CB-203,Maintenance work.
| 10:03 | 11:27 | Faridpur-Gopalganj(N) 132 kV Ckt-2 Scheduled S/D from Faridpur 132/33kV end Due to
maintenance at gopalgonj grid ss and from Gopalganj 400/132kVend.
| 10:36 | 20:10 | Tongi 230/132/33kV S/S 132 kV Bus-1 Scheduled S/D Due to Bay extension (PSDC)
|  | 10:40 | Naogaon 132/33kV S/S T-1 HT is restored.
|  | 10:42 | Naogaon 132/33kV S/S T-1 LT is restored.
| 10:43 | 13:59 | Kabirpur - Manikganj 132kV Ckt-2 Scheduled S/D from Kabirpur 132/33kV end Due to Relay
and DS change work and from Manikganj 132/33kV end Due to Disk Cleaning.
| 11:08 |  | Madunaghat-Sikalbaha 132kV Ckt-2 Forced S/D from Kalurghat 132/33kV end Due to 132 KV
Madunaghat Underground line trip.(Insulation Megger)
| 11:10 |  | Fenchuganj-Sreemangal 132kV Ckt-1 Project Work S/D from Fenchuganj 230/132/33kV end Due
to G2G project work
| 11:20 |  | Fenchuganj-Sreemangal 132kV Ckt-1 Project Work S/D from Sreemongol 132/33kV end Due to
G2G Project
| 11:27 | 18:47 | Juldah-Sikalbaha 132kV Ckt-1 Scheduled S/D from Juldah 132/33kV end Due to SF6 Gas
Purification from Sikalbaha Side.
| 12:38 | 13:02 | Bakerganj 132/33kV S/S 132 kV Bakerganj Patuakhali Ckt Tripped showing GE, P40 Agile | [7 empty] | 8.0MW load
|  |  | relays. | [7 empty] | interrup.
| 12:38 | 13:02 | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt Tripped from Patuakhali 132/33kV | [7 empty] | 17.0MW load
|  |  | end showing Distance Relay relays Due to Distance Relay Z-2 22.1 KM | [7 empty] | interrup.
Patuakhali 132/33kV
end
| 13:28 | 14:53 | Gopalganj 400/132kV S/S 230kV Barisal CKT-02 Forced S/D
| 15:30 |  | Barishal North-Patuakhali New Line-1,2 Started to Load Flow.
| 15:31 | 16:40 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-1 Scheduled S/D Due to NLDC Instruction
|  | 17:13 | Monakasha-Rahanpur 400kV Ckt-1 is restored.
| 02:46 | 03:11 | Ashuganj-Cumilla(N) 230 kV Ckt-1 Tripped from Cumilla(N) 230/132/33kV end showing Primary
Distance protection -Mode: RE, Value: D 1P Secondary Distance protection -A phase ,
v~fail relays.
| 03:12 | 06:08 | Ashuganj-Cumilla(N) 230 kV Ckt-1 Tripped from Cumilla(N) 230/132/33kV end showing Primary
Distance protection -Mode: RE, Value: D 1P Secondary Distance protection -A phase ,
v~fail relays.
| 03:31 | 05:39 | Ashuganj-Cumilla(N) 230 kV Ckt-2 Tripped from Cumilla(N) 230/132/33kV end showing
Secondary Distance protection -C phase , v~fail relays.
| 03:52 | 04:15 | Sonargaon 132/33kV S/S OPSL(IEL-2) Tripped showing Line Distance 21L relays Due to line
distance protection showing
| 04:37 | 06:33 | Aminbazar-Manikgonj PP 132kV Ckt-1 Tripped from Aminbazar 400/230/132kV end showing Auto
reclose relays Due to Manikgonj ckt-1 trip
| 04:38 | 05:01 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing Distance Zone 1, Y Phase
relays Due to Unknown
|  | 04:45 | Aminbazar 400/230/132kV S/S Gopalganj-1 is restored.
| 04:47 | 06:44 | Aminbazar-Meghnaghat 400kV Ckt-2 Tripped from Aminbazar 400/230/132kV end showing 86 -1 | [7 empty] | and 11.0MW load
|  |  | and 86-2 master relay trip Main CB AR Block relays Due to Meghnaghat ckt-2 trip and | [7 empty] | interrup.
|  |  | from Meghnaghat 400/230kV end showing SEL Relay relays Due to Tripped by 87L, Ground | [7 empty] | Meghnaghat
|  |  | fault & ZCOM | [7 empty] | 400/230kV end
| 05:02 | 05:13 | Daudkandi-Sonargaon 132 kV Ckt-1 Tripped from Daudkandi 132/33kV end showing R/P Dist
trip A , 22.71KM. relays Due to Sonargaon-1
| 05:25 | 05:40 | Ghorasal- Ishwardi 230 kV Ckt-1 Tripped from Ghorashal 230kV end showing 86.1,86.2 Relay | [7 empty] | 170.0MW load
|  |  | operated relays Due to unknown | [7 empty] | interrup. Ghorashal
230kV end
| 05:30 | 05:43 | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-1 Tripped showing Siprotec 7SA87(Siemens)
relays Due to C phase Ground fault
| 05:30 |  | Aminbazar 400/230/132kV S/S Gopalganj-1 Tripped showing General trip Distance trip zone
1 relays Due to General trip, dustance trip
| 05:34 | 07:57 | Gopalganj 400/132kV S/S 400kV Rooppur Forced S/D
| 05:55 | 06:49 | Tongi 230/132/33kV S/S T-01 HT Scheduled S/D Due to Rectification work.
| 05:55 | 06:49 | Tongi 230/132/33kV S/S T-01 LT Scheduled S/D Due to Rectification work
| 06:19 | 07:50 | Sonargaon 132/33kV S/S Tr-2 LT Scheduled S/D Due to Due to red hot corrective maintenance | [7 empty] | 38.0MW load
|  |  | work | [7 empty] | interrup.
| 06:19 | 07:50 | Sonargaon 132/33kV S/S Tr-2 HT Scheduled S/D Due to Due to red hot corrective maintenance | [7 empty] | 38.0MW load
interrup.
| 06:32 |  | Aminbazar-Meghnaghat 400kV Ckt-1 Tripped from Meghnaghat 400/230kV end showing SEL Relay | [7 empty] | 18.0MW load
|  |  | relays Due to Tripped 87L, Ground fault & ZCOM | [7 empty] | interrup.
Meghnaghat
400/230kV end
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 28-02-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0"MW due to gas restriction by Titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 319 | 7956000 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 310 | 6741721 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 16 | 130572 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 7 | 88320 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 85370 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 456000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 502920 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 8 | 410491 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 45 | 225065 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 52 | 1115568 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 406080 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 53 | 349920 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 219885 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 9032727.27 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 405 | 8808060 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 90 | 1219200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1781 | 37747899.27
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 17382.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 130950 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 32 | 521760 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1951580 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 146 | 3370705 | ps availability is less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 32 | 272654 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 429749 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 20160 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 29 | 552960 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21848 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 36 | 272640 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1166 | 25123634 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 2880 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 770 | 17309090.91 | ps availability is less
Chattogram Area Total |  |  |  |  | 4898.863 | 2308 | 49997993.51
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 200 | 5192000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 330 | 7860500 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 350 | 7331800 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 63940 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1108238 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 106 | 2355851 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 138240 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 126 | 2673600 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 365330 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 32 | 202560 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 461882 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1237 | 27753941
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 20 | 415680 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 78 | 1221600 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 98 | 1677600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 0 | Annual Maintenance on going
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 96480 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 92880 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 219 | 3518040
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 65372 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 985000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 723840 | ps availability is less
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 153 | 3667664 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 70 | 979000 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 422496 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 40 | 836160 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 98 | 2385870 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 20 | 417888 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7379000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 352 | 8558000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1115 | 26420290
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 877 | 20850909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 238 | 5837472 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 645840 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1100 | 23069090 | plant availability zero
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2215 | 50403311
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 125 | 2898000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 610 | 11812363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5229300 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 277 | 5651000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4231 | -
Barishal Area Total |  |  |  |  | 2700.36 | 1232 | 25594894.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 351336 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Shutdown As Per PGB PLC's Requirements.
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 190 | 4701027 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9337163 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Machine problem and fuel shortage
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 17072 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 67776 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 27744 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 35940 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1453.58 | 26657408 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 366000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 760250 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2057.58 | 42321716
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 66 | 444336 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 31474.92 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 394720 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 199455 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1123200 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 116 | 2193185.92
Eastern Grid Total |  |  |  |  | 17400.108 | 6660 | 145438163.78
Western Grid Total |  |  |  |  | 10985.595 | 5620.58 | 120513107.56
National Grid Total |  |  |  |  | 28385.703 | 12280.58 | 265951271.34
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 28-02-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8340.88 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3570.36 | MW
i) Dhaka area |  |  | 4642.88 |  | MW | i) Khulna area |  |  |  | 1357 | MW
ii) Chattogram area |  |  | 1225 |  | MW | ii) Barishal area |  |  |  | 362.16 | MW
iii) Cumilla area |  |  | 1038 |  | MW | iii) Rajshahi area |  |  |  | 1138.2 | MW
iv) Mymensingh area |  |  | 1016 |  | MW | iv) Rangpur area |  |  |  | 713 | MW
v) Sylhet area |  |  | 419 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11911.24 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 91 | 13:00 | 133 | Nawabganj | 34.4 | 13:00
2 | AKSML | 13.6 | 06:00 | 68 | Hathazari | 65 | 18:30 | 134 | Netrakona | 144 | 17:00
3 | Aftabnagar | 30 | 18:30 | 69 | Hatirjheel | 32 | 14:00 | 135 | New | 64.6 | 14:00
4 | Agargaon | 88 | 13:00 | 70 | Ishurdi | 57 | 15:00 | 136 | Niamatpur | 96 | 13:00
5 | Agrabad | 44 | 15:00 | 71 | Jaldhaka | 64 | 18:00 | 137 | Noapara | 38 | 19:00
6 | Amnura | 33 | 13:00 | 72 | Jamalpur | 104 | 09:00 | 138 | PHP | 9 | 20:00
7 | Ashuganj | 66 | 00:00 | 73 | Jashore | 114 | 18:00 | 139 | Pabna | 71 | 18:00
8 | BSRM | 198 | 08:00 | 74 | Jhenaidah | 83 | 18:00 | 140 | Palashbari | 94 | 17:00
9 | Bagerhat | 68 | 19:00 | 75 | Joydebpur | 111 | 17:00 | 141 | Panchagarh | 46 | 18:00
10 | Bajitpur | 70 | 18:00 | 76 | Joypurhat | 66 | 09:00 | 142 | Patiya | 7 | 15:00
11 | Bakerganj | 10.7 | 18:00 | 77 | Juldah | 13.5 | 14:00 | 143 | Patuakhali | 48.2 | 18:00
12 | Bakulia | 77 | 12:00 | 78 | KSRM | 27 | 10:00 | 144 | Payra | 32 | 19:30
13 | Banani | 38.6 | 14:00 | 79 | Kabirpur | 223 | 17:00 | 145 | Postogola | 43 | 13:00
14 | Bangabhaban | 6 | 11:00 | 80 | Kachua | 64 | 18:00 | 146 | Purbachal | 24 | 13:00
15 | Barapukuria | 62 | 13:00 | 81 | Kaliganj | 21 | 18:00 | 147 | Purbasadipur | 118 | 17:00
16 | Barguna | 16 | 19:30 | 82 | Kallyanpur | 93 | 13:00 | 148 | Rahanpur | 29 | 08:00
17 | Barishal | 81 | 18:00 | 83 | Kalurghat | 34 | 15:00 | 149 | Rahim | 36 | 12:00
18 | Barishal-230 | 70 | 19:00 | 84 | Kamrangirchar | 76 | 16:00 | 150 | Rajbari | 54 | 04:00
19 | Baroaulia | 58 | 15:00 | 85 | Kaptai | N/A | N/A | 151 | Rajendrapur | 124 | 18:00
20 | Baroirhat | 43 | 17:00 | 86 | Kasba | 29 | 12:00 | 152 | Rajshahi | 95 | 04:00
21 | Bashundhara | 172 | 18:00 | 87 | Kazla | 98 | 12:00 | 153 | Rajshahi-230 | 60 | 18:00
22 | BashundharaCement | 10 | 16:00 | 88 | Keranigonj | 72 | 19:30 | 154 | Ramganj | 70 | 20:00
23 | Beanibazar | 46 | 18:30 | 89 | Khagrachori | 26 | 18:00 | 155 | Rampur | 35 | 21:00
24 | Benapole | 54 | 13:00 | 90 | Khulna | 43 | 19:00 | 156 | Rangamati | 14 | 18:30
25 | Bhaluka | 131 | 14:00 | 91 | Khulshi | 177 | 13:00 | 157 | Rangpur | 124 | 18:00
26 | Bhandaria | 42 | 21:00 | 92 | Kishoreganj | 110 | 18:00 | 158 | Ruppur | 1.8 | 12:00
27 | Bhangura | 36 | 14:00 | 93 | Kodda | 307 | 16:00 | 159 | SSM | 5 | 00:00
28 | Bheramara(GK) | 46 | 18:00 | 94 | Kulaura | 29 | 18:00 | 160 | Saidpur | 100 | 16:00
29 | Bhulta | 208 | 22:00 | 95 | Kurigram | 64 | 17:00 | 161 | Satkhira | 120 | 18:00
30 | Bog-Sherpur | 56 | 04:00 | 96 | Kushtia | 116 | 18:00 | 162 | Satmasjid | 82 | 18:30
31 | Bogura | 137 | 18:00 | 97 | Laksam | 25 | 13:00 | 163 | Savar | 178 | 15:00
32 | Borhanuddin | 75 | 18:30 | 98 | Lakshmipur | 26 | 21:00 | 164 | SevenRings | 17.13 | 19:00
33 | Brahmanbaria | 102 | 18:00 | 99 | Lalbag | 70 | 17:00 | 165 | ShahCement | 32 | 09:00
34 | Cantonment | 76 | 19:00 | 100 | Lalmonirhat | 46 | 17:00 | 166 | Shahjadpur | 62 | 09:00
35 | Chandina | 18 | 18:30 | 101 | MI_Cement | 17.8 | 23:00 | 167 | Shahjibazar | 103 | 21:00
36 | Chandpur | 52 | 19:00 | 102 | Madanganj | 44 | 00:00 | 168 | Shahmirpur | 48 | 23:00
37 | Chandraghona | 27 | 18:30 | 103 | Madaripur | 77 | 19:30 | 169 | Shariatpur | 58 | 21:00
38 | Chapai | 59 | 09:00 | 104 | Madartek | 62 | 21:00 | 170 | Sherpur | 146 | 17:00
39 | Charsaidpur | 42 | 00:00 | 105 | Madunaghat | 40 | 21:00 | 171 | Shikalbaha | 29 | 15:00
40 | Chauddagram | 58 | 13:00 | 106 | Magura | 49 | 19:00 | 172 | Shitalakhya | 73.5 | 15:00
41 | Chhatak | 27 | 22:00 | 107 | Mahasthangarh | 60 | 09:00 | 173 | Sholosohor | 37 | 12:00
42 | Chowmuhani | 108 | 19:30 | 108 | Maijdee | 35 | 18:30 | 174 | Shyampur | 160 | 13:00
43 | Chuadanga | 82 | 18:00 | 109 | Manikganj | 96 | 19:00 | 175 | Siddhirganj | 117 | 12:00
44 | Coxsbazar | 113 | 21:00 | 110 | Maniknagar | 50 | 18:00 | 176 | Sirajganj | 96 | 12:00
45 | Cumilla(N) | 95 | 10:00 | 111 | Matarbari | 41 | 18:30 | 177 | Sonargaon | 154 | 12:00
46 | Cumilla(S) | 143 | 14:00 | 112 | Matuail | 64 | 14:00 | 178 | Sreemongol | 56 | 18:30
47 | Daganbhuiyan | 25 | 22:00 | 113 | Metrorail_Motijheel | 33 | 16:00 | 179 | Sreepur | 108 | 15:00
48 | Daudkandi | 111 | 21:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Srinagar | 35 | 13:00
49 | DhakaUniversity | 56 | 13:00 | 115 | Millgate | 84 | 14:00 | 181 | Sunamganj | 40 | 16:00
50 | Dhamrai | 114 | 15:00 | 116 | Mirpur | 123 | 20:00 | 182 | Sylhet | 46 | 14:00
51 | Dhanmondi | 85 | 13:00 | 117 | Mirsorai | 49 | 09:00 | 183 | Sylhet-132 | 76 | 21:00
52 | Dohazari | 87 | 18:00 | 118 | Mirzapur | 49 | 18:00 | 184 | TK | 18 | 18:30
53 | Faridpur | 115 | 18:30 | 119 | Mithapukur | 52 | 04:00 | 185 | Tangail | 156 | 18:00
54 | Fatullah | 89 | 15:00 | 120 | Modern | N/A | N/A | 186 | Taraganj | 21 | 17:00
55 | Fenchuganj | 24 | 18:30 | 121 | Mogbazar | 79.6 | 14:00 | 187 | Tasnim | 30 | 02:00
56 | Feni | 79 | 12:00 | 122 | Mongla | 45 | 19:00 | 188 | Thakurgaon | 81 | 18:00
57 | GPH | 76 | 05:00 | 123 | Motijheel | 38 | 13:00 | 189 | Tongi | 151 | 15:00
58 | Ghatail | 84 | 03:00 | 124 | Muktagacha | 35 | 18:00 | 190 | Ullahpara | 40 | 03:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 76 | 14:00 | 191 | Ullon | 48 | 21:00
60 | Ghorashal-230 | 104 | 19:00 | 126 | Muradnagar | 27 | 18:00 | 192 | Uttara | 62 | 19:00
61 | Goalpara | 24 | 18:00 | 127 | Mymensingh | 198 | 18:00 | 193 | UttaraNew | 31 | 21:00
62 | Gollamari | 88 | 19:00 | 128 | Naogaon | 111 | 18:00 | 194 | Zigatola | 60 | 20:00
63 | Gopalganj | 85.6 | 19:00 | 129 | Narail | 47 | 18:00
64 | Gulshan | 76 | 13:00 | 130 | Narinda | 55 | 15:00
65 | Halishahar | 78 | 12:00 | 131 | Narshingdi | 150 | 22:00
66 | HaripurSBU | 131 | 11:00 | 132 | Natore | 129 | 04:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 28-02-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 10366.5 | 0 |  | 10366.5
1:00 | 9775.5 | 0 |  | 9775.5
2:00 | 9506.5 | 0 |  | 9506.5
3:00 | 9642.5 | 0 |  | 9642.5
4:00 | 10616.5 | 0 |  | 10616.5
5:00 | 9607.5 | 0 |  | 9607.5
6:00 | 8617.5 | 0 |  | 8617.5
7:00 | 8861.02 | 0 |  | 8861.02
8:00 | 9559.99 | 0 |  | 9559.99
9:00 | 10385.14 | 0 |  | 10385.14
10:00 | 10596.5 | 0 |  | 10596.5
11:00 | 11006.58 | 0 |  | 11006.58
12:00 | 11372.42 | 0 |  | 11372.42
13:00 | 11657.15 | 0 |  | 11657.15
14:00 | 11901.3 | 0 |  | 11901.3
15:00 | 11763.37 | 0 |  | 11763.37
16:00 | 11892.45 | 0 |  | 11892.45
17:00 | 12139.7 | 0 |  | 12139.7
18:00 | 11952.11 | 0 |  | 11952.11
19:00 | 12255.06 | 0 |  | 12255.06
19:30 | 12280.58 | 0 |  | 12280.58
20:00 | 12257.36 | 0 |  | 12257.36
21:00 | 12156.23 | 0 |  | 12156.23
22:00 | 12121.75 | 0 |  | 12121.75
23:00 | 11492.97 | 0 |  | 11492.97
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 28-02-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5591.5 | 4775 | 10366.5 | DAILY GENERATION CURVE
00:30 | 5474.5 | 4596.5 | 10071
01:00 | 5357.5 | 4418 | 9775.5 | 28-02-2026
01:30 | 5287 | 4354 | 9641
02:00 | 5216.5 | 4290 | 9506.5
02:30 | 5263 | 4311.5 | 9574.5
03:00 | 5309.5 | 4333 | 9642.5
03:30 | 5576 | 4553.5 | 10129.5
04:00 | 5842.5 | 4774 | 10616.5
04:30 | 5563.5 | 4548.5 | 10112
05:00 | 5284.5 | 4323 | 9607.5
05:30 | 4999.5 | 4113 | 9112.5
06:00 | 4714.5 | 3903 | 8617.5
06:30 | 4805.635 | 3933.625 | 8739.26
07:00 | 4896.77 | 3964.25 | 8861.02
07:30 | 5171.93 | 4038.575 | 9210.505
08:00 | 5447.09 | 4112.9 | 9559.99
08:30 | 5585.075 | 4387.49 | 9972.565
09:00 | 5723.06 | 4662.08 | 10385.14
09:30 | 5733.415 | 4757.405 | 10490.82
10:00 | 5743.77 | 4852.73 | 10596.5
10:30 | 5841.5 | 4960.04 | 10801.54
11:00 | 5939.23 | 5067.35 | 11006.58
11:30 | 6041.48 | 5148.02 | 11189.5
12:00 | 6143.73 | 5228.69 | 11372.42
12:30 | 6194.435 | 5320.35 | 11514.785
13:00 | 6245.14 | 5412.01 | 11657.15
13:30 | 6352.565 | 5426.66 | 11779.225
14:00 | 6459.99 | 5441.31 | 11901.3
14:30 | 6428.6 | 5403.735 | 11832.335
15:00 | 6397.21 | 5366.16 | 11763.37
15:30 | 6465.735 | 5362.175 | 11827.91
16:00 | 6534.26 | 5358.19 | 11892.45
16:30 | 6617.845 | 5398.23 | 12016.075
17:00 | 6701.43 | 5438.27 | 12139.7
17:30 | 6617.515 | 5428.39 | 12045.905
18:00 | 6533.6 | 5418.51 | 11952.11
18:30 | 6622.7 | 5480.885 | 12103.585
19:00 | 6711.8 | 5543.26 | 12255.06
19:30 | 6660 | 5620.58 | 12280.58
20:00 | 6626 | 5631.36 | 12257.36
20:30 | 6570.7 | 5636.095 | 12206.795 |  | Executive Engineer
21:00 | 6515.4 | 5640.83 | 12156.23 |  | Network Operation Division
21:30 | 6498.1 | 5640.89 | 12138.99
22:00 | 6480.8 | 5640.95 | 12121.75
22:30 | 6244.4 | 5562.96 | 11807.36
23:00 | 6008 | 5484.97 | 11492.97

## En-Curve
QF-LDC-12
Date | 28-02-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3137 | 1691.5 | 877 | 0 | 110 | 1003 | 75 | 3397 | 0 | 17 | 59 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3112.5 | 1680 | 877 | 0 | 99 | 955 | 75 | 3196.5 | 0 | 17 | 59 | 0 | 0 | 0 | 0 | 28-02-2026
01:00 | 3088 | 1668.5 | 877 | 0 | 88 | 907 | 75 | 2996 | 0 | 17 | 59 | 0 | 0 | 0 | 0
01:30 | 3050 | 1594.5 | 877 | 0 | 94 | 907 | 75 | 2967.5 | 0 | 17 | 59 | 0 | 0 | 0 | 0 | Energy Generated | 265.9513 |  | MKWHr
02:00 | 3012 | 1520.5 | 877 | 0 | 100 | 907 | 75 | 2939 | 0 | 17 | 59 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3028 | 1505.5 | 877.5 | 0 | 99 | 909 | 75 | 2935.5 | 0 | 29.5 | 115.5 | 0 | 0 | 0 | 0 | Total Energy Requirement | 265.9513 |  | MKWHr
03:00 | 3044 | 1490.5 | 878 | 0 | 98 | 911 | 75 | 2932 | 0 | 42 | 172 | 0 | 0 | 0 | 0
03:30 | 3149 | 1538 | 877.5 | 0 | 99 | 983.5 | 75 | 3160 | 0 | 55 | 192.5 | 0 | 0 | 0 | 0
04:00 | 3254 | 1585.5 | 877 | 0 | 100 | 1056 | 75 | 3388 | 0 | 68 | 213 | 0 | 0 | 0 | 0
04:30 | 3203.5 | 1490 | 877 | 0 | 98 | 974.5 | 75 | 3185.5 | 0 | 34 | 174.5 | 0 | 0 | 0 | 0
05:00 | 3153 | 1394.5 | 877 | 0 | 96 | 893 | 75 | 2983 | 0 | 0 | 136 | 0 | 0 | 0 | 0
05:30 | 2958.5 | 1354.5 | 877 | 0 | 92 | 861 | 75 | 2805 | 0 | 0 | 89.5 | 0 | 0 | 0 | 0
06:00 | 2764 | 1314.5 | 877 | 0 | 88 | 829 | 75 | 2627 | 0 | 0 | 43 | 0 | 0 | 0 | 0
06:30 | 2868 | 1355 | 836 | 0 | 88 | 829.5 | 75 | 2627.5 | 17.26 | 0 | 43 | 0 | 0 | 0 | 0
07:00 | 2972 | 1395.5 | 795 | 0 | 88 | 830 | 75 | 2628 | 34.52 | 0 | 43 | 0 | 0 | 0 | 0
07:30 | 3166.5 | 1467.25 | 741.5 | 0 | 88 | 830 | 75 | 2617.5 | 109.755 | 35.5 | 79.5 | 0 | 0 | 0 | 0
08:00 | 3361 | 1539 | 688 | 0 | 88 | 830 | 75 | 2607 | 184.99 | 71 | 116 | 0 | 0 | 0 | 0
08:30 | 3328 | 1552 | 774.5 | 0 | 97 | 899.34 | 75 | 2753.5 | 275.725 | 82 | 135.5 | 0 | 0 | 0 | 0
09:00 | 3295 | 1565 | 861 | 0 | 106 | 968.68 | 75 | 2900 | 366.46 | 93 | 155 | 0 | 0 | 0 | 0
09:30 | 3298 | 1569.5 | 869.5 | 0 | 109 | 966.855 | 75 | 2900.5 | 441.465 | 102 | 159 | 0 | 0 | 0 | 0
10:00 | 3301 | 1574 | 878 | 0 | 112 | 965.03 | 75 | 2901 | 516.47 | 111 | 163 | 0 | 0 | 0 | 0
10:30 | 3264 | 1587.5 | 878 | 0 | 118 | 1008.6 | 75 | 2993.5 | 568.94 | 118 | 190 | 0 | 0 | 0 | 0
11:00 | 3227 | 1601 | 878 | 0 | 124 | 1052.17 | 75 | 3086 | 621.41 | 125 | 217 | 0 | 0 | 0 | 0
11:30 | 3229 | 1586 | 877.5 | 0 | 124 | 1086.815 | 85 | 3208.5 | 643.185 | 129 | 220.5 | 0 | 0 | 0 | 0
12:00 | 3231 | 1571 | 877 | 0 | 124 | 1121.46 | 95 | 3331 | 664.96 | 133 | 224 | 0 | 0 | 0 | 0
12:30 | 3220.5 | 1551 | 877 | 0 | 123 | 1124.03 | 87.5 | 3488.5 | 658.755 | 146 | 237 | 0 | 0 | 1.5 | 0
13:00 | 3210 | 1531 | 877 | 0 | 122 | 1126.6 | 80 | 3646 | 652.55 | 159 | 250 | 0 | 0 | 3 | 0
13:30 | 3158 | 1538 | 877.5 | 0 | 133 | 1126.685 | 80 | 3830 | 612.54 | 167 | 255 | 0 | 0 | 1.5 | 0
14:00 | 3106 | 1545 | 878 | 0 | 144 | 1126.77 | 80 | 4014 | 572.53 | 175 | 260 | 0 | 0 | 0 | 0
14:30 | 3106.5 | 1549 | 878 | 0 | 142 | 1127.465 | 80 | 3994 | 500.37 | 185 | 270 | 0 | 0 | 0 | 0
15:00 | 3107 | 1553 | 878 | 0 | 140 | 1128.16 | 80 | 3974 | 428.21 | 195 | 280 | 0 | 0 | 0 | 0
15:30 | 3152.5 | 1603 | 878 | 0 | 133 | 1125.505 | 80 | 3982 | 347.905 | 210.5 | 315.5 | 0 | 0 | 0 | 0
16:00 | 3198 | 1653 | 878 | 0 | 126 | 1122.85 | 80 | 3990 | 267.6 | 226 | 351 | 0 | 0 | 0 | 0
16:30 | 3268 | 1676.5 | 878 | 0 | 125 | 1174.3 | 80 | 3988.5 | 178.525 | 229.25 | 417 | 0 | 0 | 1 | 0
17:00 | 3338 | 1700 | 878 | 0 | 124 | 1225.75 | 80 | 3987 | 89.45 | 232.5 | 483 | 0 | 0 | 2 | 0
17:30 | 3144.5 | 1674.5 | 878 | 0 | 122 | 1246.38 | 80 | 3961 | 44.975 | 235.25 | 658.3 | 0 | 0 | 1 | 0
18:00 | 2951 | 1649 | 878 | 0 | 120 | 1267.01 | 80 | 3935 | 0.5 | 238 | 833.6 | 0 | 0 | 0 | 0
18:30 | 3144.5 | 1627 | 877.5 | 0 | 123 | 1351.135 | 80 | 3904 | 0.25 | 222.5 | 773.7 | 0 | 0 | 0 | 0
19:00 | 3338 | 1605 | 877 | 0 | 126 | 1435.26 | 80 | 3873 | 0 | 207 | 713.8 | 0 | 0 | 0 | 0
19:30 | 3340 | 1695 | 877 | 0 | 126 | 1453.58 | 80 | 3923 | 0 | 139 | 647 | 0 | 0 | 0 | 0
20:00 | 3308 | 1696 | 877 | 0 | 124 | 1457.36 | 80 | 3946 | 0 | 132 | 637 | 0 | 0 | 0 | 0
20:30 | 3294.5 | 1708.5 | 877 | 0 | 126 | 1457.095 | 80 | 3922.5 | 0 | 123.5 | 617.7 | 0 | 0 | 0 | 0
21:00 | 3281 | 1721 | 877 | 0 | 128 | 1456.83 | 80 | 3899 | 0 | 115 | 598.4 | 0 | 0 | 0 | 0
21:30 | 3264 | 1709 | 880 | 0 | 130 | 1457.89 | 80 | 3903 | 0 | 115 | 600.1 | 0 | 0 | 0 | 0
22:00 | 3247 | 1697 | 883 | 0 | 132 | 1458.95 | 80 | 3907 | 0 | 115 | 601.8 | 0 | 0 | 0 | 0
22:30 | 3202.5 | 1683 | 883.5 | 0 | 132 | 1457.46 | 80 | 3902 | 0 | 83.5 | 383.4 | 0 | 0 | 0 | 0
23:00 | 3158 | 1669 | 884 | 0 | 132 | 1455.97 | 80 | 3897 | 0 | 52 | 165 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 28-02-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 412 | 06:00 | 384 | 14:00 | Madunaghat | 410 | 06:00 | 396 | 15:00
Amtali | 425 | 06:00 | 410 | 14:00 | Meghnaghat | 411 | 03:00 | 385 | 15:00
Ashuganj | 422 | 3:00 | 388 | 15:00 | Payra | 425 | 06:00 | 411 | 16:00
Bhulta | 415 | 03:00 | 381 | 15:00 | Rahanpur | 419 | 06:00 | 385 | 13:00
Bibiana | 417 | 03:00 | 401 | 15:00 | Rampal | 415 | 06:00 | 395 | 14:00
BIPTC | 403 | 07:00 | 389 | 10:00
Bogura | 415 | 06:00 | 379 | 13:00
Gopalganj | 418 | 06:00 | 395 | 15:00
Kaliakoir | 405 | 06:00 | 379 | 14:00
Korerhat | 416 | 06:00 | 393 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 240 | 06:00 | 219 | 14:00 | Jhenaidah | 242 | 06:00 | 222 | 16:00
AKSML | 236.6 | 06:00 | 224 | 15:00 | Kachua | 238 | 06:00 | 223 | 15:00
Aminbazar | 240 | 06:00 | 219 | 14:00 | Kaliakoir | 241 | 03:00 | 222 | 14:00
Ashuganj | 237 | 02:00 | 221 | 14:00 | Keranigonj | 239 | 06:00 | 218 | 15:00
Ashuganj-400 | 237 | 02:00 | 221 | 14:00 | Khulna(S) | 242 | 02:00 | 224 | 17:00
Baghabari | 240 | 05:00 | 223 | 15:00 | Korerhat | 237 | 02:00 | 223 | 14:00
Barapukuria | 229 | 06:00 | 202 | 13:00 | Madunaghat | 235 | 06:00 | 224 | 14:00
Barapukuria-230 | 229 | 06:00 | 202 | 13:00 | Madunaghat-400 | 234 | 06:00 | 225 | 15:00
Barishal | 237 | 06:00 | 227 | 15:00 | Maniknagar | 239 | 02:00 | 220 | 15:00
Bheramara | 239 | 06:00 | 221 | 16:00 | Meghnaghat | 246 | 04:00 | 230 | 16:00
Bhulta | 240 | 03:00 | 220 | 15:00 | Meghnaghat-400 | 243 | 06:00 | 224 | 15:00
Bibiana | 242 | 06:00 | 230 | 15:00 | Mirsorai | 266 | 13:00 | 223 | 15:00
BIPTC | 242 | 06:00 | 222 | 14:00 | Rajshahi | 239 | 03:00 | 220 | 16:00
Bogura | 241 | 06:00 | 221 | 13:00 | Rampal | 240 | 06:00 | 224 | 16:00
Bogura-400 | 240 | 06:00 | 219 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Borhanuddin | 238 | 01:00 | 232 | 17:00 | Rampura | 239 | 03:00 | 218 | 15:00
BSRM | 236 | 06:00 | 222 | 15:00 | Shikalbaha | 232 | 05:00 | 222 | 14:00
Chowmuhani | N/A | N/A | N/A | N/A | Shyampur | 240 | 03:00 | 220 | 15:00
Cumilla(N) | 238 | 04:00 | 222 | 15:00 | Siddhirganj | 240 | 02:00 | 222 | 15:00
Faridpur | 236 | 06:00 | 222 | 14:00 | Sirajgonj | 243 | 06:00 | 228 | 17:00
Fenchuganj | 243 | 05:00 | 232 | 17:00 | Sreepur | 232 | 05:00 | 215 | 15:00
Feni | 239 | 06:00 | 223 | 15:00 | Tongi | 240 | 04:00 | 217 | 15:00
Ghorashal | 240 | 00:00 | 220 | 14:00
Ghorashal-230 | 237 | 03:00 | 217 | 15:00
Gopalganj | 234 | 06:00 | 221 | 14:00
GPH | 235 | 06:00 | 223 | 15:00
Haripur | 241 | 03:00 | 222 | 15:00
Hasnabad | 240 | 06:00 | 220 | 15:00
Hathazari | 231 | 06:00 | 221 | 14:00
Ishurdi | 242 | 02:00 | 224 | 17:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 05:00 | 126 | 14:00 | Magura | 139 | 06:00 | 126 | 13:00
Agargaon | 135 | 03:00 | 123 | 14:00 | Mahasthangarh | 137 | 02:00 | 124 | 13:00
Agrabad | 134 | 02:00 | 127 | 14:00 | Maijdee | 133 | 06:00 | 124 | 15:00
AKS | 133 | 06:00 | 126 | 15:00 | Manikganj | 134 | 04:00 | 127 | 13:00
Aminbazar | 140 | 06:00 | 126 | 14:00 | Maniknagar | 135 | 02:00 | 122 | 15:00
Amnura | 139 | 06:00 | 126 | 13:00 | Matarbari | 127 | 07:00 | 116 | 17:00
Ashuganj | 138 | 01:00 | 132 | 12:00 | Matuail | 137.2 | 06:00 | 125.8 | 15:00
Bagerhat | 137 | 02:00 | 120 | 17:00 | Metrorail_Motijheel | 135 | 02:00 | 122 | 15:00
Bajitpur | 135 | 05:00 | 125 | 16:00 | Metrorail_Uttara | 139 | 06:00 | 125 | 16:00
Bakerganj | 138 | 03:00 | 132 | 16:00 | Millgate | 136 | 02:00 | 122 | 14:00
Bakulia | 134 | 07:00 | 128 | 14:00 | Mirpur | 138 | 03:00 | 125 | 14:00
Banani | 139 | 06:00 | 125 | 15:00 | Mirzapur | 137 | 03:00 | 125 | 17:00
Bangabhaban | 135 | 05:00 | 121 | 16:00 | Mithapukur | 137 | 06:00 | 122 | 11:00
Barapukuria | 139 | 05:00 | 123 | 13:00 | MI_Cement | 138 | 06:00 | 124 | 15:00
Barguna | 139 | 06:00 | 132 | 16:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 138 | 06:00 | 131 | 15:00 | Mogbazar | 140 | 06:00 | 125 | 15:00
Barishal-230 | 138 | 03:00 | 131 | 17:00 | Mongla | 137 | 06:00 | 121 | 17:00
Baroaulia | 136 | 07:00 | 128 | 15:00 | Motijheel | 134 | 04:00 | 121 | 16:00
Baroirhat | 136 | 06:00 | 127 | 15:00 | Muktagacha | 132 | 22:00 | 120 | 14:00
Bashundhara | 139 | 05:00 | 126 | 14:00 | Munshiganj | 135 | 04:00 | 123 | 15:00
BashundharaCement | 135 | 01:00 | 126 | 16:00 | Muradnagar | 136 | 03:00 | 125 | 15:00
Beanibazar | 131 | 02:00 | 125 | 14:00 | Mymensingh | 132 | 22:00 | 114 | 17:00
Benapole | 136 | 02:00 | 119 | 13:00 | Naogaon | 140 | 02:00 | 122 | 12:00
Bhaluka | 135 | 05:00 | 126 | 14:00 | Narail | 139 | 02:00 | 125 | 15:00
Bhandaria | 137 | 07:00 | 127 | 17:00 | Narinda | 135 | 02:00 | 122 | 15:00
Bhangura | 137 | 01:00 | 126 | 15:00 | Narshingdi | 134 | 06:00 | 122 | 14:00
Bheramara | 140 | 06:00 | 131 | 13:00 | Natore | 138 | 05:00 | 127 | 13:00
Bheramara(GK) | 140 | 06:00 | 131 | 16:00 | Nawabganj | 139 | 03:00 | 125 | 15:00
Bhulta | 130 | 01:00 | 121 | 16:00 | Netrakona | 126 | 05:00 | 112 | 17:00
Bog-Sherpur | 139 | 06:00 | 126 | 13:00 | New | 135 | 04:00 | 123 | 14:00
Bogura | 139 | 06:00 | 126 | 13:00 | Niamatpur | 140 | 06:00 | 126 | 13:00
Bogura-230 | 140 | 06:00 | 127 | 13:00 | Noapara | 136 | 01:00 | 122 | 17:00
Brahmanbaria | 133 | 18:00 | 121 | 15:00 | Pabna | 140 | 00:00 | 129 | 13:00
Cantonment | 135 | 06:00 | 123 | 14:00 | Palashbari | 136 | 04:00 | 119 | 13:00
Chandina | 139 | 06:00 | 128 | 15:00 | Panchagarh | 138 | 06:00 | 121 | 13:00
Chandpur | 134 | 02:00 | 126 | 15:00 | Patiya | 135 | 06:00 | 129 | 18:00
Chandraghona | 137 | 03:00 | 130 | 15:00 | Patuakhali | 138 | 06:00 | 131 | 16:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 138 | 04:00 | 126 | 13:00 | Payra | 140 | 03:00 | 134 | 16:00
Charsaidpur | 136 | 05:00 | 125 | 12:00 | PHP | 135 | 03:00 | 126 | 15:00
Chauddagram | 136 | 06:00 | 126 | 14:00 | Postogola | 139 | 03:00 | 124 | 15:00
Chhatak | 130 | 03:00 | 124 | 16:00 | Purbachal | 139 | 02:00 | 125 | 15:00
Chowmuhani | 131 | 01:00 | 125 | 15:00 | Purbasadipur | 133 | 06:00 | 116 | 13:00
Chuadanga | 139 | 06:00 | 123 | 17:00 | Rahanpur | 140 | 04:00 | 129 | 13:00
Coxsbazar | 124 | 07:00 | 116 | 17:00 | Rahanpur-400 | 141 | 06:00 | 128 | 13:00
Cumilla(N) | 138 | 04:00 | 128 | 15:00 | Rahim | 136 | 02:00 | 125 | 15:00
Cumilla(S) | 138 | 03:00 | 121 | 14:00 | Rajbari | 136 | 06:00 | 127 | 14:00
Daganbhuiyan | 134 | 06:00 | 125 | 15:00 | Rajendrapur | 139 | 03:00 | 126 | 15:00
Daudkandi | 133 | 04:00 | 122 | 15:00 | Rajshahi | 139 | 06:00 | 127 | 13:00
DhakaUniversity | 139 | 04:00 | 126 | 15:00 | Rajshahi-230 | 138 | 03:00 | 127 | 13:00
Dhamrai | 138 | 01:00 | 124 | 15:00 | Ramganj | 133 | 06:00 | 123 | 16:00
Dhanmondi | 139 | 05:00 | 127 | 14:00 | Rampur | 134 | 03:00 | 128 | 14:00
Dohazari | 132 | 06:00 | 125 | 15:00 | Rampura | 139 | 06:00 | 125 | 15:00
Faridpur | 135 | 02:00 | 128 | 16:00 | Rangamati | 136 | 05:00 | 129 | 16:00
Fatullah | 139 | 06:00 | 122 | 15:00 | Rangpur | 137 | 06:00 | 124 | 12:00
Fenchuganj | 137 | 05:00 | 132 | 14:00 | Ruppur | 140 | 03:00 | 131 | 16:00
Feni | 133 | 03:00 | 125 | 15:00 | Saidpur | 137 | 06:00 | 120 | 13:00
Feni-230 | 134 | 06:00 | 125 | 15:00 | Satkhira | 137 | 06:00 | 122 | 17:00
Ghatail | 130 | 03:00 | 118 | 13:00 | Satmasjid | 135 | 06:00 | 122 | 16:00
Ghorashal | 141 | 02:00 | 133 | 12:00 | Savar | 139 | 06:00 | 122 | 15:00
Goalpara | 140 | 03:00 | 126 | 17:00 | SevenRings | 142 | 03:00 | 130 | 15:00
Gollamari | 159 | 16:00 | 126 | 17:00 | ShahCement | 136 | 05:00 | 124 | 15:00
Gopalganj | 139 | 06:00 | 128 | 11:00 | Shahjadpur | 141 | 02:00 | 131 | 13:00
Gopalganj-400 | 140 | 06:00 | 131 | 15:00 | Shahjibazar | 133 | 18:00 | 117 | 15:00
Gulshan | 138 | 05:00 | 125 | 15:00 | Shahmirpur | 135 | 02:00 | 129 | 14:00
Halishahar | 135 | 06:00 | 128 | 15:00 | Shariatpur | 139 | 06:00 | 130 | 15:00
Haripur | 137 | 03:00 | 126 | 15:00 | Sherpur | 130 | 22:00 | 113 | 16:00
HaripurSBU | 137 | 03:00 | 125 | 15:00 | Shikalbaha | 125 | 05:00 | 119 | 14:00
Hasnabad | 139 | 03:00 | 124 | 16:00 | Shikalbaha-230 | 136 | 02:00 | 130 | 14:00
Hathazari | 136 | 05:00 | 130 | 14:00 | Shitalakhya | 138 | 06:00 | 124 | 15:00
Hatirjheel | 138.8 | 06:00 | 125 | 15:00 | Sholosohor | 136 | 03:00 | 130 | 14:00
Ishurdi | 142 | 02:00 | 132 | 16:00 | Shyampur | 136 | 06:00 | 126 | 15:00
Jaldhaka | 134 | 06:00 | 118 | 13:00 | Shyampur-230 | 139 | 03:00 | 127 | 15:00
Jamalpur | 133 | 22:00 | 116 | 17:00 | Siddhirganj | 137 | 05:00 | 126 | 15:00
Jashore | 137 | 06:00 | 119 | 17:00 | Sirajganj | 136 | 05:00 | 125 | 17:00
Jhenaidah | 139 | 02:00 | 118 | 13:00 | Sonargaon | 135 | 04:00 | 126 | 16:00
Jhenaidah-230 | 140 | 02:00 | 128 | 15:00 | Sreemongol | 133 | 06:00 | 124 | 14:00
Joydebpur | 138 | 18:30 | 126 | 15:00 | Sreepur | 141 | 05:00 | 131 | 12:00
Joypurhat | 133 | 02:00 | 118 | 17:00 | Srinagar | 139 | 05:00 | 125 | 15:00
Juldah | 134 | 07:00 | 128 | 16:00 | SSM | 138 | 00:00 | 132 | 14:00
Kabirpur | 139 | 18:00 | 120 | 16:00 | Sunamganj | 129 | 05:00 | 123 | 17:00
Kachua | 136 | 06:00 | 127 | 14:00 | Sylhet | 133 | 03:00 | 127 | 14:00
Kaliakoir | 142 | 03:00 | 128 | 15:00 | Sylhet-132 | 131 | 05:00 | 128 | 15:00
Kaliganj | 140 | 05:00 | 128 | 14:00 | Tangail | 132 | 01:00 | 123 | 14:00
Kallyanpur | 140 | 01:00 | 126 | 15:00 | Taraganj | 135 | 06:00 | 119 | 13:00
Kalurghat | 137 | 06:00 | 130 | 15:00 | Tasnim | 135 | 02:00 | 125 | 14:00
Kamrangirchar | 139 | 06:00 | 124 | 16:00 | Thakurgaon | 138 | 18:30 | 119 | 13:00
Kaptai | N/A | N/A | N/A | N/A | TK | 135 | 04:00 | 129 | 14:00
Kasba | 136 | 06:00 | 124 | 15:00 | Tongi | 137 | 04:00 | 127 | 15:00
Kazla | 134 | 03:00 | 122 | 15:00 | Ullahpara | 137 | 05:00 | 126 | 13:00
Keranigonj | 139 | 03:00 | 125 | 16:00 | Ullon | 138 | 02:00 | 125 | 14:00
Khagrachori | 136 | 03:00 | 129 | 14:00 | Uttara | 139 | 06:00 | 124 | 14:00
Khulna | 139 | 05:00 | 125 | 17:00 | UttaraNew | 139 | 06:00 | 125 | 16:00
Khulna(S) | 140 | 06:00 | 127 | 17:00 | Zigatola | 139 | 06:00 | 125 | 15:00
Khulshi | 133 | 06:00 | 127 | 15:00
Kishoreganj | 133 | 05:00 | 121 | 17:00
Kodda | 138 | 03:00 | 126 | 11:00
Korerhat | 138 | 02:00 | 127 | 16:00
KSRM | 136 | 06:00 | 129 | 14:00
Kulaura | 136 | 05:00 | 131 | 14:00
Kurigram | 133 | 06:00 | 118 | 13:00
Kushtia | 136 | 04:00 | 124 | 13:00
Laksam | 136 | 06:00 | 125 | 13:00
Lakshmipur | 133 | 03:00 | 124 | 15:00
Lalbag | 139 | 06:00 | 124 | 16:00
Lalmonirhat | 132 | 05:00 | 119 | 10:00
Madanganj | 135 | 01:00 | 126 | 16:00
Madaripur | 137 | 05:00 | 130 | 15:00
Madartek | 137 | 04:00 | 125 | 16:00
Madunaghat | 137 | 06:00 | 130 | 14:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division