## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 02-03-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-03-2026 | during | 02-03-2026 | during | 02-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 338 | 298 | 412 | 412 | 412 | 412 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 0 | 0 | Engine Problem
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 335 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 54 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 0 | 23.5 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 20 | 20 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 24 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 45 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 51 | 123 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 34 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 106 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 24 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 355 | 350 | 584 | 584 | 584 | 584 | FGMO
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 400 | 350 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 108 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1638 | 1994.5 | 5946.22 | 5915.22 | 3172.05 | 3177.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 39 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 80 | 75 | 75 | 75 | 75 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 147 | 150 | 150 | 150 | 150 | 150 | ps availability is less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 85 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 48 | 64 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 51 | 50 | 68 | 68 | 68 | 68 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 0 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 5 | 18 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 97 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.33 | 0 | 3.55 | 0 | 3.55 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 50 | 50 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1165 | 1100 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 14 | 0 | 14 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 775 | 1030 | 720 | 720 | 720 | 720 | ps availability is less
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2405.33 | 2575 | 3545.41 | 3566.86 | 3051.05 | 3072.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 204 | 160 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 340 | 280 | 353.35 | 353.35 | 353.35 | 353.35 | FGMO
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 318.81 | 318.81 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 393 | 393 | 393 | 393 | 393 | 393 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 5 | 5 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 24 | 42 | 42 | 42 | 42 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 99 | 99 | 163 | 163 | 110 | 110 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 45 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 132 | 146 | 84 | 80 | 144 | 144 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 48 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 67 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1300 | 1266 | 2741.51 | 2682.51 | 2003.55 | 1948.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-03-2026 | during | 02-03-2026 | during | 02-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 10 | 11 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 59 | 87 | 60 | 80 | 60 | 80 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 69 | 98 | 70 | 115 | 70 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 146 | 202 | 366.1 | 429 | 155.1 | 218
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 30 | 0 | 0 | 42 | 42 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | ps availability is less
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 159 | 155 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 111 | 70 | 110 | 110 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 41 | 70 | 84 | 84 | 83 | 83 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 99 | 97 | 100 | 100 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 20 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 310 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 354 | 347 | 360 | 360 | 385 | 385 | Due to Air Filter DP High FGMO not available.
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1108 | 1129 | 1263 | 1263 | 1166 | 1166
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 904 | 892 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 255 | 215 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 89 | 0 | 92 | 0 | 92 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 953 | 1058 | 0 | 0 | 1148.28 | 1148.28 | plant availability zero
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2201 | 2165 | 2366 | 2274 | 2547.38 | 2455.38
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 125 | 120 | 0 | 0 | 130 | 130 | plant availability zero
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 555 | 580 | 1085.32 | 1085.32 | 622 | 622 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 15 | 15 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 241 | 275 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.59 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2700.36 | 1141.59 | 1195 | 1873.32 | 1872.32 | 1405 | 1404
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 55.37 | 0 | 50 | 0 | 50 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 4 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 198 | 197 | 220 | 220 | 220 | 220
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 406 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 32 | 32 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.94 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1073.55 | 1451.53 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 54.27 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 107 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1908.13 | 2093.53 | 3169.57 | 2952.87 | 2592.57 | 2375.87
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.2 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 175 | 0 | 181.32 | 0 | 181.32 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 212.2 | 140 | 478.52 | 262 | 444.52 | 228
System Total |  |  |  |  | 28823.2 | 28385.703 | 12060.25 | 12760.03 | 21749.65 | 21217.78 | 16537.22 | 16045.35
Forecast Scenario (02-03-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11700 |  | 0 |  | 11700
|  |  |  | 1:00 | 10840 |  | 0 |  | 10840
|  |  |  | 2:00 | 10500 |  | 0 |  | 10500
|  |  |  | 3:00 | 10710 |  | 0 |  | 10710
|  |  |  | 4:00 | 11390 |  | 0 |  | 11390
|  |  |  | 5:00 | 10530 |  | 0 |  | 10530
|  |  |  | 6:00 | 9423 |  | 0 |  | 9423
|  |  |  | 7:00 | 9300 |  | 0 |  | 9300
|  |  |  | 8:00 | 10000 |  | 0 |  | 10000
|  |  |  | 9:00 | 10890 |  | 0 |  | 10890
|  |  |  | 10:00 | 11510 |  | 0 |  | 11510
|  |  |  | 11:00 | 11760 |  | 0 |  | 11760
|  |  |  | 12:00 | 12160 |  | 0 |  | 12160
|  |  |  | 13:00 | 12600 |  | 0 |  | 12600
|  |  |  | 14:00 | 12920 |  | 0 |  | 12920
|  |  |  | 15:00 | 12580 |  | 0 |  | 12580
|  |  |  | 16:00 | 12610 |  | 0 |  | 12610
|  |  |  | 17:00 | 12740 |  | 0 |  | 12740
|  |  |  | 18:00 | 12440 |  | 0 |  | 12440
|  |  |  | 18:30 | 12500 |  | 0 |  | 12500
|  |  |  | 19:00 | 12730 |  | 0 |  | 12730
|  |  |  | 19:30 | 12860 |  | 0 |  | 12860
|  |  |  | 20:00 | 12780 |  | 0 |  | 12780
|  |  |  | 21:00 | 12780 |  | 0 |  | 12780
|  |  |  | 22:00 | 12850 |  | 0 |  | 12850
|  |  |  | 23:00 | 12600 |  | 0 |  | 12600
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 12160.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12860.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12860.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 280.343 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:28 hrs on 02-03-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 01-03-2026 | [28 empty] | Date: | 01-03-2026 | [28 empty] | Date: | 01-03-2026 | [28 empty] | Date: | 01-03-2026 | [28 empty] | Date: | 01-03-2026 | [17 empty] | Date: | 01-03-2026
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [17 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 270 | 0 | 0 | 0 | 34 | 19 | 22 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 27 | 720 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1092 | 0 | 0 | 0 | 300 | 310 | 0 | 51 | 0 | 204 | 0 | 0 | 105 | 0 | 0 | 20 | 0 | 120 | 0 | 0 | 0 | 295 | 0 | 353 | 42 | 30 | 156 | 0 | 20 | 0 | 41 | 0 | 70 | 0 | 100 | 0 | 59 | 48 | 16 | 0 | 0 | 6 | 5932 | 884 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1012 | 0 | 0 | 0 | 1218.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 123 | 220 | 0 | 0 | 622 | 0 | 5170.41 | 11102.41 | 91.59
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 13 | 22 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 5 | 720 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 1004 | 0 | 0 | 0 | 260 | 305 | 0 | 5 | 0 | 207 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 104 | 0 | 0 | 0 | 305 | 0 | 353 | 42 | 30 | 148 | 0 | 17 | 0 | 41 | 0 | 69 | 0 | 100 | 0 | 45 | 35 | 16 | 0 | 0 | 6 | 5532 | 890 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 903 | 0 | 0 | 0 | 1227.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 120 | 180 | 0 | 0 | 500 | 0 | 4809.02 | 10341.02 | 91.58
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 13 | 22 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 925 | 0 | 0 | 0 | 250 | 315 | 0 | 5 | 0 | 203 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 108 | 0 | 0 | 0 | 300 | 0 | 353 | 42 | 30 | 142 | 0 | 17 | 0 | 41 | 0 | 70 | 0 | 100 | 0 | 48 | 48 | 16 | 0 | 0 | 6 | 5427 | 894 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 885 | 0 | 0 | 0 | 1164.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 120 | 180 | 0 | 0 | 500 | 0 | 4680.96 | 10107.96 | 91.57
03:00 | 0 | 17 | 5 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 250 | 0 | 0 | 0 | 35 | 13 | 22 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 15 | 720 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 955 | 0 | 0 | 0 | 250 | 315 | 0 | 31 | 0 | 202 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 108 | 0 | 0 | 0 | 300 | 0 | 353 | 0 | 30 | 138 | 0 | 17 | 0 | 41 | 0 | 71 | 0 | 100 | 0 | 97 | 58 | 16 | 0 | 0 | 6 | 5452 | 898 | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 850 | 0 | 0 | 0 | 1318.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 120 | 180 | 0 | 0 | 525 | 0 | 4761.08 | 10213.08 | 91.56
04:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 270 | 0 | 0 | 0 | 52 | 13 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 15 | 710 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 1120 | 0 | 0 | 0 | 340 | 290 | 0 | 51 | 0 | 196 | 0 | 0 | 104 | 0 | 0 | 20 | 0 | 106 | 0 | 0 | 0 | 300 | 0 | 336 | 0 | 30 | 149 | 0 | 17 | 0 | 41 | 0 | 72 | 0 | 100 | 0 | 98 | 58 | 16 | 0 | 0 | 0 | 5817 | 903 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 931 | 0 | 0 | 0 | 1412.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 120 | 180 | 0 | 0 | 580 | 0 | 5177.11 | 10994.11 | 91.55
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 270 | 0 | 0 | 0 | 17 | 13 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 15 | 540 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 954 | 0 | 0 | 0 | 340 | 295 | 0 | 51 | 0 | 196 | 0 | 0 | 104 | 0 | 0 | 20 | 0 | 110 | 0 | 0 | 0 | 300 | 0 | 336 | 0 | 30 | 140 | 0 | 17 | 0 | 41 | 0 | 70 | 0 | 100 | 0 | 69 | 58 | 16 | 0 | 0 | 0 | 5376 | 904 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 0 | 0 | 0 | 1220.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 120 | 180 | 0 | 0 | 400 | 0 | 4755.57 | 10131.57 | 91.54
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 18 | 575 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 838 | 0 | 0 | 0 | 340 | 285 | 0 | 10 | 0 | 194 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 110 | 0 | 0 | 0 | 305 | 0 | 336 | 0 | 30 | 136 | 0 | 17 | 0 | 41 | 0 | 71 | 0 | 100 | 0 | 69 | 35 | 20 | 0 | 0 | 5 | 5061 | 904 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 818 | 0 | 0 | 0 | 910.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 100 | 180 | 0 | 0 | 300 | 0 | 3962.35 | 9023.35 | 91.53
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 295 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 80 | 0 | 10 | 575 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 834 | 1 | 0 | 0 | 340 | 310 | 0 | 10 | 0 | 206 | 0 | 0 | 50 | 0 | 0 | 14 | 0 | 88 | 0 | 5 | 0 | 290 | 0 | 353 | 0 | 30 | 137 | 0 | 10 | 0 | 41 | 0 | 71 | 0 | 100 | 0 | 69 | 35 | 20 | 0 | 0 | 6 | 5067.3 | 903 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.77 | 786 | 0 | 0 | 0 | 841.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.72 | 3 | 0 | 0 | 2.37 | 0 | 0 | 150 | 0 | 0 | 0 | 300 | 0 | 0.27 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.2 | 8 | 0.04 | 0 | 150 | 100 | 180 | 0 | 0 | 300 | 0 | 3931.63 | 8998.93 | 91.52
08:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 345 | 0 | 0 | 335 | 0 | 0 | 6 | 17 | 19 | 0 | 0 | 340 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 38 | 42 | 1.05 | 80 | 0 | 7 | 720 | 0 | 0 | 16 | 0 | 0 | 101 | 0 | 0 | 0 | 854 | 6 | 0 | 0 | 340 | 330 | 0 | 26 | 0 | 188 | 0 | 0 | 50 | 0 | 0 | 14 | 0 | 98 | 0 | 21 | 0 | 300 | 0 | 353 | 0 | 30 | 155 | 1 | 17 | 0 | 41 | 0 | 71 | 0 | 100 | 0 | 69 | 56 | 20 | 1 | 0 | 3 | 5597.05 | 666 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.86 | 845 | 0 | 0 | 0 | 931.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.88 | 10 | 0 | 0 | 7.68 | 0 | 0 | 170 | 0 | 0 | 0 | 362 | 0 | 0.47 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 1.4 | 49 | 0 | 0 | 200 | 125 | 211 | 0 | 0 | 320 | 0 | 4204.7 | 9801.75 | 91.51
09:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 335 | 0 | 0 | 15 | 17 | 19 | 22 | 0 | 350 | 0 | 0 | 56 | 0 | 0 | 36 | 0 | 0 | 50 | 50 | 2.05 | 80 | 0 | 0 | 720 | 0 | 0 | 50 | 0 | 0 | 101 | 0 | 0 | 0 | 880 | 13 | 0 | 0 | 340 | 335 | 0 | 51 | 0 | 189 | 0 | 0 | 102 | 0 | 0 | 14 | 0 | 112 | 0 | 33 | 0 | 300 | 0 | 353 | 0 | 30 | 159 | 3 | 17 | 0 | 41 | 0 | 71 | 0 | 100 | 0 | 69 | 56 | 16 | 1 | 0 | 6 | 5991.05 | 903 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.69 | 874 | 0 | 0 | 0 | 965.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.73 | 53 | 0 | 0 | 28.89 | 0 | 0 | 170 | 0 | 0 | 0 | 414 | 0 | 2.47 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 2.9 | 98 | 0.13 | 0 | 200 | 125 | 220 | 0 | 0 | 400 | 0 | 4802.78 | 10793.83 | 91.5
10:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 335 | 0 | 0 | 25 | 52 | 23 | 22 | 0 | 330 | 0 | 0 | 70 | 0 | 0 | 51 | 0 | 0 | 50 | 50 | 2.83 | 80 | 0 | 5 | 720 | 0 | 0 | 50 | 0 | 0 | 115 | 0 | 0 | 0 | 1030 | 17 | 0 | 0 | 340 | 310 | 0 | 51 | 0 | 188 | 0 | 0 | 102 | 0 | 0 | 14 | 0 | 120 | 0 | 55 | 0 | 305 | 0 | 353 | 0 | 30 | 157 | 8 | 17 | 0 | 41 | 0 | 100 | 0 | 100 | 0 | 69 | 56 | 16 | 1 | 0 | 6 | 6288.83 | 903 | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 916 | 0 | 0 | 0 | 1065.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.02 | 73 | 0 | 0 | 41.87 | 0 | 0 | 171 | 0 | 0 | 0 | 397 | 0 | 2.8 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 4.4 | 138 | 0.47 | 0 | 197 | 125 | 220 | 0 | 0 | 475 | 0 | 5125.17 | 11414 | 91.49
11:00 | 0 | 33 | 16 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 335 | 0 | 0 | 20 | 52 | 23 | 22 | 0 | 330 | 0 | 0 | 90 | 0 | 0 | 51 | 0 | 0 | 12 | 12 | 3.3 | 80 | 0 | 5 | 720 | 0 | 0 | 40 | 0 | 0 | 149 | 0 | 0 | 0 | 1050 | 19 | 0 | 0 | 393 | 335 | 0 | 51 | 0 | 192 | 0 | 0 | 99 | 0 | 0 | 14 | 0 | 126 | 0 | 64 | 0 | 305 | 0 | 354 | 0 | 30 | 153 | 10 | 17 | 0 | 41 | 0 | 110 | 0 | 99 | 0 | 69 | 56 | 10 | 2 | 0 | 6 | 6364.3 | 903 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 937 | 0 | 0 | 0 | 1070.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.12 | 86 | 0 | 0 | 52.32 | 0 | 0 | 179 | 0 | 0 | 0 | 406 | 0 | 4.83 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 5.5 | 165 | 0.57 | 0 | 198 | 125 | 220 | 0 | 0 | 545 | 0 | 5304.1 | 11668.4 | 91.48
12:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 330 | 0 | 0 | 24 | 70 | 0 | 20 | 0 | 355 | 0 | 0 | 97 | 0 | 0 | 51 | 0 | 0 | 12 | 12 | 3.33 | 80 | 0 | 5 | 775 | 0 | 0 | 39 | 0 | 0 | 147 | 0 | 0 | 0 | 1165 | 19 | 0 | 0 | 393 | 340 | 0 | 51 | 0 | 204 | 0 | 0 | 99 | 0 | 0 | 14 | 0 | 132 | 0 | 67 | 0 | 295 | 0 | 354 | 0 | 30 | 159 | 11 | 8 | 0 | 41 | 0 | 111 | 0 | 99 | 0 | 69 | 59 | 10 | 2 | 0 | 6 | 6597.33 | 904 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 953 | 0 | 0 | 0 | 1073.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.37 | 107 | 0 | 0 | 54.27 | 0 | 0 | 198 | 0 | 0 | 0 | 414 | 0 | 5.94 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 6.2 | 175 | 0.59 | 0 | 241 | 125 | 220 | 0 | 0 | 555 | 0 | 5462.92 | 12060.25 | 91.47
13:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 16 | 8 | 65 | 0 | 30 | 4 | 5 | 32 | 0 | 0 | 0 | 370 | 0 | 0 | 329 | 0 | 0 | 27 | 70 | 23 | 20 | 0 | 330 | 0 | 0 | 105 | 0 | 0 | 50 | 0 | 0 | 12 | 12 | 3.3 | 80 | 0 | 18 | 920 | 0 | 0 | 48 | 0 | 25 | 148 | 0 | 0 | 0 | 1140 | 19 | 30 | 0 | 393 | 290 | 0 | 51 | 3 | 170 | 0 | 18 | 98 | 12 | 0 | 14 | 0 | 144 | 0 | 63 | 0 | 300 | 0 | 354 | 0 | 30 | 157 | 10 | 8 | 0 | 41 | 0 | 109 | 0 | 99 | 0 | 69 | 58 | 10 | 2 | 0 | 6 | 6837.3 | 904 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 1026 | 0 | 0 | 0 | 1184.79 | 0 | 0 | 0 | 0 | 0 | 0 | 16.4 | 0 | 0 | 48.75 | 107 | 0 | 0 | 53.21 | 0 | 0 | 197 | 0 | 0 | 0 | 405 | 0 | 5.19 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 6.1 | 169 | 0.18 | 0 | 277 | 125 | 220 | 0 | 0 | 555 | 0 | 5664.62 | 12501.92 | 91.46
14:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 15.8 | 17 | 87 | 0 | 30 | 15 | 17 | 17 | 0 | 0 | 0 | 425 | 0 | 0 | 329 | 0 | 0 | 17 | 90 | 23 | 20 | 0 | 350 | 0 | 0 | 103 | 0 | 1 | 49 | 0 | 0 | 12 | 12 | 2.71 | 80 | 0 | 3 | 1030 | 0 | 0 | 50 | 0 | 17 | 148 | 0 | 0 | 0 | 1160 | 17 | 40 | 0 | 393 | 290 | 0 | 51 | 0 | 152 | 0 | 16 | 98 | 21 | 0 | 14 | 0 | 150 | 0 | 57 | 0 | 300 | 0 | 355 | 0 | 30 | 146 | 9 | 17 | 0 | 41 | 0 | 109 | 0 | 99 | 0 | 69 | 63 | 10 | 2 | 0 | 6 | 7044.51 | 904 | 242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 1094 | 0 | 0 | 0 | 1318.09 | 0 | 0 | 0 | 0 | 0 | 0 | 17.4 | 0 | 0 | 45.36 | 98 | 0 | 0 | 48.25 | 0 | 0 | 195 | 0 | 0 | 0 | 353 | 0 | 4.48 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 5.5 | 147 | 0.3 | 0 | 307 | 125 | 220 | 0 | 0 | 560 | 0 | 5784.38 | 12828.89 | 91.45
15:00 | 0 | 19 | 24 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 15 | 17 | 87 | 0 | 30 | 15 | 17 | 14 | 0 | 0 | 0 | 430 | 0 | 0 | 323 | 0 | 0 | 16 | 108 | 22.8 | 20 | 0 | 375 | 0 | 0 | 105 | 0 | 5 | 49 | 0 | 0 | 12 | 12 | 2.14 | 80 | 0 | 5 | 1030 | 0 | 0 | 40 | 0 | 15 | 147 | 0 | 0 | 0 | 1168 | 13 | 24 | 0 | 393 | 280 | 0 | 51 | 0 | 140 | 0 | 0 | 96 | 15 | 0 | 18 | 0 | 146 | 0 | 40 | 0 | 295 | 0 | 350 | 0 | 30 | 137 | 7 | 17 | 0 | 41 | 0 | 0 | 0 | 98 | 0 | 69 | 62 | 10 | 1 | 0 | 6 | 6845.94 | 904 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 1089 | 0 | 0 | 0 | 1271.32 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 21.7 | 72 | 0 | 0 | 35.21 | 0 | 0 | 195 | 0 | 0 | 0 | 405 | 0 | 3.63 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 4.1 | 108 | 0.39 | 0 | 281 | 122 | 220 | 0 | 0 | 595 | 0 | 5638.35 | 12484.29 | 91.44
16:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 25 | 17 | 87 | 0 | 45 | 15 | 18 | 32 | 0 | 0 | 0 | 405 | 0 | 10 | 325 | 0 | 0 | 15 | 108 | 22.8 | 20 | 0 | 360 | 0 | 0 | 105 | 0 | 9 | 49 | 0 | 0 | 12 | 24 | 1.21 | 80 | 0 | 8 | 1030 | 0 | 0 | 38 | 0 | 23 | 150 | 0 | 0 | 0 | 1164 | 7 | 12 | 0 | 393 | 280 | 0 | 51 | 0 | 142 | 0 | 0 | 97 | 0 | 0 | 19 | 0 | 136 | 0 | 25 | 0 | 310 | 0 | 350 | 0 | 30 | 155 | 4 | 17 | 0 | 83 | 0 | 0 | 0 | 98 | 0 | 69 | 65 | 10 | 1 | 0 | 6 | 6947.01 | 903 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 1107 | 0 | 0 | 0 | 1274.12 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 23.06 | 43 | 0 | 0 | 18.76 | 0 | 0 | 195 | 0 | 0 | 0 | 409 | 0 | 1.92 | 0 | 0 | 35 | 13 | 0 | 0 | 0 | 0 | 2.4 | 59 | 0.23 | 0 | 277 | 122 | 220 | 0 | 0 | 595 | 0 | 5568.49 | 12515.5 | 91.43
17:00 | 0 | 42 | 41 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 40 | 17 | 114 | 30 | 80 | 30 | 35 | 36 | 0 | 0 | 0 | 400 | 0 | 17 | 325 | 0 | 0 | 5 | 125 | 22.8 | 20 | 0 | 362 | 7 | 15 | 101 | 0 | 4 | 49 | 0 | 0 | 12 | 24 | 0.39 | 80 | 9 | 27 | 1030 | 0 | 0 | 38 | 0 | 32 | 150 | 0 | 0 | 0 | 1163 | 2 | 12 | 0 | 393 | 280 | 0 | 51 | 0 | 150 | 0 | 8 | 97 | 6 | 0 | 19 | 0 | 132 | 0 | 8 | 0 | 305 | 0 | 350 | 0 | 30 | 154 | 1 | 17 | 0 | 82 | 0 | 0 | 0 | 98 | 0 | 69 | 63 | 10 | 0 | 0 | 0 | 7134.19 | 893 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.56 | 1104 | 0 | 0 | 0 | 1318.95 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 6.53 | 15 | 0 | 0 | 5.89 | 0 | 0 | 195 | 0 | 0 | 0 | 414 | 0 | 0.58 | 0 | 0 | 35 | 3 | 40 | 0 | 0 | 0 | 0.8 | 19 | 0.08 | 0 | 278 | 122 | 220 | 0 | 0 | 595 | 0 | 5510.39 | 12644.58 | 91.42
18:00 | 0 | 50 | 41 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0 | 54 | 17 | 123 | 30 | 80 | 50 | 28 | 63 | 0 | 0 | 0 | 430 | 0 | 17 | 310 | 0 | 0 | 0 | 125 | 19.4 | 20 | 0 | 355 | 16 | 15 | 93 | 0 | 1 | 49 | 0 | 0 | 12 | 24 | 0 | 80 | 17 | 5 | 900 | 0 | 0 | 39 | 0 | 67 | 150 | 0 | 0 | 0 | 1096 | 0 | 12 | 0 | 393 | 280 | 0 | 10 | 0 | 160 | 0 | 17 | 70 | 17 | 0 | 19 | 0 | 128 | 0 | 0 | 24 | 300 | 0 | 300 | 0 | 30 | 154 | 0 | 20 | 0 | 82 | 0 | 0 | 0 | 97 | 0 | 97 | 87 | 10 | 0 | 0 | 0 | 6974.4 | 891 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1110 | 0 | 0 | 0 | 1441.86 | 0 | 0 | 0 | 0 | 9 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 122 | 180 | 0 | 0 | 590 | 0 | 5368.36 | 12342.76 | 91.41
19:00 | 0 | 50 | 41 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 54 | 17 | 123 | 0 | 80 | 55 | 35 | 85 | 0 | 0 | 0 | 350 | 0 | 17 | 335 | 0 | 0 | 0 | 125 | 23.5 | 20 | 0 | 415 | 0 | 0 | 0 | 0 | 1 | 50 | 0 | 0 | 0 | 24 | 0 | 80 | 17 | 21 | 1030 | 0 | 0 | 39 | 0 | 69 | 150 | 0 | 0 | 0 | 1060 | 0 | 0 | 0 | 393 | 280 | 0 | 39 | 0 | 160 | 0 | 18 | 100 | 17 | 0 | 19 | 0 | 144 | 0 | 0 | 17 | 270 | 0 | 347 | 0 | 30 | 152 | 0 | 20 | 0 | 82 | 0 | 30 | 0 | 97 | 0 | 98 | 87 | 11 | 0 | 0 | 2 | 7112.5 | 892 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005 | 0 | 0 | 0 | 1447.09 | 0 | 0 | 0 | 0 | 35 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 120 | 220 | 0 | 0 | 560 | 0 | 5521.09 | 12633.59 | 91.4
19:30 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 54 | 17 | 123 | 0 | 45 | 55 | 35 | 106 | 0 | 0 | 0 | 350 | 0 | 17 | 335 | 0 | 0 | 0 | 108 | 23.5 | 20 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 12 | 0 | 80 | 0 | 18 | 1030 | 0 | 0 | 50 | 0 | 85 | 150 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 393 | 280 | 0 | 51 | 0 | 160 | 0 | 48 | 99 | 45 | 0 | 20 | 0 | 146 | 0 | 0 | 24 | 310 | 0 | 347 | 30 | 30 | 155 | 0 | 20 | 0 | 70 | 0 | 70 | 0 | 97 | 0 | 98 | 87 | 11 | 0 | 0 | 6 | 7166.5 | 892 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1058 | 0 | 0 | 0 | 1451.53 | 0 | 0 | 0 | 0 | 35 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 120 | 220 | 0 | 0 | 580 | 0 | 5593.53 | 12760.03 | 91.4
20:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 54 | 17 | 123 | 0 | 15 | 55 | 35 | 95 | 0 | 0 | 0 | 345 | 0 | 17 | 335 | 0 | 0 | 0 | 90 | 23.5 | 20 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 12 | 0 | 80 | 17 | 25 | 1030 | 0 | 0 | 50 | 0 | 88 | 150 | 0 | 0 | 0 | 1151 | 0 | 0 | 0 | 393 | 280 | 0 | 51 | 0 | 160 | 0 | 45 | 100 | 33 | 0 | 20 | 0 | 142 | 0 | 0 | 24 | 305 | 0 | 347 | 30 | 30 | 152 | 0 | 20 | 0 | 72 | 0 | 70 | 0 | 98 | 0 | 98 | 78 | 11 | 0 | 0 | 6 | 7105.5 | 892 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 0 | 0 | 1451.23 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 110 | 220 | 0 | 0 | 570 | 0 | 5577.23 | 12682.73 | 91.39
21:00 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 54 | 17 | 123 | 0 | 0 | 55 | 35 | 103 | 0 | 0 | 0 | 360 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 23.5 | 20 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 12 | 0 | 80 | 0 | 24 | 1030 | 0 | 0 | 50 | 0 | 86 | 150 | 0 | 0 | 0 | 1165 | 0 | 0 | 0 | 393 | 280 | 0 | 51 | 0 | 160 | 0 | 50 | 100 | 47 | 0 | 20 | 0 | 142 | 0 | 0 | 0 | 305 | 0 | 347 | 30 | 30 | 159 | 0 | 20 | 0 | 65 | 0 | 75 | 0 | 98 | 0 | 98 | 78 | 11 | 0 | 0 | 6 | 7131.5 | 892 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1107 | 0 | 0 | 0 | 1452.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 120 | 220 | 0 | 0 | 600 | 0 | 5601.67 | 12733.17 | 91.39
22:00 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 54 | 0 | 123 | 0 | 0 | 55 | 35 | 105 | 0 | 0 | 0 | 355 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 22 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 12 | 0 | 80 | 0 | 24 | 1030 | 0 | 0 | 50 | 0 | 88 | 150 | 0 | 0 | 0 | 1140 | 0 | 0 | 0 | 393 | 320 | 0 | 51 | 5 | 190 | 0 | 51 | 102 | 50 | 0 | 20 | 0 | 144 | 0 | 0 | 0 | 300 | 0 | 347 | 30 | 30 | 157 | 0 | 20 | 0 | 65 | 0 | 76 | 0 | 97 | 0 | 98 | 78 | 11 | 0 | 0 | 6 | 7146 | 891 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1121 | 0 | 0 | 0 | 1452.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 409 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 120 | 220 | 0 | 0 | 605 | 0 | 5611.39 | 12757.39 | 91.37
23:00 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 54 | 0 | 98 | 0 | 0 | 55 | 35 | 35 | 0 | 0 | 0 | 335 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 22 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 12 | 0 | 80 | 0 | 24 | 800 | 0 | 0 | 33 | 0 | 34 | 150 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 393 | 320 | 0 | 51 | 10 | 199 | 0 | 34 | 103 | 17 | 0 | 20 | 0 | 136 | 0 | 0 | 0 | 295 | 0 | 348 | 30 | 30 | 151 | 0 | 20 | 0 | 52 | 0 | 76 | 0 | 98 | 0 | 59 | 49 | 11 | 0 | 0 | 6 | 6571 | 892 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1092 | 0 | 0 | 0 | 1450.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 128 | 220 | 0 | 0 | 605 | 0 | 5558.16 | 12129.16 | 91.36
Total KWH | 0 | 406848 | 428069 | 0 | 0 | 0 | 0 | 0 | 7884000 | 0 | 0 | 464868 | 162720 | 1693296 | 51360 | 415255 | 452413 | 339465 | 707040 | 0 | 0 | 0 | 9025000 | 0 | 77790 | 7500512 | 0 | 0 | 187842 | 1495200 | 442200 | 453240 | 0 | 8597272.73 | 27048 | 31113 | 935280 | 0 | 18240 | 609929 | 0 | 0 | 226560 | 341760 | 22320 | 1919460 | 70250 | 343680 | 19840000 | 0 | 0 | 656640 | 0 | 635636 | 3159371 | 0 | 0 | 0 | 25369088 | 132126 | 163927 | 0 | 8809200 | 7658500 | 0 | 1125674 | 30240 | 4475000 | 0 | 312000 | 2121086 | 281760 | 0 | 441790 | 0 | 3089280 | 0 | 444109 | 60176 | 7284000 | 0 | 8536000 | 180000 | 730920 | 3611209 | 65235 | 412416 | 0 | 1235520 | 0 | 1589000 | 0 | 2370840 | 0 | 1802400 | 1428000 | 293760 | 12550 | 0 | 121200 | 153808683.73 | 21408727 | 5732064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576070 | 23789090 | 0 | 0 | 0 | 29632685 | 0 | 0 | 0 | 0 | 83904 | 29177 | 31968 | 0 | 0 | 289748 | 656270 | 0 | 0 | 331504 | 0 | 0 | 4622282 | 0 | 0 | 0 | 9196654 | 0 | 32100 | 0 | 0 | 403016 | 211338 | 453648 | 0 | 0 | 0 | 38981.04 | 1137600 | 3868 | 0 | 5716000 | 2879000 | 5201410 | 0 | 0 | 13050181.82 | 0 | 125507285.86 | 279315969.59

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 01-03-2026
Power Supply Scenario
| Day Peak Generation |  |  | 12060.25 | MW | 12:00 Hr. | Energy Generated |  |  | 279.316 |  | MKWHr.
| Day Peak Demand |  |  | 12060.25 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 12760.03 | MW | 19:30 Hr. | Energy Demand |  |  | 279.316 |  | MKWHr.
| Evening Peak Demand |  |  | 12760.03 | MW | 19:30 Hr. | Maximum Temperature |  |  | 32.4 |  | °C
| Minimum Generation of the Day |  |  | 8998.93 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 860.53 |  | MMCFD
| Maximum Generation of the Day |  |  | 12828.89 | MW | 14:00 Hr. | Production Cost per KWHr |  |  | 5.7306 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.9022 | 0 | 6.6943 | 0 | 0 | 0.18784 | 0 | 0 | 40.7844 | Gas | 115.9418 | Gas | 397649590.8841
| Chattogram Zone |  |  | 3.5031 | 45.2091 | 3.5342 | 0 | 1.9195 | 0.15445 | 0 | 0.01824 | 54.3385 | Coal | 87.7644 | Coal | 571293903.8556
| Cumilla Zone |  |  | 24.6615 | 0 | 0.81786 | 0 | 0 | 0.44411 | 3.0893 | 0 | 29.0127 | HFO | 15.3997 | HFO | 259105616.63
| Mymensingh Zone |  |  | 0.29376 | 0 | 3.3516 | 0 | 0 | 0.01255 | 0 | 0 | 3.6579 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 25.9499 | 0 | 0 | 0 | 0 | 0.065235 | 0 | 0 | 26.0151 | Hydro | 1.9195 | Hydro | 191946
| Khulna Zone |  |  | 5.7321 | 23.7891 | 0 | 0 | 0 | 0.57607 | 21.4087 | 0 | 51.506 | Solar | 4.1417 | Solar | 65279774.808
| Barishal Zone |  |  | 8.0804 | 18.7662 | 0 | 0 | 0 | 0.003868 | 0 | 0 | 26.8505 | Import | 54.1307 | Import | 306856248.83
| Rajshahi Zone |  |  | 13.8189 | 0 | 0.14505 | 0 | 0 | 1.3096 | 29.6327 | 0 | 44.9063 | Wind | 0.01824 | Wind | 268310.4
| Rangpur Zone |  |  | 0 | 0 | 0.85666 | 0 | 0 | 1.3879 | 0 | 0 | 2.2446
| Total |  |  | 115.9418 | 87.7644 | 15.3997 | 0 | 1.9195 | 4.1417 | 54.1307 | 0.01824 | 279.316
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 397649590.8841 |  | Hydro | 191946
|  |  |  | Coal | 571293903.8556 |  | Solar | 65279774.808
|  |  |  | HFO | 259105616.63 |  | Import | 306856248.83
|  |  |  | HSD | 0 |  | Wind | 268310.4
[5 empty] | Total: | 160,06,45,391 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.4087 | Peak Hr Flow | 892.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 32650002.06 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 29.6327 | Peak Hr Flow | 1451.53 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1819 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.0893 | Peak Hr Flow | 146.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2084 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 54.1307 | Peak Hr Flow | 2489.53 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4843
|  |  |  | Chattogram |  | 0 |  | 1207
|  |  |  | Cumilla |  | 0 |  | 1131
|  |  |  | Mymensingh |  | 0 |  | 997
|  |  |  | Sylhet |  | 0 |  | 427
|  |  |  | Khulna |  | 0 |  | 1405
|  |  |  | Barishal |  | 0 |  | 359
|  |  |  | Rajshahi |  | 0 |  | 1164
|  |  |  | Rangpur |  | 0 |  | 724
|  |  |  | Total |  | 0 |  | 12257
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:16 |  | Shikalbaha 230/132kV S/S ATR 02 HT Scheduled S/D Due to Gas purification work
| 08:16 |  | Shikalbaha 230/132kV S/S ATR 02 LT Scheduled S/D Due to Gas purification work
|  | 08:56 | Aminbazar-Meghnaghat 400kV Ckt-1 is restored.
| 08:58 |  | Naogaon-Niyamatpur 132kV Ckt-1 Project Work S/D from Niamatpur 132/33kV end Due to
Multi-ckt terminal tower create.
| 08:58 |  | Niamatpur 132/33kV S/S 132 kV Naogaon ckt-2 Project Work S/D Due to Multi-ckt terminal
tower create.
| 09:46 | 13:12 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT Scheduled S/D Due to
Line disk cleaning
| 09:47 | 13:11 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Scheduled S/D Due to
Line disk cleaning
| 10:01 | 13:06 | Kabirpur - Manikganj 132kV Ckt-1 Scheduled S/D from Manikganj 132/33kV end Due to Line
disk cleaning
| 10:18 | 11:05 | Bajitpur 132/33kV S/S 132 kV Bus Coupler Scheduled S/D Due to 132 Kv CT Oil leakage
maintenance.
| 10:18 | 11:05 | Bajitpur 132/33kV S/S 132 kV Bus-1 Scheduled S/D Due to For 132 kv CT oil leakage
maintenance.
| 10:54 | 15:20 | Faridpur 132/33kV S/S Transformer-3 HT Scheduled S/D Due to bus pt oil leakage
maintenance
|  | 11:54 | BIPTC S/S 20DF24 is restored.
| 13:01 | 21:09 | Aminbazar-Meghnaghat 400kV Ckt-1 Scheduled S/D from Meghnaghat 400/230kV end Due to 400
kV Aminbazar ckt- 1 shutdown instructed by NLDC. Munshiganj SS will do their maintenance
work.
| 14:42 |  | Naogaon-Niamatpur 132 KV ckt 1 & 2 Charged From GIS Bus Naogaon End.
| 15:07 |  | Rampal 400/230kV S/S ICT-1 HT Scheduled S/D Due to NA
| 19:30 |  | Evening Peak Generation: 12729 MW.
| 19:30 |  | Evening Peak Generation: 12729 MW.
| 22:12 |  | Amtali 400/132kV S/S Amtali - RNPL 400 kV Ckt - 2 Tripped showing Micom P40 Agile relays
Due to DTT Trip
| 06:20 |  | Fenchuganj -Sylhet 132kV Ckt-1 Scheduled S/D from Beanibazar 132/33kV end Due to Line | [7 empty] | 28.0MW load
|  |  | maintenance | [7 empty] | interrup.
Beanibazar 132/33kV
end
| 06:21 |  | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Scheduled S/D from Beanibazar 132/33kV
end Due to Line maintenance
| 06:34 |  | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Project Work S/D from Fenchuganj
230/132/33kV end Due to Beanibazar Grid SS end reconductoring work
| 06:35 |  | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-1 Project Work S/D Due to Line bypass
Through ERS Tower.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 01-03-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 298 | 7884000 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 452413 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7500512 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 464868 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 51360 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 339465 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 77790 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23.5 | 442200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 453240 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 24 | 428069 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 45 | 415255 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 123 | 1693296 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 406848 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 106 | 707040 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 187842 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 162720 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 350 | 8597272.73 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 350 | 9025000 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 108 | 1495200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1994.5 | 40784390.73
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 132126 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 656640 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1919460 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 150 | 3159371 | ps availability is less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 85 | 635636 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 609929 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 226560 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 18 | 343680 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 935280 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22320 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 31113 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 70250 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 341760 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 27048 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1100 | 25369088 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 18240 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1030 | 19840000 | ps availability is less
Chattogram Area Total |  |  |  |  | 4898.863 | 2575 | 54338501
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 160 | 4475000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 280 | 7658500 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | FGMO ON
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 8809200 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 30240 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1125674 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 163927 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 24 | 60176 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 99 | 2121086 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 45 | 281760 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 146 | 3089280 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 441790 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 48 | 312000 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 444109 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1266 | 29012742
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 11 | 293760 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12550 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 87 | 1428000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 98 | 1802400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 0 | Annual Maintenance on going
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 121200 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 202 | 3657910
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 65235 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 180000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 730920 | ps availability is less
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3611209 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 70 | 1589000 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 70 | 1235520 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 97 | 2370840 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 20 | 412416 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7284000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 347 | 8536000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1129 | 26015140
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 892 | 21408727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 215 | 5732064 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 576070 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1058 | 23789090 | plant availability zero
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2165 | 51505951
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2879000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 580 | 13050181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5201410 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 275 | 5716000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3868 | -
Barishal Area Total |  |  |  |  | 2700.36 | 1195 | 26850459.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 289748 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 4 | 29177 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Shutdown As Per PGB PLC's Requirements.
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 197 | 4622282 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 406 | 9196654 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 31968 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 83904 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 32100 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1451.53 | 29632685 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 331504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 656270 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2093.53 | 44906292
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 453648 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 38981.04 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 403016 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 211338 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1137600 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 140 | 2244583.04
Eastern Grid Total |  |  |  |  | 17400.108 | 7166.5 | 153808683.73
Western Grid Total |  |  |  |  | 10985.595 | 5593.53 | 125507285.86
National Grid Total |  |  |  |  | 28385.703 | 12760.03 | 279315969.59
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 01-03-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8604.47 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3651.5 | MW
i) Dhaka area |  |  | 4842.57 |  | MW | i) Khulna area |  |  |  | 1404.6 | MW
ii) Chattogram area |  |  | 1206.9 |  | MW | ii) Barishal area |  |  |  | 358.9 | MW
iii) Cumilla area |  |  | 1131 |  | MW | iii) Rajshahi area |  |  |  | 1164 | MW
iv) Mymensingh area |  |  | 997 |  | MW | iv) Rangpur area |  |  |  | 724 | MW
v) Sylhet area |  |  | 427 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12255.97 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 73 | 19:00 | 133 | Nawabganj | 36 | 13:00
2 | AKSML | 10.7 | 23:00 | 68 | Hathazari | 64 | 22:00 | 134 | Netrakona | 148 | 18:00
3 | Aftabnagar | 32 | 17:00 | 69 | Hatirjheel | 37 | 14:00 | 135 | New | 66 | 12:00
4 | Agargaon | 93 | 13:00 | 70 | Ishurdi | 59 | 19:00 | 136 | Niamatpur | 93 | 13:00
5 | Agrabad | 48 | 12:00 | 71 | Jaldhaka | 64 | 18:00 | 137 | Noapara | 41 | 19:00
6 | Amnura | 33 | 09:00 | 72 | Jamalpur | 102 | 18:00 | 138 | PHP | 9 | 13:00
7 | Ashuganj | 72 | 23:00 | 73 | Jashore | 122 | 19:00 | 139 | Pabna | 74 | 18:00
8 | BSRM | 194 | 03:00 | 74 | Jhenaidah | 84 | 18:30 | 140 | Palashbari | 92 | 13:00
9 | Bagerhat | 68 | 19:00 | 75 | Joydebpur | 126 | 16:00 | 141 | Panchagarh | 47 | 18:00
10 | Bajitpur | 70 | 17:00 | 76 | Joypurhat | 60 | 08:00 | 142 | Patiya | 7.3 | 19:00
11 | Bakerganj | 11.04 | 20:00 | 77 | Juldah | 18 | 23:00 | 143 | Patuakhali | 46 | 18:30
12 | Bakulia | 80 | 19:00 | 78 | KSRM | 28 | 09:00 | 144 | Payra | 32 | 21:00
13 | Banani | 48 | 14:00 | 79 | Kabirpur | 239 | 16:00 | 145 | Postogola | 45 | 13:00
14 | Bangabhaban | 14 | 10:00 | 80 | Kachua | 69 | 18:00 | 146 | Purbachal | 26 | 21:00
15 | Barapukuria | 62 | 12:00 | 81 | Kaliganj | 22 | 18:00 | 147 | Purbasadipur | 120 | 13:00
16 | Barguna | 16 | 19:00 | 82 | Kallyanpur | 99 | 22:00 | 148 | Rahanpur | 28 | 13:00
17 | Barishal | 86 | 13:00 | 83 | Kalurghat | 36 | 10:00 | 149 | Rahim | 32 | 00:00
18 | Barishal-230 | 76 | 22:00 | 84 | Kamrangirchar | 75 | 13:00 | 150 | Rajbari | 58 | 19:00
19 | Baroaulia | 50 | 20:00 | 85 | Kaptai | N/A | N/A | 151 | Rajendrapur | 127 | 14:00
20 | Baroirhat | 46 | 18:30 | 86 | Kasba | 28 | 03:00 | 152 | Rajshahi | 91 | 03:00
21 | Bashundhara | 182 | 21:00 | 87 | Kazla | 84 | 00:00 | 153 | Rajshahi-230 | 78 | 14:00
22 | BashundharaCement | 12 | 10:00 | 88 | Keranigonj | 90 | 17:00 | 154 | Ramganj | 76 | 20:00
23 | Beanibazar | 48 | 21:00 | 89 | Khagrachori | 26 | 18:00 | 155 | Rampur | 33 | 18:30
24 | Benapole | 50 | 19:00 | 90 | Khulna | 46 | 19:00 | 156 | Rangamati | 15 | 18:30
25 | Bhaluka | 128 | 16:00 | 91 | Khulshi | 166 | 00:00 | 157 | Rangpur | 127 | 17:00
26 | Bhandaria | 41 | 20:00 | 92 | Kishoreganj | 109 | 18:00 | 158 | Ruppur | 3 | 11:00
27 | Bhangura | 35 | 13:00 | 93 | Kodda | 314 | 16:00 | 159 | SSM | 0 | 00:00
28 | Bheramara(GK) | 48 | 18:00 | 94 | Kulaura | 31 | 18:00 | 160 | Saidpur | 108 | 17:00
29 | Bhulta | 221 | 16:00 | 95 | Kurigram | 60 | 17:00 | 161 | Satkhira | 123 | 18:30
30 | Bog-Sherpur | 56 | 17:00 | 96 | Kushtia | 120 | 18:00 | 162 | Satmasjid | 88 | 19:30
31 | Bogura | 139 | 04:00 | 97 | Laksam | 24 | 13:00 | 163 | Savar | 208 | 15:00
32 | Borhanuddin | 72 | 21:00 | 98 | Lakshmipur | 29 | 21:00 | 164 | SevenRings | 16.78 | 20:00
33 | Brahmanbaria | 108 | 21:00 | 99 | Lalbag | 70 | 16:00 | 165 | ShahCement | 31 | 13:00
34 | Cantonment | 84 | 21:00 | 100 | Lalmonirhat | 44 | 17:00 | 166 | Shahjadpur | 69 | 17:00
35 | Chandina | 12 | 14:00 | 101 | MI_Cement | 17.4 | 02:00 | 167 | Shahjibazar | 103 | 22:00
36 | Chandpur | 60 | 21:00 | 102 | Madanganj | 48 | 15:00 | 168 | Shahmirpur | 51.5 | 00:00
37 | Chandraghona | 29 | 18:00 | 103 | Madaripur | 86 | 22:00 | 169 | Shariatpur | 66 | 21:00
38 | Chapai | 59 | 09:00 | 104 | Madartek | 66 | 21:00 | 170 | Sherpur | 144 | 18:00
39 | Charsaidpur | 44 | 15:00 | 105 | Madunaghat | 40 | 14:00 | 171 | Shikalbaha | 29 | 14:00
40 | Chauddagram | 60 | 14:00 | 106 | Magura | 51 | 19:00 | 172 | Shitalakhya | 75.7 | 15:00
41 | Chhatak | 28 | 20:00 | 107 | Mahasthangarh | 62 | 09:00 | 173 | Sholosohor | 38 | 12:00
42 | Chowmuhani | 96 | 19:00 | 108 | Maijdee | 38 | 19:30 | 174 | Shyampur | 160 | 16:00
43 | Chuadanga | 84 | 18:00 | 109 | Manikganj | 102 | 19:00 | 175 | Siddhirganj | 122 | 16:00
44 | Coxsbazar | 114 | 20:00 | 110 | Maniknagar | 54 | 14:00 | 176 | Sirajganj | 96 | 10:00
45 | Cumilla(N) | 101 | 18:30 | 111 | Matarbari | 42 | 18:30 | 177 | Sonargaon | 138 | 00:00
46 | Cumilla(S) | 149 | 14:00 | 112 | Matuail | 67 | 14:00 | 178 | Sreemongol | 58 | 22:00
47 | Daganbhuiyan | 34 | 18:30 | 113 | Metrorail_Motijheel | 20 | 15:00 | 179 | Sreepur | 116 | 17:00
48 | Daudkandi | 124 | 21:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Srinagar | 36.8 | 21:00
49 | DhakaUniversity | 66 | 13:00 | 115 | Millgate | 88 | 14:00 | 181 | Sunamganj | 42 | 21:00
50 | Dhamrai | 128 | 16:00 | 116 | Mirpur | 132 | 14:00 | 182 | Sylhet | 42 | 22:00
51 | Dhanmondi | 98 | 13:00 | 117 | Mirsorai | 47 | 07:00 | 183 | Sylhet-132 | 79 | 14:00
52 | Dohazari | 81 | 18:30 | 118 | Mirzapur | 41 | 11:00 | 184 | TK | 19 | 19:30
53 | Faridpur | 128 | 20:00 | 119 | Mithapukur | 52 | 04:00 | 185 | Tangail | 148 | 17:00
54 | Fatullah | 91 | 16:00 | 120 | Modern | N/A | N/A | 186 | Taraganj | 19 | 17:00
55 | Fenchuganj | 25 | 18:00 | 121 | Mogbazar | 90.4 | 14:00 | 187 | Tasnim | 30 | 02:00
56 | Feni | 81 | 13:00 | 122 | Mongla | 42 | 08:00 | 188 | Thakurgaon | 78 | 18:00
57 | GPH | 93 | 21:00 | 123 | Motijheel | 42 | 13:00 | 189 | Tongi | 127 | 15:00
58 | Ghatail | 78 | 18:00 | 124 | Muktagacha | 35 | 17:00 | 190 | Ullahpara | 35 | 14:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 78 | 13:00 | 191 | Ullon | 49 | 18:30
60 | Ghorashal-230 | 99 | 19:00 | 126 | Muradnagar | 31 | 20:00 | 192 | Uttara | 67 | 14:00
61 | Goalpara | 24 | 14:00 | 127 | Mymensingh | 193 | 18:00 | 193 | UttaraNew | 34 | 22:00
62 | Gollamari | 88 | 19:00 | 128 | Naogaon | 114 | 10:00 | 194 | Zigatola | 64 | 17:00
63 | Gopalganj | 90.3 | 19:00 | 129 | Narail | 49 | 19:30
64 | Gulshan | 94 | 13:00 | 130 | Narinda | 60 | 14:00
65 | Halishahar | 77 | 10:00 | 131 | Narshingdi | 154 | 21:00
66 | HaripurSBU | 130 | 15:00 | 132 | Natore | 133 | 04:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 01-03-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 11102.41 | 0 |  | 11102.41
1:00 | 10341.02 | 0 |  | 10341.02
2:00 | 10107.96 | 0 |  | 10107.96
3:00 | 10213.08 | 0 |  | 10213.08
4:00 | 10994.11 | 0 |  | 10994.11
5:00 | 10131.57 | 0 |  | 10131.57
6:00 | 9023.35 | 0 |  | 9023.35
7:00 | 8998.93 | 0 |  | 8998.93
8:00 | 9801.75 | 0 |  | 9801.75
9:00 | 10793.83 | 0 |  | 10793.83
10:00 | 11414 | 0 |  | 11414
11:00 | 11668.4 | 0 |  | 11668.4
12:00 | 12060.25 | 0 |  | 12060.25
13:00 | 12501.92 | 0 |  | 12501.92
14:00 | 12828.89 | 0 |  | 12828.89
15:00 | 12484.29 | 0 |  | 12484.29
16:00 | 12515.5 | 0 |  | 12515.5
17:00 | 12644.58 | 0 |  | 12644.58
18:00 | 12342.76 | 0 |  | 12342.76
19:00 | 12633.59 | 0 |  | 12633.59
19:30 | 12760.03 | 0 |  | 12760.03
20:00 | 12682.73 | 0 |  | 12682.73
21:00 | 12733.17 | 0 |  | 12733.17
22:00 | 12757.39 | 0 |  | 12757.39
23:00 | 12129.16 | 0 |  | 12129.16
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 01-03-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5932 | 5170.41 | 11102.41 | DAILY GENERATION CURVE
00:30 | 5732 | 4989.715 | 10721.715
01:00 | 5532 | 4809.02 | 10341.02 | 01-03-2026
01:30 | 5479.5 | 4744.99 | 10224.49
02:00 | 5427 | 4680.96 | 10107.96
02:30 | 5439.5 | 4721.02 | 10160.52
03:00 | 5452 | 4761.08 | 10213.08
03:30 | 5634.5 | 4969.095 | 10603.595
04:00 | 5817 | 5177.11 | 10994.11
04:30 | 5596.5 | 4966.34 | 10562.84
05:00 | 5376 | 4755.57 | 10131.57
05:30 | 5218.5 | 4358.96 | 9577.46
06:00 | 5061 | 3962.35 | 9023.35
06:30 | 5064.15 | 3946.99 | 9011.14
07:00 | 5067.3 | 3931.63 | 8998.93
07:30 | 5332.175 | 4068.165 | 9400.34
08:00 | 5597.05 | 4204.7 | 9801.75
08:30 | 5794.05 | 4503.74 | 10297.79
09:00 | 5991.05 | 4802.78 | 10793.83
09:30 | 6139.94 | 4963.975 | 11103.915
10:00 | 6288.83 | 5125.17 | 11414
10:30 | 6326.565 | 5214.635 | 11541.2
11:00 | 6364.3 | 5304.1 | 11668.4
11:30 | 6480.815 | 5383.51 | 11864.325
12:00 | 6597.33 | 5462.92 | 12060.25
12:30 | 6717.315 | 5563.77 | 12281.085
13:00 | 6837.3 | 5664.62 | 12501.92
13:30 | 6940.905 | 5724.5 | 12665.405
14:00 | 7044.51 | 5784.38 | 12828.89
14:30 | 6945.225 | 5711.365 | 12656.59
15:00 | 6845.94 | 5638.35 | 12484.29
15:30 | 6896.475 | 5603.42 | 12499.895
16:00 | 6947.01 | 5568.49 | 12515.5
16:30 | 7040.6 | 5539.44 | 12580.04
17:00 | 7134.19 | 5510.39 | 12644.58
17:30 | 7054.295 | 5439.375 | 12493.67
18:00 | 6974.4 | 5368.36 | 12342.76
18:30 | 7043.45 | 5444.725 | 12488.175
19:00 | 7112.5 | 5521.09 | 12633.59
19:30 | 7166.5 | 5593.53 | 12760.03
20:00 | 7105.5 | 5577.23 | 12682.73
20:30 | 7118.5 | 5589.45 | 12707.95 |  | Executive Engineer
21:00 | 7131.5 | 5601.67 | 12733.17 |  | Network Operation Division
21:30 | 7138.75 | 5606.53 | 12745.28
22:00 | 7146 | 5611.39 | 12757.39
22:30 | 6858.5 | 5584.775 | 12443.275
23:00 | 6571 | 5558.16 | 12129.16

## En-Curve
QF-LDC-12
Date | 01-03-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3205 | 1691 | 884 | 0 | 120 | 1218.41 | 80 | 3723 | 0 | 34 | 147 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3109 | 1636 | 887 | 0 | 112 | 1222.715 | 80 | 3524.5 | 0 | 25.5 | 125 | 0 | 0 | 0 | 0 | 01-03-2026
01:00 | 3013 | 1581 | 890 | 0 | 104 | 1227.02 | 80 | 3326 | 0 | 17 | 103 | 0 | 0 | 0 | 0
01:30 | 3002 | 1558 | 892 | 0 | 106 | 1195.99 | 80 | 3262.5 | 0 | 17 | 111 | 0 | 0 | 0 | 0 | Energy Generated | 279.316 |  | MKWHr
02:00 | 2991 | 1535 | 894 | 0 | 108 | 1164.96 | 80 | 3199 | 0 | 17 | 119 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2924.5 | 1491 | 896 | 0 | 108 | 1241.52 | 80 | 3215 | 0 | 37 | 167.5 | 0 | 0 | 0 | 0 | Total Energy Requirement | 279.316 |  | MKWHr
03:00 | 2858 | 1447 | 898 | 0 | 108 | 1318.08 | 80 | 3231 | 0 | 57 | 216 | 0 | 0 | 0 | 0
03:30 | 2991 | 1462.5 | 900.5 | 0 | 107 | 1365.095 | 80 | 3419.5 | 0 | 58.5 | 219.5 | 0 | 0 | 0 | 0
04:00 | 3124 | 1478 | 903 | 0 | 106 | 1412.11 | 80 | 3608 | 0 | 60 | 223 | 0 | 0 | 0 | 0
04:30 | 3111.5 | 1478.5 | 903.5 | 0 | 108 | 1316.34 | 80 | 3341 | 0 | 38.5 | 185.5 | 0 | 0 | 0 | 0
05:00 | 3099 | 1479 | 904 | 0 | 110 | 1220.57 | 80 | 3074 | 0 | 17 | 148 | 0 | 0 | 0 | 0
05:30 | 2959.5 | 1435.5 | 904 | 0 | 110 | 1065.46 | 80 | 2877.5 | 0 | 8.5 | 137 | 0 | 0 | 0 | 0
06:00 | 2820 | 1392 | 904 | 0 | 110 | 910.35 | 80 | 2681 | 0 | 0 | 126 | 0 | 0 | 0 | 0
06:30 | 2870.5 | 1371.5 | 903.5 | 0 | 99 | 875.805 | 80 | 2663 | 13.835 | 0 | 134 | 0 | 0 | 0 | 0
07:00 | 2921 | 1351 | 903 | 0 | 88 | 841.26 | 80 | 2645 | 27.67 | 0 | 142 | 0 | 0 | 0 | 0
07:30 | 3051 | 1413 | 784.5 | 0 | 93 | 886.335 | 80 | 2792 | 86.005 | 12.5 | 202 | 0 | 0 | 0 | 0
08:00 | 3181 | 1475 | 666 | 0 | 98 | 931.41 | 80 | 2939 | 144.34 | 25 | 262 | 0 | 0 | 0 | 0
08:30 | 3237.5 | 1529 | 784.5 | 0 | 105 | 948.69 | 80 | 3006.5 | 237.6 | 47 | 322 | 0 | 0 | 0 | 0
09:00 | 3294 | 1583 | 903 | 0 | 112 | 965.97 | 80 | 3074 | 330.86 | 69 | 382 | 0 | 0 | 0 | 0
09:30 | 3288 | 1584 | 903 | 0 | 116 | 1015.79 | 80 | 3206 | 416.625 | 102.5 | 392 | 0 | 0 | 0 | 0
10:00 | 3282 | 1585 | 903 | 0 | 120 | 1065.61 | 80 | 3338 | 502.39 | 136 | 402 | 0 | 0 | 0 | 0
10:30 | 3340.5 | 1578 | 903 | 0 | 123 | 1068.185 | 80 | 3394 | 541.515 | 144 | 369 | 0 | 0 | 0 | 0
11:00 | 3399 | 1571 | 903 | 0 | 126 | 1070.76 | 80 | 3450 | 580.64 | 152 | 336 | 0 | 0 | 0 | 0
11:30 | 3423 | 1569.5 | 903.5 | 0 | 129 | 1072.155 | 80 | 3569.5 | 615.67 | 161.5 | 340.5 | 0 | 0 | 0 | 0
12:00 | 3447 | 1568 | 904 | 0 | 132 | 1073.55 | 80 | 3689 | 650.7 | 171 | 345 | 0 | 0 | 0 | 0
12:30 | 3396.5 | 1561.5 | 904 | 0 | 138 | 1129.17 | 80 | 3803.5 | 639.715 | 178.7 | 450 | 0 | 0 | 0 | 0
13:00 | 3346 | 1555 | 904 | 0 | 144 | 1184.79 | 80 | 3918 | 628.73 | 186.4 | 555 | 0 | 0 | 0 | 0
13:30 | 3305 | 1582.5 | 904 | 0 | 147 | 1251.44 | 80 | 4034.5 | 591.165 | 187.9 | 581.4 | 0 | 0 | 0.5 | 0
14:00 | 3264 | 1610 | 904 | 0 | 150 | 1318.09 | 80 | 4151 | 553.6 | 189.4 | 607.8 | 0 | 0 | 1 | 0
14:30 | 3193.5 | 1620.9 | 904 | 0 | 148 | 1294.705 | 80 | 4157 | 476.885 | 197.2 | 581.4 | 0 | 0 | 3 | 0
15:00 | 3123 | 1631.8 | 904 | 0 | 146 | 1271.32 | 80 | 4163 | 400.17 | 205 | 555 | 0 | 0 | 5 | 0
15:30 | 3138 | 1651.3 | 903.5 | 0 | 141 | 1272.72 | 80 | 4168 | 324.875 | 217 | 596.5 | 0 | 0 | 7 | 0
16:00 | 3153 | 1670.8 | 903 | 0 | 136 | 1274.12 | 80 | 4173 | 249.58 | 229 | 638 | 0 | 0 | 9 | 0
16:30 | 3154 | 1675.3 | 898 | 0 | 134 | 1296.535 | 80 | 4171.5 | 165.205 | 260 | 739 | 0 | 0 | 6.5 | 0
17:00 | 3155 | 1679.8 | 893 | 0 | 132 | 1318.95 | 80 | 4170 | 80.83 | 291 | 840 | 0 | 0 | 4 | 0
17:30 | 2996.5 | 1637.1 | 892 | 0 | 130 | 1380.405 | 80 | 4060.5 | 40.665 | 307 | 967 | 0 | 0 | 2.5 | 0
18:00 | 2838 | 1594.4 | 891 | 0 | 128 | 1441.86 | 80 | 3951 | 0.5 | 323 | 1094 | 0 | 0 | 1 | 0
18:30 | 3026 | 1612.95 | 891.5 | 0 | 136 | 1444.475 | 80 | 3938 | 0.25 | 305 | 1053 | 0 | 0 | 1 | 0
19:00 | 3214 | 1631.5 | 892 | 0 | 144 | 1447.09 | 80 | 3925 | 0 | 287 | 1012 | 0 | 0 | 1 | 0
19:30 | 3238 | 1607.5 | 892 | 0 | 146 | 1451.53 | 80 | 4043 | 0 | 244 | 1058 | 0 | 0 | 0 | 0
20:00 | 3239 | 1603.5 | 892 | 0 | 142 | 1451.23 | 80 | 4121 | 0 | 176 | 978 | 0 | 0 | 0 | 0
20:30 | 3263.5 | 1625.5 | 892 | 0 | 142 | 1451.95 | 80 | 4151 | 0 | 153.5 | 948.5 | 0 | 0 | 0 | 0
21:00 | 3288 | 1647.5 | 892 | 0 | 142 | 1452.67 | 80 | 4181 | 0 | 131 | 919 | 0 | 0 | 0 | 0
21:30 | 3328.5 | 1628.75 | 891.5 | 0 | 143 | 1452.53 | 80 | 4175.5 | 0 | 131 | 914.5 | 0 | 0 | 0 | 0
22:00 | 3369 | 1610 | 891 | 0 | 144 | 1452.39 | 80 | 4170 | 0 | 131 | 910 | 0 | 0 | 0 | 0
22:30 | 3367.5 | 1590.5 | 891.5 | 0 | 140 | 1451.275 | 80 | 4051.5 | 0 | 121 | 750 | 0 | 0 | 0 | 0
23:00 | 3366 | 1571 | 892 | 0 | 136 | 1450.16 | 80 | 3933 | 0 | 111 | 590 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 01-03-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 408 | 04:00 | 382 | 15:00 | Madunaghat | 409 | 07:00 | 393 | 15:00
Amtali | 423 | 06:00 | 409 | 14:00 | Meghnaghat | 406 | 06:00 | 382 | 14:00
Ashuganj | 416 | 6:00 | 393 | 15:00 | Payra | 423 | 06:00 | 411 | 14:00
Bhulta | 410 | 06:00 | 383 | 15:00 | Rahanpur | 421 | 06:00 | 400 | 17:00
Bibiana | 413 | 02:00 | 399 | 15:00 | Rampal | 415 | 07:00 | 395 | 14:00
BIPTC | 403 | 08:00 | 391 | 12:00
Bogura | 417 | 06:00 | 389 | 14:00
Gopalganj | 416 | 07:00 | 308 | 18:00
Kaliakoir | 403 | 06:00 | 374 | 15:00
Korerhat | 411 | 06:00 | 390 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 237 | 06:00 | 217 | 15:00 | Jhenaidah | 239 | 07:00 | 221 | 14:00
AKSML | 235 | 06:00 | 223 | 14:00 | Kachua | 235 | 06:00 | 220 | 15:00
Aminbazar | 238 | 07:00 | 219 | 14:00 | Kaliakoir | 239 | 06:00 | 220 | 15:00
Ashuganj | 235 | 06:00 | 220 | 14:00 | Keranigonj | 236 | 06:00 | 216 | 15:00
Ashuganj-400 | 235 | 6:00 | 218 | 15:00 | Khulna(S) | 241 | 06:00 | 224 | 14:00
Baghabari | 238 | 05:00 | 225 | 13:00 | Korerhat | 234 | 06:00 | 221 | 15:00
Barapukuria | 229 | 06:00 | 204 | 17:00 | Madunaghat | 234 | 14:00 | 228 | 19:00
Barapukuria-230 | 229 | 6:00 | 210 | 15:00 | Madunaghat-400 | 234 | 09:00 | 225 | 15:00
Barishal | 236 | 06:00 | 226 | 14:00 | Maniknagar | 234 | 04:00 | 219 | 15:00
Bheramara | 238 | 06:00 | 222 | 14:00 | Meghnaghat | 243 | 22:00 | 230 | 12:00
Bhulta | 238 | 06:00 | 219 | 15:00 | Meghnaghat-400 | 240 | 06:00 | 223 | 15:00
Bibiana | 241 | 06:00 | 228 | 14:00 | Mirsorai | 234 | 06:00 | 223 | 14:00
BIPTC | 241 | 06:00 | 222 | 16:00 | Rajshahi | 238 | 07:00 | 220 | 16:00
Bogura | 241 | 06:00 | 223 | 17:00 | Rampal | 239 | 06:00 | 223 | 14:00
Bogura-400 | 241 | 06:00 | 224 | 17:00 | Rampur | N/A | N/A | N/A | N/A
Borhanuddin | 238 | 06:00 | 233 | 14:00 | Rampura | 236 | 06:00 | 216 | 15:00
BSRM | 234 | 08:00 | 222 | 14:00 | Shikalbaha | 236 | 19:30 | 224 | 14:00
Chowmuhani | N/A | N/A | N/A | N/A | Shyampur | 238 | 06:00 | 219 | 15:00
Cumilla(N) | 236 | 06:00 | 221 | 14:00 | Siddhirganj | 237 | 04:00 | 222 | 14:00
Faridpur | 234 | 06:00 | 221 | 14:00 | Sirajgonj | 241 | 06:00 | 230 | 14:00
Fenchuganj | 242 | 06:00 | 233 | 14:00 | Sreepur | 228 | 06:00 | 215 | 14:00
Feni | 236 | 06:00 | 222 | 15:00 | Tongi | 232 | 04:00 | 217 | 15:00
Ghorashal | 235 | 08:00 | 230 | 00:00
Ghorashal-230 | 234 | 06:00 | 215 | 15:00
Gopalganj | 233 | 06:00 | 221 | 14:00
GPH | 234 | 08:00 | 223 | 14:00
Haripur | 238 | 06:00 | 221 | 15:00
Hasnabad | 236 | 06:00 | 218 | 16:00
Hathazari | 232 | 05:00 | 222 | 14:00
Ishurdi | 241 | 06:00 | 225 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 06:00 | 123 | 15:00 | Magura | 139 | 06:00 | 124 | 14:00
Agargaon | 134 | 06:00 | 122 | 14:00 | Mahasthangarh | 137 | 06:00 | 124 | 17:00
Agrabad | 134 | 05:00 | 128 | 13:00 | Maijdee | 131 | 06:00 | 123 | 14:00
AKS | 132 | 07:00 | 127 | 14:00 | Manikganj | 137 | 18:00 | 126 | 16:00
Aminbazar | 138 | 07:00 | 125 | 14:00 | Maniknagar | 133 | 06:00 | 121 | 15:00
Amnura | 139 | 06:00 | 128 | 15:00 | Matarbari | 126 | 10:00 | 114 | 21:00
Ashuganj | 142 | 05:00 | 134 | 14:00 | Matuail | 135 | 18:00 | 125 | 15:00
Bagerhat | 135 | 06:00 | 122 | 14:00 | Metrorail_Motijheel | 133 | 06:00 | 121 | 15:00
Bajitpur | 134 | 03:00 | 125 | 17:00 | Metrorail_Uttara | 138 | 06:00 | 123 | 15:00
Bakerganj | 138 | 06:00 | 131 | 15:00 | Millgate | 137 | 06:00 | 123 | 15:00
Bakulia | 135 | 08:00 | 129 | 14:00 | Mirpur | 137 | 05:00 | 123 | 15:00
Banani | 137 | 06:00 | 123 | 15:00 | Mirzapur | 137 | 06:00 | 124 | 16:00
Bangabhaban | 133 | 06:00 | 120 | 15:00 | Mithapukur | 137 | 06:00 | 122 | 17:00
Barapukuria | 140 | 06:00 | 122 | 17:00 | MI_Cement | 136 | 06:00 | 121 | 15:00
Barguna | 138 | 03:00 | 131 | 14:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 138 | 06:00 | 130 | 14:00 | Mogbazar | 138 | 07:00 | 130 | 06:00
Barishal-230 | 138 | 06:00 | 130 | 15:00 | Mongla | 135 | 05:00 | 122 | 14:00
Baroaulia | 135 | 08:00 | 128 | 14:00 | Motijheel | 133 | 06:00 | 120 | 15:00
Baroirhat | 135 | 07:00 | 125 | 15:00 | Muktagacha | 134 | 06:00 | 117 | 16:00
Bashundhara | 138 | 10:00 | 123 | 15:00 | Munshiganj | 134 | 06:00 | 123 | 15:00
BashundharaCement | 133 | 07:00 | 124 | 15:00 | Muradnagar | 135 | 07:00 | 124 | 15:00
Beanibazar | 132 | 07:00 | 125 | 14:00 | Mymensingh | 131 | 06:00 | 115 | 16:00
Benapole | 136 | 02:00 | 117 | 14:00 | Naogaon | 139 | 06:00 | 122 | 17:00
Bhaluka | 136 | 18:30 | 127 | 14:00 | Narail | 138 | 06:00 | 123 | 14:00
Bhandaria | 136 | 07:00 | 127 | 14:00 | Narinda | 133 | 6:00 | 121 | 15:00
Bhangura | 137 | 06:00 | 126 | 16:00 | Narshingdi | 133 | 06:00 | 119 | 15:00
Bheramara | 139 | 06:00 | 132 | 13:00 | Natore | 136 | 05:00 | 127 | 17:00
Bheramara(GK) | 139 | 06:00 | 131 | 17:00 | Nawabganj | 137 | 06:00 | 123 | 15:00
Bhulta | 129 | 18:00 | 119 | 15:00 | Netrakona | 126 | 03:00 | 115 | 13:00
Bog-Sherpur | 138 | 06:00 | 126 | 17:00 | New | 137 | 06:00 | 124 | 15:00
Bogura | 138 | 06:00 | 127 | 17:00 | Niamatpur | 138 | 00:00 | 131 | 17:00
Bogura-230 | 139 | 06:00 | 128 | 17:00 | Noapara | 138 | 05:00 | 123 | 13:00
Brahmanbaria | 137 | 18:00 | 128 | 14:00 | Pabna | 139 | 06:00 | 129 | 16:00
Cantonment | 134 | 06:00 | 121 | 15:00 | Palashbari | 136 | 06:00 | 131 | 19:00
Chandina | 137 | 06:00 | 127 | 15:00 | Panchagarh | 139 | 18:30 | 124 | 13:00
Chandpur | 132 | 06:00 | 124 | 15:00 | Patiya | 134 | 07:00 | 128 | 14:00
Chandraghona | 137 | 08:00 | 130 | 14:00 | Patuakhali | 137 | 06:00 | 130 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 138 | 01:00 | 133 | 16:00 | Payra | 139 | 07:00 | 134 | 14:00
Charsaidpur | 135 | 06:00 | 124 | 15:00 | PHP | 134 | 06:00 | 126 | 14:00
Chauddagram | 134 | 06:00 | 124 | 15:00 | Postogola | 138 | 06:00 | 124 | 15:00
Chhatak | 130 | 05:00 | 124 | 13:00 | Purbachal | 137 | 06:00 | 123 | 15:00
Chowmuhani | 131 | 05:00 | 124 | 15:00 | Purbasadipur | 132 | 06:00 | 117 | 17:00
Chuadanga | 137 | 05:00 | 124 | 14:00 | Rahanpur | 141 | 06:00 | 134 | 13:00
Coxsbazar | 127 | 08:00 | 115 | 20:00 | Rahanpur-400 | 141 | 06:00 | 134 | 14:00
Cumilla(N) | 137 | 06:00 | 127 | 15:00 | Rahim | 135 | 06:00 | 125 | 15:00
Cumilla(S) | 135 | 06:00 | 120 | 13:00 | Rajbari | 136 | 07:00 | 126 | 14:00
Daganbhuiyan | 132 | 07:00 | 124 | 15:00 | Rajendrapur | 137 | 07:00 | 126 | 13:00
Daudkandi | 134 | 06:00 | 121 | 15:00 | Rajshahi | 136 | 01:00 | 127 | 14:00
DhakaUniversity | 136 | 05:00 | 124 | 15:00 | Rajshahi-230 | 137 | 06:00 | 126 | 17:00
Dhamrai | 138 | 06:00 | 123 | 15:00 | Ramganj | 130 | 07:00 | 122 | 15:00
Dhanmondi | 136.8 | 07:00 | 126 | 15:00 | Rampur | 134 | 08:00 | 128 | 14:00
Dohazari | 132 | 06:00 | 125 | 14:00 | Rampura | 137 | 06:00 | 124 | 15:00
Faridpur | 135 | 05:00 | 127 | 15:00 | Rangamati | 135 | 06:00 | 130 | 13:00
Fatullah | 137 | 06:00 | 123 | 14:00 | Rangpur | 135 | 02:00 | 122 | 17:00
Fenchuganj | 138 | 03:00 | 131 | 15:00 | Ruppur | 140 | 06:00 | 131 | 18:00
Feni | 130 | 03:00 | 124 | 14:00 | Saidpur | 136 | 06:00 | 122 | 17:00
Feni-230 | 132 | 06:00 | 124 | 15:00 | Satkhira | 137 | 06:00 | 122 | 14:00
Ghatail | 132 | 03:00 | 116 | 16:00 | Satmasjid | 132 | 04:00 | 121 | 15:00
Ghorashal | 140 | 08:00 | 133 | 17:00 | Savar | 137 | 06:00 | 122 | 15:00
Goalpara | 140 | 06:00 | 127 | 14:00 | SevenRings | 140 | 06:00 | 130 | 16:00
Gollamari | 139 | 06:00 | 127 | 14:00 | ShahCement | 135 | 06:00 | 124 | 15:00
Gopalganj | 138 | 06:00 | 128 | 14:00 | Shahjadpur | 141 | 04:00 | 132 | 12:00
Gopalganj-400 | 139 | 06:00 | 131 | 14:00 | Shahjibazar | 136 | 06:00 | 127 | 14:00
Gulshan | 137 | 06:00 | 124 | 14:00 | Shahmirpur | 135 | 09:00 | 129 | 15:00
Halishahar | 137 | 08:00 | 129 | 14:00 | Shariatpur | 138 | 07:00 | 128 | 14:00
Haripur | 135 | 06:00 | 125 | 16:00 | Sherpur | 130 | 22:00 | 111 | 16:00
HaripurSBU | 134 | 08:00 | 126 | 14:00 | Shikalbaha | 124 | 06:00 | 119 | 14:00
Hasnabad | 136 | 05:00 | 124 | 15:00 | Shikalbaha-230 | 137 | 08:00 | 129 | 14:00
Hathazari | 136 | 05:00 | 130 | 14:00 | Shitalakhya | 136 | 06:00 | 122 | 15:00
Hatirjheel | 137 | 06:00 | 124 | 15:00 | Sholosohor | 136 | 08:00 | 130 | 14:00
Ishurdi | 141 | 06:00 | 132 | 17:00 | Shyampur | 136 | 06:00 | 126 | 16:00
Jaldhaka | 134 | 06:00 | 118 | 17:00 | Shyampur-230 | 138 | 06:00 | 125 | 15:00
Jamalpur | 134 | 18:30 | 116 | 16:00 | Siddhirganj | 135 | 06:00 | 125 | 15:00
Jashore | 136 | 06:00 | 119 | 13:00 | Sirajganj | 136 | 05:00 | 124 | 17:00
Jhenaidah | 140 | 04:00 | 117 | 13:00 | Sonargaon | 134 | 05:00 | 122 | 15:00
Jhenaidah-230 | 139 | 06:00 | 127 | 14:00 | Sreemongol | 135 | 06:00 | 127 | 14:00
Joydebpur | 137 | 05:00 | 124 | 14:00 | Sreepur | 140 | 06:00 | 130 | 14:00
Joypurhat | 132 | 06:00 | 118 | 17:00 | Srinagar | 137 | 06:00 | 124 | 14:00
Juldah | 135 | 10:00 | 128 | 14:00 | SSM | 140 | 08:00 | 128 | 15:00
Kabirpur | 138 | 03:00 | 118 | 15:00 | Sunamganj | 128 | 06:00 | 123 | 14:00
Kachua | 134 | 06:00 | 125 | 15:00 | Sylhet | 134 | 06:00 | 127 | 14:00
Kaliakoir | 142 | 06:00 | 125 | 15:00 | Sylhet-132 | 131 | 05:00 | 127 | 16:00
Kaliganj | 140 | 06:00 | 127 | 14:00 | Tangail | 133 | 05:00 | 120 | 15:00
Kallyanpur | 139 | 06:00 | 125 | 15:00 | Taraganj | 134 | 05:00 | 119 | 17:00
Kalurghat | 136 | 06:00 | 130 | 15:00 | Tasnim | 134 | 06:00 | 123 | 14:00
Kamrangirchar | 137 | 06:00 | 123 | 14:00 | Thakurgaon | 139 | 18:30 | 122 | 13:00
Kaptai | N/A | N/A | N/A | N/A | TK | 135 | 05:00 | 129 | 15:00
Kasba | 134 | 07:00 | 123 | 15:00 | Tongi | 137 | 04:00 | 126 | 15:00
Kazla | 133 | 07:00 | 120 | 16:00 | Ullahpara | 137 | 06:00 | 126 | 17:00
Keranigonj | 137 | 06:00 | 124 | 14:00 | Ullon | 136 | 05:00 | 124 | 14:00
Khagrachori | 135 | 06:00 | 129 | 14:00 | Uttara | 138 | 06:00 | 123 | 14:00
Khulna | 137 | 03:00 | 128 | 06:00 | UttaraNew | 138 | 06:00 | 123 | 15:00
Khulna(S) | 140 | 06:00 | 127 | 14:00 | Zigatola | 138 | 06:00 | 123 | 15:00
Khulshi | 134 | 07:00 | 126 | 15:00
Kishoreganj | 133 | 03:00 | 122 | 17:00
Kodda | 137 | 18:00 | 123 | 16:00
Korerhat | 136 | 06:00 | 128 | 15:00
KSRM | 135 | 08:00 | 128 | 14:00
Kulaura | 137 | 06:00 | 130 | 15:00
Kurigram | 133 | 06:00 | 120 | 12:00
Kushtia | 135 | 06:00 | 124 | 13:00
Laksam | 134 | 06:00 | 125 | 15:00
Lakshmipur | 131 | 06:00 | 124 | 14:00
Lalbag | 135 | 05:00 | 123 | 16:00
Lalmonirhat | 132 | 06:00 | 118 | 17:00
Madanganj | 133 | 07:00 | 124 | 15:00
Madaripur | 138 | 06:00 | 130 | 14:00
Madartek | 136 | 07:00 | 124 | 14:00
Madunaghat | 137 | 03:00 | 130 | 14:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division