## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 03-03-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-03-2026 | during | 03-03-2026 | during | 03-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 313 | 340 | 412 | 412 | 412 | 412 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Engine Problem
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 1 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 335 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 20 | 16 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 89 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20.5 | 22 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 20 | 20 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 34 | 24 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 95 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 101 | 113 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 17 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 98 | 0 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 16 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 400 | 410 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 400 | 410 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 52 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2059.5 | 1776 | 5946.22 | 5915.22 | 3134.05 | 3158.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 34 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 80 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 31 | 221 | 220 | 225 | 150 | 150
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 16 | 0 | 105 | 105 | 95 | 95
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 48 | 64 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 47 | 51 | 68 | 68 | 68 | 68 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 50 | 0 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 3 | 29 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 20 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.08 | 0 | 3.33 | 0 | 3.33 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 36 | 0 | 100 | 100 | 50 | 50 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1161 | 1163 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 3 | 1 | 0 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 720 | 935 | 935 | 935 | 935 | 935 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2219.08 | 2501 | 3836.19 | 3852.86 | 3271.83 | 3283.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 206 | 201 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 300 | 335 | 353.35 | 353.35 | 353.35 | 353.35 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 318.81 | 318.81 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 280 | 393 | 393 | 393 | 393 | 393 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 53 | 0 | 55 | 55 | 5 | 5 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 24 | 42 | 42 | 42 | 42 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 98 | 102 | 163 | 163 | 110 | 110 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 16 | 0 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 142 | 154 | 84 | 78 | 84 | 78 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 16 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 113 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 16 | 0 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 39 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1209 | 1385 | 2741.51 | 2680.51 | 1943.55 | 1882.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-03-2026 | during | 03-03-2026 | during | 03-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 10 | 11 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 87 | 60 | 80 | 60 | 80 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 69 | 88 | 70 | 115 | 70 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 138 | 192 | 366 | 429 | 155 | 218
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 41 | 42 | 42 | 42 | 42 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | ps availability is less
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 158 | 157 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 75 | 75 | 80 | 80 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 41 | 41 | 84 | 84 | 83 | 83 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 98 | 97 | 100 | 100 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 22 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 310 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 342 | 344 | 385 | 385 | 385 | 385 | Due to Air Filter DP High FGMO not available.
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1127 | 1117 | 1300 | 1300 | 1166 | 1166
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 902 | 902 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 206 | 185 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 64.69 | 0 | 60 | 0 | 60 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1005 | 1120 | 0 | 0 | 1148.28 | 1148.28 | plant availability zero
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2177.69 | 2207 | 2332 | 2272 | 2515.38 | 2455.38
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 125 | 120 | 130 | 130 | 130 | 130 | plant availability zero
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 829 | 1078 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 15 | 15 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 249 | 276 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.51 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2700.36 | 1423.51 | 1694 | 2003.32 | 2002.32 | 1868.32 | 1867.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 20.53 | 0 | 50 | 0 | 50 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown As Per PGB PLC's Requirements.
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 199 | 191 | 220 | 220 | 220 | 220 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 32 | 32 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.05 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1116 | 1444 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 29.51 | 0 | 48 | 0 | 48 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 95 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1879.09 | 2049 | 3124.57 | 2920.87 | 2579.57 | 2375.87
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.3 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 186 | 0 | 173.96 | 0 | 173.96 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 296.3 | 0 | 471.16 | 262 | 437.16 | 228
System Total |  |  |  |  | 28823.2 | 28385.703 | 12529.17 | 12921 | 22120.97 | 21634.78 | 17070.86 | 16634.67
Forecast Scenario (03-03-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11860 |  | 0 |  | 11860
|  |  |  | 1:00 | 11250 |  | 0 |  | 11250
|  |  |  | 2:00 | 10810 |  | 0 |  | 10810
|  |  |  | 3:00 | 10930 |  | 0 |  | 10930
|  |  |  | 4:00 | 11750 |  | 0 |  | 11750
|  |  |  | 5:00 | 10850 |  | 0 |  | 10850
|  |  |  | 6:00 | 9970 |  | 0 |  | 9970
|  |  |  | 7:00 | 10220 |  | 0 |  | 10220
|  |  |  | 8:00 | 10720 |  | 0 |  | 10720
|  |  |  | 9:00 | 11510 |  | 0 |  | 11510
|  |  |  | 10:00 | 11850 |  | 0 |  | 11850
|  |  |  | 11:00 | 12210 |  | 0 |  | 12210
|  |  |  | 12:00 | 12620 |  | 0 |  | 12620
|  |  |  | 13:00 | 13100 |  | 0 |  | 13100
|  |  |  | 14:00 | 13260 |  | 0 |  | 13260
|  |  |  | 15:00 | 13000 |  | 0 |  | 13000
|  |  |  | 16:00 | 12550 |  | 0 |  | 12550
|  |  |  | 17:00 | 12680 |  | 0 |  | 12680
|  |  |  | 18:00 | 12470 |  | 0 |  | 12470
|  |  |  | 18:30 | 12600 |  | 0 |  | 12600
|  |  |  | 19:00 | 12780 |  | 0 |  | 12780
|  |  |  | 19:30 | 12780 |  | 0 |  | 12780
|  |  |  | 20:00 | 12920 |  | 0 |  | 12920
|  |  |  | 21:00 | 13020 |  | 0 |  | 13020
|  |  |  | 22:00 | 12820 |  | 0 |  | 12820
|  |  |  | 23:00 | 12300 |  | 0 |  | 12300
Probable Maximum Temperature: |  |  | 33.60°C
Probable Maximum Demand at Day Peak: |  |  | 12620.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13020.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13020.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 287.45 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:37 hrs on 03-03-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 02-03-2026
Power Supply Scenario
| Day Peak Generation |  |  | 12529.17 | MW | 12:00 Hr. | Energy Generated |  |  | 288.9732 |  | MKWHr.
| Day Peak Demand |  |  | 12529.17 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.037 |  | MKWHr.
| Evening Peak Generation |  |  | 12921 | MW | 21:00 Hr. | Energy Demand |  |  | 289.0102 |  | MKWHr.
| Evening Peak Demand |  |  | 12921 | MW | 21:00 Hr. | Maximum Temperature |  |  | 33.3 |  | °C
| Minimum Generation of the Day |  |  | 9870.23 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 844.15 |  | MMCFD
| Maximum Generation of the Day |  |  | 13169.37 | MW | 14:00 Hr. | Production Cost per KWHr |  |  | 5.8204 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.2899 | 0 | 9.1228 | 0 | 0 | 0.14049 | 0 | 0 | 43.5532 | Gas | 117.1399 | Gas | 403627197.0835
| Chattogram Zone |  |  | 3.4894 | 44.9745 | 2.7416 | 0 | 1.9234 | 0.1279 | 0 | 0.03216 | 53.289 | Coal | 94.7284 | Coal | 616292048.8786
| Cumilla Zone |  |  | 25.1744 | 0 | 1.179 | 0 | 0 | 0.28248 | 3.24 | 0 | 29.8758 | HFO | 17.4304 | HFO | 296015456.2
| Mymensingh Zone |  |  | 0.25248 | 0 | 3.391 | 0 | 0 | 0.00725 | 0 | 0 | 3.6507 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.8338 | 0 | 0 | 0 | 0 | 0.03553 | 0 | 0 | 26.8693 | Hydro | 1.9234 | Hydro | 192342
| Khulna Zone |  |  | 5.0005 | 24.0727 | 0 | 0 | 0 | 0.40896 | 21.0756 | 0 | 50.5579 | Solar | 3.4852 | Solar | 56432670.632
| Barishal Zone |  |  | 8.0698 | 25.6811 | 0 | 0 | 0 | 0.002685 | 0 | 0 | 33.7535 | Import | 54.2338 | Import | 308912688.06
| Rajshahi Zone |  |  | 14.0296 | 0 | 0.030098 | 0 | 0 | 1.0038 | 29.9181 | 0 | 44.9816 | Wind | 0.03216 | Wind | 473073.6
| Rangpur Zone |  |  | 0 | 0 | 0.96603 | 0 | 0 | 1.4761 | 0 | 0 | 2.4421
| Total |  |  | 117.1399 | 94.7284 | 17.4304 | 0 | 1.9234 | 3.4852 | 54.2338 | 0.03216 | 288.9732
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 403627197.0835 |  | Hydro | 192342
|  |  |  | Coal | 616292048.8786 |  | Solar | 56432670.632
|  |  |  | HFO | 296015456.2 |  | Import | 308912688.06
|  |  |  | HSD | 0 |  | Wind | 473073.6
[5 empty] | Total: | 168,19,45,476 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.0756 | Peak Hr Flow | 902.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 36140002.14 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 29.9181 | Peak Hr Flow | 1444.00 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2154 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.24 | Peak Hr Flow | 154.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2247 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 54.2338 | Peak Hr Flow | 2500.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4825
|  |  |  | Chattogram |  | 0 |  | 1374
|  |  |  | Cumilla |  | 0 |  | 1184
|  |  |  | Mymensingh |  | 0 |  | 998
|  |  |  | Sylhet |  | 0 |  | 440
|  |  |  | Khulna |  | 0 |  | 1405
|  |  |  | Barishal |  | 0 |  | 375
|  |  |  | Rajshahi |  | 0 |  | 1170
|  |  |  | Rangpur |  | 0 |  | 673
|  |  |  | Total |  | 0 |  | 12444
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:24 | 15:41 | Shikalbaha 230/132kV S/S ATR 01 LT Project Work S/D Due to Sf6 gas refill
| 08:27 | 15:39 | Shikalbaha 230/132kV S/S ATR 01 HT Project Work S/D Due to Sf6 gas refill
| 08:42 |  | Siddhirganj 132/33kV S/S 132kV MTR 1 Scheduled S/D Due to Coatings Work of Transformer
Body.
| 08:45 |  | Siddhirganj 230/132kV S/S MTR 1 HT Scheduled S/D Due to Painting of Transformer
| 09:06 | 17:06 | Monakasha-Rahanpur 400kV Ckt-1 Scheduled S/D from Rahanpur 400/132kV end Due to For red
hot rectification work at adani side
| 09:11 |  | Bibiyana-Kaliakoir 400 kV Ckt-1 Scheduled S/D from Bibiana 400/230kV end Due to Emergency
Maintenance
| 09:25 | 12:04 | Shyampur 132/33kV S/S GT-4 HT Scheduled S/D Due to GT-4 Transformer oil leakage for Y-
phase PT.
| 09:56 | 10:38 | Keranigonj 230/132/33kV S/S 132 kV Hasnabad Ckt. 1 Scheduled S/D Due to NLDC Instruction
| 10:00 | 10:38 | Hasnabad-Keraniganj 230kV Ckt-2 Scheduled S/D from Keranigonj 230/132/33kV end Due to
NLDC Instruction
| 10:18 | 15:12 | Shyampur 230/132kV S/S 230 kV APR (D04) Scheduled S/D Due to Take shutdown by NLDC for
relay work at Hasnabad SS end.
| 10:20 | 15:20 | APR-Hasnabad 230kV Ckt-2 Scheduled S/D from Hasnabad 230/132kV end Due to Z2 (21) relay
Card changing by SPDM-1
| 10:37 |  | 230 KV bus-2 S/D Barapukuria PS side.
| 10:51 | 14:32 | Barapukuria-Bogura 230 kV Ckt-1 Scheduled S/D from Bogura 400/230kV end Due to Emergency
BUS maintenance at Barapukuria Coal Base Thermal Power Plant and from Barapukuria
230/132/33kV end Due to 230 kv upper Bus maintenance.
| 10:56 | 17:13 | Madanganj 132/33kV S/S Madanganj -Bashundhara 132 kv Ckt Forced S/D Due to Emergency | [7 empty] | 7.0MW load
|  |  | maintenance of R-ph CT at their end | [7 empty] | interrup.
| 11:01 | 14:58 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-2 Project Work S/D from Purbasadipur 132/33kV end
Due to GIS to AIS loop and DS removal work by EEGBPS Project
|  | 11:08 | Chandpur 132/33kV S/S 402T (T-01) LT is restored.
| 11:09 | 13:00 | Chandpur 132/33kV S/S 412T (T-2) HT Scheduled S/D Due to DS maintenance
| 11:09 | 13:00 | Chandpur 132/33kV S/S 412T (T-2) LT Scheduled S/D Due to DS maintenance
|  | 11:25 | Fenchuganj -Sylhet 132kV Ckt-1 is restored.
|  | 11:26 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 is restored.
|  | 11:26 | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-1 is restored.
| 11:38 | 13:46 | Tongi 230/132/33kV S/S 132 kV Bus-1 Scheduled S/D Due to Shutdown taken by PSDC
| 12:00 |  | Day Peak Generation: 12526 MW.
| 12:03 | 16:41 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Forced S/D from Brahmanbaria 132/33kV end Due to
Due to overload of Srimangal - Fenchuganj ckt.
| 12:03 | 16:41 | Brahmanbaria-Shahjibazar 132 kV Ckt-1 Forced S/D from Brahmanbaria 132/33kV end Due to
Due to overload of Srimangal - Fenchuganj ckt.
|  | 12:09 | Shahjibazar-Sreemangal 132kV Ckt-2 is restored.
| 12:18 |  | Kabirpur 132/33kV S/S Reserve bus Scheduled S/D Due to Reserve BUS DS changing work of
Manikganj Ckt-1&2.
| 13:00 |  | Chandpur 132/33kV S/S 402T (T-01) LT Forced S/D Due to Loadshare
| 13:13 | 14:42 | Candpur (Desh)- Chandpur 132kV Ckt-1 Scheduled S/D from Chandpur 132/33kV end Due to DS
maintenance
|  | 13:40 | Muktagacha 132/33kV S/S T-1(404T) HT is restored.
|  | 13:42 | Muktagacha 132/33kV S/S T-1(404T) LT is restored.
| 13:55 |  | Muktagacha 132/33kV S/S T-2(414T) LT Project Work S/D
| 14:03 |  | Muktagacha 132/33kV S/S T-2(414T) HT Project Work S/D
| 14:26 | 14:34 | Sholosohor 132/33kV S/S TRAFO-02 LT Forced S/D Due to To remove bird nest from 33kV | [7 empty] | 10.0MW load
|  |  | gantry which is directly above the auxiliary Transformer-02. | [7 empty] | interrup.
| 15:02 | 17:34 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 Project Work S/D from Purbasadipur 132/33kV end
Due to Project work
|  | 15:35 | Amtali 400/132kV S/S Amtali - RNPL 400 kV Ckt - 2 is restored.
| 15:59 | 16:31 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing Ph Y, Z1, DIST. Send. relays
Due to Rainning
| 16:25 | 18:30 | Sonargaon 132/33kV S/S Tr-2 LT Tripped showing MVAJ relays Due to 33 kv narsingdi feeder | [7 empty] | 70.0MW load
|  |  | CB flashing and auxiliary 2 b phase loop out and all the fuses are burn out due to rain. | [7 empty] | interrup.
| 16:30 | 18:31 | Sonargaon 132/33kV S/S Tr-1 LT Tripped showing MVAJ relays Due to 33 kv Barpa, langalband | [7 empty] | 60.0MW load
|  |  | feeder flushing due to rain and auxiliary 1 r phase loop out and lay off to bus, fuses | [7 empty] | interrup.
burn out.
| 16:40 |  | Shahjibazar-Sreemangal 132kV Ckt-1 Forced S/D from Sreemongol 132/33kV end Due to For
over load of Fen ckt-2, command from NLDC.
| 16:40 |  | Shahjibazar-Sreemangal 132kV Ckt-2 Forced S/D from Sreemongol 132/33kV end Due to For
over load of Fen ckt-2, command from NLDC.
|  | 17:24 | Gopalganj 400/132kV S/S 400kV Rooppur is restored.
|  | 17:24 | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-1 is restored.
| 19:22 | 19:38 | Shahjibazar 132/33kV S/S TR-04 LT Tripped showing OC/EF Relay relays Due to Madhabpur-02
Feeder tripped
| 21:00 |  | Evening Peak Generation: 12921 MW.
| 03:57 | 05:21 | Ashuganj-Cumilla(N) 230 kV Ckt-1 Tripped from Cumilla(N) 230/132/33kV end showing Primary
Distance Protection: Mode: RE Value: D 1P Auto reclosure relay for Single Phase Red
LED Auto reclosure relay for three Phase Red LED Secondary Distance Protection A
phase Zone-1 V Fail relays.
| 04:45 | 05:32 | Ashuganj-Cumilla(N) 230 kV Ckt-2 Tripped from Cumilla(N) 230/132/33kV end showing
Secondary Distance Protection C phase Zone-1 V Fail Auto reclosure relay for Single
Phase Red LED Auto reclosure relay for three Phase Red LED relays.
| 06:00 |  | Minimum Generation: 9508 MW.
| 06:34 | 06:34 | Rangpur 132/33kV S/S Auxiliary Transformer-2 LT Scheduled S/D Due to 132kV CT Maintenance
| 06:34 |  | Rangpur 132/33kV S/S T-2 (404T) LT Scheduled S/D Due to 132kV CT Maintenance
| 06:36 | 06:36 | Rangpur 132/33kV S/S Auxiliary Transformer-2 HT Scheduled S/D Due to 132kV CT Maintenance
| 06:36 |  | Rangpur 132/33kV S/S T-2 (404T) HT Scheduled S/D Due to 132kV CT Maintenance
| 06:55 |  | Mymensingh 132/33kV S/S Bus A Project Work S/D Due to Installing Bus loop of solar ckt.
| 07:35 |  | Taraganj 132/33kV S/S Taraganj-Saidpur CKT-02 Project Work S/D Due to OPGW Joint box
connection work purpose
| 07:35 |  | Taraganj 132/33kV S/S Taraganj-Rangpur CKT-02 Project Work S/D
| 07:37 |  | Rangpur-Saidpur 132kV Ckt-2 Project Work S/D from Rangpur 132/33kV end.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 02-03-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0"MW due to gas restriction by Titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 340 | 7840800 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 216528 | Engine Problem
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7024203 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 16 | 469080 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 630720 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 307700 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 355191 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22 | 465600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 479880 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 24 | 594240 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 1180527 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 113 | 1944000 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 545280 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 1202400 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 140488 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 270720 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 410 | 9375454.55 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 410 | 9104000 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 52 | 1406400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1776 | 43553211.55
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 108540 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 577920 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1923420 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 221 | 3029526 | ps availability is less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 270981 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 675382 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 387840 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 29 | 459840 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 465600 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 19363 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 363840 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1163 | 26770906 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 3 | 32160 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 935 | 18203636.36 | ps availability is less
Chattogram Area Total |  |  |  |  | 4898.863 | 2501 | 53288954.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 201 | 4961000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 335 | 7887200 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 7950500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 557280 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 1208491 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 262618 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 24 | 153392 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 102 | 2122467 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 168960 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 154 | 3240000 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 487460 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 418320 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 175680 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 282482 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1385 | 29875850
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 11 | 252480 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7250 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 87 | 1500000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 88 | 1808400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 0 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 82560 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 192 | 3650690
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 35530 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 916000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 728640 | ps availability is less
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 157 | 3624382 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 75 | 1769000 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 41 | 1030080 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 97 | 2348480 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 22 | 500232 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7485000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 344 | 8432000 | Due to Air Filter DP High FGMO not available.
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1117 | 26869344
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 902 | 21075636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 185 | 5000544 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 408960 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1120 | 24072730 | plant availability zero
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2207 | 50557870
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2887000 | plant availability zero
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 1078 | 19725090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5182750 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 276 | 5956000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2685 | -
Barishal Area Total |  |  |  |  | 2700.36 | 1694 | 33753525.91
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 215596 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 25954 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 191 | 4749327 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9280290 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 4144 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 21780 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1444 | 29918118 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 226496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 539930 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2049 | 44981635
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 485971 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 40178.76 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 480056 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 232757 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1203120 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 0 | 2442082.76
Eastern Grid Total |  |  |  |  | 17400.108 | 6971 | 157238049.91
Western Grid Total |  |  |  |  | 10985.595 | 5950 | 131735113.67
National Grid Total |  |  |  |  | 28385.703 | 12921 | 288973163.58
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 02-03-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8820.58 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3622.7 | MW
i) Dhaka area |  |  | 4824.88 |  | MW | i) Khulna area |  |  |  | 1404.8 | MW
ii) Chattogram area |  |  | 1373.7 |  | MW | ii) Barishal area |  |  |  | 375.3 | MW
iii) Cumilla area |  |  | 1184 |  | MW | iii) Rajshahi area |  |  |  | 1169.6 | MW
iv) Mymensingh area |  |  | 998 |  | MW | iv) Rangpur area |  |  |  | 673 | MW
v) Sylhet area |  |  | 440 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12443.28 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 77 | 14:00 | 133 | Nawabganj | 38.2 | 13:00
2 | AKSML | 13.6 | 06:00 | 68 | Hathazari | 69 | 21:00 | 134 | Netrakona | 145 | 18:00
3 | Aftabnagar | 36 | 13:00 | 69 | Hatirjheel | 38 | 14:00 | 135 | New | 73.2 | 14:00
4 | Agargaon | 100 | 13:00 | 70 | Ishurdi | 59 | 13:00 | 136 | Niamatpur | 94 | 09:00
5 | Agrabad | 58 | 21:00 | 71 | Jaldhaka | 64 | 18:00 | 137 | Noapara | 38 | 14:00
6 | Amnura | 36 | 11:00 | 72 | Jamalpur | 112 | 03:00 | 138 | PHP | 9 | 13:00
7 | Ashuganj | 72 | 13:00 | 73 | Jashore | 120 | 18:00 | 139 | Pabna | 75 | 04:00
8 | BSRM | 206 | 17:00 | 74 | Jhenaidah | 84 | 18:00 | 140 | Palashbari | 94 | 17:00
9 | Bagerhat | 72 | 22:00 | 75 | Joydebpur | 137 | 16:00 | 141 | Panchagarh | 49 | 18:00
10 | Bajitpur | 70 | 19:00 | 76 | Joypurhat | 61 | 09:00 | 142 | Patiya | 8 | 19:00
11 | Bakerganj | 11.3 | 21:00 | 77 | Juldah | 14 | 00:00 | 143 | Patuakhali | 45 | 21:00
12 | Bakulia | 80 | 19:30 | 78 | KSRM | 16 | 23:00 | 144 | Payra | 32 | 21:00
13 | Banani | 50.8 | 13:00 | 79 | Kabirpur | 259 | 16:00 | 145 | Postogola | 47 | 13:00
14 | Bangabhaban | 15 | 10:00 | 80 | Kachua | 72 | 18:00 | 146 | Purbachal | 27 | 13:00
15 | Barapukuria | 63 | 13:00 | 81 | Kaliganj | 23 | 18:30 | 147 | Purbasadipur | 114 | 13:00
16 | Barguna | 18 | 22:00 | 82 | Kallyanpur | 99 | 13:00 | 148 | Rahanpur | 26 | 04:00
17 | Barishal | 88 | 14:00 | 83 | Kalurghat | 37 | 14:00 | 149 | Rahim | 39 | 13:00
18 | Barishal-230 | 78 | 19:00 | 84 | Kamrangirchar | 78 | 14:00 | 150 | Rajbari | 59 | 04:00
19 | Baroaulia | 64 | 12:00 | 85 | Kaptai | N/A | N/A | 151 | Rajendrapur | 126 | 16:00
20 | Baroirhat | 47 | 21:00 | 86 | Kasba | 29 | 04:00 | 152 | Rajshahi | 84 | 18:00
21 | Bashundhara | 182 | 14:00 | 87 | Kazla | 105 | 13:00 | 153 | Rajshahi-230 | 60 | 18:00
22 | BashundharaCement | 7 | 00:00 | 88 | Keranigonj | 90 | 14:00 | 154 | Ramganj | 94 | 21:00
23 | Beanibazar | 56 | 13:00 | 89 | Khagrachori | 26 | 18:30 | 155 | Rampur | 34 | 19:00
24 | Benapole | 50 | 09:00 | 90 | Khulna | 51 | 19:30 | 156 | Rangamati | 13 | 18:00
25 | Bhaluka | 141 | 14:00 | 91 | Khulshi | 182 | 14:00 | 157 | Rangpur | 121 | 17:00
26 | Bhandaria | 42 | 20:00 | 92 | Kishoreganj | 106 | 18:00 | 158 | Ruppur | 3.4 | 11:00
27 | Bhangura | 38 | 18:00 | 93 | Kodda | 317 | 17:00 | 159 | SSM | 8 | 23:00
28 | Bheramara(GK) | 48 | 18:00 | 94 | Kulaura | 33 | 21:00 | 160 | Saidpur | 103 | 16:00
29 | Bhulta | 225 | 11:00 | 95 | Kurigram | 64 | 18:00 | 161 | Satkhira | 127 | 18:30
30 | Bog-Sherpur | 62 | 04:00 | 96 | Kushtia | 112 | 19:00 | 162 | Satmasjid | 88 | 19:00
31 | Bogura | 130 | 17:00 | 97 | Laksam | 27 | 13:00 | 163 | Savar | 226 | 15:00
32 | Borhanuddin | 70 | 21:00 | 98 | Lakshmipur | 25 | 00:00 | 164 | SevenRings | 19.21 | 16:00
33 | Brahmanbaria | 110 | 18:30 | 99 | Lalbag | 72 | 13:00 | 165 | ShahCement | 30 | 23:00
34 | Cantonment | 86 | 13:00 | 100 | Lalmonirhat | 50 | 18:00 | 166 | Shahjadpur | 73 | 17:00
35 | Chandina | 12 | 18:30 | 101 | MI_Cement | 16.2 | 00:00 | 167 | Shahjibazar | 100 | 23:00
36 | Chandpur | 62 | 21:00 | 102 | Madanganj | 44 | 00:00 | 168 | Shahmirpur | 58 | 16:00
37 | Chandraghona | 29 | 18:30 | 103 | Madaripur | 84 | 19:00 | 169 | Shariatpur | 62 | 20:00
38 | Chapai | 59 | 13:00 | 104 | Madartek | 66 | 18:00 | 170 | Sherpur | 142 | 18:00
39 | Charsaidpur | 43 | 01:00 | 105 | Madunaghat | 43 | 19:30 | 171 | Shikalbaha | 23 | 00:00
40 | Chauddagram | 62 | 14:00 | 106 | Magura | 52 | 19:00 | 172 | Shitalakhya | 79.7 | 12:00
41 | Chhatak | 28 | 20:00 | 107 | Mahasthangarh | 62 | 10:00 | 173 | Sholosohor | 40 | 14:00
42 | Chowmuhani | 111 | 15:00 | 108 | Maijdee | 39 | 20:00 | 174 | Shyampur | 156 | 00:00
43 | Chuadanga | 85 | 18:00 | 109 | Manikganj | 110 | 19:00 | 175 | Siddhirganj | 124 | 14:00
44 | Coxsbazar | 121 | 21:00 | 110 | Maniknagar | 54 | 14:00 | 176 | Sirajganj | 100 | 10:00
45 | Cumilla(N) | 100 | 18:00 | 111 | Matarbari | 42 | 04:00 | 177 | Sonargaon | 143 | 09:00
46 | Cumilla(S) | 156 | 14:00 | 112 | Matuail | 68 | 15:00 | 178 | Sreemongol | 58 | 17:00
47 | Daganbhuiyan | 31 | 00:00 | 113 | Metrorail_Motijheel | 22 | 18:00 | 179 | Sreepur | 113 | 17:00
48 | Daudkandi | 128 | 20:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Srinagar | 36.8 | 14:00
49 | DhakaUniversity | 66 | 14:00 | 115 | Millgate | 90 | 13:00 | 181 | Sunamganj | 42 | 18:00
50 | Dhamrai | 124 | 11:00 | 116 | Mirpur | 138 | 14:00 | 182 | Sylhet | 39 | 00:00
51 | Dhanmondi | 108.6 | 13:00 | 117 | Mirsorai | 46 | 02:00 | 183 | Sylhet-132 | 98 | 13:00
52 | Dohazari | 82 | 21:00 | 118 | Mirzapur | 42 | 13:00 | 184 | TK | 19 | 18:00
53 | Faridpur | 132 | 19:00 | 119 | Mithapukur | 52 | 04:00 | 185 | Tangail | 156 | 15:00
54 | Fatullah | 96 | 16:00 | 120 | Modern | N/A | N/A | 186 | Taraganj | 19 | 16:00
55 | Fenchuganj | 30 | 18:00 | 121 | Mogbazar | 94.6 | 14:00 | 187 | Tasnim | 30 | 01:00
56 | Feni | 83 | 21:00 | 122 | Mongla | 39 | 15:00 | 188 | Thakurgaon | 80 | 18:00
57 | GPH | 96 | 17:00 | 123 | Motijheel | 46 | 13:00 | 189 | Tongi | 158 | 11:00
58 | Ghatail | 88 | 03:00 | 124 | Muktagacha | 32 | 03:00 | 190 | Ullahpara | 34 | 03:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 88 | 04:00 | 191 | Ullon | 49 | 22:00
60 | Ghorashal-230 | 106 | 22:00 | 126 | Muradnagar | 32 | 20:00 | 192 | Uttara | 74 | 13:00
61 | Goalpara | 27 | 18:00 | 127 | Mymensingh | 195 | 18:00 | 193 | UttaraNew | 33 | 13:00
62 | Gollamari | 86 | 18:30 | 128 | Naogaon | 114 | 12:00 | 194 | Zigatola | 72 | 15:00
63 | Gopalganj | 93 | 19:00 | 129 | Narail | 50 | 19:00
64 | Gulshan | 98 | 13:00 | 130 | Narinda | 62 | 13:00
65 | Halishahar | 79 | 14:00 | 131 | Narshingdi | 160 | 19:30
66 | HaripurSBU | 129 | 07:00 | 132 | Natore | 121 | 04:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 02-03-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 11761.19 | 0 |  | 11761.19
1:00 | 11156.43 | 0 |  | 11156.43
2:00 | 10710.26 | 0 |  | 10710.26
3:00 | 10831.96 | 0 |  | 10831.96
4:00 | 11654.83 | 0 |  | 11654.83
5:00 | 10753.75 | 0 |  | 10753.75
6:00 | 9870.23 | 0 |  | 9870.23
7:00 | 10123.2 | 0 |  | 10123.2
8:00 | 10624.02 | 0 |  | 10624.02
9:00 | 11418.65 | 0 |  | 11418.65
10:00 | 11750 | 0 |  | 11750
11:00 | 12113.23 | 0 |  | 12113.23
12:00 | 12529.17 | 0 |  | 12529.17
13:00 | 13006.27 | 0 |  | 13006.27
14:00 | 13169.37 | 0 |  | 13169.37
15:00 | 12902.29 | 0 |  | 12902.29
16:00 | 12457.55 | 0 |  | 12457.55
17:00 | 12586.23 | 0 |  | 12586.23
18:00 | 12370.47 | 0 |  | 12370.47
19:00 | 12662.7 | 22 |  | 12685.7
19:30 | 12666 | 19 |  | 12686
20:00 | 12806 | 15 |  | 12822
21:00 | 12921 | 0 |  | 12921
22:00 | 12726 | 0 |  | 12726
23:00 | 12411 | 0 |  | 12411
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 02-03-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6292 | 5469.19 | 11761.19 | DAILY GENERATION CURVE
00:30 | 6156.7 | 5302.11 | 11458.81
01:00 | 6021.4 | 5135.03 | 11156.43 | 02-03-2026
01:30 | 5833.75 | 5099.595 | 10933.345
02:00 | 5646.1 | 5064.16 | 10710.26
02:30 | 5675.75 | 5095.36 | 10771.11
03:00 | 5705.4 | 5126.56 | 10831.96
03:30 | 5970.45 | 5272.945 | 11243.395
04:00 | 6235.5 | 5419.33 | 11654.83
04:30 | 6003.75 | 5200.54 | 11204.29
05:00 | 5772 | 4981.75 | 10753.75
05:30 | 5562 | 4749.99 | 10311.99
06:00 | 5352 | 4518.23 | 9870.23
06:30 | 5462.63 | 4534.085 | 9996.715
07:00 | 5573.26 | 4549.94 | 10123.2
07:30 | 5667.17 | 4706.44 | 10373.61
08:00 | 5761.08 | 4862.94 | 10624.02
08:30 | 5920.865 | 5100.47 | 11021.335
09:00 | 6080.65 | 5338 | 11418.65
09:30 | 6092.17 | 5492.155 | 11584.325
10:00 | 6103.69 | 5646.31 | 11750
10:30 | 6252.665 | 5678.95 | 11931.615
11:00 | 6401.64 | 5711.59 | 12113.23
11:30 | 6577.11 | 5744.09 | 12321.2
12:00 | 6752.58 | 5776.59 | 12529.17
12:30 | 6969.325 | 5798.395 | 12767.72
13:00 | 7186.07 | 5820.2 | 13006.27
13:30 | 7258.29 | 5829.53 | 13087.82
14:00 | 7330.51 | 5838.86 | 13169.37
14:30 | 7279.75 | 5756.08 | 13035.83
15:00 | 7228.99 | 5673.3 | 12902.29
15:30 | 7136.24 | 5543.68 | 12679.92
16:00 | 7043.49 | 5414.06 | 12457.55
16:30 | 7131.075 | 5390.815 | 12521.89
17:00 | 7218.66 | 5367.57 | 12586.23
17:30 | 7057.43 | 5420.92 | 12478.35
18:00 | 6896.2 | 5474.27 | 12370.47
18:30 | 6965.45 | 5551.135 | 12516.585
19:00 | 7034.7 | 5628 | 12662.7
19:30 | 6954 | 5712 | 12666
20:00 | 6996 | 5810 | 12806
20:30 | 6983.5 | 5880 | 12863.5 |  | Executive Engineer
21:00 | 6971 | 5950 | 12921 |  | Network Operation Division
21:30 | 6867 | 5956.5 | 12823.5
22:00 | 6763 | 5963 | 12726
22:30 | 6651.5 | 5917 | 12568.5
23:00 | 6540 | 5871 | 12411

## En-Curve
QF-LDC-12
Date | 02-03-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3337 | 1627 | 892 | 0 | 132 | 1448.19 | 80 | 3840 | 0 | 43 | 362 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3289 | 1606.5 | 892 | 0 | 126 | 1385.61 | 80 | 3783.5 | 0 | 34 | 262.2 | 0 | 0 | 0 | 0 | 02-03-2026
01:00 | 3241 | 1586 | 892 | 0 | 120 | 1323.03 | 80 | 3727 | 0 | 25 | 162.4 | 0 | 0 | 0 | 0
01:30 | 3153 | 1518 | 894.5 | 0 | 123 | 1323.095 | 80 | 3654 | 0 | 25 | 162.75 | 0 | 0 | 0 | 0 | Energy Generated | 288.9732 |  | MKWHr
02:00 | 3065 | 1450 | 897 | 0 | 126 | 1323.16 | 80 | 3581 | 0 | 25 | 163.1 | 0 | 0 | 0 | 0 | Energy not Served | 0.037 |  | MKWHr
02:30 | 3065 | 1461.5 | 899.5 | 0 | 123 | 1324.36 | 80 | 3582.5 | 0 | 42.5 | 192.75 | 0 | 0 | 0 | 0 | Total Energy Requirement | 289.0102 |  | MKWHr
03:00 | 3065 | 1473 | 902 | 0 | 120 | 1325.56 | 80 | 3584 | 0 | 60 | 222.4 | 0 | 0 | 0 | 0
03:30 | 3202 | 1589 | 902 | 0 | 121 | 1367.945 | 80 | 3695.5 | 0 | 53.5 | 232.45 | 0 | 0 | 0 | 0
04:00 | 3339 | 1705 | 902 | 0 | 122 | 1410.33 | 80 | 3807 | 0 | 47 | 242.5 | 0 | 0 | 0 | 0
04:30 | 3223.5 | 1656 | 902 | 0 | 124 | 1364.04 | 80 | 3611.5 | 0 | 38 | 205.25 | 0 | 0 | 0 | 0
05:00 | 3108 | 1607 | 902 | 0 | 126 | 1317.75 | 80 | 3416 | 0 | 29 | 168 | 0 | 0 | 0 | 0
05:30 | 3038 | 1580 | 902 | 0 | 119 | 1217.49 | 80 | 3227.5 | 0 | 16.5 | 131.5 | 0 | 0 | 0 | 0
06:00 | 2968 | 1553 | 902 | 0 | 112 | 1117.23 | 80 | 3039 | 0 | 4 | 95 | 0 | 0 | 0 | 0
06:30 | 3021.5 | 1606.5 | 870.5 | 0 | 111 | 1117.605 | 80 | 3073.5 | 16.61 | 4 | 95.5 | 0 | 0 | 0 | 0
07:00 | 3075 | 1660 | 839 | 0 | 110 | 1117.98 | 80 | 3108 | 33.22 | 4 | 96 | 0 | 0 | 0 | 0
07:30 | 3051.5 | 1687 | 770 | 0 | 116 | 1190.795 | 80 | 3239.5 | 81.815 | 19 | 138 | 0 | 0 | 0 | 0
08:00 | 3028 | 1714 | 701 | 0 | 122 | 1263.61 | 80 | 3371 | 130.41 | 34 | 180 | 0 | 0 | 0 | 0
08:30 | 3031 | 1707 | 785 | 0 | 121 | 1291.305 | 80 | 3529.5 | 188.03 | 59.5 | 229 | 0 | 0 | 0 | 0
09:00 | 3034 | 1700 | 869 | 0 | 120 | 1319 | 80 | 3688 | 245.65 | 85 | 278 | 0 | 0 | 0 | 0
09:30 | 3013.5 | 1692 | 886 | 0 | 120 | 1322 | 80 | 3753.5 | 321.325 | 108.5 | 287.5 | 0 | 0 | 0 | 0
10:00 | 2993 | 1684 | 903 | 0 | 120 | 1325 | 80 | 3819 | 397 | 132 | 297 | 0 | 0 | 0 | 0
10:30 | 3010.5 | 1682.75 | 903 | 0 | 124 | 1231 | 80 | 3859 | 461.365 | 181.5 | 398.5 | 0 | 0 | 0 | 0
11:00 | 3028 | 1681.5 | 903 | 0 | 128 | 1137 | 80 | 3899 | 525.73 | 231 | 500 | 0 | 0 | 0 | 0
11:30 | 3038.5 | 1694 | 902.5 | 0 | 135 | 1126.5 | 80 | 3931.5 | 527.2 | 252.5 | 633.5 | 0 | 0 | 0 | 0
12:00 | 3049 | 1706.5 | 902 | 0 | 142 | 1116 | 80 | 3964 | 528.67 | 274 | 767 | 0 | 0 | 0 | 0
12:30 | 3047.5 | 1702.75 | 902.5 | 0 | 150 | 1116.5 | 80 | 3997.5 | 519.47 | 311 | 940 | 0 | 0 | 0.5 | 0
13:00 | 3046 | 1699 | 903 | 0 | 158 | 1117 | 80 | 4031 | 510.27 | 348 | 1113 | 0 | 0 | 1 | 0
13:30 | 3026.5 | 1683.5 | 902.5 | 0 | 159 | 1119 | 80 | 4096.5 | 483.82 | 349 | 1186.5 | 0 | 0 | 1.5 | 0
14:00 | 3007 | 1668 | 902 | 0 | 160 | 1121 | 80 | 4162 | 457.37 | 350 | 1260 | 0 | 0 | 2 | 0
14:30 | 2995.5 | 1624 | 902.5 | 0 | 155 | 1122.5 | 80 | 4133 | 416.83 | 352 | 1252.5 | 0 | 0 | 2 | 0
15:00 | 2984 | 1580 | 903 | 0 | 150 | 1124 | 80 | 4104 | 376.29 | 354 | 1245 | 0 | 0 | 2 | 0
15:30 | 3027.5 | 1569.5 | 903 | 0 | 150 | 1076.5 | 80 | 4099.5 | 297.72 | 299 | 1173.2 | 0 | 0 | 4 | 0
16:00 | 3071 | 1559 | 903 | 0 | 150 | 1029 | 80 | 4095 | 219.15 | 244 | 1101.4 | 0 | 0 | 6 | 0
16:30 | 3169 | 1636.5 | 902.5 | 0 | 146 | 1023.5 | 80 | 4076.5 | 148.59 | 281.5 | 1052.8 | 0 | 0 | 5 | 0
17:00 | 3267 | 1714 | 902 | 0 | 142 | 1018 | 80 | 4058 | 78.03 | 319 | 1004.2 | 0 | 0 | 4 | 0
17:30 | 3199.5 | 1673 | 902 | 0 | 137 | 1061 | 80 | 4094 | 39.15 | 312.5 | 976.2 | 0 | 0 | 4 | 0
18:00 | 3132 | 1632 | 902 | 0 | 132 | 1104 | 80 | 4130 | 0.27 | 306 | 948.2 | 0 | 0 | 4 | 0
18:30 | 3306 | 1594 | 845.5 | 0 | 140 | 1167.5 | 80 | 4182.5 | 0.135 | 273.5 | 923.45 | 0 | 0 | 4 | 11
19:00 | 3480 | 1556 | 789 | 0 | 148 | 1231 | 80 | 4235 | 0 | 241 | 898.7 | 0 | 0 | 4 | 22
19:30 | 3424 | 1565 | 714 | 0 | 148 | 1336 | 80 | 4292 | 0 | 206 | 895 | 0 | 0 | 6 | 19
20:00 | 3433 | 1634 | 714 | 0 | 148 | 1428 | 80 | 4316 | 0 | 206 | 842 | 0 | 0 | 5 | 15
20:30 | 3434 | 1669 | 808 | 0 | 151 | 1436 | 80 | 4444 | 0 | 187 | 650.5 | 0 | 0 | 4 | 7.5
21:00 | 3435 | 1704 | 902 | 0 | 154 | 1444 | 80 | 4572 | 0 | 168 | 459 | 0 | 0 | 3 | 0
21:30 | 3396.5 | 1718.75 | 902 | 0 | 155 | 1447.5 | 80 | 4573 | 0 | 168 | 381.25 | 0 | 0 | 1.5 | 0
22:00 | 3358 | 1733.5 | 902 | 0 | 156 | 1451 | 80 | 4574 | 0 | 168 | 303.5 | 0 | 0 | 0 | 0
22:30 | 3308 | 1701.25 | 902 | 0 | 152 | 1451 | 80 | 4559 | 0 | 156 | 259.25 | 0 | 0 | 0 | 0
23:00 | 3258 | 1669 | 902 | 0 | 148 | 1451 | 80 | 4544 | 0 | 144 | 215 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 02-03-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 404 | 06:00 | 373 | 12:00 | Madunaghat | 405 | 07:00 | 394 | 22:00
Amtali | 419 | 06:00 | 408 | 14:00 | Meghnaghat | 402 | 06:00 | 378 | 12:00
Ashuganj | 411 | 06:00 | 394 | 21:00 | Payra | 420 | 06:00 | 411 | 17:00
Bhulta | 410 | 18:00 | 385 | 10:00 | Rahanpur | 418 | 06:00 | 388 | 10:00
Bibiana | 411 | 05:00 | 402 | 09:00 | Rampal | 412 | 06:00 | 394 | 11:00
BIPTC | 402 | 07:00 | 390 | 11:00
Bogura | 409 | 18:30 | 378 | 10:00
Gopalganj | 411 | 06:00 | 394 | 21:00
Kaliakoir | 397 | 06:00 | 360 | 10:00
Korerhat | 408 | 06:00 | 391 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 235 | 18:00 | 213 | 10:00 | Jhenaidah | 236 | 06:00 | 224 | 21:00
AKSML | 232 | 06:00 | 222 | 21:00 | Kachua | 233 | 06:00 | 223 | 23:00
Aminbazar | 235 | 18:30 | 210 | 10:00 | Kaliakoir | 240 | 18:00 | 213 | 10:00
Ashuganj | 266 | 13:00 | 218 | 10:00 | Keranigonj | 234 | 18:00 | 213 | 10:00
Ashuganj-400 | 266 | 13:00 | 218 | 10:00 | Khulna(S) | 238 | 06:00 | 223 | 21:00
Baghabari | 236 | 04:00 | 221 | 09:00 | Korerhat | 230 | 04:00 | 226 | 09:00
Barapukuria | 226 | 18:30 | 201 | 13:00 | Madunaghat | 230 | 04:00 | 224 | 21:00
Barapukuria-230 | 226 | 18:30 | 201 | 13:00 | Madunaghat-400 | 231 | 07:00 | 224 | 22:00
Barishal | 234 | 06:00 | 226 | 14:00 | Maniknagar | 234 | 06:00 | 219 | 10:00
Bheramara | 234 | 06:00 | 224 | 09:00 | Meghnaghat | 245 | 03:00 | 228 | 10:00
Bhulta | 237 | 18:00 | 220 | 10:00 | Meghnaghat-400 | 237 | 06:00 | 223 | 10:00
Bibiana | 239 | 06:00 | 232 | 08:00 | Mirsorai | 232 | 06:00 | 223 | 12:00
BIPTC | 237 | 06:00 | 225 | 09:00 | Rajshahi | 234 | 02:00 | 223 | 09:00
Bogura | 238 | 06:00 | 220 | 10:00 | Rampal | 237 | 06:00 | -230 | 19:30
Bogura-400 | 237 | 18:30 | 219 | 10:00 | Rampur | N/A | N/A | N/A | N/A
Borhanuddin | 236 | 01:00 | 232 | 13:00 | Rampura | 234 | 18:00 | 218 | 11:00
BSRM | 232 | 06:00 | 222 | 12:00 | Shikalbaha | 229 | 05:00 | 221 | 23:00
Chowmuhani | N/A | N/A | N/A | N/A | Shyampur | 235 | 18:00 | 219 | 10:00
Cumilla(N) | 234 | 06:00 | 221 | 11:00 | Siddhirganj | 235 | 06:00 | 228 | 21:00
Faridpur | 230 | 05:00 | 221 | 14:00 | Sirajgonj | 239 | 06:00 | 228 | 09:00
Fenchuganj | 241 | 06:00 | 236 | 09:00 | Sreepur | 227 | 05:00 | 213 | 10:00
Feni | 233 | 06:00 | 225 | 09:00 | Tongi | 232 | 04:00 | 212 | 09:00
Ghorashal | 242 | 02:00 | 225 | 15:00
Ghorashal-230 | 231 | 18:30 | 212 | 10:00
Gopalganj | 231 | 06:00 | 221 | 21:00
GPH | 231 | 06:00 | 222 | 22:00
Haripur | 235 | 06:00 | 220 | 10:00
Hasnabad | 234 | 18:00 | 220 | 11:00
Hathazari | 228 | 18:00 | 222 | 21:00
Ishurdi | 237 | 06:00 | 227 | 09:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 18:00 | 124 | 10:00 | Magura | 136 | 06:00 | 126 | 09:00
Agargaon | 140 | 18:00 | 120 | 10:00 | Mahasthangarh | 135 | 06:00 | 122 | 09:00
Agrabad | 133 | 05:00 | 127 | 12:00 | Maijdee | 129 | 05:00 | 124 | 15:00
AKS | 131 | 06:00 | 126 | 00:00 | Manikganj | 134 | 16:00 | 123 | 10:00
Aminbazar | 137 | 18:30 | 120 | 10:00 | Maniknagar | 133 | 18:00 | 121 | 10:00
Amnura | 137 | 02:00 | 125 | 09:00 | Matarbari | 123 | 06:00 | 112 | 22:00
Ashuganj | 140 | 05:00 | 133 | 10:00 | Matuail | 133 | 06:00 | 124.2 | 10:00
Bagerhat | 134 | 06:00 | 121 | 21:00 | Metrorail_Motijheel | 133 | 18:00 | 121 | 10:00
Bajitpur | 133 | 18:00 | 126 | 10:00 | Metrorail_Uttara | 139 | 18:00 | 118 | 10:00
Bakerganj | 137 | 06:00 | 131 | 14:00 | Millgate | 134 | 02:00 | 120 | 10:00
Bakulia | 132 | 16:00 | 127 | 21:00 | Mirpur | 137 | 18:00 | 121 | 10:00
Banani | 135 | 06:00 | 125 | 09:00 | Mirzapur | 135 | 18:00 | 122 | 10:00
Bangabhaban | 130 | 04:00 | 121 | 10:00 | Mithapukur | 135 | 18:30 | 25 | 12:00
Barapukuria | 139 | 18:30 | 123 | 09:00 | MI_Cement | 134 | 18:30 | 123 | 10:00
Barguna | 137 | 06:00 | 131 | 13:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 136 | 06:00 | 130 | 14:00 | Mogbazar | 135 | 05:00 | 127 | 10:00
Barishal-230 | 136 | 06:00 | 131 | 12:00 | Mongla | 133 | 05:00 | 122 | 13:00
Baroaulia | 132 | 16:00 | 128 | 21:00 | Motijheel | 130 | 04:00 | 121 | 10:00
Baroirhat | 132 | 04:00 | 126 | 12:00 | Muktagacha | 131 | 05:00 | 114 | 13:00
Bashundhara | 134 | 02:00 | 124 | 10:00 | Munshiganj | 134 | 18:00 | 124 | 11:00
BashundharaCement | 132 | 03:00 | 124 | 10:00 | Muradnagar | 132 | 06:00 | 125 | 10:00
Beanibazar | 132 | 06:00 | 127 | 13:00 | Mymensingh | 131 | 06:00 | 115 | 10:00
Benapole | 132 | 06:00 | 116 | 14:00 | Naogaon | 135 | 06:00 | 121 | 10:00
Bhaluka | 135 | 18:30 | 127 | 09:00 | Narail | 135 | 06:00 | 126 | 09:00
Bhandaria | 135 | 07:00 | 125 | 22:00 | Narinda | 123 | 06:00 | 112 | 22:00
Bhangura | 137 | 05:00 | 126 | 10:00 | Narshingdi | 132 | 18:00 | 120 | 10:00
Bheramara | 137 | 02:00 | 132 | 09:00 | Natore | 136 | 06:00 | 128 | 10:00
Bheramara(GK) | 137 | 05:00 | 131 | 09:00 | Nawabganj | 140 | 18:00 | 124 | 10:00
Bhulta | 128 | 18:00 | 120 | 11:00 | Netrakona | 125 | 06:00 | 117 | 17:00
Bog-Sherpur | 136 | 06:00 | 125 | 10:00 | New | 137 | 18:00 | 121 | 10:00
Bogura | 137 | 05:00 | 127 | 10:00 | Niamatpur | 137 | 03:00 | 127 | 10:00
Bogura-230 | 138 | 06:00 | 126 | 10:00 | Noapara | 135 | 06:00 | 123 | 13:00
Brahmanbaria | 136 | 06:00 | 128 | 10:00 | Pabna | 136 | 02:00 | 129 | 10:00
Cantonment | 139 | 18:00 | 117 | 10:00 | Palashbari | 134 | 05:00 | 121 | 13:00
Chandina | 135 | 06:00 | 128 | 10:00 | Panchagarh | 139 | 18:30 | 122 | 09:00
Chandpur | 131 | 06:00 | 126 | 22:00 | Patiya | 132 | 06:00 | 126 | 23:00
Chandraghona | 135 | 06:00 | 130 | 21:00 | Patuakhali | 135 | 05:00 | 130 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 138 | 06:00 | 125 | 09:00 | Payra | 137 | 05:00 | 133 | 15:00
Charsaidpur | 135 | 18:00 | 124 | 10:00 | PHP | 132 | 06:00 | 126 | 12:00
Chauddagram | 132 | 05:00 | 125 | 12:00 | Postogola | 137 | 18:00 | 125 | 11:00
Chhatak | 130 | 06:00 | 125 | 13:00 | Purbachal | 135 | 05:00 | 124 | 10:00
Chowmuhani | 130 | 06:00 | 13 | 02:00 | Purbasadipur | 130 | 06:00 | 117 | 13:00
Chuadanga | 135 | 06:00 | 125 | 13:00 | Rahanpur | 140 | 06:00 | 133 | 11:00
Coxsbazar | 125 | 04:00 | 113 | 21:00 | Rahanpur-400 | 140 | 06:00 | 130 | 10:00
Cumilla(N) | 135 | 04:00 | 128 | 10:00 | Rahim | 132 | 02:00 | 124 | 10:00
Cumilla(S) | 134 | 05:00 | 118 | 12:00 | Rajbari | 133 | 06:00 | 125 | 14:00
Daganbhuiyan | 131 | 06:00 | 125 | 10:00 | Rajendrapur | 137 | 06:00 | 127 | 10:00
Daudkandi | 131 | 18:00 | 121 | 14:00 | Rajshahi | 136 | 06:00 | 128 | 10:00
DhakaUniversity | 137 | 18:00 | 125 | 10:00 | Rajshahi-230 | 134 | 02:00 | 128 | 22:00
Dhamrai | 141 | 18:30 | 119 | 10:00 | Ramganj | 128 | 06:00 | 123 | 22:00
Dhanmondi | 136.7 | 18:30 | 126 | 10:00 | Rampur | 133 | 06:00 | 126 | 23:00
Dohazari | 130 | 05:00 | 123 | 21:00 | Rampura | 136 | 18:00 | 126 | 09:00
Faridpur | 133 | 05:00 | 127 | 12:00 | Rangamati | 133 | 02:00 | 129 | 21:00
Fatullah | 137 | 18:00 | 121 | 10:00 | Rangpur | 135 | 06:00 | 122 | 17:00
Fenchuganj | 137 | 06:00 | 133 | 13:00 | Ruppur | 138 | 06:00 | 132 | 09:00
Feni | 129 | 06:00 | 125 | 12:00 | Saidpur | 134 | 06:00 | 121 | 17:00
Feni-230 | 131 | 06:00 | 126 | 09:00 | Satkhira | 135 | 06:00 | 122 | 14:00
Ghatail | 130 | 18:00 | 115 | 10:00 | Satmasjid | 139 | 18:30 | 120 | 10:00
Ghorashal | 137 | 02:00 | 132 | 11:00 | Savar | 138 | 18:00 | 117 | 10:00
Goalpara | 138 | 06:00 | 127 | 13:00 | SevenRings | 138 | 03:00 | 128 | 10:00
Gollamari | 138 | 06:00 | 127 | 13:00 | ShahCement | 135 | 18:00 | 124 | 10:00
Gopalganj | 136 | 06:00 | 128 | 12:00 | Shahjadpur | 141 | 04:00 | 130 | 10:00
Gopalganj-400 | 137 | 06:00 | 131 | 13:00 | Shahjibazar | 136 | 19:30 | 125 | 13:00
Gulshan | 135 | 06:00 | 125 | 10:00 | Shahmirpur | 134 | 06:00 | 128 | 23:00
Halishahar | 133 | 06:00 | 128 | 10:00 | Shariatpur | 136 | 05:00 | 128 | 14:00
Haripur | 134 | 18:00 | 125 | 10:00 | Sherpur | 130 | 20:00 | 115 | 10:00
HaripurSBU | 134 | 18:00 | 125 | 11:00 | Shikalbaha | 124 | 07:00 | 118 | 11:00
Hasnabad | 135 | 03:00 | 123 | 10:00 | Shikalbaha-230 | 134 | 05:00 | 128 | 23:00
Hathazari | 135 | 17:00 | 130 | 21:00 | Shitalakhya | 134 | 18:30 | 123 | 10:00
Hatirjheel | 136 | 18:00 | 124 | 10:00 | Sholosohor | 134 | 06:00 | 129 | 21:00
Ishurdi | 139 | 05:00 | 133 | 10:00 | Shyampur | 137 | 18:30 | 131 | 00:00
Jaldhaka | 133 | 06:00 | 119 | 13:00 | Shyampur-230 | 136 | 18:00 | 127 | 10:00
Jamalpur | 133 | 19:30 | 114 | 13:00 | Siddhirganj | 134 | 18:00 | 125 | 10:00
Jashore | 133 | 06:00 | 118 | 14:00 | Sirajganj | 136 | 05:00 | 123 | 10:00
Jhenaidah | 138 | 06:00 | 117 | 13:00 | Sonargaon | 132 | 17:00 | 124 | 02:00
Jhenaidah-230 | 137 | 06:00 | 128 | 10:00 | Sreemongol | 133 | 05:00 | 126 | 13:00
Joydebpur | 135 | 18:00 | 124 | 10:00 | Sreepur | 139 | 06:00 | 130 | 10:00
Joypurhat | 131 | 03:00 | 117 | 10:00 | Srinagar | 139 | 18:30 | 127 | 09:00
Juldah | 133 | 18:00 | 127 | 21:00 | SSM | 136 | 18:00 | 132 | 11:00
Kabirpur | 138 | 02:00 | 114 | 10:00 | Sunamganj | 129 | 06:00 | 123 | 13:00
Kachua | 132 | 06:00 | 127 | 12:00 | Sylhet | 133 | 03:00 | 128 | 13:00
Kaliakoir | 145 | 18:00 | 121 | 10:00 | Sylhet-132 | 130 | 01:00 | 128 | 10:00
Kaliganj | 138 | 04:00 | 129 | 13:00 | Tangail | 132 | 18:00 | 116 | 10:00
Kallyanpur | 138 | 18:00 | 120 | 10:00 | Taraganj | 133 | 06:00 | 121 | 17:00
Kalurghat | 135 | 01:00 | 130 | 10:00 | Tasnim | 130 | 18:00 | 123 | 09:00
Kamrangirchar | 140 | 18:30 | 123 | 10:00 | Thakurgaon | 139 | 18:30 | 120 | 09:00
Kaptai | N/A | N/A | N/A | N/A | TK | 134 | 05:00 | 130 | 10:00
Kasba | 131 | 05:00 | 124 | 10:00 | Tongi | 136 | 04:00 | 124 | 09:00
Kazla | 131 | 06:00 | 121 | 11:00 | Ullahpara | 135 | 06:00 | 126 | 10:00
Keranigonj | 140 | 18:00 | 122 | 10:00 | Ullon | 134 | 03:00 | 126 | 10:00
Khagrachori | 134 | 06:00 | 128 | 21:00 | Uttara | 136 | 18:00 | 122 | 10:00
Khulna | 137 | 06:00 | 125 | 13:00 | UttaraNew | 138 | 18:00 | 118 | 10:00
Khulna(S) | 138 | 06:00 | 128 | 13:00 | Zigatola | 140 | 18:30 | 124 | 10:00
Khulshi | 130 | 03:00 | 126 | 21:00
Kishoreganj | 131 | 06:00 | 124 | 10:00
Kodda | 139 | 18:00 | 121 | 09:00
Korerhat | 133 | 05:00 | 129 | 13:00
KSRM | 133 | 03:00 | 128 | 21:00
Kulaura | 135 | 01:00 | 132 | 13:00
Kurigram | 134 | 18:30 | 117 | 17:00
Kushtia | 132 | 05:00 | 124 | 12:00
Laksam | 131 | 05:00 | 13 | 09:00
Lakshmipur | 129 | 06:00 | 124 | 10:00
Lalbag | 137 | 20:00 | 124 | 10:00
Lalmonirhat | 130 | 03:00 | 120 | 13:00
Madanganj | 132 | 03:00 | 124 | 10:00
Madaripur | 135 | 05:00 | 130 | 14:00
Madartek | 135 | 01:00 | 126 | 12:00
Madunaghat | 135 | 07:00 | 130 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 02-03-2026 | [28 empty] | Date: | 02-03-2026 | [28 empty] | Date: | 02-03-2026 | [28 empty] | Date: | 02-03-2026 | [28 empty] | Date: | 02-03-2026 | [17 empty] | Date: | 02-03-2026
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [17 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 43 | 0 | 70 | 0 | 0 | 15 | 17 | 17 | 0 | 0 | 0 | 345 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 22 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 24 | 720 | 0 | 0 | 24 | 0 | 30 | 150 | 0 | 0 | 0 | 1140 | 0 | 0 | 0 | 393 | 320 | 0 | 51 | 10 | 188 | 0 | 16 | 103 | 16 | 0 | 20 | 0 | 132 | 0 | 0 | 0 | 300 | 0 | 348 | 30 | 30 | 153 | 0 | 20 | 0 | 41 | 0 | 74 | 0 | 98 | 0 | 59 | 49 | 11 | 0 | 0 | 6 | 6292 | 892 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1104 | 0 | 0 | 0 | 1448.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 128 | 220 | 0 | 0 | 605 | 0 | 5469.19 | 11761.19 | 91.35
01:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 15.4 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 22 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 720 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 385 | 320 | 0 | 51 | 10 | 199 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 120 | 0 | 0 | 0 | 315 | 0 | 348 | 30 | 30 | 142 | 0 | 20 | 0 | 41 | 0 | 74 | 0 | 98 | 0 | 58 | 49 | 11 | 0 | 0 | 6 | 6021.4 | 892 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1011 | 0 | 0 | 0 | 1323.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 128 | 180 | 0 | 0 | 560 | 0 | 5135.03 | 11156.43 | 91.34
02:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 16.1 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 22 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 30 | 720 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1086 | 0 | 0 | 0 | 300 | 320 | 0 | 51 | 10 | 196 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 126 | 0 | 0 | 0 | 310 | 0 | 348 | 30 | 30 | 140 | 0 | 20 | 0 | 41 | 0 | 74 | 0 | 98 | 0 | 58 | 49 | 11 | 0 | 0 | 6 | 5646.1 | 897 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1008 | 0 | 0 | 0 | 1323.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 128 | 180 | 0 | 0 | 550 | 0 | 5064.16 | 10710.26 | 91.33
03:00 | 0 | 5 | 16 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 15.4 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 250 | 0 | 0 | 0 | 35 | 22 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 30 | 720 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1080 | 0 | 0 | 0 | 300 | 320 | 0 | 51 | 10 | 200 | 0 | 0 | 51 | 0 | 0 | 20 | 0 | 120 | 0 | 0 | 0 | 305 | 0 | 348 | 30 | 30 | 138 | 0 | 20 | 0 | 41 | 0 | 74 | 0 | 98 | 0 | 97 | 57 | 11 | 0 | 0 | 6 | 5705.4 | 902 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 997 | 0 | 0 | 0 | 1325.56 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 128 | 220 | 0 | 0 | 555 | 0 | 5126.56 | 10831.96 | 91.32
04:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 16.5 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 22 | 21 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 30 | 720 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 350 | 320 | 0 | 51 | 12 | 201 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 122 | 0 | 0 | 0 | 310 | 0 | 342 | 30 | 30 | 157 | 0 | 20 | 0 | 52 | 0 | 75 | 0 | 98 | 0 | 98 | 58 | 11 | 0 | 0 | 0 | 6235.5 | 902 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 0 | 0 | 1410.33 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 128 | 220 | 0 | 0 | 555 | 0 | 5419.33 | 11654.83 | 91.31
05:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 22 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 30 | 720 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 980 | 0 | 0 | 0 | 310 | 320 | 0 | 51 | 28 | 199 | 0 | 0 | 51 | 0 | 0 | 20 | 0 | 126 | 0 | 0 | 0 | 310 | 0 | 342 | 30 | 30 | 157 | 0 | 17 | 0 | 41 | 0 | 76 | 0 | 98 | 0 | 69 | 58 | 16 | 0 | 0 | 0 | 5772 | 902 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1017 | 0 | 0 | 0 | 1317.75 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 100 | 180 | 0 | 0 | 500 | 0 | 4981.75 | 10753.75 | 91.3
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 22 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 30 | 720 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 850 | 0 | 0 | 0 | 300 | 320 | 0 | 51 | 47 | 194 | 0 | 0 | 51 | 0 | 0 | 20 | 0 | 112 | 0 | 0 | 0 | 305 | 0 | 342 | 30 | 30 | 154 | 0 | 17 | 0 | 41 | 0 | 74 | 0 | 98 | 0 | 45 | 45 | 16 | 0 | 0 | 5 | 5352 | 902 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 857 | 0 | 0 | 0 | 1117.23 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 100 | 180 | 0 | 0 | 445 | 0 | 4518.23 | 9870.23 | 91.29
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 280 | 0 | 0 | 1 | 0 | 22 | 21 | 0 | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26 | 80 | 0 | 13 | 720 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 948 | 1 | 0 | 0 | 320 | 320 | 0 | 51 | 53 | 216 | 0 | 0 | 102 | 0 | 0 | 19 | 0 | 110 | 0 | 2 | 0 | 305 | 0 | 342 | 30 | 30 | 143 | 0 | 17 | 0 | 41 | 0 | 74 | 0 | 98 | 0 | 45 | 45 | 16 | 0 | 0 | 6 | 5573.26 | 839 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 813 | 0 | 0 | 0 | 1117.98 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 2.04 | 4 | 0 | 0 | 3.39 | 0 | 0 | 186 | 0 | 0 | 0 | 398 | 0 | 0.32 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.2 | 11 | 0.01 | 0 | 182 | 100 | 220 | 0 | 0 | 445 | 0 | 4549.94 | 10123.2 | 91.28
08:00 | 0 | 5 | 8 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 280 | 0 | 0 | 5 | 17 | 20 | 21 | 0 | 420 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 1.08 | 80 | 0 | 7 | 720 | 0 | 0 | 5 | 0 | 0 | 25 | 0 | 0 | 0 | 1026 | 2 | 0 | 0 | 300 | 300 | 0 | 51 | 53 | 191 | 0 | 0 | 102 | 0 | 0 | 19 | 0 | 122 | 0 | 15 | 0 | 305 | 0 | 342 | 10 | 30 | 140 | 0 | 17 | 0 | 41 | 0 | 75 | 0 | 99 | 0 | 69 | 57 | 16 | 0 | 0 | 6 | 5761.08 | 701 | 218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 888 | 0 | 0 | 0 | 1263.61 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 5.94 | 16 | 0 | 0 | 11.26 | 0 | 0 | 182 | 0 | 0 | 0 | 414 | 0 | 0.66 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 1.4 | 40 | 0.07 | 0 | 247 | 128 | 220 | 0 | 0 | 490 | 0 | 4862.94 | 10624.02 | 91.27
09:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 280 | 0 | 0 | 10 | 52 | 0 | 21 | 0 | 400 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 36 | 36 | 1.65 | 80 | 0 | 6 | 720 | 0 | 0 | 26 | 0 | 0 | 28 | 0 | 0 | 0 | 1160 | 6 | 0 | 0 | 300 | 300 | 0 | 51 | 53 | 209 | 0 | 0 | 102 | 0 | 0 | 19 | 0 | 120 | 0 | 25 | 0 | 310 | 0 | 342 | 10 | 30 | 152 | 1 | 17 | 0 | 41 | 0 | 75 | 0 | 99 | 0 | 69 | 57 | 16 | 1 | 0 | 6 | 6080.65 | 869 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.23 | 980 | 0 | 0 | 0 | 1319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.04 | 33 | 0 | 0 | 12.42 | 0 | 0 | 174 | 0 | 0 | 0 | 408 | 0 | 0.93 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 3.1 | 88 | 0.28 | 0 | 278 | 125 | 220 | 0 | 0 | 550 | 0 | 5338 | 11418.65 | 91.26
10:00 | 0 | 17 | 29 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 280 | 0 | 0 | 13 | 52 | 0 | 20 | 0 | 400 | 0 | 0 | 14 | 0 | 0 | 34 | 0 | 0 | 36 | 36 | 2.69 | 80 | 0 | 2 | 720 | 0 | 0 | 33 | 0 | 0 | 25 | 0 | 0 | 0 | 1152 | 15 | 0 | 0 | 280 | 300 | 0 | 43 | 53 | 204 | 0 | 0 | 102 | 0 | 0 | 19 | 0 | 120 | 0 | 28 | 0 | 310 | 0 | 342 | 14 | 30 | 159 | 3 | 17 | 0 | 41 | 0 | 74 | 0 | 98 | 0 | 69 | 57 | 16 | 1 | 0 | 0 | 6103.69 | 903 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 1042 | 0 | 0 | 0 | 1325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.79 | 71 | 0 | 0 | 15.1 | 0 | 0 | 169 | 0 | 0 | 0 | 414 | 0 | 2.6 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 4.5 | 140 | 0.32 | 0 | 278 | 125 | 220 | 0 | 0 | 627 | 0 | 5646.31 | 11750 | 91.25
11:00 | 0 | 31 | 34 | 0 | 0 | 0 | 0 | 0 | 292 | 0 | 0 | 15 | 17 | 44 | 45 | 45 | 0 | 13 | 48 | 0 | 0 | 0 | 385 | 0 | 0 | 280 | 0 | 0 | 22 | 70 | 16.5 | 20 | 0 | 400 | 0 | 0 | 12 | 0 | 0 | 51 | 0 | 0 | 36 | 36 | 3.14 | 80 | 0 | 4 | 720 | 0 | 0 | 33 | 0 | 2 | 31 | 0 | 0 | 0 | 1160 | 18 | 0 | 0 | 280 | 300 | 0 | 43 | 51 | 207 | 0 | 2 | 99 | 2 | 0 | 16 | 0 | 128 | 0 | 45 | 0 | 315 | 0 | 342 | 42 | 30 | 153 | 8 | 17 | 0 | 41 | 0 | 76 | 0 | 98 | 0 | 69 | 57 | 16 | 1 | 0 | 0 | 6401.64 | 903 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.8 | 1052 | 0 | 0 | 0 | 1137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.96 | 70 | 0 | 0 | 32.75 | 0 | 0 | 199 | 0 | 0 | 0 | 402 | 0 | 3.93 | 0 | 0 | 35 | 31 | 34 | 0 | 0 | 0 | 5.8 | 170 | 0.35 | 0 | 257 | 125 | 220 | 0 | 0 | 710 | 0 | 5711.59 | 12113.23 | 91.24
12:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 20 | 17 | 101 | 89 | 95 | 0 | 35 | 98 | 0 | 0 | 0 | 400 | 0 | 17 | 280 | 0 | 0 | 16 | 70 | 20.5 | 20 | 0 | 400 | 0 | 0 | 20 | 0 | 0 | 47 | 0 | 0 | 50 | 36 | 3.08 | 80 | 0 | 3 | 720 | 0 | 0 | 34 | 0 | 16 | 31 | 0 | 0 | 0 | 1161 | 18 | 0 | 0 | 280 | 300 | 0 | 43 | 53 | 206 | 0 | 16 | 98 | 16 | 0 | 16 | 0 | 142 | 0 | 39 | 0 | 315 | 0 | 342 | 42 | 30 | 158 | 9 | 17 | 0 | 41 | 0 | 75 | 0 | 98 | 0 | 69 | 58 | 10 | 1 | 0 | 0 | 6752.58 | 902 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.69 | 1005 | 0 | 0 | 0 | 1116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.53 | 95 | 0 | 0 | 29.51 | 0 | 0 | 199 | 0 | 0 | 0 | 414 | 0 | 5.05 | 0 | 0 | 35 | 35 | 34 | 0 | 0 | 0 | 6.3 | 186 | 0.51 | 0 | 249 | 125 | 220 | 0 | 0 | 829 | 0 | 5776.59 | 12529.17 | 91.23
13:00 | 0 | 50 | 48 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 46 | 17 | 132 | 130 | 195 | 17 | 35 | 97 | 0 | 0 | 0 | 395 | 0 | 55 | 280 | 0 | 0 | 24 | 70 | 20 | 16 | 0 | 400 | 0 | 0 | 70 | 0 | 1 | 50 | 0 | 0 | 50 | 38 | 3.07 | 80 | 0 | 9 | 720 | 0 | 0 | 46 | 0 | 14 | 46 | 0 | 0 | 0 | 1144 | 17 | 50 | 0 | 280 | 300 | 0 | 43 | 53 | 202 | 0 | 17 | 98 | 17 | 21 | 18 | 0 | 158 | 0 | 49 | 0 | 310 | 0 | 342 | 42 | 30 | 157 | 6 | 17 | 0 | 41 | 0 | 75 | 0 | 98 | 0 | 69 | 58 | 10 | 2 | 0 | 0 | 7186.07 | 903 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 994 | 0 | 0 | 0 | 1117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.92 | 79 | 0 | 0 | 43.32 | 0 | 0 | 195 | 0 | 0 | 0 | 414 | 0 | 5.43 | 0 | 0 | 35 | 33 | 34 | 0 | 0 | 0 | 6 | 184 | 0.53 | 0 | 278 | 125 | 220 | 0 | 0 | 895 | 0 | 5820.2 | 13006.27 | 91.22
14:00 | 0 | 50 | 51 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 47 | 17 | 132 | 130 | 195 | 30 | 35 | 157 | 0 | 0 | 0 | 370 | 0 | 55 | 280 | 0 | 0 | 22 | 70 | 20 | 16 | 0 | 400 | 0 | 0 | 95 | 0 | 2 | 49 | 0 | 0 | 50 | 38 | 1.51 | 80 | 0 | 6 | 720 | 0 | 0 | 48 | 0 | 38 | 79 | 0 | 0 | 0 | 1160 | 15 | 42 | 0 | 280 | 300 | 0 | 43 | 45 | 212 | 0 | 17 | 98 | 15 | 25 | 19 | 0 | 160 | 0 | 27 | 0 | 310 | 0 | 342 | 42 | 30 | 156 | 4 | 22 | 0 | 41 | 0 | 75 | 0 | 98 | 0 | 88 | 67 | 7 | 2 | 0 | 0 | 7330.51 | 902 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.58 | 1040 | 0 | 0 | 0 | 1121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.45 | 72 | 0 | 0 | 42.33 | 0 | 0 | 191 | 0 | 0 | 0 | 348 | 0 | 3.68 | 0 | 0 | 35 | 31 | 34 | 0 | 0 | 0 | 5.5 | 162 | 0.32 | 0 | 277 | 125 | 220 | 0 | 0 | 965 | 0 | 5838.86 | 13169.37 | 91.21
15:00 | 0 | 50 | 51 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 47 | 17 | 130 | 129 | 195 | 30 | 35 | 148 | 0 | 0 | 0 | 346 | 0 | 55 | 280 | 0 | 0 | 10 | 90 | 20 | 20 | 0 | 400 | 0 | 0 | 102 | 0 | 2 | 34 | 0 | 0 | 50 | 38 | 0.99 | 80 | 0 | 6 | 720 | 0 | 0 | 50 | 0 | 48 | 120 | 0 | 0 | 0 | 1140 | 9 | 42 | 0 | 280 | 280 | 0 | 43 | 0 | 197 | 0 | 18 | 98 | 15 | 0 | 20 | 0 | 150 | 0 | 31 | 0 | 315 | 0 | 342 | 42 | 30 | 156 | 4 | 22 | 0 | 52 | 0 | 73 | 0 | 97 | 0 | 89 | 67 | 7 | 1 | 0 | 0 | 7228.99 | 903 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.36 | 1030 | 0 | 0 | 0 | 1124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.84 | 72 | 0 | 0 | 18.11 | 0 | 0 | 190 | 0 | 0 | 0 | 343 | 0 | 1.59 | 0 | 0 | 35 | 22 | 34 | 0 | 0 | 0 | 4.4 | 125 | 0 | 0 | 199 | 110 | 180 | 0 | 0 | 1015 | 0 | 5673.3 | 12902.29 | 91.2
16:00 | 0 | 50 | 24 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 47.4 | 17 | 148 | 46 | 95 | 30 | 35 | 146 | 0 | 0 | 0 | 340 | 0 | 55 | 280 | 0 | 0 | 12 | 90 | 20 | 20 | 0 | 400 | 0 | 0 | 95 | 0 | 6 | 34 | 0 | 0 | 50 | 38 | 1.09 | 80 | 0 | 13 | 720 | 0 | 0 | 50 | 0 | 25 | 197 | 0 | 0 | 0 | 1160 | 3 | 24 | 0 | 280 | 295 | 0 | 43 | 0 | 198 | 0 | 17 | 98 | 15 | 0 | 20 | 0 | 150 | 0 | 11 | 0 | 305 | 0 | 342 | 42 | 30 | 144 | 2 | 22 | 0 | 52 | 0 | 76 | 0 | 97 | 0 | 88 | 57 | 6 | 1 | 0 | 0 | 7043.49 | 903 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.37 | 944 | 0 | 0 | 0 | 1029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.92 | 41 | 0 | 0 | 14.8 | 0 | 0 | 189 | 0 | 0 | 0 | 350 | 0 | 1.39 | 0 | 0 | 35 | 16 | 34 | 0 | 0 | 0 | 2.4 | 69 | 0.18 | 0 | 201 | 100 | 180 | 0 | 0 | 1070 | 0 | 5414.06 | 12457.55 | 91.19
17:00 | 0 | 50 | 24 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 48.2 | 17 | 149 | 46 | 95 | 30 | 35 | 152 | 0 | 0 | 0 | 410 | 0 | 55 | 250 | 0 | 0 | 3 | 125 | 20 | 20 | 0 | 425 | 0 | 0 | 24 | 0 | 4 | 50 | 0 | 0 | 12 | 38 | 0.46 | 80 | 0 | 27 | 720 | 0 | 0 | 50 | 0 | 17 | 220 | 0 | 0 | 0 | 1162 | 2 | 24 | 0 | 320 | 345 | 0 | 51 | 0 | 207 | 0 | 16 | 98 | 16 | 1 | 20 | 0 | 142 | 0 | 6 | 24 | 310 | 0 | 342 | 34 | 30 | 148 | 1 | 22 | 0 | 41 | 0 | 76 | 0 | 97 | 0 | 89 | 67 | 6 | 0 | 0 | 0 | 7218.66 | 902 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 902 | 0 | 0 | 0 | 1018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7 | 16 | 0 | 0 | 6.28 | 0 | 0 | 188 | 0 | 0 | 0 | 414 | 0 | 0.63 | 0 | 0 | 35 | 5 | 34 | 0 | 0 | 0 | 0.9 | 22 | 0.06 | 0 | 204 | 125 | 220 | 0 | 0 | 1070 | 0 | 5367.57 | 12586.23 | 91.19
18:00 | 0 | 34 | 42 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 48.2 | 17 | 149 | 30 | 95 | 15 | 17 | 106 | 0 | 0 | 0 | 465 | 0 | 17 | 240 | 0 | 0 | 0 | 125 | 20 | 20 | 0 | 320 | 0 | 0 | 0 | 0 | 4 | 51 | 0 | 0 | 12 | 12 | 0 | 80 | 0 | 27 | 720 | 0 | 0 | 50 | 0 | 16 | 182 | 0 | 0 | 0 | 1120 | 0 | 24 | 0 | 370 | 320 | 0 | 51 | 0 | 202 | 0 | 15 | 51 | 17 | 25 | 20 | 0 | 132 | 0 | 0 | 24 | 310 | 0 | 342 | 42 | 30 | 156 | 0 | 22 | 0 | 41 | 0 | 75 | 0 | 97 | 0 | 98 | 75 | 8 | 0 | 0 | 0 | 6896.2 | 902 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26 | 990 | 0 | 0 | 0 | 1104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 378 | 0 | 0.01 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 110 | 180 | 0 | 0 | 1070 | 0 | 5474.27 | 12370.47 | 91.17
19:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 24.7 | 17 | 149 | 0 | 95 | 15 | 17 | 105 | 0 | 0 | 0 | 355 | 0 | 17 | 334 | 0 | 0 | 0 | 125 | 22 | 20 | 0 | 340 | 0 | 0 | 0 | 0 | 4 | 51 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 26 | 720 | 0 | 0 | 33 | 0 | 17 | 222 | 0 | 0 | 0 | 1179 | 0 | 0 | 0 | 393 | 350 | 0 | 51 | 0 | 210 | 0 | 16 | 100 | 16 | 61 | 20 | 0 | 148 | 0 | 0 | 24 | 290 | 0 | 343 | 41 | 30 | 149 | 0 | 22 | 0 | 41 | 0 | 74 | 0 | 97 | 0 | 88 | 86 | 11 | 0 | 0 | 2 | 7034.7 | 789 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 978 | 0 | 0 | 0 | 1231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283 | 120 | 220 | 0 | 0 | 1075 | 0 | 5628 | 12662.7 | 91.16
19:30 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 15 | 17 | 149 | 0 | 45 | 15 | 17 | 106 | 0 | 0 | 0 | 390 | 0 | 17 | 335 | 0 | 0 | 0 | 90 | 22 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 6 | 51 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 720 | 0 | 0 | 33 | 0 | 15 | 222 | 0 | 0 | 0 | 1180 | 0 | 0 | 0 | 393 | 330 | 0 | 43 | 0 | 198 | 0 | 16 | 100 | 17 | 112 | 20 | 0 | 148 | 0 | 0 | 24 | 310 | 0 | 344 | 41 | 30 | 158 | 0 | 22 | 0 | 41 | 0 | 75 | 0 | 97 | 0 | 88 | 87 | 11 | 0 | 0 | 6 | 6954 | 714 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1044 | 0 | 0 | 0 | 1336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 120 | 220 | 0 | 0 | 1072 | 0 | 5712 | 12666
20:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 16 | 17 | 149 | 0 | 45 | 15 | 17 | 104 | 0 | 0 | 0 | 400 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 22 | 20 | 0 | 350 | 0 | 0 | 0 | 0 | 5 | 51 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 30 | 720 | 0 | 0 | 33 | 0 | 15 | 220 | 0 | 0 | 0 | 1163 | 0 | 0 | 0 | 393 | 330 | 0 | 43 | 0 | 202 | 0 | 17 | 100 | 16 | 112 | 20 | 0 | 148 | 0 | 0 | 24 | 310 | 0 | 344 | 41 | 30 | 156 | 0 | 22 | 0 | 41 | 0 | 75 | 0 | 97 | 0 | 88 | 87 | 11 | 0 | 0 | 6 | 6996 | 714 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1081 | 0 | 0 | 0 | 1428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 120 | 220 | 0 | 0 | 1075 | 0 | 5810 | 12806 | 91.15
21:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 16 | 17 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 22 | 20 | 0 | 410 | 0 | 0 | 0 | 0 | 3 | 51 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 935 | 0 | 0 | 19 | 0 | 0 | 221 | 0 | 0 | 0 | 1163 | 0 | 0 | 0 | 393 | 335 | 0 | 43 | 0 | 201 | 0 | 0 | 102 | 0 | 113 | 20 | 0 | 154 | 0 | 0 | 24 | 310 | 0 | 344 | 41 | 30 | 157 | 0 | 22 | 0 | 41 | 0 | 75 | 0 | 97 | 0 | 88 | 87 | 11 | 0 | 0 | 6 | 6971 | 902 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 0 | 0 | 0 | 1444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 120 | 220 | 0 | 0 | 1078 | 0 | 5950 | 12921 | 91.14
22:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 16.5 | 17 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 435 | 0 | 0 | 300 | 0 | 0 | 0 | 52 | 20.5 | 20 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 27 | 935 | 0 | 0 | 19 | 0 | 0 | 225 | 0 | 0 | 0 | 1163 | 0 | 0 | 0 | 375 | 305 | 0 | 51 | 0 | 200 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 156 | 0 | 0 | 24 | 310 | 0 | 344 | 41 | 30 | 157 | 0 | 22 | 0 | 41 | 0 | 75 | 0 | 97 | 0 | 88 | 87 | 10 | 0 | 0 | 6 | 6763 | 902 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1122 | 0 | 0 | 0 | 1451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 125 | 220 | 0 | 0 | 1078 | 0 | 5963 | 12726 | 91.13
23:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 15 | 17 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 300 | 0 | 0 | 0 | 52 | 20 | 20 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 31 | 935 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1163 | 0 | 0 | 0 | 385 | 300 | 0 | 51 | 0 | 194 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 148 | 0 | 0 | 0 | 305 | 0 | 344 | 41 | 30 | 149 | 0 | 22 | 0 | 41 | 0 | 76 | 0 | 97 | 0 | 59 | 48 | 10 | 0 | 0 | 6 | 6540 | 902 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1103 | 0 | 0 | 0 | 1451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 125 | 220 | 0 | 0 | 1068 | 0 | 5871 | 12411 | 91.12
Total KWH | 0 | 545280 | 594240 | 0 | 0 | 0 | 0 | 0 | 7840800 | 0 | 0 | 469080 | 270720 | 1944000 | 630720 | 1180527 | 216528 | 307700 | 1202400 | 0 | 0 | 0 | 9104000 | 0 | 355191 | 7024203 | 0 | 0 | 140488 | 1406400 | 465600 | 479880 | 0 | 9375454.55 | 0 | 0 | 465600 | 0 | 32160 | 675382 | 0 | 0 | 387840 | 363840 | 19363 | 1923420 | 0 | 459840 | 18203636.36 | 0 | 0 | 577920 | 0 | 270981 | 3029526 | 0 | 0 | 0 | 26770906 | 108540 | 262618 | 0 | 7950500 | 7887200 | 0 | 1208491 | 557280 | 4961000 | 0 | 175680 | 2122467 | 168960 | 418320 | 487460 | 0 | 3240000 | 0 | 282482 | 153392 | 7485000 | 0 | 8432000 | 916000 | 728640 | 3624382 | 35530 | 500232 | 0 | 1030080 | 0 | 1769000 | 0 | 2348480 | 0 | 1808400 | 1500000 | 252480 | 7250 | 0 | 82560 | 157238049.91 | 21075636 | 5000544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408960 | 24072730 | 0 | 0 | 0 | 29918118 | 0 | 0 | 0 | 0 | 0 | 25954 | 4144 | 0 | 0 | 215596 | 539930 | 0 | 0 | 226496 | 0 | 0 | 4749327 | 0 | 0 | 0 | 9280290 | 0 | 21780 | 0 | 0 | 480056 | 232757 | 485971 | 0 | 0 | 0 | 40178.76 | 1203120 | 2685 | 0 | 5956000 | 2887000 | 5182750 | 0 | 0 | 19725090.91 | 0 | 131735113.67 | 288973163.58