## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 04-03-2026 | [28 empty] | Date: | 04-03-2026 | [28 empty] | Date: | 04-03-2026 | [28 empty] | Date: | 04-03-2026 | [28 empty] | Date: | 04-03-2026 | [17 empty] | Date: | 04-03-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [17 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 300 | 0 | 0 | 0 | 35 | 21 | 20 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 22 | 720 | 0 | 0 | 12 | 0 | 0 | 226 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 345 | 300 | 0 | 51 | 0 | 197 | 0 | 0 | 101 | 0 | 0 | 20 | 0 | 132 | 0 | 0 | 0 | 305 | 0 | 364 | 41 | 30 | 140 | 0 | 21 | 0 | 41 | 0 | 74 | 0 | 99 | 0 | 58 | 48 | 0 | 0 | 0 | 6 | 6152 | 902 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 0 | 0 | 0 | 1284.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 125 | 220 | 0 | 0 | 1000 | 0 | 5585.37 | 11737.37 | 90.9
01:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 21 | 20 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 22 | 720 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1061 | 0 | 0 | 0 | 340 | 285 | 0 | 51 | 0 | 190 | 0 | 0 | 102 | 0 | 0 | 19 | 0 | 126 | 0 | 0 | 0 | 300 | 0 | 353 | 41 | 30 | 134 | 0 | 20 | 0 | 41 | 0 | 75 | 0 | 99 | 0 | 45 | 35 | 0 | 0 | 0 | 6 | 5865 | 902 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 938 | 0 | 0 | 0 | 1118.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 125 | 220 | 0 | 0 | 990 | 0 | 5244.09 | 11109.09 | 90.89
02:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 21 | 20 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 27 | 720 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 340 | 295 | 0 | 51 | 0 | 194 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 126 | 0 | 0 | 0 | 295 | 0 | 329 | 41 | 30 | 134 | 0 | 20 | 0 | 41 | 0 | 76 | 0 | 99 | 0 | 45 | 35 | 0 | 0 | 0 | 6 | 5698 | 902 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 901 | 0 | 0 | 0 | 1022.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 100 | 180 | 0 | 0 | 990 | 0 | 4993.92 | 10691.92 | 90.88
03:00 | 0 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 300 | 0 | 0 | 0 | 52 | 21 | 20 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 27 | 720 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1008 | 0 | 0 | 0 | 340 | 305 | 0 | 51 | 0 | 201 | 0 | 0 | 51 | 0 | 0 | 20 | 0 | 126 | 0 | 0 | 0 | 315 | 0 | 335 | 41 | 30 | 136 | 0 | 20 | 0 | 41 | 0 | 75 | 0 | 99 | 0 | 95 | 57 | 0 | 0 | 0 | 6 | 5837 | 902 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 897 | 0 | 0 | 0 | 1023.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 100 | 180 | 0 | 0 | 993 | 0 | 5038.02 | 10875.02 | 90.87
04:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 21 | 20 | 0 | 350 | 0 | 0 | 0 | 0 | 8 | 34 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 37 | 720 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1144 | 0 | 0 | 0 | 340 | 290 | 0 | 51 | 0 | 194 | 0 | 0 | 104 | 0 | 0 | 20 | 0 | 134 | 0 | 0 | 0 | 305 | 0 | 322 | 41 | 30 | 158 | 0 | 20 | 0 | 41 | 0 | 75 | 0 | 100 | 0 | 98 | 57 | 0 | 0 | 0 | 0 | 6251 | 902 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 976 | 0 | 0 | 0 | 1119.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 120 | 200 | 0 | 0 | 991 | 0 | 5402.11 | 11653.11 | 90.86
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 21 | 20 | 0 | 310 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 33 | 720 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 986 | 0 | 0 | 0 | 300 | 295 | 0 | 51 | 0 | 192 | 0 | 0 | 105 | 0 | 0 | 20 | 0 | 124 | 0 | 0 | 0 | 295 | 0 | 322 | 41 | 30 | 151 | 0 | 20 | 0 | 41 | 0 | 75 | 0 | 100 | 0 | 68 | 57 | 0 | 0 | 0 | 0.5 | 5772.5 | 902 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 912 | 0 | 0 | 0 | 965.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 122 | 200 | 0 | 0 | 735 | 0 | 4810.57 | 10583.07 | 90.85
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 250 | 0 | 0 | 0 | 35 | 21 | 20 | 0 | 310 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 6 | 720 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 838 | 0 | 0 | 0 | 230 | 295 | 0 | 5 | 0 | 193 | 0 | 0 | 49 | 0 | 0 | 20 | 0 | 114 | 0 | 0 | 0 | 300 | 0 | 328 | 41 | 30 | 145 | 0 | 17 | 0 | 11 | 0 | 75 | 0 | 100 | 0 | 45 | 35 | 0 | 0 | 0 | 6 | 5158 | 902 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754 | 0 | 0 | 0 | 829.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 100 | 200 | 0 | 0 | 650 | 0 | 4335.64 | 9493.64 | 90.84
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 250 | 0 | 0 | 2 | 70 | 21 | 20 | 0 | 340 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0.25 | 80 | 0 | 5 | 720 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 845 | 1 | 0 | 0 | 230 | 310 | 0 | 5 | 0 | 205 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 112 | 0 | 6 | 0 | 300 | 0 | 354 | 41 | 30 | 136 | 1 | 17 | 0 | 11 | 0 | 75 | 0 | 100 | 0 | 69 | 57 | 0 | 0 | 0 | 6 | 5320.25 | 902 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 759 | 0 | 0 | 0 | 833.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.01 | 6 | 0 | 0 | 2.83 | 0 | 0 | 150 | 0 | 0 | 0 | 376 | 0 | 0.32 | 0 | 0 | 0 | 1 | 34 | 0 | 0 | 0 | 0 | 10 | 0.04 | 0 | 181 | 100 | 204 | 0 | 0 | 650 | 0 | 4411.39 | 9731.64 | 90.83
08:00 | 0 | 8 | 10 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 6 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 250 | 0 | 0 | 9 | 70 | 20.5 | 20 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.03 | 80 | 0 | 5 | 720 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 860 | 6 | 0 | 0 | 393 | 345 | 0 | 33 | 0 | 166 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 114 | 0 | 22 | 0 | 305 | 0 | 396 | 41 | 30 | 149 | 2 | 17 | 0 | 41 | 0 | 75 | 0 | 100 | 0 | 69 | 57 | 0 | 1 | 0 | 2 | 5877.53 | 667 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 778 | 0 | 0 | 0 | 832.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.28 | 26 | 0 | 0 | 15.31 | 0 | 0 | 194 | 0 | 0 | 0 | 414 | 0 | 1.41 | 0 | 0 | 0 | 8 | 34 | 0 | 0 | 0 | 1.5 | 45 | 0.17 | 0 | 182 | 120 | 208 | 0 | 0 | 675 | 0 | 4437.98 | 10315.51 | 90.82
09:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 64 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 250 | 0 | 0 | 17 | 90 | 20.5 | 20 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.97 | 80 | 0 | 4 | 720 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 995 | 13 | 0 | 0 | 340 | 330 | 0 | 51 | 0 | 142 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 118 | 0 | 41 | 0 | 300 | 0 | 375 | 41 | 30 | 159 | 5 | 17 | 0 | 41 | 0 | 76 | 0 | 99 | 0 | 69 | 57 | 0 | 1 | 0 | 3 | 6109.47 | 902 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 820 | 0 | 0 | 0 | 925.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.91 | 51 | 0 | 0 | 29.4 | 0 | 0 | 195 | 0 | 0 | 0 | 414 | 0 | 2.69 | 0 | 0 | 35 | 17 | 34 | 0 | 0 | 0 | 3 | 88 | 0.33 | 0 | 182 | 120 | 220 | 0 | 0 | 795 | 0 | 5097.16 | 11206.63 | 90.81
10:00 | 0 | 19 | 24 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 87 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 250 | 0 | 0 | 24 | 125 | 20 | 20 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 80 | 0 | 4 | 720 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1100 | 16 | 0 | 0 | 335 | 325 | 0 | 51 | 0 | 144 | 29 | 0 | 100 | 0 | 0 | 20 | 0 | 126 | 0 | 56 | 0 | 310 | 0 | 376 | 41 | 30 | 157 | 8 | 17 | 0 | 42 | 0 | 74 | 0 | 98 | 0 | 69 | 58 | 0 | 2 | 0 | 1 | 6324.8 | 902 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 856 | 0 | 0 | 0 | 923.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.79 | 72 | 0 | 0 | 41.5 | 0 | 0 | 196 | 0 | 0 | 0 | 414 | 0 | 3.93 | 0 | 0 | 50 | 25 | 40 | 0 | 0 | 0 | 4.8 | 122 | 0.49 | 0 | 179 | 120 | 220 | 0 | 0 | 900 | 0 | 5361 | 11685.8 | 90.81
11:00 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 99 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 250 | 0 | 0 | 28 | 108 | 20 | 20 | 0 | 400 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 3.21 | 80 | 0 | 4 | 720 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1102 | 19 | 0 | 0 | 345 | 330 | 0 | 51 | 0 | 217 | 39 | 0 | 99 | 0 | 0 | 20 | 0 | 126 | 0 | 65 | 0 | 310 | 0 | 390 | 42 | 30 | 153 | 10 | 17 | 0 | 42 | 0 | 74 | 0 | 98 | 0 | 69 | 58 | 0 | 2 | 0 | 0 | 6469.21 | 899 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 832 | 0 | 0 | 0 | 923.16 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 43.41 | 88 | 0 | 0 | 50.82 | 0 | 0 | 196 | 0 | 0 | 0 | 414 | 0 | 4.65 | 0 | 0 | 50 | 30 | 64 | 0 | 0 | 0 | 6.2 | 156 | 0.56 | 0 | 180 | 120 | 220 | 0 | 0 | 980 | 0 | 5522.8 | 11992.01 | 90.8
12:00 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 108 | 95 | 0 | 0 | 9 | 16 | 0 | 0 | 0 | 350 | 0 | 0 | 280 | 0 | 0 | 30 | 108 | 20 | 20 | 0 | 400 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 3.42 | 80 | 0 | 3 | 720 | 0 | 0 | 17 | 0 | 0 | 220 | 0 | 0 | 0 | 1140 | 18 | 0 | 0 | 320 | 325 | 0 | 51 | 0 | 208 | 39 | 0 | 97 | 0 | 0 | 20 | 0 | 136 | 0 | 67 | 0 | 310 | 0 | 389 | 42 | 30 | 157 | 10 | 17 | 0 | 41 | 0 | 74 | 0 | 97 | 0 | 69 | 58 | 0 | 2 | 0 | 0 | 6608.42 | 899 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 853 | 0 | 0 | 0 | 1102.39 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 45.99 | 99 | 0 | 0 | 54 | 0 | 0 | 195 | 0 | 0 | 0 | 413 | 0 | 5.08 | 0 | 0 | 50 | 30 | 49 | 0 | 0 | 0 | 6.4 | 166 | 0.46 | 0 | 179 | 120 | 220 | 0 | 0 | 1000 | 0 | 5756.32 | 12364.74 | 90.8
13:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 17 | 0 | 122 | 78 | 30 | 5 | 17 | 15 | 0 | 0 | 0 | 355 | 0 | 0 | 280 | 0 | 0 | 28 | 108 | 20 | 20 | 0 | 400 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 24 | 3.12 | 80 | 0 | 15 | 720 | 0 | 0 | 30 | 0 | 0 | 217 | 0 | 0 | 0 | 1160 | 19 | 0 | 0 | 300 | 325 | 0 | 51 | 0 | 202 | 20 | 0 | 96 | 0 | 0 | 20 | 0 | 138 | 0 | 67 | 0 | 305 | 0 | 392 | 42 | 30 | 154 | 10 | 17 | 0 | 41 | 0 | 75 | 0 | 96 | 10 | 68 | 58 | 0 | 2 | 0 | 0 | 6721.12 | 899 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 938 | 0 | 0 | 0 | 1123.44 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 42.99 | 99 | 0 | 0 | 53 | 0 | 0 | 193 | 0 | 0 | 0 | 414 | 0 | 5.02 | 0 | 0 | 50 | 30 | 49 | 0 | 0 | 0 | 6.2 | 158 | 0.57 | 0 | 230 | 120 | 220 | 0 | 0 | 1000 | 0 | 5897.22 | 12618.34 | 90.79
14:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 16.3 | 0 | 122 | 62 | 30 | 15 | 17 | 16 | 0 | 0 | 0 | 355 | 0 | 0 | 280 | 0 | 0 | 25 | 108 | 20 | 20 | 0 | 400 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 24 | 2.28 | 80 | 0 | 4 | 830 | 0 | 0 | 32 | 0 | 0 | 217 | 0 | 0 | 0 | 1160 | 17 | 0 | 0 | 280 | 335 | 0 | 51 | 0 | 181 | 20 | 0 | 96 | 0 | 0 | 20 | 0 | 148 | 0 | 57 | 0 | 310 | 0 | 392 | 42 | 30 | 154 | 8 | 17 | 0 | 41 | 0 | 74 | 0 | 95 | 17 | 68 | 58 | 0 | 2 | 0 | 0 | 6791.58 | 899 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 977 | 0 | 0 | 0 | 1186.59 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 40.07 | 83 | 0 | 0 | 45.41 | 0 | 0 | 190 | 0 | 0 | 0 | 414 | 0 | 3.87 | 0 | 0 | 50 | 26 | 49 | 0 | 0 | 0 | 3.7 | 140 | 0.49 | 0 | 229 | 120 | 220 | 0 | 0 | 1015 | 0 | 5941.13 | 12732.71 | 90.79
15:00 | 0 | 50 | 32 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 15.8 | 1 | 122 | 62 | 30 | 15 | 17 | 17 | 0 | 0 | 0 | 350 | 0 | 0 | 280 | 0 | 0 | 20 | 108 | 20 | 20 | 0 | 400 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 24 | 1.88 | 80 | 0 | 5 | 890 | 0 | 0 | 32 | 0 | 0 | 217 | 0 | 0 | 0 | 1160 | 13 | 0 | 0 | 230 | 330 | 0 | 51 | 0 | 196 | 20 | 0 | 95 | 0 | 0 | 20 | 0 | 148 | 0 | 45 | 0 | 315 | 0 | 392 | 42 | 30 | 153 | 6 | 20 | 0 | 41 | 0 | 39 | 0 | 95 | 17 | 68 | 58 | 0 | 1 | 22.17 | 0 | 6766.85 | 899 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 1022 | 0 | 0 | 0 | 1226.65 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 30.04 | 63 | 0 | 0 | 38.39 | 0 | 0 | 190 | 0 | 0 | 0 | 414 | 0 | 3.67 | 0 | 0 | 50 | 20 | 48 | 0 | 0 | 0 | 4.2 | 103 | 0.37 | 0 | 229 | 120 | 220 | 0 | 0 | 1045 | 0 | 5967.32 | 12734.17 | 90.78
16:00 | 0 | 50 | 32 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 15.8 | 17 | 122 | 62 | 30 | 15 | 17 | 16 | 0 | 0 | 0 | 355 | 0 | 0 | 280 | 0 | 0 | 11 | 108 | 20 | 20 | 0 | 428 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 24 | 0.99 | 80 | 0 | 10 | 925 | 0 | 0 | 32 | 0 | 0 | 217 | 0 | 0 | 0 | 1168 | 8 | 0 | 0 | 230 | 350 | 0 | 51 | 0 | 213 | 0 | 0 | 96 | 0 | 0 | 20 | 0 | 134 | 0 | 25 | 0 | 315 | 0 | 395 | 42 | 0 | 153 | 4 | 20 | 0 | 41 | 0 | 41 | 0 | 95 | 17 | 58 | 58 | 0 | 1 | 13.3 | 0 | 6784.09 | 899 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 1045 | 0 | 0 | 0 | 1214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.74 | 37 | 0 | 0 | 22.28 | 0 | 0 | 188 | 0 | 0 | 0 | 414 | 0 | 2.09 | 0 | 0 | 50 | 11 | 48 | 0 | 0 | 0 | 2.6 | 58 | 0.22 | 0 | 231 | 120 | 220 | 0 | 0 | 1045 | 0 | 5832.93 | 12617.02 | 90.78
17:00 | 0 | 50 | 32 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 16.9 | 17 | 122 | 62 | 40 | 15 | 17 | 51 | 0 | 0 | 0 | 360 | 0 | 10 | 280 | 0 | 0 | 4 | 125 | 20 | 20 | 0 | 400 | 0 | 0 | 0 | 0 | 3 | 50 | 0 | 0 | 0 | 24 | 0.28 | 80 | 2 | 24 | 925 | 0 | 0 | 32 | 0 | 9 | 217 | 0 | 0 | 0 | 1150 | 3 | 2 | 0 | 230 | 325 | 0 | 51 | 0 | 218 | 0 | 3 | 97 | 7 | 0 | 20 | 0 | 138 | 0 | 10 | 0 | 310 | 0 | 392 | 42 | 0 | 154 | 1 | 20 | 0 | 41 | 0 | 69 | 0 | 95 | 17 | 67 | 58 | 0 | 0 | 4.57 | 0 | 6883.75 | 899 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 1055 | 0 | 0 | 0 | 1319.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7 | 16 | 0 | 0 | 7.45 | 0 | 0 | 185 | 0 | 0 | 0 | 409 | 0 | 0.72 | 0 | 0 | 110 | 4 | 92 | 0 | 0 | 0 | 0.9 | 20 | 0 | 0 | 277 | 120 | 220 | 0 | 0 | 1078 | 0 | 6000.21 | 12883.96 | 90.78
18:00 | 0 | 50 | 32 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 15.8 | 17 | 122 | 62 | 80 | 15 | 17 | 52 | 0 | 0 | 0 | 350 | 0 | 17 | 280 | 0 | 0 | 0 | 142 | 17 | 20 | 0 | 320 | 0 | 0 | 0 | 0 | 3 | 60 | 0 | 0 | 0 | 24 | 0 | 80 | 32 | 27 | 907 | 0 | 0 | 32 | 0 | 50 | 182 | 0 | 0 | 0 | 1085 | 0 | 50 | 0 | 245 | 290 | 0 | 10 | 0 | 192 | 0 | 50 | 90 | 23 | 0 | 20 | 0 | 126 | 0 | 0 | 7 | 305 | 0 | 378 | 33 | 0 | 154 | 0 | 20 | 0 | 41 | 0 | 70 | 0 | 95 | 17 | 77 | 95 | 0 | 0 | 0 | 0 | 6778.8 | 899 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46 | 1042 | 0 | 0 | 0 | 1440.12 | 0 | 0 | 0 | 35 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 115 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 252 | 120 | 180 | 0 | 0 | 1074 | 0 | 5959.58 | 12738.38 | 90.77
19:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 15.8 | 17 | 105 | 0 | 30 | 0 | 0 | 16 | 0 | 0 | 0 | 320 | 0 | 0 | 329 | 0 | 0 | 0 | 142 | 20 | 21 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 80 | 30 | 29 | 925 | 0 | 0 | 0 | 0 | 48 | 225 | 0 | 0 | 0 | 1160 | 0 | 12 | 0 | 350 | 325 | 0 | 31 | 0 | 197 | 0 | 24 | 0 | 17 | 0 | 20 | 0 | 136 | 0 | 0 | 0 | 300 | 0 | 378 | 41 | 0 | 144 | 0 | 20 | 0 | 40 | 0 | 70 | 0 | 97 | 17 | 78 | 95 | 0 | 0 | 0 | 0 | 6669.8 | 899 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 932 | 0 | 0 | 0 | 1447.38 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 115 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 120 | 220 | 0 | 0 | 1048 | 0 | 5959.38 | 12629.18 | 90.76
19:30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 17 | 105 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 353 | 0 | 0 | 331 | 0 | 0 | 0 | 142 | 20 | 21 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 925 | 0 | 0 | 0 | 0 | 15 | 225 | 0 | 0 | 0 | 1145 | 0 | 3 | 0 | 360 | 315 | 0 | 51 | 0 | 192 | 0 | 17 | 0 | 16 | 0 | 20 | 0 | 134 | 0 | 0 | 0 | 305 | 0 | 370 | 41 | 0 | 150 | 0 | 20 | 0 | 41 | 0 | 69 | 0 | 97 | 17 | 94 | 96 | 0 | 0 | 0 | 0 | 6614 | 899 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1030 | 0 | 0 | 0 | 1455.56 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 115 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 120 | 220 | 0 | 0 | 1070 | 0 | 6111.56 | 12725.56 | 90.76
20:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 17 | 105 | 0 | 15 | 0 | 0 | 16 | 0 | 0 | 0 | 355 | 0 | 0 | 330 | 0 | 0 | 0 | 125 | 21 | 21 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 925 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 295 | 335 | 0 | 51 | 0 | 202 | 0 | 16 | 0 | 15 | 0 | 20 | 0 | 136 | 0 | 0 | 0 | 300 | 0 | 406 | 41 | 0 | 145 | 0 | 20 | 0 | 41 | 0 | 71 | 0 | 97 | 17 | 88 | 88 | 0 | 0 | 0 | 1 | 6601 | 899 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 1444.17 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 115 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 120 | 220 | 0 | 0 | 1076 | 0 | 6145.17 | 12746.17 | 90.76
21:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 17 | 105 | 0 | 15 | 0 | 0 | 16 | 0 | 0 | 0 | 374 | 0 | 0 | 330 | 0 | 0 | 0 | 90 | 21 | 21 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 35 | 925 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1170 | 0 | 0 | 0 | 260 | 345 | 0 | 51 | 0 | 192 | 0 | 17 | 0 | 17 | 0 | 20 | 0 | 148 | 0 | 0 | 0 | 310 | 0 | 410 | 41 | 0 | 147 | 0 | 20 | 0 | 41 | 0 | 70 | 0 | 98 | 17 | 88 | 88 | 0 | 0 | 0 | 6 | 6567 | 899 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1124 | 0 | 0 | 0 | 1450.4 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 120 | 220 | 0 | 0 | 1085 | 0 | 6190.4 | 12757.4 | 90.76
22:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 20 | 105 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 365 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 21 | 21 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 32 | 925 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 260 | 325 | 0 | 51 | 0 | 193 | 0 | 16 | 0 | 16 | 0 | 20 | 0 | 150 | 0 | 0 | 0 | 300 | 0 | 376 | 41 | 0 | 158 | 0 | 20 | 0 | 41 | 0 | 70 | 0 | 98 | 17 | 88 | 78 | 0 | 0 | 0 | 6 | 6444 | 899 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1121 | 0 | 0 | 0 | 1443.57 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 120 | 220 | 0 | 0 | 1081 | 0 | 6178.57 | 12622.57 | 90.75
23:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 345 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 21 | 22 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 35 | 720 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 260 | 320 | 0 | 51 | 0 | 193 | 0 | 14 | 0 | 17 | 0 | 20 | 0 | 140 | 0 | 0 | 0 | 300 | 0 | 386 | 41 | 0 | 150 | 0 | 20 | 0 | 41 | 0 | 71 | 0 | 98 | 17 | 58 | 49 | 0 | 0 | 0 | 6 | 6120 | 899 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1090 | 0 | 0 | 0 | 1410.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261 | 120 | 220 | 0 | 0 | 1070 | 0 | 5909.17 | 12029.17 | 90.74
Total KWH | 0 | 588480 | 375360 | 0 | 0 | 0 | 0 | 0 | 8002800 | 0 | 0 | 118800 | 161280 | 1841328 | 638880 | 375862 | 92979 | 127641 | 280800 | 0 | 0 | 0 | 8636800 | 0 | 32970 | 7045530 | 0 | 0 | 198894 | 2068800 | 491400 | 478080 | 0 | 9144545.45 | 0 | 0 | 0 | 0 | 85440 | 475901 | 0 | 0 | 0 | 142080 | 20758 | 1922640 | 77782 | 441120 | 19192727.27 | 0 | 0 | 234240 | 0 | 134655 | 5137616 | 0 | 0 | 0 | 26007270 | 130140 | 92000 | 0 | 7244500 | 8056010 | 0 | 1147102 | 0 | 4769000 | 167400 | 153600 | 1630236 | 122400 | 0 | 515000 | 0 | 3156480 | 0 | 466064 | 13424 | 7404000 | 0 | 8968000 | 980000 | 467520 | 3599918 | 66170 | 468408 | 0 | 896640 | 0 | 1654000 | 0 | 2356960 | 203400 | 1676400 | 1468800 | 0 | 13150 | 44190 | 66000 | 152570370.72 | 21429090 | 4432320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606240 | 22778180 | 0 | 0 | 0 | 27206545 | 0 | 0 | 0 | 78816 | 185952 | 19971 | 0 | 0 | 0 | 307160 | 654150 | 0 | 0 | 361504 | 0 | 0 | 4738691 | 0 | 0 | 0 | 9688436 | 0 | 33600 | 0 | 0 | 1158032 | 203030 | 1222224 | 0 | 0 | 0 | 41298.24 | 1073520 | 3852 | 0 | 5389000 | 2836000 | 5267260 | 0 | 0 | 23749818.18 | 0 | 133464689.42 | 286035060.14

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 05-03-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-03-2026 | during | 05-03-2026 | during | 05-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Demand "0"MW due to gas restriction by Titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 341 | 355 | 412 | 412 | 412 | 412 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 1 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 330 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 95 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 9 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 21 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 20 | 21 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 108 | 105 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 17 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 16 | 16 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 400 | 385 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 350 | 374 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 108 | 90 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1835 | 1746 | 5946.22 | 5915.22 | 3189.05 | 3213.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 17 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 80 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 220 | 225 | 220 | 225 | 220 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 56 | 64 | 56 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 51 | 51 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 3 | 35 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.42 | 0 | 3.57 | 0 | 3.57 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1140 | 1170 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 13 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 720 | 925 | 720 | 720 | 935 | 935 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2214.42 | 2435 | 3609.43 | 3620.86 | 3383.07 | 3394.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 208 | 192 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 325 | 345 | 353.35 | 353.35 | 353.35 | 353.35 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 318.81 | 318.81 | 0 | 0 | FGMO ON
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 320 | 260 | 393 | 393 | 393 | 393 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 39 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 5 | 5 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 42 | 42 | 42 | 42 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 97 | 0 | 163 | 163 | 0 | 0 | Tripped
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 17 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 136 | 148 | 84 | 78 | 84 | 78 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 17 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 67 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1263 | 1050 | 2741.51 | 2680.51 | 1833.55 | 1772.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-03-2026 | during | 05-03-2026 | during | 05-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 88 | 80 | 80 | 60 | 80 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 69 | 88 | 70 | 115 | 70 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 0 | 0 | 45.12 | 0 | 45.12 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 129 | 199 | 431.12 | 429 | 200.12 | 218
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 41 | 42 | 42 | 42 | 42 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 0 | 30 | 30 | 30 | 30 | ps availability is less
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 147 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 74 | 70 | 110 | 110 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 41 | 41 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 97 | 98 | 100 | 100 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 20 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 389 | 410 | 385 | 385 | 385 | 385 | Due to Air Filter DP High FGMO not available.
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1167 | 1137 | 1329 | 1329 | 1166 | 1166
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 899 | 899 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 178 | 165 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 87 | 0 | 89 | 0 | 89 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 853 | 1124 | 0 | 0 | 1148.28 | 1148.28 | plant availability zero
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2017 | 2188 | 2361 | 2272 | 2544.38 | 2455.38
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 0 | 0 | 130 | 130 | Plant availability less
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 1000 | 1085 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 15 | 15 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 179 | 278 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.46 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2700.36 | 1519.46 | 1703 | 1873.32 | 1872.32 | 1868.32 | 1867.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 45.99 | 0 | 50 | 0 | 50 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 4 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown As Per PGB PLC's Requirements.
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 195 | 187 | 220 | 220 | 220 | 220 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 413 | 414 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 40 | 40 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.08 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1102.39 | 1450.4 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 54 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 99 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1918.46 | 2086.4 | 3145.57 | 2928.87 | 2592.57 | 2375.87
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 50 | 50 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 49 | 98 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.4 | 0 | 6.2 | 0 | 6.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 50 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 166 | 0 | 173.72 | 0 | 173.72 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 301.4 | 213 | 521.92 | 312 | 437.92 | 228
System Total |  |  |  |  | 28823.2 | 28385.703 | 12364.74 | 12757.4 | 21959.09 | 21359.78 | 17214.98 | 16690.67
Forecast Scenario (05-03-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11730 |  | 0 |  | 11730
|  |  |  | 1:00 | 11100 |  | 0 |  | 11100
|  |  |  | 2:00 | 10690 |  | 0 |  | 10690
|  |  |  | 3:00 | 10870 |  | 0 |  | 10870
|  |  |  | 4:00 | 11650 |  | 0 |  | 11650
|  |  |  | 5:00 | 10580 |  | 0 |  | 10580
|  |  |  | 6:00 | 9490 |  | 0 |  | 9490
|  |  |  | 7:00 | 9730 |  | 0 |  | 9730
|  |  |  | 8:00 | 10310 |  | 0 |  | 10310
|  |  |  | 9:00 | 11200 |  | 0 |  | 11200
|  |  |  | 10:00 | 11680 |  | 0 |  | 11680
|  |  |  | 11:00 | 11990 |  | 0 |  | 11990
|  |  |  | 12:00 | 12360 |  | 0 |  | 12360
|  |  |  | 13:00 | 12610 |  | 0 |  | 12610
|  |  |  | 14:00 | 12760 |  | 0 |  | 12760
|  |  |  | 15:00 | 12770 |  | 0 |  | 12770
|  |  |  | 16:00 | 12640 |  | 0 |  | 12640
|  |  |  | 17:00 | 12920 |  | 0 |  | 12920
|  |  |  | 18:00 | 12760 |  | 0 |  | 12760
|  |  |  | 18:30 | 12600 |  | 0 |  | 12600
|  |  |  | 19:00 | 12640 |  | 0 |  | 12640
|  |  |  | 19:30 | 12740 |  | 0 |  | 12740
|  |  |  | 20:00 | 12760 |  | 0 |  | 12760
|  |  |  | 21:00 | 12770 |  | 0 |  | 12770
|  |  |  | 22:00 | 12620 |  | 0 |  | 12620
|  |  |  | 23:00 | 12000 |  | 0 |  | 12000
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 12360.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12770.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12770.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 282.63 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:45 hrs on 05-03-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 04-03-2026
Power Supply Scenario
| Day Peak Generation |  |  | 12364.74 | MW | 12:00 Hr. | Energy Generated |  |  | 286.0351 |  | MKWHr.
| Day Peak Demand |  |  | 12364.74 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.206 |  | MKWHr.
| Evening Peak Generation |  |  | 12757.4 | MW | 21:00 Hr. | Energy Demand |  |  | 286.2411 |  | MKWHr.
| Evening Peak Demand |  |  | 12775.4 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32.7 |  | °C
| Minimum Generation of the Day |  |  | 9493.64 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 841.75 |  | MMCFD
| Maximum Generation of the Day |  |  | 12883.96 | MW | 17:00 Hr. | Production Cost per KWHr |  |  | 5.7121 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.7992 | 0 | 6.7032 | 0 | 0 | 0.19889 | 0 | 0 | 40.7012 | Gas | 116.6653 | Gas | 399017314.6365
| Chattogram Zone |  |  | 5.5787 | 45.2 | 1.0647 | 0 | 1.9226 | 0.1509 | 0 | 0.08544 | 54.0024 | Coal | 97.117 | Coal | 631765393.7975
| Cumilla Zone |  |  | 23.5292 | 0 | 0.38142 | 0 | 0 | 0.46606 | 3.1565 | 0 | 27.5332 | HFO | 14.2289 | HFO | 243914296.88
| Mymensingh Zone |  |  | 0 | 0 | 3.4146 | 0 | 0 | 0.05734 | 0 | 0 | 3.4719 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.7954 | 0 | 0 | 0 | 0 | 0.06617 | 0 | 0 | 26.8616 | Hydro | 1.9226 | Hydro | 192264
| Khulna Zone |  |  | 4.4323 | 22.7782 | 0 | 0 | 0 | 0.60624 | 21.4291 | 0 | 49.2458 | Solar | 4.2237 | Solar | 66390496.848
| Barishal Zone |  |  | 8.1033 | 29.1388 | 0 | 0 | 0 | 0.003852 | 0 | 0 | 37.2459 | Import | 51.7921 | Import | 291322457.85
| Rajshahi Zone |  |  | 14.4271 | 0 | 0.28474 | 0 | 0 | 1.3564 | 27.2065 | 0 | 43.2748 | Wind | 0.08544 | Wind | 1256822.4
| Rangpur Zone |  |  | 0 | 0 | 2.3803 | 0 | 0 | 1.3178 | 0 | 0 | 3.6981
| Total |  |  | 116.6653 | 97.117 | 14.2289 | 0 | 1.9226 | 4.2237 | 51.7921 | 0.08544 | 286.0351
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 399017314.6365 |  | Hydro | 192264
|  |  |  | Coal | 631765393.7975 |  | Solar | 66390496.848
|  |  |  | HFO | 243914296.88 |  | Import | 291322457.85
|  |  |  | HSD | 0 |  | Wind | 1256822.4
[5 empty] | Total: | 163,38,59,046 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.4291 | Peak Hr Flow | 899.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 38863054.54 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.2065 | Peak Hr Flow | 1450.40 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2371 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.1565 | Peak Hr Flow | 148.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2436 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 51.7921 | Peak Hr Flow | 2497.40 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4841
|  |  |  | Chattogram |  | 0 |  | 1281
|  |  |  | Cumilla |  | 0 |  | 1139
|  |  |  | Mymensingh |  | 0 |  | 1005
|  |  |  | Sylhet |  | 0 |  | 465
|  |  |  | Khulna |  | 17 |  | 1395
|  |  |  | Barishal |  | 0 |  | 360
|  |  |  | Rajshahi |  | 0 |  | 1190
|  |  |  | Rangpur |  | 0 |  | 712
|  |  |  | Total |  | 17 |  | 12388
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:04 | 11:44 | Rangpur-Saidpur 132kV Ckt-1 Project Work S/D from Rangpur 132/33kV end. and from Saidpur
132/33kV end Due to OPGW work
| 08:04 | 11:44 | Taraganj 132/33kV S/S Taraganj-Rangpur CKT-01 Project Work S/D
| 08:05 | 11:45 | Taraganj 132/33kV S/S Taraganj-Saidpur CKT-01 Project Work S/D
| 08:29 | 15:59 | Chandraghona-Kaptai 132 kV Ckt-1 Scheduled S/D from Chandraghona 132/33kV end Due to
Annual maintenance
|  | 08:40 | Sonargaon 132/33kV S/S Tr-1 HT is restored.
|  | 08:42 | Sonargaon 132/33kV S/S Tr-1 LT is restored.
| 09:10 |  | Bibiyana-Kaliakoir 400 kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to
Line Insulator Disk Cleaning.
| 09:15 | 17:40 | Ghorasal-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end.
| 09:19 | 16:30 | Aminbazar-Meghnaghat 400kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end Due to
Transmission Line maintenance.
| 10:30 | 11:37 | Baroirhat-Hathazari 132 kV Ckt-1 Forced S/D from Hathazari 230/132/33kV end Due to
Hathazari–Korerhat Ckt-01 to carry out Emergency Right of Way work.
|  | 10:30 | Mymensingh 132/33kV S/S Bus B is restored.
| 10:35 | 11:14 | Siddhirganj 132/33kV S/S 120MW EGCB GT2 Tripped showing LBB initiation relays Due to N/A
| 10:35 | 14:32 | Siddhirganj-Ullon (T at Maniknagar) 132kV Ckt-1 Tripped from Siddhirganj 132/33kV end
showing Gen.trip, B-phase pick up,Z-1,Z-2/3, 5.2KM relays Due to N/A
| 10:35 | 11:49 | Haripur-Siddirganj 132kV Ckt-1 Tripped from Haripur 230/132kV end showing DEF, Z3 CN
relays. and from Siddhirganj 132/33kV end showing Dist. relay trip 5.2KM, gen. trip,
R,Y,B-phase trip, Z-1 trip relays Due to N/A
| 10:35 | 11:16 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Tripped showing LBB initiation relays Due to N/A
| 11:09 | 12:11 | Shahmirpur-Sikalbaha 132kV Ckt-2 Scheduled S/D from Shahmirpur 132/33kV end Due to For
Relay Testing
|  | 11:15 | Mymensingh 132/33kV S/S Transformer-3 (424T) LT is restored.
|  | 11:15 | Mymensingh 132/33kV S/S Transformer-3 (424T) HT is restored.
| 11:23 | 18:03 | Natore-Rajshahi 132kV Ckt-1 Scheduled S/D from Natore 132/33kV end.
|  | 12:14 | Mymensingh 132/33kV S/S 50 MW Solar Plant is restored.
| 12:15 | 12:39 | Shahmirpur-Sikalbaha 132kV Ckt-1 Scheduled S/D from Shahmirpur 132/33kV end.
| 12:30 | 13:45 | Sonargaon 132/33kV S/S Tr-1 LT Scheduled S/D Due to PBS 33 MIEZ FEEDER heat shrink | [7 empty] | 52.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 12:31 | 13:44 | Sonargaon 132/33kV S/S Tr-1 HT Scheduled S/D Due to PBS 33 MIEZ FEEDER heat shrink | [7 empty] | 52.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 12:40 | 14:48 | Ashuganj-Cumilla(N) 230 kV Ckt-2 Scheduled S/D from Ashuganj 230/132/33kV end.
| 12:43 | 13:12 | Juldah-Shahmirpur 132kV Ckt-1 Scheduled S/D from Shahmirpur 132/33kV end Due to For
Relay Testing
| 13:11 | 13:19 | Shahjibazar 132/33kV S/S TR-04 LT Tripped showing Trip Relay-1 relays Due to Habiganj
Bypass & Shaistaganj Feeder OC/EF Fault.
| 13:14 | 13:42 | Juldah-Shahmirpur 132kV Ckt-2 Scheduled S/D from Shahmirpur 132/33kV end Due to For
Relay Testing
| 16:37 |  | Rampura-Ullon-2 132kV Ckt-2 Tripped from Rampura 230/132kV end showing Distance , Z1, BN
relays Due to U/G Cable injury
| 05:21 | 05:36 | Bhandaria 132/33kV S/S Transformer-2 LT Tripped showing Over current pro. Trip, K86.1 | [7 empty] | 15.0MW load
|  |  | trip, K86.2 trip relays Due to 33 kV kathalia feeder fault | [7 empty] | interrup.
| 05:21 | 05:21 | Bhandaria 132/33kV S/S Transformer-1 HT Tripped showing K86.1 &k86.2 trip relays Due to | [7 empty] | 15.0MW load
|  |  | Kathalia 33 kv feedar fault | [7 empty] | interrup.
| 05:21 | 05:36 | Bhandaria 132/33kV S/S Transformer-1 LT Tripped showing Over current pro. Trip, | [7 empty] | 15.0MW load
|  |  | K86.1trip, K86.2 trip relays Due to 33kV kathalia feeder fault | [7 empty] | interrup.
| 06:00 |  | Minimum generation 9632 MW
| 06:00 |  | Minimum generation 9632 MW
| 07:10 |  | Daudkandi 132/33kV S/S Transformer-2 LT Scheduled S/D Due to T-2 Shutdown For 33 KV side
Bay Breaker Extention Work by PBS-3 Team.
| 07:12 |  | Daudkandi 132/33kV S/S Transformer-2 HT Scheduled S/D Due to T-2 Shutdown For 33 KV side
Bay Breaker Extention Work by PBS-3 Team.
| 07:20 |  | Hathazari 230/132/33kV S/S AKSML-02 Tripped showing RED 670 REL 670 relays.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 04-03-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0"MW due to gas restriction by Titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 355 | 8002800 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 92979 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 7045530 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 118800 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 638880 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 127641 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 32970 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21 | 491400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 478080 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 375360 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 15 | 375862 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 105 | 1841328 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 588480 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 16 | 280800 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 198894 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 161280 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 385 | 9144545.45 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 374 | 8636800 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 90 | 2068800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1746 | 40701229.45
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 130140 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 234240 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1922640 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 225 | 5137616 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 134655 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 475901 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 35 | 441120 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20758 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 77782 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 142080 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1170 | 26007270 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 85440 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 925 | 19192727.27 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 2435 | 54002369.27
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 192 | 4769000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 345 | 8056010 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 260 | 7244500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 167400 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1147102 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 92000 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 13424 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 1630236 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 122400 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 148 | 3156480 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 515000 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 17 | 153600 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 466064 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1050 | 27533216
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13150 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 88 | 1468800 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 88 | 1676400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 44190 | Annual Maintenance on going
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 66000 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 203400 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 199 | 3471940
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 66170 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 980000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 467520 | ps availability is less
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 147 | 3599918 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 70 | 1654000 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 41 | 896640 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 98 | 2356960 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 20 | 468408 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7404000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 410 | 8968000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1137 | 26861616
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 899 | 21429090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 165 | 4432320 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 606240 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1124 | 22778180 | plant availability zero
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2188 | 49245830
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2836000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 1085 | 23749818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5267260 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 278 | 5389000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3852 | -
Barishal Area Total |  |  |  |  | 2700.36 | 1703 | 37245930.18
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 307160 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 19971 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 187 | 4738691 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9688436 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 185952 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 78816 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 33600 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1450.4 | 27206545 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 361504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 654150 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2086.4 | 43274825
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 1222224 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 41298.24 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1158032 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 203030 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1073520 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 213 | 3698104.24
Eastern Grid Total |  |  |  |  | 17400.108 | 6567 | 152570370.72
Western Grid Total |  |  |  |  | 10985.595 | 6190.4 | 133464689.42
National Grid Total |  |  |  |  | 28385.703 | 12757.4 | 286035060.14
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 04-03-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8731.2 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3640.2 | MW
i) Dhaka area |  |  | 4841.1 |  | MW | i) Khulna area |  |  |  | 1378.5 | MW
ii) Chattogram area |  |  | 1281.1 |  | MW | ii) Barishal area |  |  |  | 360.1 | MW
iii) Cumilla area |  |  | 1139 |  | MW | iii) Rajshahi area |  |  |  | 1189.6 | MW
iv) Mymensingh area |  |  | 1005 |  | MW | iv) Rangpur area |  |  |  | 712 | MW
v) Sylhet area |  |  | 465 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12371.4 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 76 | 19:00 | 133 | Nawabganj | 38.2 | 13:00
2 | AKSML | 16 | 07:00 | 68 | Hathazari | 68 | 18:30 | 134 | Netrakona | 151 | 17:00
3 | Aftabnagar | 32 | 13:00 | 69 | Hatirjheel | 36 | 13:00 | 135 | New | 70 | 12:00
4 | Agargaon | 90 | 13:00 | 70 | Ishurdi | 58 | 18:00 | 136 | Niamatpur | 100 | 13:00
5 | Agrabad | 64 | 13:00 | 71 | Jaldhaka | 66 | 18:00 | 137 | Noapara | 40 | 19:00
6 | Amnura | 36 | 09:00 | 72 | Jamalpur | 107 | 04:00 | 138 | PHP | 8 | 13:00
7 | Ashuganj | 72 | 00:00 | 73 | Jashore | 116 | 18:30 | 139 | Pabna | 73 | 13:00
8 | BSRM | 190 | 13:00 | 74 | Jhenaidah | 82 | 19:00 | 140 | Palashbari | 96 | 18:00
9 | Bagerhat | 67 | 18:30 | 75 | Joydebpur | 131 | 17:00 | 141 | Panchagarh | 49 | 17:00
10 | Bajitpur | 69 | 18:00 | 76 | Joypurhat | 62 | 18:00 | 142 | Patiya | 7.5 | 18:30
11 | Bakerganj | 10.6 | 19:00 | 77 | Juldah | 14.5 | 14:00 | 143 | Patuakhali | 44 | 18:30
12 | Bakulia | 82 | 19:30 | 78 | KSRM | 12 | 00:00 | 144 | Payra | 30 | 18:30
13 | Banani | 47.6 | 13:00 | 79 | Kabirpur | 236 | 12:00 | 145 | Postogola | 46 | 13:00
14 | Bangabhaban | 15 | 10:00 | 80 | Kachua | 67 | 18:30 | 146 | Purbachal | 26 | 13:00
15 | Barapukuria | 62 | 12:00 | 81 | Kaliganj | 22 | 13:00 | 147 | Purbasadipur | 122 | 13:00
16 | Barguna | 16 | 20:00 | 82 | Kallyanpur | 96 | 22:00 | 148 | Rahanpur | 29 | 03:00
17 | Barishal | 82 | 18:00 | 83 | Kalurghat | 39 | 11:00 | 149 | Rahim | 44 | 11:00
18 | Barishal-230 | 72 | 18:30 | 84 | Kamrangirchar | 79 | 13:00 | 150 | Rajbari | 57 | 19:00
19 | Baroaulia | 63 | 14:00 | 85 | Kaptai | N/A | N/A | 151 | Rajendrapur | 124 | 10:00
20 | Baroirhat | 45 | 18:30 | 86 | Kasba | 30 | 04:00 | 152 | Rajshahi | 101 | 18:00
21 | Bashundhara | 174 | 13:00 | 87 | Kazla | 101 | 16:00 | 153 | Rajshahi-230 | 62 | 18:00
22 | BashundharaCement | 13 | 01:00 | 88 | Keranigonj | 84 | 13:00 | 154 | Ramganj | 84 | 18:00
23 | Beanibazar | 52 | 21:00 | 89 | Khagrachori | 28 | 18:30 | 155 | Rampur | 35 | 00:00
24 | Benapole | 50 | 13:00 | 90 | Khulna | 49 | 19:00 | 156 | Rangamati | 15 | 18:30
25 | Bhaluka | 135 | 16:00 | 91 | Khulshi | 161 | 23:00 | 157 | Rangpur | 124 | 17:00
26 | Bhandaria | 40 | 21:00 | 92 | Kishoreganj | 120 | 18:00 | 158 | Ruppur | 3.4 | 15:00
27 | Bhangura | 37 | 18:00 | 93 | Kodda | 314 | 14:00 | 159 | SSM | 1 | 01:00
28 | Bheramara(GK) | 44 | 18:00 | 94 | Kulaura | 34 | 18:30 | 160 | Saidpur | 101 | 17:00
29 | Bhulta | 234 | 11:00 | 95 | Kurigram | 62 | 17:00 | 161 | Satkhira | 121 | 18:30
30 | Bog-Sherpur | 70 | 04:00 | 96 | Kushtia | 114 | 18:00 | 162 | Satmasjid | 87 | 19:00
31 | Bogura | 138 | 18:00 | 97 | Laksam | 24 | 00:00 | 163 | Savar | 204 | 14:00
32 | Borhanuddin | 71 | 21:00 | 98 | Lakshmipur | 16 | 00:00 | 164 | SevenRings | 16.8 | 02:00
33 | Brahmanbaria | 110 | 18:30 | 99 | Lalbag | 70 | 13:00 | 165 | ShahCement | 33 | 00:00
34 | Cantonment | 86 | 17:00 | 100 | Lalmonirhat | 50 | 18:00 | 166 | Shahjadpur | 72 | 17:00
35 | Chandina | 11 | 18:30 | 101 | MI_Cement | 17.4 | 21:00 | 167 | Shahjibazar | 105 | 22:00
36 | Chandpur | 58 | 13:00 | 102 | Madanganj | 42 | 15:00 | 168 | Shahmirpur | 53 | 00:00
37 | Chandraghona | 30 | 18:30 | 103 | Madaripur | 82 | 21:00 | 169 | Shariatpur | 61 | 18:30
38 | Chapai | 67 | 04:00 | 104 | Madartek | 63 | 22:00 | 170 | Sherpur | 136 | 18:00
39 | Charsaidpur | 44 | 15:00 | 105 | Madunaghat | 43 | 21:00 | 171 | Shikalbaha | 27 | 00:00
40 | Chauddagram | 63 | 13:00 | 106 | Magura | 51 | 19:00 | 172 | Shitalakhya | 76.3 | 15:00
41 | Chhatak | 29 | 17:00 | 107 | Mahasthangarh | 76 | 13:00 | 173 | Sholosohor | 40 | 12:00
42 | Chowmuhani | 108 | 18:00 | 108 | Maijdee | 35 | 00:00 | 174 | Shyampur | 168 | 10:00
43 | Chuadanga | 81 | 19:00 | 109 | Manikganj | 104 | 20:00 | 175 | Siddhirganj | 121 | 15:00
44 | Coxsbazar | 129 | 21:00 | 110 | Maniknagar | 53 | 18:00 | 176 | Sirajganj | 100 | 17:00
45 | Cumilla(N) | 100 | 14:00 | 111 | Matarbari | 43 | 18:00 | 177 | Sonargaon | 146 | 21:00
46 | Cumilla(S) | 150 | 22:00 | 112 | Matuail | 71 | 12:00 | 178 | Sreemongol | 57 | 18:30
47 | Daganbhuiyan | 29 | 17:00 | 113 | Metrorail_Motijheel | 31 | 12:00 | 179 | Sreepur | 115 | 16:00
48 | Daudkandi | 118 | 20:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Srinagar | 35.02 | 18:00
49 | DhakaUniversity | 66 | 13:00 | 115 | Millgate | 88 | 12:00 | 181 | Sunamganj | 42 | 17:00
50 | Dhamrai | 128 | 16:00 | 116 | Mirpur | 129 | 14:00 | 182 | Sylhet | 43 | 13:00
51 | Dhanmondi | 104 | 13:00 | 117 | Mirsorai | 43 | 05:00 | 183 | Sylhet-132 | 82 | 21:00
52 | Dohazari | 88 | 18:30 | 118 | Mirzapur | 41 | 18:00 | 184 | TK | 20 | 18:30
53 | Faridpur | 122 | 19:00 | 119 | Mithapukur | 53 | 17:00 | 185 | Tangail | 152 | 17:00
54 | Fatullah | 90 | 15:00 | 120 | Modern | N/A | N/A | 186 | Taraganj | 19 | 12:00
55 | Fenchuganj | 27 | 18:30 | 121 | Mogbazar | 90.4 | 14:00 | 187 | Tasnim | 32 | 15:00
56 | Feni | 80 | 14:00 | 122 | Mongla | 37 | 19:30 | 188 | Thakurgaon | 83 | 17:00
57 | GPH | 21 | 00:00 | 123 | Motijheel | 43 | 13:00 | 189 | Tongi | 144 | 12:00
58 | Ghatail | 82 | 18:00 | 124 | Muktagacha | 35 | 17:00 | 190 | Ullahpara | 42 | 03:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 75 | 13:00 | 191 | Ullon | 47 | 18:00
60 | Ghorashal-230 | 106 | 19:00 | 126 | Muradnagar | 31 | 18:00 | 192 | Uttara | 72 | 13:00
61 | Goalpara | 27 | 19:00 | 127 | Mymensingh | 183 | 17:00 | 193 | UttaraNew | 31 | 13:00
62 | Gollamari | 88 | 19:00 | 128 | Naogaon | 114 | 13:00 | 194 | Zigatola | 62 | 14:00
63 | Gopalganj | 87 | 19:00 | 129 | Narail | 48 | 18:30
64 | Gulshan | 92 | 12:00 | 130 | Narinda | 60 | 13:00
65 | Halishahar | 77 | 14:00 | 131 | Narshingdi | 155 | 21:00
66 | HaripurSBU | 124 | 15:00 | 132 | Natore | 121 | 04:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 04-03-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 11737.37 | 0 |  | 11737.37
1:00 | 11109.09 | 0 |  | 11109.09
2:00 | 10691.92 | 0 |  | 10691.92
3:00 | 10875.02 | 0 |  | 10875.02
4:00 | 11653.11 | 0 |  | 11653.11
5:00 | 10583.07 | 0 |  | 10583.07
6:00 | 9493.64 | 0 |  | 9493.64
7:00 | 9731.64 | 0 |  | 9731.64
8:00 | 10315.51 | 0 |  | 10315.51
9:00 | 11206.63 | 0 |  | 11206.63
10:00 | 11685.8 | 0 |  | 11685.8
11:00 | 11992.01 | 0 |  | 11992.01
12:00 | 12364.74 | 0 |  | 12364.74
13:00 | 12618.34 | 0 |  | 12618.34
14:00 | 12732.71 | 30 |  | 12763.71
15:00 | 12734.17 | 38 |  | 12774.17
16:00 | 12617.02 | 31 |  | 12649.02
17:00 | 12883.96 | 39 |  | 12924.96
18:00 | 12738.38 | 22 |  | 12761.38
19:00 | 12629.18 | 11 |  | 12640.68
19:30 | 12725.56 | 14 |  | 12740.56
20:00 | 12746.17 | 18 |  | 12764.98
21:00 | 12757.4 | 17 |  | 12775.4
22:00 | 12622.57 | 0 |  | 12622.57
23:00 | 12029.17 | 0 |  | 12029.17
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 04-03-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6152 | 5585.37 | 11737.37 | DAILY GENERATION CURVE
00:30 | 6008.5 | 5414.73 | 11423.23
01:00 | 5865 | 5244.09 | 11109.09 | 04-03-2026
01:30 | 5781.5 | 5119.005 | 10900.505
02:00 | 5698 | 4993.92 | 10691.92
02:30 | 5767.5 | 5015.97 | 10783.47
03:00 | 5837 | 5038.02 | 10875.02
03:30 | 6044 | 5220.065 | 11264.065
04:00 | 6251 | 5402.11 | 11653.11
04:30 | 6011.75 | 5106.34 | 11118.09
05:00 | 5772.5 | 4810.57 | 10583.07
05:30 | 5465.25 | 4573.105 | 10038.355
06:00 | 5158 | 4335.64 | 9493.64
06:30 | 5239.125 | 4373.515 | 9612.64
07:00 | 5320.25 | 4411.39 | 9731.64
07:30 | 5598.89 | 4424.685 | 10023.575
08:00 | 5877.53 | 4437.98 | 10315.51
08:30 | 5993.5 | 4767.57 | 10761.07
09:00 | 6109.47 | 5097.16 | 11206.63
09:30 | 6217.135 | 5229.08 | 11446.215
10:00 | 6324.8 | 5361 | 11685.8
10:30 | 6397.005 | 5441.9 | 11838.905
11:00 | 6469.21 | 5522.8 | 11992.01
11:30 | 6538.815 | 5639.56 | 12178.375
12:00 | 6608.42 | 5756.32 | 12364.74
12:30 | 6664.77 | 5826.77 | 12491.54
13:00 | 6721.12 | 5897.22 | 12618.34
13:30 | 6756.35 | 5919.175 | 12675.525
14:00 | 6791.58 | 5941.13 | 12732.71
14:30 | 6779.215 | 5954.225 | 12733.44
15:00 | 6766.85 | 5967.32 | 12734.17
15:30 | 6775.47 | 5900.125 | 12675.595
16:00 | 6784.09 | 5832.93 | 12617.02
16:30 | 6833.92 | 5916.57 | 12750.49
17:00 | 6883.75 | 6000.21 | 12883.96
17:30 | 6831.275 | 5979.895 | 12811.17
18:00 | 6778.8 | 5959.58 | 12738.38
18:30 | 6724.3 | 5959.48 | 12683.78
19:00 | 6669.8 | 5959.38 | 12629.18
19:30 | 6614 | 6111.56 | 12725.56
20:00 | 6601 | 6145.17 | 12746.17
20:30 | 6584 | 6167.785 | 12751.785 |  | Executive Engineer
21:00 | 6567 | 6190.4 | 12757.4 |  | Network Operation Division
21:30 | 6505.5 | 6184.485 | 12689.985
22:00 | 6444 | 6178.57 | 12622.57
22:30 | 6282 | 6043.87 | 12325.87
23:00 | 6120 | 5909.17 | 12029.17

## En-Curve
QF-LDC-12
Date | 04-03-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3320 | 1636 | 902 | 0 | 132 | 1284.37 | 80 | 4132 | 0 | 93 | 158 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3283.5 | 1609.5 | 902 | 0 | 129 | 1201.23 | 80 | 4003.5 | 0 | 84 | 130.5 | 0 | 0 | 0 | 0 | 04-03-2026
01:00 | 3247 | 1583 | 902 | 0 | 126 | 1118.09 | 80 | 3875 | 0 | 75 | 103 | 0 | 0 | 0 | 0
01:30 | 3150.5 | 1566 | 902 | 0 | 126 | 1070.505 | 80 | 3827.5 | 0 | 75 | 103 | 0 | 0 | 0 | 0 | Energy Generated | 286.0351 |  | MKWHr
02:00 | 3054 | 1549 | 902 | 0 | 126 | 1022.92 | 80 | 3780 | 0 | 75 | 103 | 0 | 0 | 0 | 0 | Energy not Served | 0.206 |  | MKWHr
02:30 | 3083 | 1542.5 | 902 | 0 | 126 | 1022.97 | 80 | 3794 | 0 | 93.5 | 139.5 | 0 | 0 | 0 | 0 | Total Energy Requirement | 286.2411 |  | MKWHr
03:00 | 3112 | 1536 | 902 | 0 | 126 | 1023.02 | 80 | 3808 | 0 | 112 | 176 | 0 | 0 | 0 | 0
03:30 | 3195 | 1592 | 902 | 0 | 130 | 1071.065 | 80 | 3957 | 0 | 124.5 | 208.5 | 0 | 0 | 4 | 0
04:00 | 3278 | 1648 | 902 | 0 | 134 | 1119.11 | 80 | 4106 | 0 | 137 | 241 | 0 | 0 | 8 | 0
04:30 | 3224 | 1615 | 902 | 0 | 129 | 1042.34 | 80 | 3819.5 | 0 | 86 | 214.25 | 0 | 0 | 6 | 0
05:00 | 3170 | 1582 | 902 | 0 | 124 | 965.57 | 80 | 3533 | 0 | 35 | 187.5 | 0 | 0 | 4 | 0
05:30 | 3018 | 1493.5 | 902 | 0 | 119 | 897.605 | 80 | 3336.5 | 0 | 35 | 153.75 | 0 | 0 | 3 | 0
06:00 | 2866 | 1405 | 902 | 0 | 114 | 829.64 | 80 | 3140 | 0 | 35 | 120 | 0 | 0 | 2 | 0
06:30 | 2909.5 | 1412 | 902 | 0 | 113 | 831.415 | 80 | 3147.5 | 19.725 | 52.5 | 143 | 0 | 0 | 2 | 0
07:00 | 2953 | 1419 | 902 | 0 | 112 | 833.19 | 80 | 3155 | 39.45 | 70 | 166 | 0 | 0 | 2 | 0
07:30 | 3163.5 | 1493.75 | 784.5 | 0 | 113 | 832.75 | 80 | 3185 | 109.075 | 94 | 167 | 0 | 0 | 1 | 0
08:00 | 3374 | 1568.5 | 667 | 0 | 114 | 832.31 | 80 | 3215 | 178.7 | 118 | 168 | 0 | 0 | 0 | 0
08:30 | 3322 | 1590.5 | 784.5 | 0 | 116 | 879.07 | 80 | 3363.5 | 263 | 147.5 | 215 | 0 | 0 | 0 | 0
09:00 | 3270 | 1612.5 | 902 | 0 | 118 | 925.83 | 80 | 3512 | 347.3 | 177 | 262 | 0 | 0 | 0 | 0
09:30 | 3274 | 1614.25 | 902 | 0 | 122 | 924.66 | 80 | 3633.5 | 416.805 | 195.5 | 283.5 | 0 | 0 | 0 | 0
10:00 | 3278 | 1616 | 902 | 0 | 126 | 923.49 | 80 | 3755 | 486.31 | 214 | 305 | 0 | 0 | 0 | 0
10:30 | 3328 | 1609 | 900.5 | 0 | 126 | 923.325 | 80 | 3784.5 | 538.08 | 223 | 322.5 | 0 | 0 | 4 | 0
11:00 | 3378 | 1602 | 899 | 0 | 126 | 923.16 | 80 | 3814 | 589.85 | 232 | 340 | 0 | 0 | 8 | 0
11:30 | 3373 | 1605.5 | 899 | 0 | 131 | 1012.775 | 80 | 3853 | 607.1 | 248.5 | 358 | 0 | 0 | 10.5 | 0
12:00 | 3368 | 1609 | 899 | 0 | 136 | 1102.39 | 80 | 3892 | 624.35 | 265 | 376 | 0 | 0 | 13 | 0
12:30 | 3342.5 | 1613.5 | 899 | 0 | 137 | 1112.915 | 80 | 3970 | 617.625 | 269 | 435.5 | 0 | 0 | 14.5 | 0
13:00 | 3317 | 1618 | 899 | 0 | 138 | 1123.44 | 80 | 4048 | 610.9 | 273 | 495 | 0 | 0 | 16 | 0
13:30 | 3298.5 | 1615 | 899 | 0 | 143 | 1155.015 | 80 | 4129.5 | 570.86 | 265 | 504.65 | 0 | 0 | 15 | 15
14:00 | 3280 | 1612 | 899 | 0 | 148 | 1186.59 | 80 | 4211 | 530.82 | 257 | 514.3 | 0 | 0 | 14 | 30
14:30 | 3241.5 | 1613.5 | 899 | 0 | 148 | 1206.62 | 80 | 4278.5 | 483.27 | 256.5 | 514.55 | 0 | 0 | 12 | 34
15:00 | 3203 | 1615 | 899 | 0 | 148 | 1226.65 | 80 | 4346 | 435.72 | 256 | 514.8 | 0 | 0 | 10 | 38
15:30 | 3200 | 1634 | 899 | 0 | 141 | 1220.325 | 80 | 4380 | 342.47 | 254 | 517.3 | 0 | 0 | 7.5 | 34.5
16:00 | 3197 | 1653 | 899 | 0 | 134 | 1214 | 80 | 4414 | 249.22 | 252 | 519.8 | 0 | 0 | 5 | 31
16:30 | 3197.5 | 1646.5 | 899 | 0 | 136 | 1266.72 | 80 | 4449.5 | 169.92 | 285.5 | 615.85 | 0 | 0 | 4 | 35
17:00 | 3198 | 1640 | 899 | 0 | 138 | 1319.44 | 80 | 4485 | 90.62 | 319 | 711.9 | 0 | 0 | 3 | 39
17:30 | 3087.5 | 1552 | 899 | 0 | 132 | 1379.78 | 80 | 4422.5 | 45.54 | 336 | 873.85 | 0 | 0 | 3 | 30.5
18:00 | 2977 | 1464 | 899 | 0 | 126 | 1440.12 | 80 | 4360 | 0.46 | 353 | 1035.8 | 0 | 0 | 3 | 22
18:30 | 3084.5 | 1494.5 | 899 | 0 | 131 | 1443.75 | 80 | 4350.5 | 0.23 | 290 | 908.8 | 0 | 0 | 1.5 | 16.5
19:00 | 3192 | 1525 | 899 | 0 | 136 | 1447.38 | 80 | 4341 | 0 | 227 | 781.8 | 0 | 0 | 0 | 11
19:30 | 3211 | 1590 | 899 | 0 | 134 | 1455.56 | 80 | 4443 | 0 | 226 | 687 | 0 | 0 | 0 | 14
20:00 | 3217 | 1603 | 899 | 0 | 136 | 1444.17 | 80 | 4538 | 0 | 209 | 620 | 0 | 0 | 0 | 18
20:30 | 3214.5 | 1624 | 899 | 0 | 142 | 1447.285 | 80 | 4560 | 0 | 158 | 627 | 0 | 0 | 0 | 17.5
21:00 | 3212 | 1645 | 899 | 0 | 148 | 1450.4 | 80 | 4582 | 0 | 107 | 634 | 0 | 0 | 0 | 17
21:30 | 3186 | 1627 | 899 | 0 | 149 | 1446.985 | 80 | 4572 | 0 | 107 | 623 | 0 | 0 | 0 | 8.5
22:00 | 3160 | 1609 | 899 | 0 | 150 | 1443.57 | 80 | 4562 | 0 | 107 | 612 | 0 | 0 | 0 | 0
22:30 | 3148 | 1597 | 899 | 0 | 145 | 1426.87 | 80 | 4431.5 | 0 | 122.5 | 476 | 0 | 0 | 0 | 0
23:00 | 3136 | 1585 | 899 | 0 | 140 | 1410.17 | 80 | 4301 | 0 | 138 | 340 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 04-03-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 401 | 06:00 | 372 | 15:00 | Madunaghat | 405 | 07:00 | 389 | 16:00
Amtali | 418 | 06:00 | 404 | 13:00 | Meghnaghat | 400 | 05:00 | 376 | 15:00
Ashuganj | 414 | 5:00 | 386 | 15:00 | Payra | 420 | 06:00 | 408 | 15:00
Bhulta | 407 | 05:00 | 378 | 15:00 | Rahanpur | 422 | 06:00 | 402 | 17:00
Bibiana | 411 | 06:00 | 401 | 15:00 | Rampal | 410 | 05:00 | 394 | 13:00
BIPTC | 403 | 08:00 | 391 | 12:00
Bogura | 414 | 06:00 | 387 | 17:00
Gopalganj | 410 | 06:00 | 387 | 15:00
Kaliakoir | 393 | 06:00 | 360 | 15:00
Korerhat | 407 | 05:00 | 386 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 238 | 06:00 | 217 | 15:00 | Jhenaidah | 237 | 06:00 | 221 | 13:00
AKSML | 231.6 | 08:00 | 220.2 | 16:00 | Kachua | 232 | 05:00 | 217 | 15:00
Aminbazar | 237 | 05:00 | 217 | 15:00 | Kaliakoir | 239 | 06:00 | 218 | 15:00
Ashuganj | 234 | 06:00 | 216 | 15:00 | Keranigonj | 236 | 06:00 | 215 | 15:00
Ashuganj-400 | 234 | 06:00 | 216 | 15:00 | Khulna(S) | 239 | 06:00 | 222 | 16:00
Baghabari | 236 | 05:00 | 223 | 17:00 | Korerhat | 231 | 05:00 | 218 | 14:00
Barapukuria | 223 | 05:00 | 200 | 16:00 | Madunaghat | 233 | 13:00 | 221 | 14:00
Barapukuria-230 | 223 | 05:00 | 200 | 16:00 | Madunaghat-400 | 231 | 07:00 | 221 | 16:00
Barishal | 234 | 05:00 | 224 | 14:00 | Maniknagar | 234 | 05:00 | 216 | 15:00
Bheramara | 234 | 05:00 | 221 | 13:00 | Meghnaghat | 242 | 06:00 | 225 | 15:00
Bhulta | 235 | 06:00 | 216 | 15:00 | Meghnaghat-400 | 237 | 05:00 | 220 | 15:00
Bibiana | 238 | 18:30 | 230 | 16:00 | Mirsorai | 232 | 06:00 | 218 | 15:00
BIPTC | 237 | 05:00 | 222 | 13:00 | Rajshahi | 234 | 7:00 | 219 | 13:00
Bogura | 239 | 05:00 | 224 | 16:00 | Rampal | 237 | 06:00 | 222 | 14:00
Bogura-400 | 239 | 06:00 | 223 | 17:00 | Rampur | N/A | N/A | N/A | N/A
Borhanuddin | 236 | 08:00 | 231 | 15:00 | Rampura | 233 | 05:00 | 214 | 15:00
BSRM | 231 | 05:00 | 219 | 15:00 | Shikalbaha | 229 | 07:00 | 219 | 15:00
Chowmuhani | 231 | 7:00 | 217 | 15:00 | Shyampur | 236 | 05:00 | 216 | 15:00
Cumilla(N) | 233 | 05:00 | 217 | 15:00 | Siddhirganj | 236 | 03:00 | 218 | 14:00
Faridpur | 232 | 06:00 | 218 | 14:00 | Sirajgonj | 240 | 05:00 | 229 | 16:00
Fenchuganj | 241 | 06:00 | 234 | 16:00 | Sreepur | 228 | 06:00 | 213 | 17:00
Feni | 233 | 05:00 | 218 | 15:00 | Tongi | 234 | 04:00 | 212 | 15:00
Ghorashal | 232 | 02:00 | 220 | 16:00
Ghorashal-230 | 232 | 05:00 | 213 | 16:00
Gopalganj | 230 | 06:00 | 218 | 14:00
GPH | 231 | 05:00 | 220 | 15:00
Haripur | 234 | 05:00 | 217 | 15:00
Hasnabad | 237 | 04:00 | 216 | 15:00
Hathazari | 228 | 05:00 | 216 | 15:00
Ishurdi | 238 | 05:00 | 224 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 06:00 | 125 | 12:00 | Magura | 136 | 06:00 | 124 | 13:00
Agargaon | 141 | 06:00 | 128 | 15:00 | Mahasthangarh | 136 | 05:00 | 123 | 17:00
Agrabad | 132 | 05:00 | 126 | 12:00 | Maijdee | 130 | 06:00 | 121 | 14:00
AKS | 130 | 05:00 | 125 | 12:00 | Manikganj | 136 | 18:00 | 125 | 11:00
Aminbazar | 137 | 05:00 | 124 | 14:00 | Maniknagar | 132 | 07:00 | 119 | 14:00
Amnura | 139 | 05:00 | 127 | 13:00 | Matarbari | 125 | 13:00 | 110 | 22:00
Ashuganj | 142 | 08:00 | 133 | 15:00 | Matuail | 133 | 05:00 | 122 | 15:00
Bagerhat | 135 | 05:00 | 121 | 16:00 | Metrorail_Motijheel | 139 | 08:00 | 119 | 14:00
Bajitpur | 134 | 06:00 | 122 | 16:00 | Metrorail_Uttara | 137 | 06:00 | 122 | 14:00
Bakerganj | 137 | 06:00 | 130 | 14:00 | Millgate | 136 | 06:00 | 121 | 14:00
Bakulia | 131 | 05:00 | 126 | 19:00 | Mirpur | 136 | 06:00 | 122 | 15:00
Banani | 136 | 06:00 | 124 | 12:00 | Mirzapur | 136 | 05:00 | 124 | 12:00
Bangabhaban | 132 | 06:00 | 119 | 14:00 | Mithapukur | 136 | 05:00 | 122 | 17:00
Barapukuria | 137 | 05:00 | 121 | 17:00 | MI_Cement | 135.3 | 06:00 | 120 | 15:00
Barguna | 137 | 06:00 | 130 | 14:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 136 | 03:00 | 130 | 13:00 | Mogbazar | 138 | 03:00 | 125 | 12:00
Barishal-230 | 136 | 05:00 | 129 | 16:00 | Mongla | 136 | 06:00 | 122 | 13:00
Baroaulia | 132 | 05:00 | 126 | 16:00 | Motijheel | 132 | 06:00 | 119 | 14:00
Baroirhat | 133 | 06:00 | 125 | 15:00 | Muktagacha | 129 | 03:00 | 117 | 17:00
Bashundhara | 136 | 06:00 | 124 | 12:00 | Munshiganj | 131 | 18:00 | 121 | 15:00
BashundharaCement | 132 | 07:00 | 128 | 00:00 | Muradnagar | 132 | 05:00 | 121 | 15:00
Beanibazar | 131 | 07:00 | 125 | 16:00 | Mymensingh | 130 | 06:00 | 113 | 17:00
Benapole | 134 | 02:00 | 116 | 13:00 | Naogaon | 135 | 06:00 | 122 | 13:00
Bhaluka | 137 | 06:00 | 123 | 17:00 | Narail | 137 | 06:00 | 123 | 13:00
Bhandaria | 134 | 05:00 | 126 | 14:00 | Narinda | 132 | 07:00 | 119 | 14:00
Bhangura | 135 | 05:00 | 127 | 12:00 | Narshingdi | 129 | 18:00 | 119 | 16:00
Bheramara | 137 | 06:00 | 131 | 10:00 | Natore | 133 | 00:00 | 128 | 10:00
Bheramara(GK) | 137 | 05:00 | 131 | 12:00 | Nawabganj | 141 | 03:00 | 125 | 15:00
Bhulta | 127 | 05:00 | 119 | 15:00 | Netrakona | 126 | 06:00 | 108 | 17:00
Bog-Sherpur | 137 | 06:00 | 126 | 16:00 | New | 137 | 05:00 | 122 | 15:00
Bogura | 138 | 05:00 | 127 | 16:00 | Niamatpur | 140 | 05:00 | 133 | 13:00
Bogura-230 | 138 | 05:00 | 128 | 16:00 | Noapara | 137 | 06:00 | 121 | 13:00
Brahmanbaria | 138 | 07:00 | 126 | 14:00 | Pabna | 137 | 05:00 | 129 | 13:00
Cantonment | 140 | 05:00 | 127 | 15:00 | Palashbari | 133 | 05:00 | 120 | 16:00
Chandina | 135 | 05:00 | 124 | 15:00 | Panchagarh | 137 | 05:00 | 123 | 08:00
Chandpur | 131 | 04:00 | 122 | 15:00 | Patiya | 130 | 08:00 | 124 | 21:00
Chandraghona | 135 | 07:00 | 128 | 15:00 | Patuakhali | 135 | 05:00 | 129 | 16:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 139 | 05:00 | 133 | 13:00 | Payra | 138 | 06:00 | 133 | 15:00
Charsaidpur | 132 | 05:00 | 121 | 15:00 | PHP | 133 | 07:00 | 124 | 15:00
Chauddagram | 132 | 05:00 | 123 | 14:00 | Postogola | 137 | 06:00 | 122 | 15:00
Chhatak | 130 | 06:00 | 124 | 14:00 | Purbachal | 135 | 05:00 | 124 | 11:00
Chowmuhani | 127 | 05:00 | 121 | 15:00 | Purbasadipur | 130 | 05:00 | 117 | 16:00
Chuadanga | 137 | 06:00 | 123 | 13:00 | Rahanpur | 141 | 06:00 | 135 | 13:00
Coxsbazar | 121 | 09:00 | 109 | 21:00 | Rahanpur-400 | 141 | 05:00 | 135 | 13:00
Cumilla(N) | 134 | 05:00 | 124 | 15:00 | Rahim | 132 | 05:00 | 123 | 16:00
Cumilla(S) | 133 | 05:00 | 121 | 14:00 | Rajbari | 134 | 06:00 | 124 | 15:00
Daganbhuiyan | 131 | 06:00 | 122 | 15:00 | Rajendrapur | 137 | 06:00 | 124 | 16:00
Daudkandi | 130 | 05:00 | 119 | 15:00 | Rajshahi | 136 | 06:00 | 126 | 13:00
DhakaUniversity | 135 | 05:00 | 125 | 12:00 | Rajshahi-230 | 135 | 02:00 | 126 | 13:00
Dhamrai | 141 | 05:00 | 127 | 15:00 | Ramganj | 129 | 06:00 | 119 | 15:00
Dhanmondi | 136 | 05:00 | 125 | 11:00 | Rampur | 132 | 05:00 | 126 | 12:00
Dohazari | 129 | 07:00 | 119 | 21:00 | Rampura | 135 | 05:00 | 124 | 12:00
Faridpur | 134 | 06:00 | 126 | 17:00 | Rangamati | 134 | 04:00 | 127 | 14:00
Fatullah | 137 | 06:00 | 121 | 15:00 | Rangpur | 137 | 05:00 | 119 | 16:00
Fenchuganj | 136 | 05:00 | 131 | 16:00 | Ruppur | 138 | 04:00 | 131 | 13:00
Feni | 129 | 06:00 | 123 | 13:00 | Saidpur | 136 | 06:00 | 120 | 16:00
Feni-230 | 131 | 05:00 | 122 | 15:00 | Satkhira | 135 | 05:00 | 121 | 17:00
Ghatail | 129 | 04:00 | 117 | 12:00 | Satmasjid | 140 | 05:00 | 127 | 15:00
Ghorashal | 139 | 05:00 | 129 | 15:00 | Savar | 136 | 06:00 | 120 | 15:00
Goalpara | 139 | 06:00 | 126 | 13:00 | SevenRings | 139 | 05:00 | 129 | 15:00
Gollamari | 138 | 05:00 | 126 | 16:00 | ShahCement | 132 | 05:00 | 121 | 15:00
Gopalganj | 137 | 06:00 | 126 | 14:00 | Shahjadpur | 140 | 03:00 | 130 | 17:00
Gopalganj-400 | 137 | 05:00 | 129 | 13:00 | Shahjibazar | 137 | 08:00 | 124 | 15:00
Gulshan | 135 | 06:00 | 124 | 12:00 | Shahmirpur | 133 | 06:00 | 126 | 20:00
Halishahar | 132 | 05:00 | 126 | 14:00 | Shariatpur | 136 | 05:00 | 127 | 14:00
Haripur | 132 | 05:00 | 122 | 15:00 | Sherpur | 128 | 19:30 | 111 | 12:00
HaripurSBU | 136 | 22:00 | 122 | 19:00 | Shikalbaha | 121 | 02:00 | 116 | 16:00
Hasnabad | 136 | 04:00 | 123 | 15:00 | Shikalbaha-230 | 134 | 07:00 | 127 | 14:00
Hathazari | 133 | 03:00 | 128 | 12:00 | Shitalakhya | 135.3 | 06:00 | 120 | 15:00
Hatirjheel | 135 | 05:00 | 125 | 12:00 | Sholosohor | 134 | 06:00 | 128 | 12:00
Ishurdi | 139 | 05:00 | 132 | 13:00 | Shyampur | 134 | 05:00 | 123 | 15:00
Jaldhaka | 133 | 05:00 | 118 | 16:00 | Shyampur-230 | 136 | 05:00 | 124 | 12:00
Jamalpur | 131 | 03:00 | 115 | 12:00 | Siddhirganj | 133 | 05:00 | 123 | 15:00
Jashore | 135 | 06:00 | 116 | 13:00 | Sirajganj | 134 | 02:00 | 124 | 16:00
Jhenaidah | 138 | 05:00 | 116 | 13:00 | Sonargaon | 131 | 06:00 | 120 | 15:00
Jhenaidah-230 | 138 | 06:00 | 127 | 13:00 | Sreemongol | 131 | 05:00 | 125 | 16:00
Joydebpur | 135 | 18:00 | 124 | 16:00 | Sreepur | 140 | 06:00 | 129 | 14:00
Joypurhat | 132 | 05:00 | 117 | 17:00 | Srinagar | 143 | 05:00 | 125 | 15:00
Juldah | 132 | 01:00 | 125 | 21:00 | SSM | 134 | 17:00 | 125 | 10:00
Kabirpur | 138 | 04:00 | 116 | 15:00 | Sunamganj | 128 | 05:00 | 122 | 20:00
Kachua | 132 | 05:00 | 123 | 15:00 | Sylhet | 133 | 06:00 | 126 | 17:00
Kaliakoir | 143 | 05:00 | 129 | 15:00 | Sylhet-132 | 130 | 03:00 | 127 | 13:00
Kaliganj | 138 | 04:00 | 126 | 13:00 | Tangail | 130 | 02:00 | 118 | 17:00
Kallyanpur | 136 | 05:00 | 124 | 14:00 | Taraganj | 135 | 05:00 | 120 | 17:00
Kalurghat | 134 | 05:00 | 128 | 15:00 | Tasnim | 131 | 05:00 | 120 | 16:00
Kamrangirchar | 142 | 04:00 | 120 | 15:00 | Thakurgaon | 135 | 22:00 | 122 | 13:00
Kaptai | N/A | N/A | N/A | N/A | TK | 133 | 03:00 | 128 | 12:00
Kasba | 132 | 05:00 | 120 | 15:00 | Tongi | 138 | 04:00 | 124 | 15:00
Kazla | 131 | 06:00 | 118 | 16:00 | Ullahpara | 136 | 05:00 | 126 | 16:00
Keranigonj | 142 | 05:00 | 126 | 15:00 | Ullon | 135 | 06:00 | 124 | 12:00
Khagrachori | 133 | 06:00 | 126 | 16:00 | Uttara | 136 | 05:00 | 122 | 15:00
Khulna | 138 | 06:00 | 125 | 13:00 | UttaraNew | 137 | 06:00 | 122 | 15:00
Khulna(S) | 139 | 06:00 | 126 | 16:00 | Zigatola | 142 | 05:00 | 126 | 15:00
Khulshi | 131 | 06:00 | 124 | 20:00
Kishoreganj | 133 | 06:00 | 120 | 16:00
Kodda | 139 | 18:00 | 123 | 11:00
Korerhat | 134 | 05:00 | 127 | 14:00
KSRM | 133 | 06:00 | 126 | 14:00
Kulaura | 136 | 06:00 | 130 | 16:00
Kurigram | 135 | 05:00 | 118 | 17:00
Kushtia | 134 | 06:00 | 123 | 13:00
Laksam | 132 | 06:00 | 122 | 13:00
Lakshmipur | 130 | 06:00 | 121 | 15:00
Lalbag | 142 | 04:00 | 125 | 15:00
Lalmonirhat | 134 | 05:00 | 118 | 16:00
Madanganj | 132 | 07:00 | 128 | 00:00
Madaripur | 136 | 05:00 | 129 | 13:00
Madartek | 134 | 03:00 | 124 | 12:00
Madunaghat | 134 | 06:00 | 128 | 14:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division