## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 07-03-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-03-2026 | during | 07-03-2026 | during | 07-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 336 | 315 | 412 | 412 | 412 | 412 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 250 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 33.4 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19 | 18 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 22 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 3 | 34 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 2 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 14 | 85 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 26 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 335 | 390 | 584 | 584 | 584 | 584 | FGMO
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 300 | 355 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 108 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1436 | 1645.4 | 5495.22 | 5465.22 | 3206.05 | 3232.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 80 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 225 | 220 | 220 | 220 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 67 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 56 | 64 | 56 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 68 | 68 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 20 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.12 | 0 | 3.33 | 0 | 3.33 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1170 | 1160 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 2 | 0 | 2 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 575 | 635 | 580 | 580 | 580 | 580 | ps availability is less
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2062.12 | 2187 | 3488.19 | 3487.86 | 2941.83 | 2941.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 210 | 196 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 92 | 240 | 240 | 240 | 240 | Plant availability less
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 51 | 325 | 318.81 | 318.81 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 370 | 330 | 393 | 393 | 220 | 220 | FGMO
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 32 | 32 | 32 | 32 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 97 | 101 | 163 | 163 | 100 | 100 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 51 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 126 | 140 | 84 | 80 | 84 | 80 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 51 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 64 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 973 | 1357 | 2623.16 | 2559.16 | 1637.2 | 1573.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-03-2026 | during | 07-03-2026 | during | 07-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 16 | 21 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 87 | 78 | 60 | 80 | 60 | 80 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 65 | 115 | 115 | 115 | 70 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 41.01 | 0 | 45.12 | 0 | 45.12 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 11 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 217.01 | 225 | 456.12 | 429 | 200.12 | 218
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 42 | 42 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 30 | 30 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 154 | 156 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 71 | 70 | 70 | 70 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 40 | 40 | 86 | 86 | 42 | 42 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 96 | 95 | 100 | 100 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 22 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 255 | 300 | 341 | 341 | 150 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 406 | 365 | 385 | 385 | 385 | 385 | Due to Air Filter DP High FGMO not available.
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1091 | 1090 | 1242 | 1242 | 904 | 1061
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 900 | 899 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 200 | 205 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 89 | 0 | 76 | 0 | 76 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 883 | 1127 | 0 | 0 | 1148.28 | 1148.28 | plant availability zero
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2072 | 2231 | 2356 | 2280 | 2531.38 | 2455.38
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 880 | 1085 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 15 | 15 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 280 | 276 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.58 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2700.36 | 1500.58 | 1701 | 2003.32 | 2002.32 | 1868.32 | 1867.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 41.95 | 0 | 48 | 0 | 48 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 202 | 189 | 220 | 220 | 220 | 220 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 409 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Machine problem and fuel shortage
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 50 | 50 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.32 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1135 | 1451 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 43.31 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 87 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1927.58 | 2049 | 3127.57 | 2923.87 | 2579.57 | 2375.87
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 50 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 99 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.7 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 29 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 162 | 0 | 168.5 | 0 | 168.5 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 196.7 | 264 | 465.7 | 262 | 431.7 | 228
System Total |  |  |  |  | 28823.2 | 28385.703 | 11475.99 | 12749.4 | 21257.28 | 20651.43 | 16300.17 | 15952.32
Forecast Scenario (07-03-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11290 |  | 0 |  | 11290
|  |  |  | 1:00 | 10650 |  | 0 |  | 10650
|  |  |  | 2:00 | 10360 |  | 0 |  | 10360
|  |  |  | 3:00 | 10510 |  | 0 |  | 10510
|  |  |  | 4:00 | 11570 |  | 0 |  | 11570
|  |  |  | 5:00 | 10470 |  | 0 |  | 10470
|  |  |  | 6:00 | 9390 |  | 0 |  | 9390
|  |  |  | 7:00 | 9650 |  | 0 |  | 9650
|  |  |  | 8:00 | 10420 |  | 0 |  | 10420
|  |  |  | 9:00 | 11320 |  | 0 |  | 11320
|  |  |  | 10:00 | 11550 |  | 0 |  | 11550
|  |  |  | 11:00 | 11990 |  | 0 |  | 11990
|  |  |  | 12:00 | 12390 |  | 0 |  | 12390
|  |  |  | 13:00 | 12700 |  | 0 |  | 12700
|  |  |  | 14:00 | 12970 |  | 0 |  | 12970
|  |  |  | 15:00 | 12820 |  | 0 |  | 12820
|  |  |  | 16:00 | 12960 |  | 0 |  | 12960
|  |  |  | 17:00 | 13230 |  | 0 |  | 13230
|  |  |  | 18:00 | 13020 |  | 0 |  | 13020
|  |  |  | 18:30 | 13150 |  | 0 |  | 13150
|  |  |  | 19:00 | 13350 |  | 0 |  | 13350
|  |  |  | 19:30 | 13380 |  | 0 |  | 13380
|  |  |  | 20:00 | 13360 |  | 0 |  | 13360
|  |  |  | 21:00 | 13250 |  | 0 |  | 13250
|  |  |  | 22:00 | 13210 |  | 0 |  | 13210
|  |  |  | 23:00 | 12520 |  | 0 |  | 12520
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 12390.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13380.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13380.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 243.5896 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:17 hrs on 07-03-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 06-03-2026 | [28 empty] | Date: | 06-03-2026 | [28 empty] | Date: | 06-03-2026 | [28 empty] | Date: | 06-03-2026 | [28 empty] | Date: | 06-03-2026 | [17 empty] | Date: | 06-03-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [17 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 300 | 0 | 0 | 0 | 70 | 14 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 28 | 780 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 250 | 300 | 18 | 51 | 0 | 199 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 142 | 0 | 0 | 0 | 300 | 0 | 387 | 41 | 0 | 154 | 0 | 17 | 0 | 41 | 0 | 70 | 0 | 97 | 0 | 59 | 48 | 11 | 0 | 0 | 6 | 6095 | 900 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1111 | 0 | 0 | 0 | 1393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 52 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 125 | 220 | 0 | 0 | 1080 | 0 | 6017 | 12112 | 90.62
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 300 | 0 | 0 | 0 | 52 | 21.5 | 22 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 28 | 780 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1111 | 0 | 0 | 0 | 215 | 315 | 3 | 51 | 0 | 140 | 0 | 0 | 101 | 0 | 0 | 20 | 0 | 132 | 0 | 0 | 0 | 305 | 0 | 398 | 41 | 0 | 152 | 0 | 17 | 0 | 41 | 0 | 71 | 0 | 97 | 0 | 59 | 48 | 11 | 0 | 0 | 6 | 5937.5 | 899 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 938 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 50 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259 | 125 | 220 | 0 | 0 | 1000 | 0 | 5512 | 11449.5 | 90.61
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 250 | 0 | 0 | 0 | 35 | 21.5 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 780 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1110 | 0 | 0 | 0 | 215 | 280 | 11 | 51 | 0 | 142 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 122 | 0 | 0 | 0 | 300 | 0 | 364 | 41 | 0 | 142 | 0 | 17 | 0 | 41 | 0 | 70 | 0 | 98 | 0 | 59 | 48 | 12 | 0 | 0 | 6 | 5722.5 | 899 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 909 | 0 | 0 | 0 | 1221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 53 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257 | 100 | 180 | 0 | 0 | 1000 | 0 | 5315 | 11037.5 | 90.6
03:00 | 0 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 250 | 0 | 0 | 0 | 52 | 21.5 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 780 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 215 | 280 | 22 | 51 | 0 | 140 | 0 | 0 | 104 | 0 | 0 | 20 | 0 | 126 | 0 | 0 | 0 | 305 | 0 | 350 | 41 | 0 | 138 | 0 | 17 | 0 | 41 | 0 | 70 | 0 | 98 | 0 | 87 | 57 | 12 | 0 | 0 | 6 | 5758.5 | 900 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 893 | 0 | 0 | 0 | 1314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 53 | 45 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254 | 100 | 180 | 0 | 0 | 1040 | 0 | 5490 | 11248.5 | 90.59
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 250 | 0 | 0 | 0 | 70 | 21.5 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 720 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1190 | 0 | 0 | 0 | 215 | 270 | 33 | 51 | 0 | 129 | 0 | 0 | 104 | 0 | 0 | 20 | 0 | 124 | 0 | 0 | 0 | 300 | 0 | 368 | 41 | 0 | 152 | 0 | 17 | 0 | 41 | 0 | 71 | 0 | 98 | 0 | 98 | 57 | 12 | 0 | 0 | 0 | 5951.5 | 899 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 967 | 0 | 0 | 0 | 1454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 53 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 125 | 180 | 0 | 0 | 1000 | 0 | 5868 | 11819.5 | 90.58
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 250 | 0 | 0 | 0 | 52 | 19 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 720 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 976 | 0 | 0 | 0 | 215 | 270 | 44 | 51 | 0 | 129 | 0 | 0 | 104 | 0 | 0 | 20 | 0 | 124 | 0 | 0 | 0 | 290 | 0 | 365 | 41 | 0 | 139 | 0 | 17 | 0 | 41 | 0 | 71 | 0 | 98 | 0 | 68 | 58 | 12 | 0 | 0 | 0 | 5591 | 900 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 915 | 0 | 0 | 0 | 1197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 125 | 180 | 0 | 0 | 820 | 0 | 5202 | 10793 | 90.57
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 15.5 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 14 | 720 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 850 | 0 | 0 | 0 | 215 | 270 | 62 | 5 | 0 | 124 | 0 | 0 | 104 | 0 | 0 | 20 | 0 | 114 | 0 | 0 | 0 | 290 | 0 | 352 | 41 | 0 | 135 | 0 | 17 | 0 | 5 | 0 | 70 | 0 | 98 | 0 | 55 | 45 | 12 | 0 | 0 | 0 | 5115.5 | 899 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 792 | 0 | 0 | 0 | 962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 125 | 180 | 0 | 0 | 700 | 0 | 4572 | 9687.5 | 90.56
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 250 | 0 | 0 | 2 | 0 | 16 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26 | 80 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 861 | 2 | 0 | 0 | 215 | 270 | 47 | 5 | 0 | 124 | 0 | 0 | 104 | 0 | 0 | 20 | 0 | 116 | 0 | 6 | 0 | 295 | 0 | 358 | 41 | 0 | 138 | 1 | 17 | 0 | 5 | 0 | 70 | 0 | 98 | 0 | 55 | 45 | 12 | 0 | 2.35 | 0 | 5132.61 | 781 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 803 | 0 | 0 | 0 | 859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.28 | 4 | 0 | 0 | 2.37 | 0 | 0 | 130 | 0 | 0 | 0 | 372 | 0 | 0.24 | 0 | 55 | 0 | 2 | 0 | 0 | 0 | 0 | 0.4 | 9 | 0.02 | 0 | 202 | 117 | 180 | 0 | 0 | 680 | 0 | 4386.31 | 9518.92 | 90.55
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 335 | 0 | 0 | 7 | 0 | 18 | 22 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 80 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 1005 | 6 | 0 | 0 | 215 | 270 | 77 | 5 | 0 | 118 | 0 | 0 | 103 | 0 | 0 | 20 | 0 | 98 | 0 | 22 | 0 | 305 | 0 | 347 | 41 | 0 | 159 | 3 | 17 | 0 | 5 | 0 | 70 | 0 | 98 | 0 | 68 | 57 | 12 | 1 | 10.8 | 4 | 5499.75 | 665 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 830 | 0 | 0 | 0 | 839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.34 | 22 | 0 | 0 | 11.46 | 0 | 0 | 130 | 0 | 0 | 0 | 377 | 0 | 1.07 | 0 | 55 | 0 | 7 | 0 | 0 | 0 | 0 | 2.2 | 44 | 0.08 | 0 | 201 | 117 | 180 | 0 | 0 | 680 | 0 | 4380.15 | 9879.9 | 90.54
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 333 | 0 | 0 | 14 | 17 | 18 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.85 | 80 | 0 | 0 | 780 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 970 | 11 | 0 | 0 | 220 | 120 | 62 | 10 | 0 | 128 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 118 | 0 | 40 | 0 | 260 | 0 | 389 | 41 | 0 | 160 | 4 | 17 | 0 | 31 | 0 | 71 | 0 | 96 | 0 | 68 | 58 | 18 | 1 | 21.73 | 6 | 5514.58 | 900 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 818 | 0 | 0 | 0 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.35 | 44 | 0 | 0 | 22.52 | 0 | 0 | 170 | 0 | 0 | 0 | 414 | 0 | 2.18 | 0 | 55 | 0 | 15 | 0 | 0 | 0 | 0 | 3.2 | 87 | 0.19 | 0 | 249 | 117 | 214 | 0 | 0 | 703 | 0 | 4921.44 | 10436.02 | 90.53
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 329 | 0 | 0 | 20 | 48 | 19 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.55 | 80 | 0 | 0 | 780 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 945 | 15 | 0 | 0 | 235 | 0 | 47 | 43 | 0 | 203 | 0 | 0 | 99 | 0 | 0 | 20 | 0 | 114 | 0 | 54 | 0 | 150 | 0 | 392 | 42 | 0 | 158 | 8 | 17 | 0 | 40 | 0 | 69 | 0 | 97 | 0 | 68 | 58 | 18 | 1 | 31.45 | 6 | 5391 | 900 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 815 | 0 | 0 | 0 | 1016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.27 | 65 | 0 | 0 | 33.76 | 0 | 0 | 196 | 0 | 0 | 0 | 414 | 0 | 3.26 | 0 | 55 | 0 | 22 | 0 | 0 | 0 | 0 | 4.4 | 125 | 0.47 | 0 | 277 | 112 | 220 | 0 | 0 | 800 | 0 | 5317.16 | 10708.16 | 90.52
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 300 | 0 | 0 | 25 | 52 | 20 | 22 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.96 | 80 | 0 | 0 | 630 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1110 | 17 | 0 | 0 | 250 | 0 | 73 | 43 | 0 | 203 | 0 | 0 | 98 | 0 | 0 | 20 | 0 | 124 | 0 | 62 | 0 | 145 | 0 | 392 | 42 | 0 | 157 | 9 | 17 | 0 | 40 | 0 | 70 | 0 | 97 | 0 | 68 | 58 | 16 | 2 | 37.99 | 6 | 5475.95 | 900 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 825 | 0 | 0 | 0 | 1090 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.07 | 79 | 0 | 0 | 41 | 0 | 0 | 200 | 0 | 0 | 0 | 414 | 0 | 3.86 | 0 | 55 | 0 | 27 | 0 | 0 | 0 | 0 | 5.5 | 152 | 0.57 | 0 | 278 | 120 | 220 | 0 | 0 | 820 | 0 | 5553 | 11028.95 | 90.51
12:00 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 17 | 14 | 0 | 0 | 0 | 300 | 0 | 0 | 300 | 0 | 0 | 26 | 70 | 19 | 14 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.12 | 80 | 0 | 0 | 575 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1170 | 18 | 0 | 0 | 370 | 0 | 51 | 43 | 0 | 210 | 0 | 0 | 97 | 0 | 0 | 12 | 0 | 126 | 0 | 64 | 0 | 255 | 0 | 406 | 42 | 0 | 154 | 10 | 17 | 0 | 40 | 0 | 71 | 0 | 96 | 0 | 65 | 87 | 16 | 2 | 41.01 | 6 | 5779.13 | 900 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 883 | 0 | 0 | 0 | 1135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.95 | 87 | 0 | 0 | 43.31 | 0 | 0 | 202 | 0 | 0 | 0 | 414 | 0 | 4.32 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 5.7 | 162 | 0.58 | 0 | 280 | 120 | 220 | 0 | 0 | 880 | 0 | 5696.86 | 11475.99 | 90.5
13:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 35 | 62 | 0 | 0 | 0 | 440 | 0 | 0 | 299 | 0 | 0 | 24 | 108 | 15 | 14 | 0 | 310 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 2.9 | 80 | 0 | 0 | 575 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1168 | 17 | 0 | 0 | 350 | 0 | 55 | 43 | 0 | 205 | 0 | 0 | 96 | 0 | 0 | 18 | 0 | 138 | 0 | 63 | 0 | 315 | 0 | 396 | 42 | 0 | 153 | 10 | 20 | 0 | 40 | 0 | 70 | 0 | 96 | 0 | 68 | 87 | 11 | 2 | 39.73 | 6 | 6107.63 | 901 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 998 | 0 | 0 | 0 | 1313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.49 | 89 | 0 | 0 | 35.53 | 0 | 0 | 199 | 0 | 0 | 0 | 414 | 0 | 2.66 | 0 | 0 | 50 | 27 | 46 | 0 | 0 | 0 | 5.6 | 149 | 0.48 | 0 | 277 | 120 | 220 | 0 | 0 | 900 | 0 | 6071.76 | 12179.39 | 90.49
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 250 | 0 | 0 | 20 | 70 | 18 | 14 | 0 | 340 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 2.87 | 80 | 0 | 0 | 575 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1160 | 16 | 0 | 0 | 375 | 0 | 73 | 43 | 0 | 210 | 0 | 0 | 95 | 0 | 0 | 18 | 0 | 130 | 0 | 56 | 0 | 315 | 0 | 396 | 42 | 0 | 153 | 8 | 21 | 0 | 40 | 0 | 71 | 0 | 95 | 0 | 70 | 45 | 11 | 2 | 33.86 | 6 | 5779.73 | 900 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 899 | 0 | 0 | 0 | 1131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.42 | 75 | 0 | 0 | 26.84 | 0 | 0 | 199 | 0 | 0 | 0 | 414 | 0 | 3.51 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 4.8 | 137 | 0.51 | 0 | 220 | 120 | 220 | 0 | 0 | 830 | 0 | 5512.08 | 11291.81 | 90.48
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 0 | 0 | 320 | 0 | 0 | 18 | 70 | 18 | 14 | 0 | 330 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 1.67 | 80 | 0 | 15 | 635 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1160 | 12 | 0 | 0 | 355 | 0 | 103 | 43 | 0 | 210 | 0 | 0 | 94 | 0 | 0 | 18 | 0 | 132 | 0 | 43 | 0 | 320 | 0 | 396 | 42 | 0 | 152 | 6 | 21 | 0 | 40 | 0 | 69 | 0 | 96 | 0 | 59 | 45 | 12 | 1 | 24.3 | 6 | 5988.97 | 900 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 892 | 0 | 0 | 0 | 1233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.99 | 52 | 0 | 0 | 21.23 | 0 | 0 | 194 | 0 | 0 | 0 | 414 | 0 | 2.27 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 3.7 | 106 | 0.39 | 0 | 250 | 120 | 220 | 0 | 0 | 878 | 0 | 5584.58 | 11573.55 | 90.47
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 250 | 0 | 0 | 11 | 70 | 18 | 14 | 0 | 340 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0.92 | 80 | 0 | 20 | 635 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1195 | 7 | 0 | 0 | 375 | 0 | 110 | 43 | 0 | 209 | 0 | 0 | 95 | 0 | 0 | 20 | 0 | 130 | 0 | 25 | 0 | 320 | 0 | 392 | 42 | 0 | 150 | 3 | 21 | 0 | 40 | 0 | 69 | 0 | 96 | 0 | 59 | 58 | 12 | 1 | 9.71 | 0 | 5882.63 | 900 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 998 | 0 | 0 | 0 | 1323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.41 | 33 | 0 | 0 | 12.74 | 0 | 0 | 190 | 0 | 0 | 0 | 414 | 0 | 1.2 | 0 | 52 | 0 | 12 | 0 | 0 | 0 | 0 | 2.3 | 54 | 0.24 | 0 | 259 | 120 | 220 | 0 | 0 | 894 | 0 | 5732.89 | 11615.52 | 90.46
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 10 | 0 | 9 | 0 | 0 | 0 | 16 | 63 | 0 | 0 | 0 | 370 | 0 | 0 | 250 | 0 | 0 | 4 | 108 | 16 | 14 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31 | 80 | 0 | 20 | 635 | 0 | 0 | 0 | 0 | 4 | 220 | 0 | 0 | 0 | 1175 | 2 | 0 | 0 | 360 | 0 | 114 | 43 | 0 | 210 | 0 | 1 | 95 | 0 | 0 | 20 | 0 | 136 | 0 | 10 | 0 | 310 | 0 | 392 | 42 | 0 | 151 | 1 | 21 | 0 | 40 | 0 | 70 | 0 | 96 | 0 | 68 | 66 | 12 | 0 | 2.89 | 0 | 5964.2 | 900 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 1080 | 0 | 0 | 0 | 1457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.62 | 12 | 0 | 0 | 3.68 | 0 | 0 | 174 | 0 | 0 | 0 | 414 | 0 | 0.39 | 0 | 51 | 35 | 4 | 49 | 0 | 0 | 0 | 0.8 | 21 | 0.09 | 0 | 280 | 120 | 220 | 0 | 0 | 938 | 0 | 5972.58 | 11936.78 | 90.44
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 17.2 | 0 | 34 | 0 | 0 | 0 | 35 | 68 | 0 | 0 | 0 | 405 | 0 | 0 | 250 | 0 | 0 | 0 | 108 | 16 | 14 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 20 | 635 | 0 | 0 | 0 | 0 | 16 | 223 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 340 | 0 | 143 | 51 | 0 | 202 | 0 | 16 | 97 | 0 | 0 | 20 | 0 | 132 | 0 | 0 | 0 | 305 | 0 | 401 | 42 | 0 | 152 | 0 | 21 | 0 | 40 | 0 | 70 | 0 | 95 | 0 | 88 | 78 | 16 | 0 | 0 | 0 | 6061.2 | 901 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54 | 1098 | 0 | 0 | 0 | 1454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 50 | 114 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254 | 120 | 180 | 0 | 0 | 1050 | 0 | 6093.66 | 12154.86 | 90.42
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 16.2 | 0 | 34 | 0 | 0 | 0 | 35 | 82 | 0 | 0 | 0 | 335 | 0 | 0 | 250 | 0 | 0 | 0 | 108 | 18 | 14 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 20 | 635 | 0 | 0 | 0 | 0 | 16 | 223 | 0 | 0 | 0 | 1175 | 0 | 0 | 0 | 375 | 0 | 169 | 51 | 0 | 212 | 0 | 17 | 99 | 0 | 0 | 20 | 0 | 142 | 0 | 0 | 0 | 305 | 0 | 401 | 42 | 0 | 148 | 0 | 22 | 0 | 40 | 0 | 69 | 0 | 95 | 0 | 89 | 86 | 20 | 0 | 0 | 0 | 6201.2 | 901 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1063 | 0 | 0 | 0 | 1454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 50 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 284 | 120 | 220 | 0 | 0 | 1085 | 0 | 6179 | 12380.2 | 90.4
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 33.2 | 0 | 34 | 0 | 0 | 0 | 35 | 85 | 0 | 0 | 0 | 350 | 0 | 0 | 250 | 0 | 0 | 0 | 108 | 18 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 20 | 635 | 0 | 0 | 0 | 0 | 42 | 223 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 354 | 0 | 206 | 51 | 0 | 204 | 0 | 50 | 99 | 10 | 0 | 20 | 0 | 144 | 0 | 0 | 0 | 310 | 0 | 365 | 41 | 0 | 156 | 0 | 22 | 0 | 40 | 0 | 71 | 0 | 94 | 0 | 89 | 87 | 20 | 0 | 0 | 6 | 6251.2 | 831 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1125 | 0 | 0 | 0 | 1454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 50 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 120 | 220 | 0 | 0 | 1084 | 0 | 6168 | 12419.2
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 30.9 | 0 | 34 | 0 | 0 | 0 | 35 | 86 | 0 | 0 | 0 | 360 | 0 | 0 | 250 | 0 | 0 | 0 | 108 | 18 | 22 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 20 | 635 | 0 | 0 | 0 | 0 | 47 | 223 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 345 | 0 | 240 | 51 | 0 | 201 | 0 | 47 | 99 | 34 | 0 | 20 | 0 | 144 | 0 | 0 | 0 | 305 | 0 | 367 | 41 | 0 | 156 | 0 | 22 | 0 | 40 | 0 | 71 | 0 | 97 | 0 | 98 | 86 | 21 | 0 | 0 | 6 | 6317.9 | 805 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1125 | 0 | 0 | 0 | 1445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 50 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 120 | 220 | 0 | 0 | 1085 | 0 | 6141 | 12458.9 | 90.38
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 33.4 | 0 | 34 | 0 | 0 | 0 | 35 | 85 | 0 | 0 | 0 | 355 | 0 | 0 | 250 | 0 | 0 | 0 | 108 | 18 | 22 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 20 | 635 | 0 | 0 | 0 | 0 | 67 | 225 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 330 | 92 | 325 | 51 | 0 | 196 | 0 | 51 | 101 | 51 | 0 | 20 | 0 | 140 | 0 | 0 | 0 | 300 | 0 | 365 | 42 | 0 | 156 | 0 | 22 | 0 | 40 | 0 | 70 | 0 | 95 | 0 | 115 | 78 | 21 | 0 | 0 | 11 | 6504.4 | 899 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1127 | 0 | 0 | 0 | 1451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 409 | 0 | 0 | 0 | 50 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 120 | 220 | 0 | 0 | 1085 | 0 | 6245 | 12749.4 | 90.37
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 33 | 0 | 34 | 0 | 0 | 0 | 35 | 87 | 0 | 0 | 0 | 360 | 0 | 0 | 250 | 0 | 0 | 0 | 108 | 12 | 22 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 20 | 635 | 0 | 0 | 0 | 0 | 66 | 226 | 0 | 0 | 0 | 1170 | 0 | 0 | 0 | 220 | 50 | 285 | 51 | 0 | 167 | 0 | 50 | 102 | 50 | 0 | 20 | 0 | 144 | 0 | 0 | 0 | 305 | 0 | 366 | 42 | 0 | 158 | 0 | 22 | 0 | 40 | 0 | 71 | 0 | 96 | 0 | 115 | 58 | 21 | 0 | 0 | 6 | 6292 | 899 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1123 | 0 | 0 | 0 | 1449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 50 | 50 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 120 | 220 | 0 | 0 | 1085 | 0 | 6183 | 12475 | 90.36
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 28.4 | 0 | 34 | 0 | 0 | 0 | 17 | 52 | 0 | 0 | 0 | 350 | 0 | 0 | 250 | 0 | 0 | 0 | 90 | 12 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 20 | 580 | 0 | 0 | 0 | 0 | 34 | 226 | 0 | 0 | 0 | 1170 | 0 | 0 | 0 | 260 | 0 | 280 | 51 | 0 | 195 | 0 | 47 | 101 | 17 | 0 | 20 | 0 | 144 | 0 | 0 | 0 | 310 | 0 | 357 | 41 | 0 | 156 | 0 | 22 | 0 | 40 | 0 | 69 | 0 | 96 | 0 | 97 | 49 | 18 | 0 | 0 | 6 | 6005.4 | 900 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1125 | 0 | 0 | 0 | 1452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 50 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 120 | 220 | 0 | 0 | 1085 | 0 | 6125 | 12130.4 | 90.35
Total KWH | 0 | 47040 | 21120 | 0 | 0 | 0 | 0 | 0 | 8161200 | 0 | 0 | 180000 | 0 | 506448 | 0 | 0 | 0 | 280894 | 619200 | 0 | 0 | 0 | 8353314 | 0 | 0 | 6622957 | 0 | 0 | 171151 | 1640400 | 430200 | 466200 | 0 | 8373181.82 | 0 | 0 | 0 | 0 | 50880 | 237498 | 0 | 0 | 0 | 0 | 19199 | 1925340 | 0 | 362880 | 16385454.55 | 0 | 0 | 0 | 0 | 302764 | 5067286 | 0 | 0 | 0 | 26476361 | 122580 | 0 | 0 | 6720000 | 2760200 | 2640000 | 1008422 | 0 | 4347000 | 0 | 248640 | 2379921 | 179520 | 0 | 470970 | 0 | 3046080 | 0 | 443691 | 0 | 6984000 | 0 | 9297000 | 984000 | 0 | 3637555 | 61725 | 461664 | 0 | 830400 | 0 | 1649000 | 0 | 2308530 | 0 | 1824000 | 1466400 | 340800 | 11800 | 256220 | 106080 | 141287166.37 | 21312727 | 4741920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 511920 | 23120000 | 0 | 0 | 0 | 29659542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264440 | 574710 | 0 | 0 | 255760 | 0 | 0 | 4515218 | 0 | 0 | 0 | 9651636 | 0 | 24480 | 0 | 1023709 | 757817 | 189028 | 1009891 | 0 | 0 | 0 | 38389.92 | 1048320 | 3783 | 0 | 6218000 | 2853000 | 5221060 | 0 | 0 | 22896000 | 0 | 135891350.92 | 277178517.29

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 06-03-2026
Power Supply Scenario
| Day Peak Generation |  |  | 11475.99 | MW | 12:00 Hr. | Energy Generated |  |  | 277.1785 |  | MKWHr.
| Day Peak Demand |  |  | 11475.99 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.065 |  | MKWHr.
| Evening Peak Generation |  |  | 12749.4 | MW | 21:00 Hr. | Energy Demand |  |  | 277.2435 |  | MKWHr.
| Evening Peak Demand |  |  | 12749.4 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34.3 |  | °C
| Minimum Generation of the Day |  |  | 9518.92 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 825.07 |  | MMCFD
| Maximum Generation of the Day |  |  | 12749.4 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 5.5421 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 32.4071 | 0 | 3.2951 | 0 | 0 | 0.17115 | 0 | 0 | 35.8733 | Gas | 111.6395 | Gas | 382452175.6494
| Chattogram Zone |  |  | 5.4302 | 42.8618 | 0.54026 | 0 | 1.9253 | 0.14178 | 0 | 0.05088 | 50.9502 | Coal | 96.1195 | Coal | 626556113.8115
| Cumilla Zone |  |  | 20.3265 | 0 | 0.42816 | 0 | 0 | 0.44369 | 3.0461 | 0 | 24.2444 | HFO | 9.4277 | HFO | 155643598.26
| Mymensingh Zone |  |  | 0.3408 | 0 | 3.3965 | 0 | 0 | 0.26802 | 0 | 0 | 4.0053 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.1521 | 0 | 0 | 0 | 0 | 0.061725 | 0 | 0 | 26.2139 | Hydro | 1.9253 | Hydro | 192534
| Khulna Zone |  |  | 4.7419 | 23.12 | 0 | 0 | 0 | 0.51192 | 21.3127 | 0 | 49.6866 | Solar | 3.9972 | Solar | 64281205.984
| Barishal Zone |  |  | 8.0741 | 29.114 | 0 | 0 | 0 | 0.003783 | 0 | 0 | 37.1918 | Import | 54.0183 | Import | 306277714.16
| Rajshahi Zone |  |  | 14.1669 | 0 | 0 | 0 | 0 | 1.1194 | 29.6595 | 0 | 44.9458 | Wind | 0.05088 | Wind | 748444.8
| Rangpur Zone |  |  | 0 | 1.0237 | 1.7677 | 0 | 0 | 1.2757 | 0 | 0 | 4.0672
| Total |  |  | 111.6395 | 96.1195 | 9.4277 | 0 | 1.9253 | 3.9972 | 54.0183 | 0.05088 | 277.1785
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 382452175.6494 |  | Hydro | 192534
|  |  |  | Coal | 626556113.8115 |  | Solar | 64281205.984
|  |  |  | HFO | 155643598.26 |  | Import | 306277714.16
|  |  |  | HSD | 0 |  | Wind | 748444.8
[5 empty] | Total: | 153,61,51,786 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.3127 | Peak Hr Flow | 899.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 45126854.54 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 29.6595 | Peak Hr Flow | 1451.00 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2357 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.0461 | Peak Hr Flow | 140.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2586 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 54.0183 | Peak Hr Flow | 2490.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4545
|  |  |  | Chattogram |  | 0 |  | 1274
|  |  |  | Cumilla |  | 0 |  | 1211
|  |  |  | Mymensingh |  | 0 |  | 1080
|  |  |  | Sylhet |  | 0 |  | 525
|  |  |  | Khulna |  | 0 |  | 1389
|  |  |  | Barishal |  | 0 |  | 354
|  |  |  | Rajshahi |  | 0 |  | 1183
|  |  |  | Rangpur |  | 0 |  | 703
|  |  |  | Total |  | 0 |  | 12264
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:18 | 10:37 | Meghnaghat 400/230kV S/S ATR-1 HT Scheduled S/D Due to for maintenance work.
| 08:19 | 08:47 | Cumilla(S) 132/33kV S/S TR-3 LT Tripped showing RET 650 ,REF615 relays. | [7 empty] | 33.0MW load
interrup.
| 08:27 | 10:38 | Meghnaghat 400/230kV S/S ATR-1 LT Scheduled S/D Due to for maintenance work.
| 09:30 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- GT
|  | 10:14 | Daudkandi 132/33kV S/S Transformer-2 LT is restored.
|  | 11:25 | Rahanpur 400/132kV S/S Rahanpur-Chapainawabganj 132 KV Line Ckt-02 is restored.
|  | 11:26 | Chapainawabganj-Rahanpur 132kV Ckt-1 is restored.
|  | 11:26 | Chapai 132/33kV S/S Chapai Rahanpur ckt 2 is restored.
|  | 11:26 | Chapai 132/33kV S/S Main Bus is restored.
| 11:36 |  | Barapukuria Unit-1 tripped due to feed pump problem.
|  | 11:44 | Amnura-Chapainawabganj-132kV Ckt-1 is restored.
|  | 11:46 | C.nawabganj-Rajshahi 132 kV Ckt-1 is restored.
| 12:00 |  | Day Peak Generation: 11473 MW.
| 13:31 |  | Ashuganj (South) 360 MW CCPP ST was sync.
| 19:57 | 20:56 | Bhangura 132/33kV S/S Tr-2(413T) LT Forced S/D Due to 33Kv ct red hot
| 20:00 | 20:58 | Bhangura 132/33kV S/S Tr-2(413T) HT Forced S/D Due to 33 KV CT Red hot
| 20:24 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- gt
| 21:00 |  | Evening peak Generation is 12749 MW
|  | 21:43 | Jashore 132/33kV S/S JH-1(L2) is restored.
| 21:51 | 00:05 | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to 33 kV section DS-C and Mehendigonj | [7 empty] | 35.0MW load
|  |  | source DS repair | [7 empty] | interrup.
| 21:51 | 00:07 | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to 33 kV section DS-C and Mehendigonj | [7 empty] | 35.0MW load
|  |  | source DS repair | [7 empty] | interrup.
| 22:17 |  | Ashuganj North 360 MW was shutdown.
| 22:17 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- GT
| 03:35 |  | Baroaulia-Hathazari 132 kV Ckt-1 Tripped from Hathazari 230/132/33kV end showing Alstom
Quadrahmo relays Due to R-phase wire broken
| 07:50 |  | Kabirpur 132/33kV S/S Main bus Scheduled S/D Due to DS changing work
| 07:55 |  | Kabirpur 132/33kV S/S XFR, T-3 HT Scheduled S/D Due to DS changing work
| 07:55 |  | Kabirpur 132/33kV S/S XFR, T-3 LT Scheduled S/D Due to DS changing work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 06-03-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0"MW due to gas restriction by Titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 315 | 8161200 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 250 | 6622957 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 33.4 | 180000 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 280894 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18 | 430200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 466200 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 21120 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 34 | 506448 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 47040 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 85 | 619200 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 171151 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 390 | 8373181.82 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 355 | 8353314 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 108 | 1640400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1645.4 | 35873305.82
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 122580 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1925340 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 225 | 5067286 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 67 | 302764 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 237498 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 362880 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 19199 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1160 | 26476361 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 50880 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 635 | 16385454.55 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 2187 | 50950242.55
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 196 | 4347000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 92 | 2760200 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 325 | 2640000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 330 | 6720000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1008422 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 101 | 2379921 | Tripped
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 179520 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 140 | 3046080 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 470970 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 51 | 248640 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 443691 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1357 | 24244444
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 21 | 340800 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 78 | 1466400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 115 | 1824000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 256220 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 11 | 106080 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 225 | 4005300
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 61725 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 984000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 156 | 3637555 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 70 | 1649000 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 40 | 830400 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 95 | 2308530 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 22 | 461664 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 6984000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 365 | 9297000 | Due to Air Filter DP High FGMO not available.
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1090 | 26213874
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 899 | 21312727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 205 | 4741920 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 511920 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1127 | 23120000 | plant availability zero
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2231 | 49686567
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2853000 | Plant availability less
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 1085 | 22896000 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5221060 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 276 | 6218000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3783 | -
Barishal Area Total |  |  |  |  | 2700.36 | 1701 | 37191843
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 264440 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Shutdown As Per PGB PLC's Requirements.
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 189 | 4515218 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 409 | 9651636 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 24480 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1451 | 29659542 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 255760 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 574710 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2049 | 44945786
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1023709 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 99 | 1009891 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 38389.92 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 757817 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 189028 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1048320 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 264 | 4067154.92
Eastern Grid Total |  |  |  |  | 17400.108 | 6504.4 | 141287166.37
Western Grid Total |  |  |  |  | 10985.595 | 6245 | 135891350.92
National Grid Total |  |  |  |  | 28385.703 | 12749.4 | 277178517.29
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 06-03-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8634.46 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3628.6 | MW
i) Dhaka area |  |  | 4544.86 |  | MW | i) Khulna area |  |  |  | 1389 | MW
ii) Chattogram area |  |  | 1273.6 |  | MW | ii) Barishal area |  |  |  | 354 | MW
iii) Cumilla area |  |  | 1211 |  | MW | iii) Rajshahi area |  |  |  | 1182.6 | MW
iv) Mymensingh area |  |  | 1080 |  | MW | iv) Rangpur area |  |  |  | 703 | MW
v) Sylhet area |  |  | 525 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12263.06 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 70 | 22:00 | 133 | Nawabganj | 37.6 | 13:00
2 | AKSML | 15.6 | 21:00 | 68 | Hathazari | 67 | 21:00 | 134 | Netrakona | 153 | 17:00
3 | Aftabnagar | 32 | 19:00 | 69 | Hatirjheel | 31 | 15:00 | 135 | New | 54 | 11:00
4 | Agargaon | 88 | 19:30 | 70 | Ishurdi | 58 | 04:00 | 136 | Niamatpur | 92 | 08:00
5 | Agrabad | 44 | 19:00 | 71 | Jaldhaka | 70 | 18:00 | 137 | Noapara | 33 | 18:30
6 | Amnura | 34 | 08:00 | 72 | Jamalpur | 110 | 17:00 | 138 | PHP | 8 | 16:00
7 | Ashuganj | 73 | 23:00 | 73 | Jashore | 118 | 19:00 | 139 | Pabna | 74 | 04:00
8 | BSRM | 198 | 03:00 | 74 | Jhenaidah | 82 | 18:00 | 140 | Palashbari | 98 | 17:00
9 | Bagerhat | 69 | 22:00 | 75 | Joydebpur | 94 | 16:00 | 141 | Panchagarh | 49 | 18:00
10 | Bajitpur | 77 | 18:00 | 76 | Joypurhat | 64 | 09:00 | 142 | Patiya | 7 | 13:00
11 | Bakerganj | 10.56 | 19:30 | 77 | Juldah | 13 | 00:00 | 143 | Patuakhali | 43 | 22:00
12 | Bakulia | 81 | 00:00 | 78 | KSRM | 13 | 14:00 | 144 | Payra | 30 | 19:30
13 | Banani | 37.2 | 19:30 | 79 | Kabirpur | 191 | 00:00 | 145 | Postogola | 45 | 00:00
14 | Bangabhaban | 4 | 10:00 | 80 | Kachua | 73 | 18:30 | 146 | Purbachal | 25 | 21:00
15 | Barapukuria | 58 | 10:00 | 81 | Kaliganj | 23 | 13:00 | 147 | Purbasadipur | 121 | 13:00
16 | Barguna | 16 | 21:00 | 82 | Kallyanpur | 96 | 13:00 | 148 | Rahanpur | 26 | 04:00
17 | Barishal | 78 | 22:00 | 83 | Kalurghat | 28 | 00:00 | 149 | Rahim | 80 | 16:00
18 | Barishal-230 | 68 | 18:00 | 84 | Kamrangirchar | 72 | 00:00 | 150 | Rajbari | 58 | 19:00
19 | Baroaulia | 53 | 12:00 | 85 | Kaptai | N/A | N/A | 151 | Rajendrapur | 112 | 00:00
20 | Baroirhat | 47 | 18:30 | 86 | Kasba | 32 | 20:00 | 152 | Rajshahi | 98 | 04:00
21 | Bashundhara | 172 | 21:00 | 87 | Kazla | 94 | 00:00 | 153 | Rajshahi-230 | 59 | 04:00
22 | BashundharaCement | 8 | 00:00 | 88 | Keranigonj | 74 | 13:00 | 154 | Ramganj | 82 | 13:00
23 | Beanibazar | 60 | 18:30 | 89 | Khagrachori | 28 | 18:30 | 155 | Rampur | 35 | 00:00
24 | Benapole | 52 | 13:00 | 90 | Khulna | 45 | 19:00 | 156 | Rangamati | 15 | 18:30
25 | Bhaluka | 130 | 11:00 | 91 | Khulshi | 174 | 12:00 | 157 | Rangpur | 126 | 18:00
26 | Bhandaria | 48 | 21:00 | 92 | Kishoreganj | 119 | 18:00 | 158 | Ruppur | 2.8 | 10:00
27 | Bhangura | 41 | 13:00 | 93 | Kodda | 249 | 00:00 | 159 | SSM | 3 | 04:00
28 | Bheramara(GK) | 48 | 18:00 | 94 | Kulaura | 40 | 18:30 | 160 | Saidpur | 83 | 13:00
29 | Bhulta | 212 | 02:00 | 95 | Kurigram | 64 | 17:00 | 161 | Satkhira | 125 | 19:00
30 | Bog-Sherpur | 70 | 04:00 | 96 | Kushtia | 113 | 03:00 | 162 | Satmasjid | 85 | 20:00
31 | Bogura | 127 | 21:00 | 97 | Laksam | 26 | 21:00 | 163 | Savar | 162 | 13:00
32 | Borhanuddin | 71 | 21:00 | 98 | Lakshmipur | 21 | 21:00 | 164 | SevenRings | 16.56 | 17:00
33 | Brahmanbaria | 118 | 20:00 | 99 | Lalbag | 55 | 00:00 | 165 | ShahCement | 30 | 21:00
34 | Cantonment | 88 | 13:00 | 100 | Lalmonirhat | 50 | 17:00 | 166 | Shahjadpur | 58 | 09:00
35 | Chandina | 12 | 18:30 | 101 | MI_Cement | 17.5 | 21:00 | 167 | Shahjibazar | 113 | 21:00
36 | Chandpur | 60 | 21:00 | 102 | Madanganj | 48 | 17:00 | 168 | Shahmirpur | 41.5 | 00:00
37 | Chandraghona | 32 | 18:30 | 103 | Madaripur | 87 | 21:00 | 169 | Shariatpur | 66 | 13:00
38 | Chapai | 60 | 20:00 | 104 | Madartek | 66 | 13:00 | 170 | Sherpur | 150 | 18:00
39 | Charsaidpur | 55 | 16:00 | 105 | Madunaghat | 41 | 21:00 | 171 | Shikalbaha | 28.5 | 00:00
40 | Chauddagram | 66 | 13:00 | 106 | Magura | 50 | 18:30 | 172 | Shitalakhya | 57.6 | 15:00
41 | Chhatak | 33 | 18:30 | 107 | Mahasthangarh | 72 | 04:00 | 173 | Sholosohor | 36 | 21:00
42 | Chowmuhani | 112 | 20:00 | 108 | Maijdee | 37 | 21:00 | 174 | Shyampur | 142 | 00:00
43 | Chuadanga | 95 | 03:00 | 109 | Manikganj | 102 | 21:00 | 175 | Siddhirganj | 101 | 12:00
44 | Coxsbazar | 118 | 21:00 | 110 | Maniknagar | 51 | 13:00 | 176 | Sirajganj | 94 | 04:00
45 | Cumilla(N) | 101 | 12:00 | 111 | Matarbari | 42 | 03:00 | 177 | Sonargaon | 145 | 02:00
46 | Cumilla(S) | 146 | 19:30 | 112 | Matuail | 64 | 00:00 | 178 | Sreemongol | 64 | 18:00
47 | Daganbhuiyan | 25 | 18:30 | 113 | Metrorail_Motijheel | 20 | 20:00 | 179 | Sreepur | 95 | 17:00
48 | Daudkandi | 126 | 20:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Srinagar | 38.6 | 13:00
49 | DhakaUniversity | 40 | 12:00 | 115 | Millgate | 68 | 12:00 | 181 | Sunamganj | 48 | 21:00
50 | Dhamrai | 110 | 00:00 | 116 | Mirpur | 124 | 13:00 | 182 | Sylhet | 48 | 21:00
51 | Dhanmondi | 85 | 19:30 | 117 | Mirsorai | 45 | 07:00 | 183 | Sylhet-132 | 90 | 21:00
52 | Dohazari | 86 | 21:00 | 118 | Mirzapur | 44 | 12:00 | 184 | TK | 19 | 20:00
53 | Faridpur | 119 | 19:00 | 119 | Mithapukur | 56 | 04:00 | 185 | Tangail | 160 | 13:00
54 | Fatullah | 85 | 00:00 | 120 | Modern | N/A | N/A | 186 | Taraganj | 21 | 17:00
55 | Fenchuganj | 30 | 18:30 | 121 | Mogbazar | 65.6 | 13:00 | 187 | Tasnim | 22 | 16:00
56 | Feni | 85 | 21:00 | 122 | Mongla | 38 | 00:00 | 188 | Thakurgaon | 83 | 13:00
57 | GPH | 3 | 01:00 | 123 | Motijheel | 35 | 13:00 | 189 | Tongi | 137 | 15:00
58 | Ghatail | 86 | 17:00 | 124 | Muktagacha | 37 | 17:00 | 190 | Ullahpara | 34 | 10:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 76 | 13:00 | 191 | Ullon | 59 | 20:00
60 | Ghorashal-230 | 97 | 00:00 | 126 | Muradnagar | 34 | 18:30 | 192 | Uttara | 70 | 19:30
61 | Goalpara | 24 | 00:00 | 127 | Mymensingh | 194 | 17:00 | 193 | UttaraNew | 26 | 18:30
62 | Gollamari | 84 | 19:30 | 128 | Naogaon | 108 | 10:00 | 194 | Zigatola | 68 | 19:30
63 | Gopalganj | 89.3 | 19:00 | 129 | Narail | 50 | 19:30
64 | Gulshan | 74 | 19:00 | 130 | Narinda | 48 | 21:00
65 | Halishahar | 61.5 | 19:30 | 131 | Narshingdi | 157 | 21:00
66 | HaripurSBU | 110 | 00:00 | 132 | Natore | 116 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 06-03-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 12112 | 0 |  | 12112
1:00 | 11449.5 | 0 |  | 11449.5
2:00 | 11037.5 | 0 |  | 11037.5
3:00 | 11248.5 | 0 |  | 11248.5
4:00 | 11819.5 | 0 |  | 11819.5
5:00 | 10793 | 0 |  | 10793
6:00 | 9687.5 | 0 |  | 9687.5
7:00 | 9518.92 | 0 |  | 9518.92
8:00 | 9879.9 | 0 |  | 9879.9
9:00 | 10436.02 | 0 |  | 10436.02
10:00 | 10708.16 | 0 |  | 10708.16
11:00 | 11028.95 | 0 |  | 11028.95
12:00 | 11475.99 | 0 |  | 11475.99
13:00 | 12179.39 | 0 |  | 12179.39
14:00 | 11291.81 | 0 |  | 11291.81
15:00 | 11573.55 | 10 |  | 11583.55
16:00 | 11615.52 | 29 |  | 11645.52
17:00 | 11936.78 | 26 |  | 11963.78
18:00 | 12154.86 | 0 |  | 12154.86
19:00 | 12380.2 | 0 |  | 12380.2
19:30 | 12419.2 | 0 |  | 12419.2
20:00 | 12458.9 | 0 |  | 12458.9
21:00 | 12749.4 | 0 |  | 12749.4
22:00 | 12475 | 0 |  | 12475
23:00 | 12130.4 | 0 |  | 12130.4
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 06-03-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6095 | 6017 | 12112 | DAILY GENERATION CURVE
00:30 | 6016.25 | 5764.5 | 11780.75
01:00 | 5937.5 | 5512 | 11449.5 | 06-03-2026
01:30 | 5830 | 5413.5 | 11243.5
02:00 | 5722.5 | 5315 | 11037.5
02:30 | 5740.5 | 5402.5 | 11143
03:00 | 5758.5 | 5490 | 11248.5
03:30 | 5855 | 5679 | 11534
04:00 | 5951.5 | 5868 | 11819.5
04:30 | 5771.25 | 5535 | 11306.25
05:00 | 5591 | 5202 | 10793
05:30 | 5353.25 | 4887 | 10240.25
06:00 | 5115.5 | 4572 | 9687.5
06:30 | 5124.055 | 4479.155 | 9603.21
07:00 | 5132.61 | 4386.31 | 9518.92
07:30 | 5316.18 | 4383.23 | 9699.41
08:00 | 5499.75 | 4380.15 | 9879.9
08:30 | 5507.165 | 4650.795 | 10157.96
09:00 | 5514.58 | 4921.44 | 10436.02
09:30 | 5452.79 | 5119.3 | 10572.09
10:00 | 5391 | 5317.16 | 10708.16
10:30 | 5433.475 | 5435.08 | 10868.555
11:00 | 5475.95 | 5553 | 11028.95
11:30 | 5627.54 | 5624.93 | 11252.47
12:00 | 5779.13 | 5696.86 | 11475.99
12:30 | 5943.38 | 5884.31 | 11827.69
13:00 | 6107.63 | 6071.76 | 12179.39
13:30 | 5943.68 | 5791.92 | 11735.6
14:00 | 5779.73 | 5512.08 | 11291.81
14:30 | 5884.35 | 5548.33 | 11432.68
15:00 | 5988.97 | 5584.58 | 11573.55
15:30 | 5935.8 | 5658.735 | 11594.535
16:00 | 5882.63 | 5732.89 | 11615.52
16:30 | 5923.415 | 5852.735 | 11776.15
17:00 | 5964.2 | 5972.58 | 11936.78
17:30 | 6012.7 | 6033.12 | 12045.82
18:00 | 6061.2 | 6093.66 | 12154.86
18:30 | 6131.2 | 6136.33 | 12267.53
19:00 | 6201.2 | 6179 | 12380.2
19:30 | 6251.2 | 6168 | 12419.2
20:00 | 6317.9 | 6141 | 12458.9
20:30 | 6411.15 | 6193 | 12604.15 |  | Executive Engineer
21:00 | 6504.4 | 6245 | 12749.4 |  | Network Operation Division
21:30 | 6398.2 | 6214 | 12612.2
22:00 | 6292 | 6183 | 12475
22:30 | 6148.7 | 6154 | 12302.7
23:00 | 6005.4 | 6125 | 12130.4

## En-Curve
QF-LDC-12
Date | 06-03-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3217 | 1537 | 900 | 0 | 142 | 1393 | 80 | 4490 | 0 | 121 | 232 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3161 | 1554.75 | 899.5 | 0 | 137 | 1308.5 | 80 | 4314 | 0 | 112 | 214 | 0 | 0 | 0 | 0 | 06-03-2026
01:00 | 3105 | 1572.5 | 899 | 0 | 132 | 1224 | 80 | 4138 | 0 | 103 | 196 | 0 | 0 | 0 | 0
01:30 | 2996 | 1518 | 899 | 0 | 127 | 1222.5 | 80 | 4123.5 | 0 | 94.5 | 183 | 0 | 0 | 0 | 0 | Energy Generated | 277.1785 |  | MKWHr
02:00 | 2887 | 1463.5 | 899 | 0 | 122 | 1221 | 80 | 4109 | 0 | 86 | 170 | 0 | 0 | 0 | 0 | Energy not Served | 0.065 |  | MKWHr
02:30 | 2849 | 1449 | 899.5 | 0 | 124 | 1267.5 | 80 | 4144.5 | 0 | 101 | 228.5 | 0 | 0 | 0 | 0 | Total Energy Requirement | 277.2435 |  | MKWHr
03:00 | 2811 | 1434.5 | 900 | 0 | 126 | 1314 | 80 | 4180 | 0 | 116 | 287 | 0 | 0 | 0 | 0
03:30 | 2920 | 1486.5 | 899.5 | 0 | 125 | 1384 | 80 | 4201 | 0 | 131 | 307 | 0 | 0 | 0 | 0
04:00 | 3029 | 1538.5 | 899 | 0 | 124 | 1454 | 80 | 4222 | 0 | 146 | 327 | 0 | 0 | 0 | 0
04:30 | 3033.5 | 1530.75 | 899.5 | 0 | 124 | 1325.5 | 80 | 3953 | 0 | 99 | 260.5 | 0 | 0 | 0.5 | 0
05:00 | 3038 | 1523 | 900 | 0 | 124 | 1197 | 80 | 3684 | 0 | 52 | 194 | 0 | 0 | 1 | 0
05:30 | 2951.5 | 1428.25 | 899.5 | 0 | 119 | 1079.5 | 80 | 3499.5 | 0 | 34.5 | 147 | 0 | 0 | 1.5 | 0
06:00 | 2865 | 1333.5 | 899 | 0 | 114 | 962 | 80 | 3315 | 0 | 17 | 100 | 0 | 0 | 2 | 0
06:30 | 2873.5 | 1338.25 | 840 | 0 | 115 | 910.5 | 80 | 3318 | 18.46 | 8.5 | 100 | 0 | 0 | 1 | 0
07:00 | 2882 | 1343 | 781 | 0 | 116 | 859 | 80 | 3321 | 36.92 | 0 | 100 | 0 | 0 | 0 | 0
07:30 | 2959.5 | 1362 | 723 | 0 | 107 | 849 | 80 | 3406 | 98.41 | 0 | 114.5 | 0 | 0 | 0 | 0
08:00 | 3037 | 1381 | 665 | 0 | 98 | 839 | 80 | 3491 | 159.9 | 0 | 129 | 0 | 0 | 0 | 0
08:30 | 3044.5 | 1384 | 782.5 | 0 | 108 | 853.5 | 80 | 3533 | 233.46 | 8.5 | 130.5 | 0 | 0 | 0 | 0
09:00 | 3052 | 1387 | 900 | 0 | 118 | 868 | 80 | 3575 | 307.02 | 17 | 132 | 0 | 0 | 0 | 0
09:30 | 3062.5 | 1308 | 900 | 0 | 116 | 942 | 80 | 3623.5 | 375.59 | 32.5 | 132 | 0 | 0 | 0 | 0
10:00 | 3073 | 1229 | 900 | 0 | 114 | 1016 | 80 | 3672 | 444.16 | 48 | 132 | 0 | 0 | 0 | 0
10:30 | 3077.5 | 1246.5 | 900 | 0 | 119 | 1053 | 80 | 3695 | 515.555 | 50 | 132 | 0 | 0 | 0 | 0
11:00 | 3082 | 1264 | 900 | 0 | 124 | 1090 | 80 | 3718 | 586.95 | 52 | 132 | 0 | 0 | 0 | 0
11:30 | 3114.5 | 1336.5 | 900 | 0 | 125 | 1112.5 | 80 | 3753 | 606.97 | 62 | 162 | 0 | 0 | 0 | 0
12:00 | 3147 | 1409 | 900 | 0 | 126 | 1135 | 80 | 3788 | 626.99 | 72 | 192 | 0 | 0 | 0 | 0
12:30 | 3139.5 | 1498.5 | 900.5 | 0 | 132 | 1224 | 80 | 3853 | 609.69 | 106.5 | 281.5 | 0 | 0 | 2.5 | 0
13:00 | 3132 | 1588 | 901 | 0 | 138 | 1313 | 80 | 3918 | 592.39 | 141 | 371 | 0 | 0 | 5 | 0
13:30 | 3110 | 1570 | 900.5 | 0 | 134 | 1222 | 80 | 3801 | 556.6 | 105.5 | 246 | 0 | 0 | 10 | 0
14:00 | 3088 | 1552 | 900 | 0 | 130 | 1131 | 80 | 3684 | 520.81 | 70 | 121 | 0 | 0 | 15 | 0
14:30 | 3140.5 | 1591.5 | 900 | 0 | 131 | 1182 | 80 | 3749.5 | 458.18 | 70 | 115.5 | 0 | 0 | 14.5 | 5
15:00 | 3193 | 1631 | 900 | 0 | 132 | 1233 | 80 | 3815 | 395.55 | 70 | 110 | 0 | 0 | 14 | 10
15:30 | 3170.5 | 1603.5 | 900 | 0 | 131 | 1278 | 80 | 3924 | 311.035 | 70 | 113.5 | 0 | 0 | 13 | 19.5
16:00 | 3148 | 1576 | 900 | 0 | 130 | 1323 | 80 | 4033 | 226.52 | 70 | 117 | 0 | 0 | 12 | 29
16:30 | 3141.5 | 1568 | 900 | 0 | 133 | 1390 | 80 | 4096 | 153.65 | 89 | 219 | 0 | 0 | 6 | 27.5
17:00 | 3135 | 1560 | 900 | 0 | 136 | 1457 | 80 | 4159 | 80.78 | 108 | 321 | 0 | 0 | 0 | 26
17:30 | 3134 | 1577 | 900.5 | 0 | 134 | 1455.5 | 80 | 4173 | 40.72 | 108 | 443.1 | 0 | 0 | 0 | 13
18:00 | 3133 | 1594 | 901 | 0 | 132 | 1454 | 80 | 4187 | 0.66 | 108 | 565.2 | 0 | 0 | 0 | 0
18:30 | 3167 | 1603.5 | 901 | 0 | 137 | 1454 | 80 | 4239.5 | 0.33 | 108 | 577.2 | 0 | 0 | 0 | 0
19:00 | 3201 | 1613 | 901 | 0 | 142 | 1454 | 80 | 4292 | 0 | 108 | 589.2 | 0 | 0 | 0 | 0
19:30 | 3158 | 1629 | 831 | 0 | 144 | 1454 | 80 | 4330 | 0 | 108 | 685.2 | 0 | 0 | 0 | 0
20:00 | 3198 | 1629 | 805 | 0 | 144 | 1445 | 80 | 4332 | 0 | 108 | 717.9 | 0 | 0 | 0 | 0
20:30 | 3274 | 1621.5 | 852 | 0 | 142 | 1448 | 80 | 4332.5 | 0 | 108 | 746.15 | 0 | 0 | 0 | 0
21:00 | 3350 | 1614 | 899 | 0 | 140 | 1451 | 80 | 4333 | 0 | 108 | 774.4 | 0 | 0 | 0 | 0
21:30 | 3248.5 | 1619.5 | 899 | 0 | 142 | 1450 | 80 | 4336.5 | 0 | 108 | 728.7 | 0 | 0 | 0 | 0
22:00 | 3147 | 1625 | 899 | 0 | 144 | 1449 | 80 | 4340 | 0 | 108 | 683 | 0 | 0 | 0 | 0
22:30 | 3143 | 1599 | 899.5 | 0 | 144 | 1450.5 | 80 | 4313.5 | 0 | 99 | 574.2 | 0 | 0 | 0 | 0
23:00 | 3139 | 1573 | 900 | 0 | 144 | 1452 | 80 | 4287 | 0 | 90 | 465.4 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 06-03-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 401 | 08:00 | 384 | 16:00 | Madunaghat | 404 | 07:00 | 395 | 00:00
Amtali | 418 | 06:00 | 409 | 17:00 | Meghnaghat | 400 | 07:00 | 385 | 15:00
Ashuganj | 412 | 7:00 | 389 | 15:00 | Payra | 420 | 08:00 | 411 | 16:00
Bhulta | 405 | 06:00 | 382 | 16:00 | Rahanpur | 416 | 06:00 | 396 | 17:00
Bibiana | 408 | 05:00 | 392 | 16:00 | Rampal | 410 | 06:00 | 398 | 13:00
BIPTC | 403 | 08:00 | 389 | 12:00
Bogura | 405 | 06:00 | 382 | 17:00
Gopalganj | 409 | 07:00 | 396 | 00:00
Kaliakoir | 389 | 06:00 | 360 | 16:00
Korerhat | 405 | 06:00 | 394 | 16:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 236 | 06:00 | 224 | 16:00 | Jhenaidah | 236 | 07:00 | 222 | 13:00
AKSML | 239 | 09:00 | 224 | 00:00 | Kachua | 232 | 06:00 | 224 | 12:00
Aminbazar | 236 | 07:00 | 226 | 12:00 | Kaliakoir | 237 | 07:00 | 221 | 16:00
Ashuganj | 231 | 05:00 | 219 | 16:00 | Keranigonj | 235 | 07:00 | 223 | 16:00
Ashuganj-400 | 232 | 7:00 | 218 | 15:00 | Khulna(S) | 238 | 06:00 | 225 | 19:00
Baghabari | 235 | 06:00 | 224 | 16:00 | Korerhat | 230 | 02:00 | 224 | 12:00
Barapukuria | 220 | 21:00 | 196 | 12:00 | Madunaghat | 230 | 06:00 | 224 | 00:00
Barapukuria-230 | 220 | 21:00 | 207 | 13:00 | Madunaghat-400 | 231 | 06:00 | 225 | 00:00
Barishal | 233 | 06:00 | 227 | 16:00 | Maniknagar | 231 | 04:00 | 223 | 16:00
Bheramara | 234 | 03:00 | 221 | 16:00 | Meghnaghat | 240 | 05:00 | 231 | 16:00
Bhulta | 234 | 06:00 | 222 | 16:00 | Meghnaghat-400 | 237 | 07:00 | 227 | 15:00
Bibiana | 237 | 06:00 | 227 | 16:00 | Mirsorai | 231 | 07:00 | 223 | 00:00
BIPTC | 236 | 03:00 | 221 | 16:00 | Rajshahi | 233 | 03:00 | 220 | 13:00
Bogura | 239 | 06:00 | 224 | 17:00 | Rampal | 237 | 06:00 | 226 | 13:00
Bogura-400 | 239 | 06:00 | 225 | 17:00 | Rampur | N/A | N/A | N/A | N/A
Borhanuddin | 238 | 06:00 | 232 | 13:00 | Rampura | 232 | 06:00 | 220 | 16:00
BSRM | 230 | 06:00 | 224 | 00:00 | Shikalbaha | 229 | 07:00 | 222 | 12:00
Chowmuhani | 231 | 06:00 | 223 | 16:00 | Shyampur | 235 | 07:00 | 224 | 16:00
Cumilla(N) | 233 | 07:00 | 224 | 00:00 | Siddhirganj | 234 | 04:00 | 225 | 15:00
Faridpur | 231 | 06:00 | 221 | 17:00 | Sirajgonj | 238 | 05:00 | 229 | 17:00
Fenchuganj | 236 | 08:00 | 231 | 15:00 | Sreepur | 227 | 06:00 | 214 | 16:00
Feni | 232 | 06:00 | 224 | 16:00 | Tongi | 230 | 04:00 | 216 | 15:00
Ghorashal | 235 | 06:00 | 225 | 00:00
Ghorashal-230 | 231 | 06:00 | 215 | 16:00
Gopalganj | 230 | 08:00 | 221 | 17:00
GPH | 230 | 06:00 | 224 | 12:00
Haripur | 235 | 07:00 | 224 | 16:00
Hasnabad | 235 | 06:00 | 224 | 16:00
Hathazari | 229 | 08:00 | 220 | 18:30
Ishurdi | 237 | 07:00 | 223 | 16:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 06:00 | 130 | 16:00 | Magura | 135 | 02:00 | 125 | 12:00
Agargaon | 140 | 07:00 | 132 | 16:00 | Mahasthangarh | 135 | 05:00 | 124 | 17:00
Agrabad | 132 | 05:00 | 127 | 15:00 | Maijdee | 129 | 06:00 | 124 | 16:00
AKS | 130 | 06:00 | 126 | 00:00 | Manikganj | 134 | 05:00 | 125 | 16:00
Aminbazar | 136 | 04:00 | 131 | 12:00 | Maniknagar | 131 | 06:00 | 124 | 16:00
Amnura | 137 | 06:00 | 127 | 09:00 | Matarbari | 129 | 09:00 | 111 | 18:30
Ashuganj | 141 | 08:00 | 133 | 16:00 | Matuail | 133 | 07:00 | 126.5 | 16:00
Bagerhat | 136 | 06:00 | 121 | 19:00 | Metrorail_Motijheel | 132 | 07:00 | 124 | 16:00
Bajitpur | 131 | 02:00 | 125 | 14:00 | Metrorail_Uttara | 136 | 06:00 | 123 | 16:00
Bakerganj | 137 | 05:00 | 131 | 17:00 | Millgate | 134 | 04:00 | 124 | 16:00
Bakulia | 132 | 07:00 | 127 | 13:00 | Mirpur | 134 | 05:00 | 128 | 00:00
Banani | 138 | 07:00 | 129 | 16:00 | Mirzapur | 134 | 05:00 | 123 | 15:00
Bangabhaban | 132 | 06:00 | 124 | 16:00 | Mithapukur | 135 | 03:00 | 121 | 12:00
Barapukuria | 136 | 20:00 | 120 | 12:00 | MI_Cement | 134 | 05:00 | 127 | 16:00
Barguna | 136 | 05:00 | 131 | 14:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 136 | 06:00 | 131 | 13:00 | Mogbazar | 137 | 08:00 | 130 | 13:00
Barishal-230 | 137 | 06:00 | 131 | 16:00 | Mongla | 135 | 06:00 | 123 | 19:00
Baroaulia | 133 | 08:00 | 128 | 19:00 | Motijheel | 131 | 06:00 | 124 | 16:00
Baroirhat | 132 | 06:00 | 127 | 16:00 | Muktagacha | 130 | 05:00 | 116 | 15:00
Bashundhara | 138 | 06:00 | 130 | 12:00 | Munshiganj | 131 | 07:00 | 125 | 16:00
BashundharaCement | 134 | 01:00 | 126 | 17:00 | Muradnagar | 132 | 06:00 | 124 | 16:00
Beanibazar | 131 | 07:00 | 124 | 15:00 | Mymensingh | 130 | 20:00 | 114 | 16:00
Benapole | 133 | 06:00 | 118 | 13:00 | Naogaon | 134 | 05:00 | 123 | 17:00
Bhaluka | 134 | 05:00 | 124 | 16:00 | Narail | 135 | 06:00 | 124 | 21:00
Bhandaria | 135 | 08:00 | 126 | 19:30 | Narinda | 131 | 6:00 | 124 | 16:00
Bhangura | 134 | 03:00 | 127 | 15:00 | Narshingdi | 128 | 05:00 | 122 | 00:00
Bheramara | 136 | 02:00 | 130 | 17:00 | Natore | 135 | 02:00 | 127 | 17:00
Bheramara(GK) | 136 | 06:00 | 130 | 16:00 | Nawabganj | 138 | 06:00 | 130 | 16:00
Bhulta | 126 | 06:00 | 120 | 00:00 | Netrakona | 126 | 02:00 | 108 | 17:00
Bog-Sherpur | 136 | 05:00 | 127 | 17:00 | New | 136 | 06:00 | 125 | 16:00
Bogura | 137 | 05:00 | 127 | 17:00 | Niamatpur | 138 | 06:00 | 131 | 16:00
Bogura-230 | 138 | 06:00 | 128 | 17:00 | Noapara | 134 | 07:00 | 123 | 19:00
Brahmanbaria | 135 | 04:00 | 127 | 16:00 | Pabna | 136 | 07:00 | 129 | 16:00
Cantonment | 139 | 06:00 | 132 | 16:00 | Palashbari | 132 | 05:00 | 119 | 12:00
Chandina | 134 | 06:00 | 125 | 17:00 | Panchagarh | 138 | 18:30 | 119 | 12:00
Chandpur | 130 | 07:00 | 126 | 00:00 | Patiya | 131 | 08:00 | 125 | 19:00
Chandraghona | 134 | 06:00 | 130 | 12:00 | Patuakhali | 135 | 05:00 | 131 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 136 | 05:00 | 128 | 17:00 | Payra | 138 | 06:00 | 134 | 16:00
Charsaidpur | 132 | 07:00 | 126 | 00:00 | PHP | 132 | 07:00 | 127 | 00:00
Chauddagram | 132 | 06:00 | 126 | 11:00 | Postogola | 136 | 06:00 | 130 | 00:00
Chhatak | 130 | 05:00 | 122 | 18:30 | Purbachal | 138 | 07:00 | 129 | 16:00
Chowmuhani | 129 | 06:00 | 125 | 00:00 | Purbasadipur | 133 | 03:00 | 115 | 12:00
Chuadanga | 135 | 06:00 | 124 | 13:00 | Rahanpur | 138 | 03:00 | 132 | 17:00
Coxsbazar | 121 | 08:00 | 113 | 19:30 | Rahanpur-400 | 140 | 07:00 | 132 | 17:00
Cumilla(N) | 135 | 06:00 | 128 | 12:00 | Rahim | 132 | 07:00 | 127 | 00:00
Cumilla(S) | 133 | 06:00 | 120 | 15:00 | Rajbari | 138 | 12:00 | 127 | 13:00
Daganbhuiyan | 130 | 06:00 | 125 | 16:00 | Rajendrapur | 136 | 07:00 | 126 | 17:00
Daudkandi | 130 | 07:00 | 122 | 16:00 | Rajshahi | 134 | 05:00 | 126 | 15:00
DhakaUniversity | 138 | 06:00 | 130 | 16:00 | Rajshahi-230 | 134 | 02:00 | 127 | 12:00
Dhamrai | 140 | 04:00 | 130 | 16:00 | Ramganj | 127 | 05:00 | 123 | 15:00
Dhanmondi | 139 | 07:00 | 130 | 16:00 | Rampur | 131 | 06:00 | 125 | 23:00
Dohazari | 129 | 07:00 | 121 | 19:00 | Rampura | 138 | 06:00 | 130 | 16:00
Faridpur | 133 | 06:00 | 128 | 00:00 | Rangamati | 133 | 06:00 | 129 | 12:00
Fatullah | 135 | 06:00 | 128 | 00:00 | Rangpur | 135 | 05:00 | 124 | 16:00
Fenchuganj | 134 | 05:00 | 130 | 15:00 | Ruppur | 137 | 05:00 | 130 | 17:00
Feni | 130 | 07:00 | 124 | 17:00 | Saidpur | 134 | 06:00 | 120 | 12:00
Feni-230 | 130 | 06:00 | 125 | 16:00 | Satkhira | 135 | 06:00 | 121 | 19:00
Ghatail | 130 | 21:00 | 116 | 16:00 | Satmasjid | 139 | 06:00 | 129 | 18:00
Ghorashal | 138 | 05:00 | 130 | 14:00 | Savar | 134 | 07:00 | 127 | 00:00
Goalpara | 139 | 06:00 | 127 | 18:30 | SevenRings | 139 | 07:00 | 129 | 16:00
Gollamari | 138 | 06:00 | 127 | 18:00 | ShahCement | 132 | 07:00 | 126 | 00:00
Gopalganj | 136 | 06:00 | 128 | 19:00 | Shahjadpur | 138 | 02:00 | 131 | 17:00
Gopalganj-400 | 136 | 06:00 | 131 | 17:00 | Shahjibazar | 134 | 05:00 | 125 | 17:00
Gulshan | 138 | 06:00 | 129 | 16:00 | Shahmirpur | 133 | 07:00 | 128 | 12:00
Halishahar | 132 | 06:00 | 127 | 12:00 | Shariatpur | 136 | 06:00 | 129 | 13:00
Haripur | 133 | 08:00 | 126 | 16:00 | Sherpur | 129 | 21:00 | 111 | 15:00
HaripurSBU | 132 | 05:00 | 126 | 16:00 | Shikalbaha | 123 | 06:00 | 117 | 19:30
Hasnabad | 134 | 04:00 | 126 | 04:00 | Shikalbaha-230 | 134 | 07:00 | 129 | 00:00
Hathazari | 134 | 07:00 | 129 | 18:30 | Shitalakhya | 134 | 05:00 | 127 | 16:00
Hatirjheel | 138 | 06:00 | 129 | 16:00 | Sholosohor | 138 | 18:30 | 130 | 00:00
Ishurdi | 138 | 02:00 | 131 | 17:00 | Shyampur | 135 | 07:00 | 125 | 16:00
Jaldhaka | 133 | 04:00 | 116 | 12:00 | Shyampur-230 | 136 | 07:00 | 129 | 16:00
Jamalpur | 133 | 21:00 | 114 | 15:00 | Siddhirganj | 133 | 06:00 | 127 | 16:00
Jashore | 134 | 06:00 | 119 | 19:00 | Sirajganj | 134 | 04:00 | 125 | 17:00
Jhenaidah | 136 | 03:00 | 115 | 13:00 | Sonargaon | 131 | 06:00 | 125 | 16:00
Jhenaidah-230 | 137 | 07:00 | 127 | 13:00 | Sreemongol | 131 | 06:00 | 123 | 17:00
Joydebpur | 134 | 07:00 | 123 | 15:00 | Sreepur | 138 | 06:00 | 130 | 16:00
Joypurhat | 131 | 02:00 | 118 | 12:00 | Srinagar | 139 | 06:00 | 131 | 16:00
Juldah | 132 | 10:00 | 127 | 19:00 | SSM | 136 | 05:00 | 132 | 00:00
Kabirpur | 137 | 04:00 | 120 | 16:00 | Sunamganj | 127 | 06:00 | 121 | 12:00
Kachua | 132 | 07:00 | 127 | 01:00 | Sylhet | 132 | 07:00 | 124 | 19:00
Kaliakoir | 143 | 07:00 | 129 | 16:00 | Sylhet-132 | 130 | 05:00 | 126 | 13:00
Kaliganj | 137 | 06:00 | 128 | 13:00 | Tangail | 130 | 05:00 | 118 | 15:00
Kallyanpur | 136 | 06:00 | 129 | 00:00 | Taraganj | 134 | 19:00 | 120 | 12:00
Kalurghat | 134 | 07:00 | 130 | 00:00 | Tasnim | 136 | 15:00 | 125 | 01:00
Kamrangirchar | 139 | 07:00 | 129 | 00:00 | Thakurgaon | 137 | 18:30 | 116 | 12:00
Kaptai | N/A | N/A | N/A | N/A | TK | 133 | 04:00 | 129 | 12:00
Kasba | 132 | 06:00 | 124 | 16:00 | Tongi | 136 | 04:00 | 126 | 15:00
Kazla | 128 | 05:00 | 124 | 13:00 | Ullahpara | 135 | 05:00 | 127 | 17:00
Keranigonj | 138 | 06:00 | 131 | 16:00 | Ullon | 138 | 07:00 | 129 | 16:00
Khagrachori | 134 | 07:00 | 128 | 12:00 | Uttara | 135 | 07:00 | 123 | 16:00
Khulna | 137 | 06:00 | 126 | 18:30 | UttaraNew | 136 | 06:00 | 123 | 16:00
Khulna(S) | 138 | 06:00 | 128 | 19:00 | Zigatola | 139 | 07:00 | 131 | 16:00
Khulshi | 131 | 06:00 | 126 | 12:00
Kishoreganj | 132 | 04:00 | 121 | 16:00
Kodda | 134 | 05:00 | 121 | 15:00
Korerhat | 133 | 04:00 | 128 | 12:00
KSRM | 133 | 03:00 | 128 | 12:00
Kulaura | 134 | 06:00 | 129 | 13:00
Kurigram | 132 | 05:00 | 118 | 17:00
Kushtia | 132 | 06:00 | 123 | 13:00
Laksam | 132 | 07:00 | 126 | 16:00
Lakshmipur | 129 | 06:00 | 124 | 00:00
Lalbag | 136 | 07:00 | 130 | 16:00
Lalmonirhat | 132 | 01:00 | 116 | 17:00
Madanganj | 134 | 01:00 | 126 | 17:00
Madaripur | 135 | 06:00 | 130 | 17:00
Madartek | 137 | 06:00 | 129 | 13:00
Madunaghat | 134 | 07:00 | 129 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division