## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 08-03-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-03-2026 | during | 08-03-2026 | during | 08-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 6 | 97.7 | 97.7 | 7 | 7 | Demand "0"MW due to gas restriction by Titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 330 | 332 | 412 | 412 | 412 | 412 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 1 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 280 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 47.8 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 45 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23 | 24 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 8 | 16 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 195 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 25 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 34 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 153 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 320 | 310 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 360 | 350 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 142 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1420 | 2285.8 | 5945.22 | 5915.22 | 3213.05 | 3240.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 80 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 226 | 220 | 225 | 220 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 90 | 105 | 105 | 95 | 95
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 | 56 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 68 | 68 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 50 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 4 | 21 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.21 | 0 | 3.33 | 0 | 3.33 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 16 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 50 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 36 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 15 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1100 | 1160 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 5 | 0 | 3 | 0 | 3 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 600 | 515 | 720 | 720 | 580 | 580 | ps availability is less
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2029.21 | 2360 | 3574.19 | 3573.86 | 2943.83 | 2951.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 197 | 195 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 353.35 | 353.35 | 0 | 220 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 335 | 340 | 318.81 | 318.81 | 318.81 | 318.81 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 330 | 300 | 393 | 393 | 220 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 123 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 8 | 32 | 32 | 32 | 32 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 98 | 100 | 163 | 163 | 100 | 100 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 128 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 142 | 154 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 106 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 65 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1238 | 1525 | 2741.51 | 2670.51 | 1797.01 | 1732.01
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-03-2026 | during | 08-03-2026 | during | 08-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 18 | 18 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 57 | 77 | 60 | 80 | 60 | 80 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 115 | 98 | 70 | 115 | 70 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 43.41 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 241.41 | 199 | 411.1 | 429 | 200.1 | 218
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 42 | 42 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 158 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 70 | 70 | 70 | 70 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 41 | 41 | 83 | 83 | 42 | 42 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 96 | 97 | 100 | 100 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 20 | 17 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 295 | 341 | 341 | 150 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 390 | 380 | 385 | 385 | 385 | 385 | -
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1140 | 1100 | 1259 | 1259 | 904 | 1061
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 900 | 902 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 265 | 230 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 91 | 0 | 88 | 0 | 88 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 898 | 1116 | 0 | 0 | 1148.28 | 1148.28 | plant availability zero
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2154 | 2248 | 2368 | 2280 | 2543.38 | 2455.38
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 850 | 1082 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 15 | 15 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 277 | 307 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.51 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2700.36 | 1467.51 | 1729 | 2003.32 | 2002.32 | 1868.32 | 1867.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 49.35 | 0 | 40 | 0 | 40 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 48 | 48 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 190 | 188 | 220 | 220 | 220 | 220 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 350 | 402 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 26 | 0 | 40 | 40 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.92 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1041.78 | 1461.18 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 52.14 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 100 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1814.19 | 2151.18 | 3157.57 | 2961.87 | 2571.57 | 2375.87
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 50 | 50 | 50 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 49 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.1 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 23 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 168 | 0 | 170.17 | 0 | 170.17 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 230.1 | 149 | 517.37 | 312 | 433.37 | 228
System Total |  |  |  |  | 28823.2 | 28385.703 | 11734.42 | 13746.98 | 21977.28 | 21403.78 | 16474.63 | 16129.13
Forecast Scenario (08-03-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11500 |  | 0 |  | 11500
|  |  |  | 1:00 | 10850 |  | 0 |  | 10850
|  |  |  | 2:00 | 10550 |  | 0 |  | 10550
|  |  |  | 3:00 | 10700 |  | 0 |  | 10700
|  |  |  | 4:00 | 11770 |  | 0 |  | 11770
|  |  |  | 5:00 | 10660 |  | 0 |  | 10660
|  |  |  | 6:00 | 9580 |  | 0 |  | 9580
|  |  |  | 7:00 | 9840 |  | 0 |  | 9840
|  |  |  | 8:00 | 10610 |  | 0 |  | 10610
|  |  |  | 9:00 | 11520 |  | 0 |  | 11520
|  |  |  | 10:00 | 11750 |  | 0 |  | 11750
|  |  |  | 11:00 | 12200 |  | 0 |  | 12200
|  |  |  | 12:00 | 12600 |  | 0 |  | 12600
|  |  |  | 13:00 | 12920 |  | 0 |  | 12920
|  |  |  | 14:00 | 13190 |  | 0 |  | 13190
|  |  |  | 15:00 | 13030 |  | 0 |  | 13030
|  |  |  | 16:00 | 13180 |  | 0 |  | 13180
|  |  |  | 17:00 | 13039.97 |  | 391.5786 |  | 13450
|  |  |  | 18:00 | 12988.14 |  | 240.5263 |  | 13240
|  |  |  | 18:30 | 12984.9 |  | 396.4205 |  | 13400
|  |  |  | 19:00 | 12933.63 |  | 712.7834 |  | 13680
|  |  |  | 19:30 | 12942.63 |  | 818.7884 |  | 13800
|  |  |  | 20:00 | 12951.63 |  | 982.0933 |  | 13980
|  |  |  | 21:00 | 13000.9 |  | 1020.9905 |  | 14070
|  |  |  | 22:00 | 13000.9 |  | 696.2905 |  | 13730
|  |  |  | 23:00 | 12740 |  | 0 |  | 12740
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 12600.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14070.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13000.90 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 287.10517 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 12:09 hrs on 08-03-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 07-03-2026
Power Supply Scenario
| Day Peak Generation |  |  | 11734.42 | MW | 12:00 Hr. | Energy Generated |  |  | 288.4045 |  | MKWHr.
| Day Peak Demand |  |  | 11902.42 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.161 |  | MKWHr.
| Evening Peak Generation |  |  | 13746.98 | MW | 21:00 Hr. | Energy Demand |  |  | 289.5655 |  | MKWHr.
| Evening Peak Demand |  |  | 13746.98 | MW | 21:00 Hr. | Maximum Temperature |  |  | 33.7 |  | °C
| Minimum Generation of the Day |  |  | 9594 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 851.66 |  | MMCFD
| Maximum Generation of the Day |  |  | 13746.98 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 5.8903 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 32.3201 | 0 | 7.7106 | 0 | 0 | 0.17481 | 0 | 0 | 40.2056 | Gas | 114.9082 | Gas | 394572651.9694
| Chattogram Zone |  |  | 5.3352 | 39.3109 | 2.7987 | 0 | 1.9228 | 0.13869 | 0 | 0.132 | 49.6383 | Coal | 94.7867 | Coal | 618717841.0404
| Cumilla Zone |  |  | 22.9357 | 0 | 2.2323 | 0 | 0 | 0.43637 | 3.2909 | 0 | 28.8953 | HFO | 19.1064 | HFO | 312996059.91
| Mymensingh Zone |  |  | 0.42432 | 0 | 3.834 | 0 | 0 | 0.28426 | 0 | 0 | 4.5426 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.388 | 0 | 0 | 0 | 0 | 0.062723 | 0 | 0 | 26.4507 | Hydro | 1.9228 | Hydro | 192282
| Khulna Zone |  |  | 5.847 | 23.8836 | 0 | 0 | 0 | 0.54648 | 21.064 | 0 | 51.3411 | Solar | 4.219 | Solar | 67355458.29
| Barishal Zone |  |  | 7.8882 | 30.6387 | 0 | 0 | 0 | 0.003316 | 0 | 0 | 38.5303 | Import | 53.3294 | Import | 303026803.94
| Rajshahi Zone |  |  | 13.7696 | 0 | 0.72171 | 0 | 0 | 1.3353 | 28.9745 | 0 | 44.8011 | Wind | 0.132 | Wind | 1941720
| Rangpur Zone |  |  | 0 | 0.95345 | 1.809 | 0 | 0 | 1.2371 | 0 | 0 | 3.9996
| Total |  |  | 114.9082 | 94.7867 | 19.1064 | 0 | 1.9228 | 4.219 | 53.3294 | 0.132 | 288.4045
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 394572651.9694 |  | Hydro | 192282
|  |  |  | Coal | 618717841.0404 |  | Solar | 67355458.29
|  |  |  | HFO | 312996059.91 |  | Import | 303026803.94
|  |  |  | HSD | 0 |  | Wind | 1941720
[5 empty] | Total: | 169,88,02,817 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.064 | Peak Hr Flow | 902.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 45179381.82 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 28.9745 | Peak Hr Flow | 1461.18 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2118 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.2909 | Peak Hr Flow | 154.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2572 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.3294 | Peak Hr Flow | 2517.18 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5059
|  |  |  | Chattogram |  | 0 |  | 1315
|  |  |  | Cumilla |  | 0 |  | 1261
|  |  |  | Mymensingh |  | 0 |  | 1147
|  |  |  | Sylhet |  | 0 |  | 531
|  |  |  | Khulna |  | 0 |  | 1524
|  |  |  | Barishal |  | 0 |  | 385
|  |  |  | Rajshahi |  | 0 |  | 1282
|  |  |  | Rangpur |  | 0 |  | 767
|  |  |  | Total |  | 0 |  | 13271
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:43 |  | Aminbazar-Meghnaghat 400kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Scheduled shutdown
| 08:48 | 16:48 | Baroirhat-Hathazari 132 kV Ckt-1 Scheduled S/D from Baroirhat 132/33kV end Due to Annual
deadline checking
| 08:55 | 14:30 | Chowmuhani 230/132/33kV S/S ATR-01 HT Project Work S/D Due to 230 KV Outside painting
final work.
| 09:18 | 11:09 | Baroirhat 132/33kV S/S TR-1, 406T HT Scheduled S/D Due to Pbs 33 kv red hot Maintenance
work
| 09:19 | 11:10 | Baroirhat 132/33kV S/S TR-1, 406T LT Scheduled S/D Due to Pbs 33 kv red hot Maintenance
work
| 09:47 | 11:09 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 LT Scheduled S/D Due to Scheduled shutdown
| 09:47 | 11:06 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 HT Scheduled S/D Due to Scheduled shutdown
| 09:56 |  | BSRM-Mirsharai 230 kV Ckt-2 Project Work S/D from BSRM 230/33kV end Due to For Project
Work
| 10:01 | 13:04 | Daudkandi 132/33kV S/S Transformer-2 LT Scheduled S/D Due to 33 KV side- bay extension | [7 empty] | 30.0MW load
|  |  | work by Comilla PBS-3 | [7 empty] | interrup.
| 10:02 | 13:02 | Daudkandi 132/33kV S/S Transformer-2 HT Scheduled S/D Due to 33 KV side- bay extension
work by Comilla PBS-3
| 10:07 | 13:07 | Daudkandi 132/33kV S/S Transformer-3 LT Scheduled S/D Due to 33 KV side- bay extension | [7 empty] | 20.0MW load
|  |  | work by Comilla PBS-3 | [7 empty] | interrup.
| 10:08 | 13:05 | Daudkandi 132/33kV S/S Transformer-3 HT Scheduled S/D Due to 33 KV side- bay extension
work by Comilla PBS-3
|  | 10:29 | Kabirpur 132/33kV S/S XFR, T-3 HT is restored.
|  | 10:30 | Kabirpur 132/33kV S/S XFR, T-3 LT is restored.
| 10:37 | 11:18 | Rajshahi-Rajshahi(New) 132kV Ckt-2 Forced S/D from Rajshahi 132/33kV end Due to E/S
maintenance
| 10:38 | 11:18 | HVDC Bheramera- Rajshahi 230kV Ckt-2 Project Work S/D from Rajshahi 230/132/33kV end
Due to 132kV Rajshahi SS end project work
| 10:43 | 13:31 | Kabirpur 132/33kV S/S XFR, T-2 LT Scheduled S/D Due to For 132 kV Main Bus DS Changing
Work
| 10:44 | 13:31 | Kabirpur 132/33kV S/S XFR, T-2 HT Scheduled S/D Due to For 132 kV Main Bus DS Changing
Work
| 12:00 |  | Day Peak Generation: 11731 MW
| 13:06 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- gt
| 15:23 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- GT
|  | 15:38 | Kabirpur 132/33kV S/S Main bus is restored.
| 15:53 | 16:27 | Barishal 230/132kV S/S ATR-1 HT Project Work S/D
| 15:53 | 16:24 | Barishal 230/132kV S/S ATR-1 LT Forced S/D Due to Oil Refiled for Aux-1
|  | 19:50 | Barapukuria-Bogura 230 kV Ckt-2 is restored.
| 21:00 |  | Peak generation 13746 MW
| 23:59 | 02:12 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Forced S/D Due to Sky Wire Damaged
|  | 00:27 | Baroaulia-Hathazari 132 kV Ckt-1 is restored.
| 05:06 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- gt
| 06:00 |  | Minimum generation 10381 MW
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 07-03-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 6 | 69000 | Demand "0"MW due to gas restriction by Titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 332 | 7992000 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 389261 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 6402366 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 47.8 | 355680 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 45 | 218880 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 386946 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 396666 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 24 | 459000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 527400 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 180000 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 805920 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1539648 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 313920 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 153 | 1264320 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 174813 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 253800 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 310 | 8388181.82 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 350 | 8482165 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1605600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2285.8 | 40205566.82
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 117450 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 638400 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1922820 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 226 | 4976185 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 90 | 626436 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 359926 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 345600 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 21 | 359040 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21238 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 95345 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 50 | 294398 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 36 | 353280 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 15 | 85309 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1160 | 25936361 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 132000 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 515 | 13374545.46 | ps availability is less
Chattogram Area Total |  |  |  |  | 4898.863 | 2360 | 49638333.46
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 195 | 4801000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 197300 | Plant availability less
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 340 | 7282000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 300 | 6873000 | FGMO
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1093258 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 123 | 592145 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 8 | 59536 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2205896 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 128 | 829920 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 154 | 3290880 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 483290 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 106 | 750720 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 436373 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1525 | 28895318
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 18 | 424320 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 77 | 1260000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 98 | 2468400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 270810 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 105600 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 199 | 4542580
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 62723 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 983000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 158 | 3560400 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 70 | 1678000 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 41 | 960000 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 97 | 2309250 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 475368 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7348000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 380 | 9074000 | Due to Air Filter DP High FGMO not available.
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1100 | 26450741
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 902 | 21064000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 230 | 5846976 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 546480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1116 | 23883640 | plant availability zero
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2248 | 51341096
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2725000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 1082 | 24376727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5163210 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6262000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3316 | -
Barishal Area Total |  |  |  |  | 2700.36 | 1729 | 38530253.27
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 278336 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 188 | 4415664 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 402 | 9353890 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Machine problem and fuel shortage
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 156272 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 310464 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 50 | 254976 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 34320 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1461.18 | 28974546 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 349488 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 673150 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2151.18 | 44801106
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 953454 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 1084617 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 31787.4 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 724425 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 144708 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1060560 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 149 | 3999551.4
Eastern Grid Total |  |  |  |  | 17400.108 | 7469.8 | 149732539.28
Western Grid Total |  |  |  |  | 10985.595 | 6277.18 | 138672006.67
National Grid Total |  |  |  |  | 28385.703 | 13746.98 | 288404545.95
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 07-03-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9313.08 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3957.9 | MW
i) Dhaka area |  |  | 5059.48 |  | MW | i) Khulna area |  |  |  | 1524 | MW
ii) Chattogram area |  |  | 1314.6 |  | MW | ii) Barishal area |  |  |  | 385.3 | MW
iii) Cumilla area |  |  | 1261 |  | MW | iii) Rajshahi area |  |  |  | 1281.6 | MW
iv) Mymensingh area |  |  | 1147 |  | MW | iv) Rangpur area |  |  |  | 767 | MW
v) Sylhet area |  |  | 531 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13270.98 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 81 | 19:00 | 133 | Nawabganj | 39.4 | 21:00
2 | AKSML | 19 | 19:00 | 68 | Hathazari | 74 | 19:00 | 134 | Netrakona | 150 | 19:30
3 | Aftabnagar | 34 | 19:00 | 69 | Hatirjheel | 34 | 15:00 | 135 | New | 72.4 | 14:00
4 | Agargaon | 95 | 20:00 | 70 | Ishurdi | 64 | 14:00 | 136 | Niamatpur | 94 | 09:00
5 | Agrabad | 48 | 14:00 | 71 | Jaldhaka | 68 | 17:00 | 137 | Noapara | 42 | 19:00
6 | Amnura | 36 | 12:00 | 72 | Jamalpur | 103 | 17:00 | 138 | PHP | 7 | 01:00
7 | Ashuganj | 77 | 23:00 | 73 | Jashore | 126 | 19:00 | 139 | Pabna | 77 | 18:00
8 | BSRM | 188 | 23:00 | 74 | Jhenaidah | 87 | 18:00 | 140 | Palashbari | 100 | 18:00
9 | Bagerhat | 75 | 19:00 | 75 | Joydebpur | 128 | 16:00 | 141 | Panchagarh | 59 | 17:00
10 | Bajitpur | 76 | 19:00 | 76 | Joypurhat | 64 | 09:00 | 142 | Patiya | 8.1 | 20:00
11 | Bakerganj | 11.3 | 21:00 | 77 | Juldah | 14.5 | 14:00 | 143 | Patuakhali | 46 | 20:00
12 | Bakulia | 84 | 19:30 | 78 | KSRM | 13 | 17:00 | 144 | Payra | 32 | 21:00
13 | Banani | 42 | 14:00 | 79 | Kabirpur | 254 | 17:00 | 145 | Postogola | 47 | 19:30
14 | Bangabhaban | 6 | 10:00 | 80 | Kachua | 77 | 21:00 | 146 | Pubail | N/A | N/A
15 | Barapukuria | 64 | 09:00 | 81 | Kaliganj | 24 | 18:30 | 147 | Purbachal | 26 | 19:00
16 | Barguna | 16 | 19:00 | 82 | Kallyanpur | 102 | 19:30 | 148 | Purbasadipur | 127 | 17:00
17 | Barishal | 87 | 14:00 | 83 | Kalurghat | 35 | 15:00 | 149 | Rahanpur | 26 | 21:00
18 | Barishal-230 | 82 | 19:00 | 84 | Kamrangirchar | 77 | 19:00 | 150 | Rahim | 26 | 10:00
19 | Baroaulia | 60 | 11:00 | 85 | Kaptai | N/A | N/A | 151 | Rajbari | 59 | 18:00
20 | Baroirhat | 52 | 19:30 | 86 | Kasba | 32 | 18:30 | 152 | Rajendrapur | 122 | 15:00
21 | Bashundhara | 186 | 21:00 | 87 | Kazla | 101 | 15:00 | 153 | Rajshahi | 105 | 17:00
22 | BashundharaCement | 3 | 23:00 | 88 | Keranigonj | 85 | 19:30 | 154 | Rajshahi-230 | 60 | 18:00
23 | Beanibazar | 60 | 20:00 | 89 | Khagrachori | 30 | 19:00 | 155 | Ramganj | 84 | 18:30
24 | Benapole | 52 | 13:00 | 90 | Khulna | 53 | 19:30 | 156 | Rampur | 36 | 19:00
25 | Bhaluka | 144 | 17:00 | 91 | Khulshi | 172 | 00:00 | 157 | Rangamati | 15 | 18:30
26 | Bhandaria | 44 | 18:30 | 92 | Kishoreganj | 121 | 18:00 | 158 | Rangpur | 140 | 18:00
27 | Bhangura | 41 | 14:00 | 93 | Kodda | 272 | 17:00 | 159 | Ruppur | 2 | 11:00
28 | Bheramara(GK) | 51 | 18:00 | 94 | Kulaura | 40 | 18:30 | 160 | SSM | 0 | 00:00
29 | Bhulta | 211 | 22:00 | 95 | Kurigram | 70 | 17:00 | 161 | Saidpur | 107 | 17:00
30 | Bog-Sherpur | 64 | 17:00 | 96 | Kushtia | 119 | 18:00 | 162 | Satkhira | 130 | 18:30
31 | Bogura | 142 | 22:00 | 97 | Laksam | 28 | 13:00 | 163 | Satmasjid | 93 | 21:00
32 | Borhanuddin | 76 | 21:00 | 98 | Lakshmipur | 30 | 20:00 | 164 | Savar | 204 | 15:00
33 | Brahmanbaria | 117 | 22:00 | 99 | Lalbag | 70 | 13:00 | 165 | SevenRings | 17.64 | 20:00
34 | Cantonment | 92 | 20:00 | 100 | Lalmonirhat | 52 | 18:00 | 166 | ShahCement | 30 | 01:00
35 | Chandina | 12 | 18:00 | 101 | MI_Cement | 17.5 | 10:00 | 167 | Shahjadpur | 73 | 17:00
36 | Chandpur | 64 | 19:30 | 102 | Madanganj | 36 | 00:00 | 168 | Shahjibazar | 115 | 19:00
37 | Chandraghona | 33 | 19:00 | 103 | Madaripur | 88 | 20:00 | 169 | Shahmirpur | 53 | 23:00
38 | Chapai | 60 | 13:00 | 104 | Madartek | 68 | 21:00 | 170 | Shariatpur | 66 | 19:00
39 | Charsaidpur | 44 | 01:00 | 105 | Madunaghat | 50 | 15:00 | 171 | Sherpur | 156 | 18:00
40 | Chauddagram | 65 | 21:00 | 106 | Magura | 54 | 19:00 | 172 | Shikalbaha | 25 | 00:00
41 | Chhatak | 30 | 00:00 | 107 | Mahasthangarh | 70 | 03:00 | 173 | Shitalakhya | 80.9 | 15:00
42 | Chowmuhani | 114 | 21:00 | 108 | Maijdee | 40 | 20:00 | 174 | Sholosohor | 41 | 14:00
43 | Chuadanga | 91 | 18:00 | 109 | Manikganj | 105 | 18:30 | 175 | Shyampur | 168 | 10:00
44 | Coxsbazar | 128 | 21:00 | 110 | Maniknagar | 65 | 21:00 | 176 | Siddhirganj | 124 | 15:00
45 | Cumilla(N) | 109 | 17:00 | 111 | Matarbari | 45 | 03:00 | 177 | Sirajganj | 102 | 17:00
46 | Cumilla(S) | 160 | 15:00 | 112 | Matuail | 71.4 | 15:00 | 178 | Sonargaon | 150 | 21:00
47 | Daganbhuiyan | 29 | 19:00 | 113 | Metrorail_Motijheel | 22 | 13:00 | 179 | Sreemongol | 64 | 21:00
48 | Daudkandi | 122 | 23:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sreepur | 109 | 16:00
49 | DhakaUniversity | 56 | 13:00 | 115 | Millgate | 92 | 14:00 | 181 | Srinagar | 39.4 | 21:00
50 | Dhamrai | 120 | 22:00 | 116 | Mirpur | 136 | 20:00 | 182 | Sunamganj | 49 | 21:00
51 | Dhanmondi | 97 | 13:00 | 117 | Mirsorai | 49 | 09:00 | 183 | Sylhet | 50 | 22:00
52 | Dohazari | 101 | 20:00 | 118 | Mirzapur | 55 | 19:00 | 184 | Sylhet-132 | 101 | 21:00
53 | Faridpur | 135 | 18:30 | 119 | Mithapukur | 54 | 17:00 | 185 | TK | 22 | 21:00
54 | Fatullah | 82 | 15:00 | 120 | Modern | N/A | N/A | 186 | Tangail | 172 | 19:00
55 | Fenchuganj | 31 | 18:30 | 121 | Mogbazar | 80 | 14:00 | 187 | Taraganj | 23 | 17:00
56 | Feni | 90 | 21:00 | 122 | Mongla | 42 | 19:30 | 188 | Tasnim | 18 | 16:00
57 | GPH | 3 | 01:00 | 123 | Motijheel | 38 | 13:00 | 189 | Thakurgaon | 91 | 17:00
58 | Ghatail | 96 | 18:00 | 124 | Muktagacha | 39 | 18:00 | 190 | Tongi | 158 | 17:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 86 | 22:00 | 191 | Ullahpara | 36 | 09:00
60 | Ghorashal-230 | 108 | 22:00 | 126 | Muradnagar | 33 | 18:30 | 192 | Ullon | 55 | 00:00
61 | Goalpara | 33 | 18:30 | 127 | Mymensingh | 197 | 21:00 | 193 | Uttara | 73 | 19:30
62 | Gollamari | 92 | 19:00 | 128 | Naogaon | 119 | 13:00 | 194 | UttaraNew | 27 | 17:00
63 | Gopalganj | 90 | 21:00 | 129 | Narail | 53 | 19:00 | 195 | Zigatola | 73 | 19:30
64 | Gulshan | 84 | 13:00 | 130 | Narinda | 62 | 13:00
65 | Halishahar | 79 | 16:00 | 131 | Narshingdi | 165 | 19:00
66 | HaripurSBU | 127 | 16:00 | 132 | Natore | 128 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 07-03-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 11666 | 0 |  | 11666
1:00 | 11084 | 0 |  | 11084
2:00 | 10741 | 0 |  | 10741
3:00 | 10772 | 0 |  | 10772
4:00 | 11559 | 0 |  | 11559
5:00 | 10502 | 0 |  | 10502
6:00 | 9594 | 0 |  | 9594
7:00 | 9751.39 | 0 |  | 9751.39
8:00 | 10433.92 | 0 |  | 10433.92
9:00 | 11016.77 | 60 |  | 11079.77
10:00 | 11049.17 | 101 |  | 11155.17
11:00 | 11382.67 | 77 |  | 11462.67
12:00 | 11734.42 | 161 |  | 11902.42
13:00 | 12153.87 | 192 |  | 12354.87
14:00 | 12384.86 | 181 |  | 12573.86
15:00 | 12357.23 | 188 |  | 12553.23
16:00 | 12475.21 | 142 |  | 12623.21
17:00 | 13263.75 | 0 |  | 13263.75
18:00 | 13208.81 | 59 |  | 13270.81
19:00 | 13381.56 | 0 |  | 13381.56
19:30 | 13579.74 | 0 |  | 13579.74
20:00 | 13605.12 | 0 |  | 13605.12
21:00 | 13746.98 | 0 |  | 13746.98
22:00 | 13436.52 | 0 |  | 13436.52
23:00 | 13093.97 | 0 |  | 13093.97
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 07-03-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5801 | 5865 | 11666 | DAILY GENERATION CURVE
00:30 | 5694 | 5681 | 11375
01:00 | 5587 | 5497 | 11084 | 07-03-2026
01:30 | 5472.5 | 5440 | 10912.5
02:00 | 5358 | 5383 | 10741
02:30 | 5340.5 | 5416 | 10756.5
03:00 | 5323 | 5449 | 10772
03:30 | 5576 | 5589.5 | 11165.5
04:00 | 5829 | 5730 | 11559
04:30 | 5644.5 | 5386 | 11030.5
05:00 | 5460 | 5042 | 10502
05:30 | 5251 | 4797 | 10048
06:00 | 5042 | 4552 | 9594
06:30 | 5140.165 | 4532.53 | 9672.695
07:00 | 5238.33 | 4513.06 | 9751.39
07:30 | 5406.09 | 4686.565 | 10092.655
08:00 | 5573.85 | 4860.07 | 10433.92
08:30 | 5626.97 | 5098.375 | 10725.345
09:00 | 5680.09 | 5336.68 | 11016.77
09:30 | 5769.655 | 5263.315 | 11032.97
10:00 | 5859.22 | 5189.95 | 11049.17
10:30 | 5954.75 | 5261.17 | 11215.92
11:00 | 6050.28 | 5332.39 | 11382.67
11:30 | 6059.45 | 5499.095 | 11558.545
12:00 | 6068.62 | 5665.8 | 11734.42
12:30 | 6139.905 | 5804.24 | 11944.145
13:00 | 6211.19 | 5942.68 | 12153.87
13:30 | 6175.34 | 6094.025 | 12269.365
14:00 | 6139.49 | 6245.37 | 12384.86
14:30 | 6100.745 | 6270.3 | 12371.045
15:00 | 6062 | 6295.23 | 12357.23
15:30 | 6145.5 | 6270.72 | 12416.22
16:00 | 6229 | 6246.21 | 12475.21
16:30 | 6552.815 | 6316.665 | 12869.48
17:00 | 6876.63 | 6387.12 | 13263.75
17:30 | 6909.815 | 6326.465 | 13236.28
18:00 | 6943 | 6265.81 | 13208.81
18:30 | 7070 | 6225.185 | 13295.185
19:00 | 7197 | 6184.56 | 13381.56
19:30 | 7325.5 | 6254.24 | 13579.74
20:00 | 7358.5 | 6246.62 | 13605.12
20:30 | 7414.15 | 6261.9 | 13676.05 |  | Executive Engineer
21:00 | 7469.8 | 6277.18 | 13746.98 |  | Network Operation Division
21:30 | 7369.4 | 6222.35 | 13591.75
22:00 | 7269 | 6167.52 | 13436.52
22:30 | 7110.3 | 6154.945 | 13265.245
23:00 | 6951.6 | 6142.37 | 13093.97

## En-Curve
QF-LDC-12
Date | 07-03-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3171 | 1573 | 900 | 0 | 136 | 1361 | 80 | 4160 | 0 | 70 | 215 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3072.5 | 1547 | 900 | 0 | 129 | 1312.5 | 80 | 4055.5 | 0 | 61 | 217.5 | 0 | 0 | 0 | 0 | 07-03-2026
01:00 | 2974 | 1521 | 900 | 0 | 122 | 1264 | 80 | 3951 | 0 | 52 | 220 | 0 | 0 | 0 | 0
01:30 | 2900 | 1470.5 | 900 | 0 | 121 | 1265.5 | 80 | 3903.5 | 0 | 52 | 220 | 0 | 0 | 0 | 0 | Energy Generated | 288.4045 |  | MKWHr
02:00 | 2826 | 1420 | 900 | 0 | 120 | 1267 | 80 | 3856 | 0 | 52 | 220 | 0 | 0 | 0 | 0 | Energy not Served | 1.161 |  | MKWHr
02:30 | 2835.5 | 1380 | 900 | 0 | 122 | 1266.5 | 80 | 3843.5 | 0 | 62.5 | 266.5 | 0 | 0 | 0 | 0 | Total Energy Requirement | 289.5655 |  | MKWHr
03:00 | 2845 | 1340 | 900 | 0 | 124 | 1266 | 80 | 3831 | 0 | 73 | 313 | 0 | 0 | 0 | 0
03:30 | 2976 | 1470 | 899.5 | 0 | 126 | 1264.5 | 80 | 3953.5 | 0 | 71.5 | 324.5 | 0 | 0 | 0 | 0
04:00 | 3107 | 1600 | 899 | 0 | 128 | 1263 | 80 | 4076 | 0 | 70 | 336 | 0 | 0 | 0 | 0
04:30 | 3077.5 | 1543.5 | 899.5 | 0 | 126 | 1160 | 80 | 3838 | 0 | 43.5 | 262.5 | 0 | 0 | 0 | 0
05:00 | 3048 | 1487 | 900 | 0 | 124 | 1057 | 80 | 3600 | 0 | 17 | 189 | 0 | 0 | 0 | 0
05:30 | 2951 | 1433 | 900 | 0 | 120 | 959.5 | 80 | 3424 | 0 | 8.5 | 171.5 | 0 | 0 | 0.5 | 0
06:00 | 2854 | 1379 | 900 | 0 | 116 | 862 | 80 | 3248 | 0 | 0 | 154 | 0 | 0 | 1 | 0
06:30 | 2944 | 1411.5 | 829 | 0 | 113 | 863.5 | 80 | 3251.5 | 19.195 | 0 | 157.5 | 0 | 0 | 3.5 | 0
07:00 | 3034 | 1444 | 758 | 0 | 110 | 865 | 80 | 3255 | 38.39 | 0 | 161 | 0 | 0 | 6 | 0
07:30 | 3103 | 1467.5 | 710.5 | 0 | 113 | 936.5 | 80 | 3384.5 | 91.655 | 15 | 184.5 | 0 | 0 | 6.5 | 0
08:00 | 3172 | 1491 | 663 | 0 | 116 | 1008 | 80 | 3514 | 144.92 | 30 | 208 | 0 | 0 | 7 | 0
08:30 | 3168.5 | 1478.5 | 781.5 | 0 | 120 | 1017.31 | 80 | 3534.5 | 230.035 | 40.5 | 271 | 0 | 0 | 3.5 | 30
09:00 | 3165 | 1466 | 900 | 0 | 124 | 1026.62 | 80 | 3555 | 315.15 | 51 | 334 | 0 | 0 | 0 | 60
09:30 | 3223 | 1489 | 900 | 0 | 128 | 974.38 | 80 | 3474 | 391.59 | 51 | 322 | 0 | 0 | 0 | 80.5
10:00 | 3281 | 1512 | 900 | 0 | 132 | 922.14 | 80 | 3393 | 468.03 | 51 | 310 | 0 | 0 | 0 | 101
10:30 | 3337.5 | 1568.5 | 900 | 0 | 133 | 921.275 | 80 | 3377.5 | 535.145 | 51 | 312 | 0 | 0 | 0 | 89
11:00 | 3394 | 1625 | 900 | 0 | 134 | 920.41 | 80 | 3362 | 602.26 | 51 | 314 | 0 | 0 | 0 | 77
11:30 | 3347 | 1589 | 900 | 0 | 138 | 981.095 | 80 | 3543.5 | 633.95 | 51 | 292.5 | 0 | 0 | 2.5 | 119
12:00 | 3300 | 1553 | 900 | 0 | 142 | 1041.78 | 80 | 3725 | 665.64 | 51 | 271 | 0 | 0 | 5 | 161
12:30 | 3343 | 1554.5 | 900.5 | 0 | 147 | 1032.185 | 80 | 3890.5 | 657.96 | 60 | 265.5 | 0 | 0 | 13 | 176.5
13:00 | 3386 | 1556 | 901 | 0 | 152 | 1022.59 | 80 | 4056 | 650.28 | 69 | 260 | 0 | 0 | 21 | 192
13:30 | 3319 | 1579.5 | 900.5 | 0 | 156 | 1099.12 | 80 | 4179 | 589.495 | 73.75 | 272.5 | 0 | 0 | 20.5 | 186.5
14:00 | 3252 | 1603 | 900 | 0 | 160 | 1175.65 | 80 | 4302 | 528.71 | 78.5 | 285 | 0 | 0 | 20 | 181
14:30 | 3182.5 | 1603.5 | 900 | 0 | 160 | 1229.42 | 80 | 4277 | 480.175 | 77.75 | 358.7 | 0 | 0 | 22 | 184.5
15:00 | 3113 | 1604 | 900 | 0 | 160 | 1283.19 | 80 | 4252 | 431.64 | 77 | 432.4 | 0 | 0 | 24 | 188
15:30 | 3168.5 | 1590.5 | 900.5 | 0 | 156 | 1305.485 | 80 | 4246 | 346.435 | 77 | 521.8 | 0 | 0 | 24 | 165
16:00 | 3224 | 1577 | 901 | 0 | 152 | 1327.78 | 80 | 4240 | 261.23 | 77 | 611.2 | 0 | 0 | 24 | 142
16:30 | 3249.5 | 1624.5 | 900.5 | 0 | 153 | 1390.02 | 80 | 4237 | 175.86 | 170.5 | 869.1 | 0 | 0 | 19.5 | 71
17:00 | 3275 | 1672 | 900 | 0 | 154 | 1452.26 | 80 | 4234 | 90.49 | 264 | 1127 | 0 | 0 | 15 | 0
17:30 | 3278 | 1624.5 | 900 | 0 | 145 | 1451.03 | 80 | 4171.5 | 46.25 | 289 | 1240.5 | 0 | 0 | 10.5 | 29.5
18:00 | 3281 | 1577 | 900 | 0 | 136 | 1449.8 | 80 | 4109 | 2.01 | 314 | 1354 | 0 | 0 | 6 | 59
18:30 | 3352.5 | 1624.5 | 830.5 | 0 | 146 | 1454.18 | 80 | 4138.5 | 1.005 | 305 | 1360 | 0 | 0 | 3 | 29.5
19:00 | 3424 | 1672 | 761 | 0 | 156 | 1458.56 | 80 | 4168 | 0 | 296 | 1366 | 0 | 0 | 0 | 0
19:30 | 3342 | 1544.5 | 713 | 0 | 148 | 1461.24 | 80 | 4236 | 0 | 296 | 1759 | 0 | 0 | 0 | 0
20:00 | 3315 | 1544 | 713 | 0 | 148 | 1457.62 | 80 | 4215 | 0 | 296 | 1836.5 | 0 | 0 | 0 | 0
20:30 | 3317.5 | 1539.5 | 807.5 | 0 | 151 | 1459.4 | 80 | 4222.5 | 0 | 296 | 1802.65 | 0 | 0 | 0 | 0
21:00 | 3320 | 1535 | 902 | 0 | 154 | 1461.18 | 80 | 4230 | 0 | 296 | 1768.8 | 0 | 0 | 0 | 0
21:30 | 3314.5 | 1537 | 902 | 0 | 152 | 1457.85 | 80 | 4228 | 0 | 264.5 | 1655.9 | 0 | 0 | 0 | 0
22:00 | 3309 | 1539 | 902 | 0 | 150 | 1454.52 | 80 | 4226 | 0 | 233 | 1543 | 0 | 0 | 0 | 0
22:30 | 3310 | 1544 | 902 | 0 | 147 | 1452.445 | 80 | 4227.5 | 0 | 208.5 | 1393.8 | 0 | 0 | 0 | 0
23:00 | 3311 | 1549 | 902 | 0 | 144 | 1450.37 | 80 | 4229 | 0 | 184 | 1244.6 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 07-03-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 392 | 00:00 | 379 | 14:00 | Madunaghat | 405 | 07:00 | 395 | 00:00
Amtali | 417 | 06:00 | 406 | 15:00 | Meghnaghat | 399 | 06:00 | 381 | 15:00
Ashuganj | 409 | 06:00 | 390 | 14:00 | Payra | 417 | 06:00 | 409 | 14:00
Bhulta | 400 | 06:00 | 378 | 15:00 | Rahanpur | 416 | 06:00 | 397 | 17:00
Bibiana | 409 | 06:00 | 397 | 14:00 | Rampal | 410 | 06:00 | 395 | 14:00
BIPTC | 403 | 08:00 | 388 | 13:00
Bogura | 406 | 06:00 | 382 | 16:00
Gopalganj | 409 | 06:00 | 390 | 14:00
Kaliakoir | 393 | 06:00 | 372 | 14:00
Korerhat | 405 | 06:00 | 393 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 236 | 06:00 | 221 | 15:00 | Jhenaidah | 237 | 06:00 | 221 | 13:00
AKSML | 233.8 | 06:00 | 223 | 13:00 | Kachua | 233 | 06:00 | 222 | 13:00
Aminbazar | 236 | 05:00 | 223 | 14:00 | Kaliakoir | 237 | 06:00 | 225 | 15:00
Ashuganj | 234 | 06:00 | 220 | 16:00 | Keranigonj | 235 | 06:00 | 220 | 14:00
Ashuganj-400 | 234 | 06:00 | 220 | 16:00 | Khulna(S) | 240 | 06:00 | 224 | 14:00
Baghabari | 236 | 06:00 | 223 | 16:00 | Korerhat | 231 | 06:00 | 223 | 13:00
Barapukuria | 223 | 20:00 | 196 | 10:00 | Madunaghat | 230 | 06:00 | 224 | 13:00
Barapukuria-230 | 223 | 20:00 | 196 | 10:00 | Madunaghat-400 | 232 | 07:00 | 225 | 00:00
Barishal | 233 | 06:00 | 224 | 14:00 | Maniknagar | 233 | 06:00 | 219 | 15:00
Bheramara | 235 | 20:00 | 221 | 12:00 | Meghnaghat | 241 | 06:00 | 230 | 13:00
Bhulta | 233 | 06:00 | 219 | 15:00 | Meghnaghat-400 | 237 | 06:00 | 223 | 15:00
Bibiana | 239 | 06:00 | 228 | 14:00 | Mirsorai | 236 | 10:00 | 229 | 00:00
BIPTC | 237 | 05:00 | 222 | 13:00 | Rajshahi | 233 | 03:00 | 220 | 12:00
Bogura | 240 | 06:00 | 226 | 16:00 | Rampal | 237 | 06:00 | 225 | 13:00
Bogura-400 | 240 | 06:00 | 225 | 16:00 | Rampur | N/A | N/A | N/A | N/A
Borhanuddin | 237 | 08:00 | 231 | 14:00 | Rampura | 232 | 06:00 | 218 | 15:00
BSRM | 233 | 06:00 | 222 | 13:00 | Shikalbaha | 230 | 07:00 | 222 | 13:00
Chowmuhani | 232 | 06:00 | 221 | 13:00 | Shyampur | 235 | 06:00 | 221 | 14:00
Cumilla(N) | 232 | 06:00 | 222 | 14:00 | Siddhirganj | 235 | 06:00 | 222 | 14:00
Faridpur | 231 | 06:00 | 219 | 14:00 | Sirajgonj | 240 | 05:00 | 230 | 13:00
Fenchuganj | 239 | 06:00 | 231 | 14:00 | Sreepur | 228 | 06:00 | 216 | 15:00
Feni | 234 | 06:00 | 223 | 13:00 | Tongi | 232 | 04:00 | 220 | 13:00
Ghorashal | 235 | 03:00 | 230 | 00:00
Ghorashal-230 | 231 | 06:00 | 217 | 15:00
Gopalganj | 230 | 06:00 | 219 | 14:00
GPH | 232 | 06:00 | 226 | 00:00
Haripur | 235 | 06:00 | 221 | 15:00
Hasnabad | 235 | 04:00 | 220 | 14:00
Hathazari | 230 | 08:00 | 219 | 13:00
Ishurdi | 237 | 06:00 | 225 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 05:00 | 128 | 14:00 | Magura | 135 | 06:00 | 123 | 13:00
Agargaon | 139 | 07:00 | 130 | 13:00 | Mahasthangarh | 135 | 05:00 | 125 | 10:00
Agrabad | 133 | 06:00 | 125 | 14:00 | Maijdee | 130 | 06:00 | 123 | 13:00
AKS | 131 | 18:00 | 126 | 14:00 | Manikganj | 135 | 05:00 | 122 | 17:00
Aminbazar | 136 | 05:00 | 128 | 14:00 | Maniknagar | 131 | 06:00 | 120 | 15:00
Amnura | 137 | 06:00 | 128 | 15:00 | Matarbari | 124 | 08:00 | 112 | 19:00
Ashuganj | 142 | 06:00 | 134 | 15:00 | Matuail | 132 | 04:00 | 124 | 15:00
Bagerhat | 135 | 05:00 | 121 | 19:00 | Metrorail_Motijheel | 136 | 20:00 | 120 | 15:00
Bajitpur | 132 | 03:00 | 123 | 17:00 | Metrorail_Uttara | 134 | 06:00 | 126 | 16:00
Bakerganj | 136 | 06:00 | 130 | 14:00 | Millgate | 135 | 08:00 | 126 | 16:00
Bakulia | 133 | 09:00 | 127 | 13:00 | Mirpur | 136 | 06:00 | 126 | 14:00
Banani | 137 | 06:00 | 127 | 13:00 | Mirzapur | 136 | 06:00 | 126 | 17:00
Bangabhaban | 130 | 06:00 | 121 | 14:00 | Mithapukur | 135 | 19:30 | 120 | 16:00
Barapukuria | 138 | 20:00 | 120 | 10:00 | MI_Cement | 136 | 06:00 | 123 | 15:00
Barguna | 136 | 06:00 | 129 | 16:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 136 | 06:00 | 128 | 16:00 | Mogbazar | 138 | 08:00 | 129 | 14:00
Barishal-230 | 137 | 06:00 | 130 | 13:00 | Mongla | 135 | 05:00 | 122 | 17:00
Baroaulia | 133 | 06:00 | 129 | 00:00 | Motijheel | 130 | 06:00 | 121 | 14:00
Baroirhat | 133 | 07:00 | 126 | 14:00 | Muktagacha | 130 | 00:00 | 120 | 17:00
Bashundhara | 137 | 05:00 | 127 | 15:00 | Munshiganj | 130 | 06:00 | 123 | 14:00
BashundharaCement | 131 | 14:00 | 127 | 05:00 | Muradnagar | 131 | 07:00 | 124 | 14:00
Beanibazar | 131 | 06:00 | 123 | 14:00 | Mymensingh | 133 | 03:00 | 113 | 17:00
Benapole | 135 | 06:00 | 121 | 13:00 | Naogaon | 134 | 05:00 | 122 | 16:00
Bhaluka | 134 | 05:00 | 126 | 17:00 | Narail | 134 | 06:00 | 122 | 13:00
Bhandaria | 134 | 06:00 | 125 | 16:00 | Narinda | 131 | 06:00 | 120 | 15:00
Bhangura | 134 | 04:00 | 126 | 13:00 | Narshingdi | 128 | 06:00 | 121 | 15:00
Bheramara | 135 | 02:00 | 130 | 13:00 | Natore | 135 | 05:00 | 127 | 12:00
Bheramara(GK) | 136 | 03:00 | 131 | 11:00 | Nawabganj | 139 | 06:00 | 128 | 14:00
Bhulta | 126 | 08:00 | 121 | 14:00 | Netrakona | 124 | 06:00 | 111 | 17:00
Bog-Sherpur | 136 | 03:00 | 126 | 16:00 | New | 135 | 08:00 | 127 | 16:00
Bogura | 137 | 04:00 | 127 | 16:00 | Niamatpur | 138 | 05:00 | 130 | 17:00
Bogura-230 | 138 | 05:00 | 129 | 13:00 | Noapara | 135 | 04:00 | 124 | 19:00
Brahmanbaria | 135 | 09:00 | 128 | 15:00 | Pabna | 137 | 06:00 | 129 | 11:00
Cantonment | 140 | 06:00 | 130 | 14:00 | Palashbari | 131 | 05:00 | 121 | 16:00
Chandina | 135 | 06:00 | 128 | 13:00 | Panchagarh | 138 | 20:00 | 121 | 10:00
Chandpur | 134 | 22:00 | 126 | 13:00 | Patiya | 132 | 06:00 | 125 | 13:00
Chandraghona | 135 | 07:00 | 129 | 14:00 | Patuakhali | 135 | 06:00 | 129 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 135 | 04:00 | 131 | 15:00 | Payra | 137 | 03:00 | 134 | 13:00
Charsaidpur | 131 | 04:00 | 124 | 14:00 | PHP | 132 | 06:00 | 126 | 13:00
Chauddagram | 132 | 06:00 | 125 | 15:00 | Postogola | 136 | 04:00 | 126 | 14:00
Chhatak | 129 | 06:00 | 122 | 14:00 | Pubail | N/A | N/A | N/A | N/A
Chowmuhani | 128 | 19:30 | 123 | 13:00 | Purbachal | 138 | 06:00 | 127 | 14:00
Chuadanga | 137 | 06:00 | 122 | 13:00 | Purbasadipur | 133 | 20:00 | 115 | 10:00
Coxsbazar | 123 | 07:00 | 113 | 21:00 | Rahanpur | 139 | 06:00 | 132 | 17:00
Cumilla(N) | 134 | 06:00 | 127 | 15:00 | Rahanpur-400 | 139 | 00:00 | 133 | 16:00
Cumilla(S) | 136 | 01:00 | 118 | 15:00 | Rahim | 132 | 06:00 | 124 | 15:00
Daganbhuiyan | 131 | 06:00 | 125 | 13:00 | Rajbari | 133 | 06:00 | 125 | 14:00
Daudkandi | 130 | 06:00 | 120 | 14:00 | Rajendrapur | 135 | 02:00 | 127 | 15:00
DhakaUniversity | 136 | 03:00 | 128 | 15:00 | Rajshahi | 135 | 06:00 | 125 | 12:00
Dhamrai | 141 | 06:00 | 132 | 14:00 | Rajshahi-230 | 135 | 06:00 | 127 | 12:00
Dhanmondi | 137 | 05:00 | 128 | 15:00 | Ramganj | 129 | 21:00 | 123 | 13:00
Dohazari | 129 | 06:00 | 122 | 00:00 | Rampur | 133 | 18:00 | 124 | 14:00
Faridpur | 133 | 06:00 | 32 | 07:00 | Rampura | 138 | 06:00 | 128 | 14:00
Fatullah | 136 | 06:00 | 124 | 15:00 | Rangamati | 133 | 06:00 | 128 | 14:00
Fenchuganj | 135 | 06:00 | 129 | 14:00 | Rangpur | 135 | 19:30 | 121 | 10:00
Feni | 129 | 06:00 | 124 | 13:00 | Ruppur | 137 | 05:00 | 131 | 12:00
Feni-230 | 131 | 06:00 | 125 | 13:00 | Saidpur | 135 | 20:00 | 119 | 10:00
Ghatail | 131 | 04:00 | 118 | 17:00 | Satkhira | 136 | 06:00 | 121 | 19:00
Ghorashal | 138 | 05:00 | 131 | 13:00 | Satmasjid | 139 | 07:00 | 130 | 13:00
Goalpara | 140 | 06:00 | 127 | 19:00 | Savar | 134 | 03:00 | 125 | 15:00
Gollamari | 138 | 06:00 | 29 | 18:00 | SevenRings | 139 | 06:00 | 130 | 14:00
Gopalganj | 137 | 06:00 | 127 | 14:00 | ShahCement | 131 | 04:00 | 124 | 14:00
Gopalganj-400 | 137 | 06:00 | 129 | 15:00 | Shahjadpur | 139 | 04:00 | 130 | 16:00
Gulshan | 137 | 06:00 | 127 | 15:00 | Shahjibazar | 136 | 06:00 | 125 | 15:00
Halishahar | 133 | 06:00 | 124 | 14:00 | Shahmirpur | 133 | 19:30 | 126 | 14:00
Haripur | 133 | 06:00 | 125 | 14:00 | Shariatpur | 136 | 07:00 | 127 | 14:00
HaripurSBU | 133 | 06:00 | 125 | 14:00 | Sherpur | 131 | 02:00 | 115 | 17:00
Hasnabad | 136 | 05:00 | 126 | 13:00 | Shikalbaha | 124 | 08:00 | 19 | 12:00
Hathazari | 135 | 08:00 | 129 | 14:00 | Shikalbaha-230 | 134 | 06:00 | 129 | 11:00
Hatirjheel | 138 | 06:00 | 127 | 15:00 | Shitalakhya | 136 | 06:00 | 123 | 15:00
Ishurdi | 138 | 05:00 | 132 | 12:00 | Sholosohor | 134 | 07:00 | 129 | 13:00
Jaldhaka | 133 | 20:00 | 119 | 10:00 | Shyampur | 134 | 05:00 | 128 | 10:00
Jamalpur | 134 | 01:00 | 118 | 17:00 | Shyampur-230 | 136 | 06:00 | 126 | 14:00
Jashore | 136 | 06:00 | 123 | 13:00 | Siddhirganj | 133 | 06:00 | 125 | 15:00
Jhenaidah | 138 | 06:00 | 115 | 16:00 | Sirajganj | 134 | 03:00 | 124 | 16:00
Jhenaidah-230 | 138 | 06:00 | 126 | 16:00 | Sonargaon | 130 | 04:00 | 123 | 14:00
Joydebpur | 134 | 06:00 | 124 | 16:00 | Sreemongol | 130 | 06:00 | 124 | 13:00
Joypurhat | 130 | 02:00 | 117 | 16:00 | Sreepur | 139 | 03:00 | 131 | 12:00
Juldah | 132 | 06:00 | 126 | 14:00 | Srinagar | 138 | 06:00 | 128 | 14:00
Kabirpur | 138 | 06:00 | 122 | 16:00 | SSM | 138 | 06:00 | 134 | 00:00
Kachua | 132 | 06:00 | 126 | 13:00 | Sunamganj | 127 | 06:00 | 121 | 14:00
Kaliakoir | 143 | 04:00 | 132 | 13:00 | Sylhet | 131 | 06:00 | 124 | 14:00
Kaliganj | 138 | 05:00 | 126 | 13:00 | Sylhet-132 | 129 | 05:00 | 126 | 16:00
Kallyanpur | 134 | 01:00 | 127 | 13:00 | Tangail | 132 | 05:00 | 121 | 17:00
Kalurghat | 134 | 06:00 | 129 | 14:00 | Taraganj | 133 | 20:00 | 120 | 10:00
Kamrangirchar | 138 | 05:00 | 125 | 14:00 | Tasnim | 131 | 06:00 | 123 | 14:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 137 | 20:00 | 118 | 10:00
Kasba | 131 | 06:00 | 123 | 14:00 | TK | 134 | 05:00 | 129 | 14:00
Kazla | 130 | 06:00 | 120 | 15:00 | Tongi | 137 | 07:00 | 129 | 17:00
Keranigonj | 139 | 06:00 | 129 | 14:00 | Ullahpara | 135 | 05:00 | 126 | 17:00
Khagrachori | 134 | 06:00 | 127 | 13:00 | Ullon | 137 | 06:00 | 127 | 15:00
Khulna | 138 | 05:00 | 126 | 16:00 | Uttara | 135 | 06:00 | 126 | 14:00
Khulna(S) | 140 | 06:00 | 128 | 14:00 | UttaraNew | 134 | 06:00 | 126 | 16:00
Khulshi | 132 | 08:00 | 123 | 13:00 | Zigatola | 138 | 06:00 | 37 | 02:00
Kishoreganj | 131 | 05:00 | 121 | 17:00
Kodda | 138 | 20:00 | 123 | 14:00
Korerhat | 133 | 06:00 | 129 | 13:00
KSRM | 133 | 06:00 | 128 | 15:00
Kulaura | 134 | 06:00 | 128 | 14:00
Kurigram | 133 | 20:00 | 119 | 16:00
Kushtia | 130 | 06:00 | 122 | 16:00
Laksam | 132 | 06:00 | 125 | 13:00
Lakshmipur | 130 | 06:00 | 123 | 13:00
Lalbag | 136 | 02:00 | 128 | 14:00
Lalmonirhat | 130 | 14:00 | 120 | 17:00
Madanganj | 131 | 14:00 | 127 | 05:00
Madaripur | 134 | 04:00 | 130 | 13:00
Madartek | 136 | 07:00 | 127 | 15:00
Madunaghat | 134 | 06:00 | 130 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 07-03-2026 | [28 empty] | Date: | 07-03-2026 | [28 empty] | Date: | 07-03-2026 | [28 empty] | Date: | 07-03-2026 | [28 empty] | Date: | 07-03-2026 | [17 empty] | Date: | 07-03-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 250 | 0 | 0 | 0 | 70 | 12 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 20 | 580 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1162 | 0 | 0 | 0 | 280 | 0 | 280 | 51 | 0 | 197 | 0 | 0 | 103 | 0 | 0 | 20 | 0 | 136 | 0 | 0 | 0 | 305 | 0 | 363 | 41 | 0 | 157 | 0 | 22 | 0 | 40 | 0 | 69 | 0 | 96 | 0 | 107 | 48 | 18 | 0 | 0 | 6 | 5801 | 900 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 1361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 50 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 120 | 220 | 0 | 0 | 1050 | 0 | 5865 | 11666 | 90.34
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 250 | 0 | 0 | 0 | 52 | 12 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 27 | 580 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1065 | 0 | 0 | 0 | 280 | 0 | 280 | 51 | 0 | 197 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 122 | 0 | 0 | 0 | 305 | 0 | 340 | 41 | 0 | 140 | 0 | 22 | 0 | 42 | 0 | 71 | 0 | 96 | 0 | 115 | 48 | 19 | 0 | 0 | 6 | 5587 | 900 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 975 | 0 | 0 | 0 | 1264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 48 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238 | 100 | 180 | 0 | 0 | 1045 | 0 | 5497 | 11084 | 90.33
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 250 | 0 | 0 | 0 | 52 | 12 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 580 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 1050 | 0 | 0 | 0 | 240 | 0 | 280 | 51 | 0 | 193 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 120 | 0 | 0 | 0 | 300 | 0 | 320 | 41 | 0 | 137 | 0 | 22 | 0 | 42 | 0 | 69 | 0 | 96 | 0 | 115 | 48 | 20 | 0 | 0 | 6 | 5358 | 900 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 962 | 0 | 0 | 0 | 1267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 48 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 100 | 180 | 0 | 0 | 1000 | 0 | 5383 | 10741 | 90.32
03:00 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 250 | 0 | 0 | 0 | 70 | 12 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 580 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 1055 | 0 | 0 | 0 | 240 | 0 | 280 | 51 | 0 | 195 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 124 | 0 | 0 | 0 | 240 | 0 | 338 | 41 | 0 | 134 | 0 | 22 | 0 | 40 | 0 | 70 | 0 | 96 | 0 | 115 | 48 | 21 | 0 | 0 | 6 | 5323 | 900 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 930 | 0 | 0 | 0 | 1266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 48 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 100 | 180 | 0 | 0 | 1000 | 0 | 5449 | 10772 | 90.31
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 250 | 0 | 0 | 0 | 70 | 12 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 580 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1150 | 0 | 0 | 0 | 240 | 0 | 280 | 51 | 0 | 191 | 0 | 0 | 104 | 0 | 0 | 20 | 0 | 128 | 0 | 0 | 0 | 290 | 0 | 367 | 41 | 0 | 154 | 0 | 22 | 0 | 40 | 0 | 69 | 0 | 96 | 0 | 115 | 48 | 21 | 0 | 0 | 0 | 5829 | 899 | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 0 | 0 | 0 | 1263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 48 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246 | 115 | 220 | 0 | 0 | 1050 | 0 | 5730 | 11559 | 90.3
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 12 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 580 | 0 | 0 | 6 | 0 | 0 | 227 | 0 | 0 | 0 | 1010 | 0 | 0 | 0 | 240 | 0 | 280 | 51 | 0 | 199 | 0 | 0 | 104 | 0 | 0 | 20 | 0 | 124 | 0 | 0 | 0 | 300 | 0 | 340 | 41 | 0 | 136 | 0 | 22 | 0 | 40 | 0 | 70 | 0 | 96 | 0 | 115 | 8 | 21 | 0 | 0 | 0 | 5460 | 900 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 890 | 0 | 0 | 0 | 1057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 47 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 120 | 180 | 0 | 0 | 900 | 0 | 5042 | 10502 | 90.29
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 310 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 580 | 0 | 0 | 30 | 0 | 0 | 186 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 240 | 0 | 250 | 20 | 0 | 189 | 0 | 0 | 104 | 0 | 0 | 20 | 0 | 116 | 0 | 0 | 0 | 300 | 0 | 318 | 41 | 0 | 136 | 0 | 20 | 0 | 40 | 0 | 70 | 0 | 96 | 0 | 115 | 8 | 21 | 0 | 0 | 1 | 5042 | 900 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 815 | 0 | 0 | 0 | 862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 115 | 180 | 0 | 0 | 800 | 0 | 4552 | 9594 | 90.28
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 250 | 0 | 0 | 2 | 0 | 14 | 22 | 0 | 378 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0.26 | 80 | 0 | 13 | 580 | 0 | 0 | 32 | 0 | 0 | 186 | 0 | 0 | 0 | 855 | 2 | 0 | 0 | 240 | 0 | 290 | 20 | 0 | 207 | 0 | 0 | 103 | 0 | 0 | 20 | 0 | 110 | 0 | 5 | 0 | 295 | 0 | 354 | 41 | 0 | 137 | 1 | 20 | 0 | 40 | 0 | 71 | 0 | 96 | 0 | 115 | 8 | 22 | 0 | 3.07 | 6 | 5238.33 | 758 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.42 | 800 | 0 | 0 | 0 | 865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.89 | 5 | 0 | 0 | 3.09 | 0 | 0 | 150 | 0 | 0 | 0 | 350 | 0 | 0.33 | 0 | 47 | 0 | 1 | 0 | 0 | 0 | 0 | 0.3 | 8 | 0.03 | 0 | 173 | 115 | 180 | 0 | 0 | 800 | 0 | 4513.06 | 9751.39 | 90.27
08:00 | 0 | 5 | 8 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 250 | 0 | 0 | 3 | 17 | 24 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 25 | 0.91 | 80 | 0 | 8 | 580 | 0 | 0 | 34 | 0 | 0 | 227 | 0 | 0 | 0 | 945 | 6 | 0 | 0 | 300 | 0 | 300 | 20 | 0 | 194 | 0 | 0 | 103 | 0 | 0 | 20 | 0 | 116 | 0 | 10 | 0 | 310 | 0 | 330 | 41 | 0 | 142 | 3 | 20 | 0 | 40 | 0 | 70 | 0 | 96 | 0 | 115 | 15 | 22 | 1 | 12.94 | 6 | 5573.85 | 663 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.31 | 852 | 0 | 0 | 0 | 1008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.26 | 27 | 0 | 0 | 14.54 | 0 | 0 | 150 | 0 | 0 | 0 | 400 | 0 | 1.44 | 0 | 50 | 0 | 5 | 0 | 0 | 0 | 0 | 1.4 | 34 | 0.12 | 0 | 239 | 110 | 180 | 0 | 0 | 848 | 0 | 4860.07 | 10433.92 | 90.26
09:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 250 | 0 | 0 | 5 | 17 | 23 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 25 | 1.78 | 80 | 0 | 5 | 580 | 0 | 0 | 45 | 0 | 0 | 225 | 0 | 0 | 0 | 950 | 12 | 0 | 0 | 300 | 0 | 300 | 20 | 0 | 196 | 0 | 0 | 103 | 0 | 0 | 20 | 0 | 124 | 0 | 34 | 0 | 305 | 0 | 338 | 41 | 0 | 136 | 6 | 20 | 0 | 40 | 0 | 71 | 0 | 96 | 0 | 115 | 56 | 22 | 1 | 23.31 | 6 | 5680.09 | 900 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.51 | 842 | 0 | 0 | 0 | 1026.62 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 8.06 | 54 | 0 | 0 | 29.53 | 0 | 0 | 150 | 0 | 0 | 0 | 400 | 0 | 2.86 | 0 | 50 | 0 | 12 | 34 | 0 | 0 | 0 | 2.8 | 71 | 0.3 | 0 | 239 | 100 | 180 | 0 | 0 | 894 | 0 | 5336.68 | 11016.77 | 90.25
10:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 4 | 49 | 0 | 0 | 0 | 355 | 0 | 0 | 250 | 0 | 0 | 10 | 17 | 23 | 22 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.69 | 80 | 0 | 5 | 580 | 0 | 0 | 13 | 0 | 0 | 220 | 0 | 0 | 0 | 960 | 16 | 0 | 0 | 360 | 0 | 300 | 20 | 0 | 207 | 0 | 0 | 101 | 0 | 0 | 20 | 0 | 132 | 0 | 53 | 0 | 310 | 0 | 355 | 41 | 0 | 141 | 8 | 20 | 0 | 41 | 0 | 70 | 0 | 96 | 0 | 115 | 55 | 22 | 2 | 34.53 | 6 | 5859.22 | 900 | 269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 834 | 0 | 0 | 0 | 922.14 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 13.91 | 77 | 0 | 0 | 39.87 | 0 | 0 | 150 | 0 | 0 | 0 | 414 | 0 | 3.99 | 0 | 0 | 0 | 16 | 34 | 0 | 0 | 0 | 3.6 | 115 | 0.44 | 0 | 199 | 100 | 180 | 0 | 0 | 820 | 0 | 5189.95 | 11049.17 | 90.24
11:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 17 | 51 | 0 | 0 | 0 | 365 | 0 | 0 | 250 | 0 | 0 | 30 | 17 | 23 | 22 | 0 | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.12 | 80 | 0 | 4 | 570 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 960 | 19 | 0 | 0 | 355 | 0 | 325 | 28 | 0 | 209 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 134 | 0 | 62 | 0 | 310 | 0 | 407 | 42 | 0 | 147 | 9 | 20 | 0 | 41 | 0 | 69 | 0 | 96 | 0 | 115 | 57 | 20 | 2 | 40.16 | 6 | 6050.28 | 900 | 269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 830 | 0 | 0 | 0 | 920.41 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 46.66 | 90 | 0 | 0 | 46.47 | 0 | 0 | 160 | 0 | 0 | 0 | 414 | 0 | 4.99 | 0 | 0 | 0 | 22 | 34 | 0 | 0 | 0 | 4.3 | 134 | 0.56 | 0 | 202 | 120 | 220 | 0 | 0 | 800 | 0 | 5332.39 | 11382.67 | 90.23
12:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 360 | 0 | 0 | 250 | 0 | 0 | 31 | 17 | 23 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 3.21 | 80 | 0 | 4 | 600 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1100 | 18 | 0 | 0 | 330 | 0 | 335 | 51 | 0 | 197 | 0 | 0 | 98 | 0 | 0 | 20 | 0 | 142 | 0 | 65 | 0 | 315 | 0 | 390 | 42 | 0 | 157 | 9 | 20 | 0 | 41 | 0 | 70 | 0 | 96 | 0 | 115 | 57 | 18 | 2 | 43.41 | 6 | 6068.62 | 900 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 898 | 0 | 0 | 0 | 1041.78 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 49.35 | 100 | 0 | 0 | 52.14 | 0 | 0 | 190 | 0 | 0 | 0 | 350 | 0 | 4.92 | 0 | 0 | 0 | 23 | 34 | 0 | 0 | 0 | 5.1 | 168 | 0.51 | 0 | 277 | 120 | 220 | 0 | 0 | 850 | 0 | 5665.8 | 11734.42 | 90.22
13:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 14 | 0 | 0 | 0 | 360 | 0 | 0 | 250 | 0 | 0 | 29 | 35 | 23 | 22 | 0 | 340 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 3.24 | 80 | 0 | 7 | 600 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1165 | 18 | 0 | 0 | 380 | 0 | 335 | 51 | 0 | 197 | 0 | 0 | 98 | 0 | 0 | 20 | 0 | 152 | 0 | 63 | 0 | 310 | 0 | 393 | 42 | 0 | 154 | 9 | 8 | 0 | 41 | 0 | 70 | 0 | 96 | 0 | 115 | 57 | 16 | 2 | 40.95 | 6 | 6211.19 | 901 | 261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 1004 | 0 | 0 | 0 | 1022.59 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 47.48 | 98 | 0 | 0 | 51.16 | 0 | 0 | 197 | 0 | 0 | 0 | 385 | 0 | 4.99 | 0 | 0 | 0 | 21 | 34 | 0 | 0 | 0 | 4.9 | 170 | 0.56 | 0 | 277 | 120 | 220 | 0 | 0 | 1010 | 0 | 5942.68 | 12153.87 | 90.21
14:00 | 0 | 1 | 8 | 0 | 0 | 0 | 0 | 6 | 351 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 17 | 38 | 0 | 0 | 0 | 365 | 0 | 0 | 250 | 0 | 0 | 25 | 52 | 23 | 22 | 0 | 380 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 2.83 | 80 | 0 | 4 | 590 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1180 | 15 | 0 | 0 | 215 | 101 | 280 | 51 | 0 | 138 | 0 | 0 | 97 | 0 | 0 | 20 | 0 | 160 | 0 | 58 | 0 | 310 | 0 | 393 | 42 | 0 | 153 | 8 | 8 | 0 | 41 | 0 | 70 | 0 | 96 | 0 | 115 | 57 | 16 | 2 | 36.66 | 6 | 6139.49 | 900 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 1115 | 0 | 0 | 0 | 1175.65 | 0 | 0 | 0 | 0 | 0 | 0 | 17.5 | 0 | 0 | 41.83 | 84 | 0 | 0 | 44.17 | 0 | 0 | 196 | 0 | 0 | 0 | 414 | 0 | 4.51 | 0 | 25 | 0 | 19 | 34 | 0 | 0 | 0 | 4.4 | 153 | 0.31 | 0 | 307 | 120 | 220 | 0 | 0 | 1085 | 0 | 6245.37 | 12384.86 | 90.2
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 6 | 344 | 0 | 0 | 15.4 | 0 | 60 | 0 | 0 | 4 | 17 | 54 | 0 | 0 | 0 | 355 | 0 | 17 | 250 | 0 | 0 | 21 | 52 | 23 | 22 | 0 | 380 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 10 | 12 | 1.94 | 80 | 0 | 3 | 515 | 0 | 0 | 18 | 0 | 0 | 219 | 0 | 0 | 0 | 1180 | 13 | 0 | 0 | 215 | 50 | 220 | 51 | 0 | 127 | 0 | 27 | 97 | 31 | 0 | 20 | 0 | 160 | 0 | 45 | 0 | 310 | 0 | 397 | 42 | 0 | 153 | 6 | 20 | 0 | 41 | 0 | 70 | 0 | 96 | 0 | 69 | 58 | 12 | 1 | 16.66 | 6 | 6062 | 900 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 1117 | 0 | 0 | 0 | 1283.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.22 | 65 | 0 | 0 | 37.55 | 0 | 0 | 193 | 0 | 0 | 0 | 408 | 0 | 3.75 | 0 | 53 | 0 | 15 | 34 | 0 | 0 | 0 | 3.3 | 109 | 0.22 | 0 | 307 | 120 | 220 | 0 | 0 | 1080 | 0 | 6295.23 | 12357.23 | 90.19
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 6 | 345 | 0 | 0 | 16.2 | 8 | 68 | 0 | 30 | 17 | 17 | 51 | 0 | 0 | 0 | 355 | 0 | 17 | 300 | 0 | 0 | 12 | 52 | 0 | 22 | 0 | 370 | 0 | 10 | 0 | 0 | 24 | 0 | 0 | 0 | 24 | 36 | 1.12 | 80 | 1 | 2 | 515 | 0 | 0 | 28 | 0 | 10 | 220 | 0 | 0 | 0 | 1165 | 8 | 4 | 0 | 250 | 0 | 220 | 51 | 0 | 204 | 0 | 32 | 97 | 40 | 0 | 20 | 0 | 152 | 0 | 27 | 0 | 315 | 0 | 394 | 42 | 0 | 153 | 3 | 22 | 0 | 41 | 0 | 71 | 0 | 96 | 0 | 69 | 58 | 12 | 1 | 13.68 | 6 | 6229 | 901 | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 1123 | 0 | 0 | 0 | 1327.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.83 | 41 | 0 | 0 | 22.43 | 0 | 0 | 190 | 0 | 0 | 0 | 414 | 0 | 2.24 | 0 | 50 | 35 | 9 | 34 | 0 | 0 | 0 | 1.8 | 61 | 0.13 | 0 | 307 | 120 | 220 | 0 | 0 | 1080 | 0 | 6246.21 | 12475.21 | 90.18
17:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 7 | 343 | 0 | 0 | 32 | 24 | 81 | 15 | 95 | 30 | 35 | 99 | 0 | 0 | 0 | 435 | 0 | 35 | 300 | 0 | 0 | 5 | 142 | 23 | 22 | 0 | 350 | 3 | 16 | 0 | 0 | 15 | 34 | 0 | 0 | 24 | 36 | 0.31 | 80 | 15 | 18 | 515 | 0 | 0 | 48 | 0 | 55 | 221 | 0 | 0 | 0 | 1160 | 2 | 35 | 0 | 300 | 0 | 255 | 51 | 0 | 197 | 0 | 54 | 97 | 49 | 0 | 20 | 0 | 154 | 0 | 10 | 15 | 310 | 0 | 382 | 42 | 0 | 153 | 1 | 22 | 0 | 41 | 0 | 70 | 0 | 96 | 0 | 69 | 58 | 12 | 0 | 5.32 | 5 | 6876.63 | 900 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 1122 | 0 | 0 | 0 | 1452.26 | 0 | 0 | 0 | 20 | 10 | 0 | 0 | 0 | 0 | 6.21 | 15 | 0 | 0 | 7.15 | 0 | 0 | 189 | 0 | 0 | 0 | 407 | 0 | 0.75 | 0 | 50 | 109 | 3 | 90 | 0 | 0 | 0 | 0.7 | 21 | 0.05 | 0 | 307 | 120 | 220 | 0 | 0 | 1080 | 0 | 6387.12 | 13263.75 | 90.17
18:00 | 0 | 50 | 13 | 0 | 0 | 0 | 0 | 6 | 321 | 0 | 0 | 33 | 35 | 126 | 45 | 95 | 30 | 35 | 103 | 0 | 0 | 0 | 455 | 0 | 35 | 300 | 0 | 0 | 1 | 142 | 17 | 22 | 0 | 350 | 17 | 16 | 0 | 0 | 6 | 48 | 0 | 0 | 24 | 36 | 0 | 80 | 16 | 24 | 515 | 0 | 0 | 50 | 0 | 68 | 218 | 0 | 0 | 0 | 1095 | 0 | 60 | 0 | 300 | 0 | 300 | 10 | 0 | 196 | 0 | 69 | 70 | 49 | 0 | 20 | 0 | 136 | 0 | 0 | 16 | 305 | 0 | 405 | 42 | 0 | 155 | 0 | 22 | 0 | 11 | 0 | 69 | 0 | 96 | 0 | 98 | 75 | 12 | 0 | 0 | 0 | 6943 | 900 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1117 | 0 | 0 | 0 | 1449.8 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 404 | 0 | 0.01 | 0 | 50 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 120 | 180 | 0 | 0 | 1050 | 0 | 6265.81 | 13208.81 | 90.16
19:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 6 | 345 | 0 | 0 | 40 | 35 | 142 | 45 | 70 | 30 | 35 | 130 | 0 | 0 | 0 | 400 | 0 | 35 | 328 | 0 | 0 | 0 | 142 | 26 | 22 | 0 | 415 | 16 | 16 | 0 | 0 | 0 | 51 | 0 | 0 | 36 | 36 | 0 | 80 | 17 | 11 | 515 | 0 | 0 | 50 | 0 | 60 | 224 | 0 | 0 | 0 | 1160 | 0 | 45 | 0 | 300 | 0 | 340 | 40 | 0 | 206 | 0 | 55 | 98 | 44 | 0 | 20 | 0 | 156 | 0 | 0 | 8 | 300 | 0 | 404 | 42 | 0 | 149 | 0 | 22 | 0 | 41 | 0 | 69 | 0 | 96 | 0 | 98 | 77 | 19 | 0 | 0 | 0 | 7197 | 761 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1096 | 0 | 0 | 0 | 1458.56 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 50 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 0 | 1040 | 0 | 6184.56 | 13381.56 | 90.15
19:30 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 6 | 330 | 0 | 0 | 46 | 35 | 136 | 45 | 150 | 55 | 35 | 148 | 0 | 0 | 0 | 350 | 0 | 55 | 290 | 0 | 0 | 0 | 142 | 25.5 | 22 | 0 | 310 | 15 | 16 | 0 | 0 | 0 | 51 | 0 | 0 | 50 | 36 | 0 | 80 | 25 | 15 | 515 | 0 | 0 | 50 | 0 | 72 | 225 | 0 | 0 | 0 | 1160 | 0 | 100 | 0 | 300 | 0 | 340 | 51 | 0 | 196 | 0 | 106 | 99 | 100 | 0 | 20 | 0 | 148 | 0 | 0 | 8 | 310 | 0 | 390 | 42 | 0 | 157 | 0 | 17 | 0 | 41 | 0 | 70 | 0 | 96 | 0 | 98 | 77 | 19 | 0 | 0 | 0 | 7325.5 | 713 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 0 | 0 | 0 | 1461.24 | 0 | 0 | 0 | 70 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 50 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 0 | 1084 | 0 | 6254.24 | 13579.74
20:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 6 | 329 | 0 | 0 | 48.5 | 35 | 132 | 45 | 195 | 55 | 35 | 147 | 0 | 0 | 0 | 360 | 0 | 55 | 280 | 0 | 0 | 0 | 142 | 25 | 22 | 0 | 310 | 15 | 16 | 0 | 0 | 0 | 51 | 0 | 0 | 50 | 36 | 0 | 80 | 46 | 11 | 515 | 0 | 0 | 50 | 0 | 73 | 225 | 0 | 0 | 0 | 1150 | 0 | 95 | 0 | 300 | 0 | 340 | 51 | 0 | 191 | 0 | 94 | 99 | 114 | 0 | 20 | 0 | 148 | 0 | 0 | 8 | 305 | 0 | 386 | 42 | 0 | 156 | 0 | 17 | 0 | 41 | 0 | 71 | 0 | 96 | 0 | 98 | 77 | 19 | 0 | 0 | 1 | 7358.5 | 713 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1113 | 0 | 0 | 0 | 1457.62 | 0 | 0 | 0 | 70 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 50 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 0 | 1080 | 0 | 6246.62 | 13605.12 | 90.14
21:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 6 | 332 | 0 | 0 | 47.8 | 35 | 149 | 45 | 195 | 55 | 35 | 153 | 0 | 0 | 0 | 350 | 0 | 55 | 280 | 0 | 0 | 0 | 142 | 24 | 22 | 0 | 310 | 15 | 16 | 0 | 0 | 0 | 51 | 0 | 0 | 50 | 36 | 0 | 80 | 50 | 21 | 515 | 0 | 0 | 50 | 0 | 90 | 226 | 0 | 0 | 0 | 1160 | 0 | 123 | 0 | 300 | 0 | 340 | 51 | 0 | 195 | 0 | 106 | 100 | 128 | 0 | 20 | 0 | 154 | 0 | 0 | 8 | 295 | 0 | 380 | 42 | 0 | 158 | 0 | 17 | 0 | 41 | 0 | 70 | 0 | 97 | 0 | 98 | 77 | 18 | 0 | 0 | 6 | 7469.8 | 902 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1116 | 0 | 0 | 0 | 1461.18 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 50 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 0 | 1082 | 0 | 6277.18 | 13746.98 | 90.13
22:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 6 | 330 | 0 | 0 | 46 | 35 | 149 | 15 | 95 | 55 | 35 | 147 | 0 | 0 | 0 | 343 | 0 | 55 | 280 | 0 | 0 | 0 | 125 | 24 | 22 | 0 | 310 | 13 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 50 | 36 | 0 | 80 | 48 | 24 | 515 | 0 | 0 | 50 | 0 | 88 | 226 | 0 | 0 | 0 | 1164 | 0 | 125 | 0 | 300 | 0 | 340 | 51 | 0 | 195 | 0 | 104 | 102 | 127 | 0 | 20 | 0 | 150 | 0 | 0 | 0 | 305 | 0 | 372 | 42 | 0 | 156 | 0 | 17 | 0 | 41 | 0 | 69 | 0 | 96 | 0 | 98 | 77 | 17 | 0 | 0 | 6 | 7269 | 902 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 0 | 0 | 0 | 1454.52 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 50 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 0 | 1080 | 0 | 6167.52 | 13436.52 | 90.12
23:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 6 | 336 | 0 | 0 | 46.6 | 17 | 134 | 0 | 30 | 55 | 35 | 148 | 0 | 0 | 0 | 345 | 0 | 55 | 280 | 0 | 0 | 0 | 108 | 24 | 22 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 50 | 36 | 0 | 80 | 47 | 25 | 515 | 0 | 0 | 50 | 0 | 89 | 226 | 0 | 0 | 0 | 1160 | 0 | 45 | 0 | 300 | 0 | 340 | 51 | 0 | 195 | 0 | 102 | 95 | 130 | 0 | 20 | 0 | 144 | 0 | 0 | 0 | 310 | 0 | 372 | 42 | 0 | 158 | 0 | 17 | 0 | 41 | 0 | 70 | 0 | 96 | 0 | 58 | 48 | 12 | 0 | 0 | 0 | 6951.6 | 902 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 0 | 0 | 1450.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 50 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 0 | 1085 | 0 | 6142.37 | 13093.97 | 90.11
Total KWH | 0 | 313920 | 180000 | 0 | 0 | 0 | 0 | 69000 | 7992000 | 0 | 0 | 355680 | 253800 | 1539648 | 218880 | 805920 | 389261 | 386946 | 1264320 | 0 | 0 | 0 | 8482165 | 0 | 396666 | 6402366 | 0 | 0 | 174813 | 1605600 | 459000 | 527400 | 0 | 8388181.82 | 85309 | 95345 | 0 | 0 | 132000 | 359926 | 0 | 0 | 345600 | 353280 | 21238 | 1922820 | 294398 | 359040 | 13374545.46 | 0 | 0 | 638400 | 0 | 626436 | 4976185 | 0 | 0 | 0 | 25936361 | 117450 | 592145 | 0 | 6873000 | 197300 | 7282000 | 1093258 | 0 | 4801000 | 0 | 750720 | 2205896 | 829920 | 0 | 483290 | 0 | 3290880 | 0 | 436373 | 59536 | 7348000 | 0 | 9074000 | 983000 | 0 | 3560400 | 62723 | 475368 | 0 | 960000 | 0 | 1678000 | 0 | 2309250 | 0 | 2468400 | 1260000 | 424320 | 13450 | 270810 | 105600 | 149732539.28 | 21064000 | 5846976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 546480 | 23883640 | 0 | 0 | 0 | 28974546 | 0 | 0 | 0 | 254976 | 310464 | 0 | 156272 | 0 | 0 | 278336 | 673150 | 0 | 0 | 349488 | 0 | 0 | 4415664 | 0 | 0 | 0 | 9353890 | 0 | 34320 | 0 | 953454 | 724425 | 144708 | 1084617 | 0 | 0 | 0 | 31787.4 | 1060560 | 3316 | 0 | 6262000 | 2725000 | 5163210 | 0 | 0 | 24376727.27 | 0 | 138672006.67 | 288404545.95