## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-01-07 | Monday
|  | Date (day): | 2019-01-07 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10691 | MW |  |  | (b) At Evening Peak Hour : |  | 12142 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-01-06 | 2019-01-07 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit #1 Under maint.
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | On test.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  |  | On test.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 250 | 280 | 380 | 380
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 20 | 20 | 40 | 40 | 38 |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 100 | 100
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 362 | 348 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 266 | 305 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 330 | 370 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 7 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 |  |  | Reserve
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 32 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 30 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 185 | 112 | 130 | 130 |  |  | FGMO
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 130 | 175 | 170 | 170
0 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
21 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 7 | 102 | 102
22 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 47 | 47 | 47 |  |  | Engine problem
23 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 18 | 54 | 54 | 54
24 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
25 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 18 | 55 | 55 | 55
26 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 17 | 36 | 36 |  | 19 | Engine problem
27 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 8 | 46 | 8 | 46 |  | 62 | Engine problem
28 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 55 | 58 | 58 |  | 22 | Engine problem
29 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
30 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 38 | 43 | 43 | 43 |  | 9 | Engine problem
32 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
33 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 84 | 150 | 300
34 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
37 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 0 | 56 | 130 | 130 |  | 19 | Engine problem
| Dhaka area Total |  |  |  |  | 6034 | 5798 | 1838 | 2275 | 3962 | 4350 | 298 | 531
38 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 150 | 150 | 30 |  | Gas shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
40 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 45 | 46 | 50 | 50
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 45 | 43 | 75 | 75 |  | 155 | Low water lavel
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint.
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 120 | 100 | 120 | 140 |  |  | FGMO
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 40 | 50 | 50 | 50
47 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 49 | 0 | 70
48 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 0 | 68
49 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 50 | 64 | 90 | 90 |  | 10 | Engine problem
50 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 80 | 80 | 100 | 100
51 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 6 | 28 | 20 | 20
52 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 46 | 51 | 90 | 100 |  | 8 | Engine problem
| Chattogram area Total |  |  |  |  | 1761 | 1681 | 597 | 724 | 812 | 960 | 210 | 438
53 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 80 | 100 | 100 | 29 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 100 | 100 | 34 |  | Gas shortage
54 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 205 | 184 | 210 | 210 |  |  | FGMO
55 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | S/D from (06/01/19 to 21/01/2019)
56 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 272 | 272 | 360 | 360 |  |  | FGMO
57 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 37 | 40 | 40 | 40 |  | 5 | Engine problem
58 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 |  |  | Gas shortage
59 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
60 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 16 | 179 |  | Gas Shortage
61 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
62 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 62 | 150 | 150
63 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 30 | 85 | 85 | 85
64 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 40
65 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 100 | 100 |  | 63 | FGMO & STG under maint.
66 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 17 | 140 | 180 | 180
67 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
68 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 92 | 118 | 84 | 112
69 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 8 | 16 | 0 | 33
70 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
71 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 22 | 22
72 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1032 | 1297 | 1685 | 1894 | 425 | 428
73 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 169 | 146 | 200 | 200 | 2
74 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
75 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 7 | 81 | 80 | 80 |  | 15 | Engine problem.
76 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2.5 | 0 | 2 | 0
77 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 7 | 100 | 100 | 200
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 207.5 | 349 | 404 | 502 | 2 | 15
78 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 56 | 56 | 56 | 56
79 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 62 | 62 | 63 | 63
80 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
81 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 256 | 256 | 270 | 280 |  |  | FGMO
82 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 22 | 51 | 51
83 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 0 | 49 | 21 | 21 |  | 23 | Engine problem
84 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
85 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 50 | 40 | 66 | 66 |  |  | FGMO
86 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 30 | 86 | 86 | 86
87 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 44 | 49 | 50 | 50
88 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 77 | 108 | 78 | 140
89 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
90 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 39 | 43 | 50 | 50
91 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 25 | 0 | 25
92 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 290 | 341 | 341 |  |  | FGMO
| Bibiyana-3 285MW |  | Gas | PDB | 285 MW | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
93 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 0 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1076 | 1237 | 1326 | 1433 | 0 | 23
94 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 522 | 679 | 540 | 678
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
95 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 32 | 115 | 115
96 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 40 | 0 | 40
97 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve
98 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 80
99 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 340 | 410 | 410
100 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 40 | 40 | 40
0 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
102 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 105 | 105 | 105
| Khulna Area Total |  |  |  |  | 2223 | 2209 | 847 | 1236 | 1310 | 1614 | 0 | 0
103 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 80 | 110 | 110
104 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
105 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 26 | 25 | 25 |  | 8 | Engine problem
106 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 194 | 178 | 194 | 194
107 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 32 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 244 | 381 | 424 | 454 | 0 | 8
108 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage.
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 50 | 70 | 80 | 80 |  | 20
109 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
110 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
111 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 50 | 50 | 50 | 50
112 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 8 | 50 | 50 | 50
113 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 50 | 50
114 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 192 | 180 | 200 | 200 | 210 |  | Gas shortage
115 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 |  |  | Gas shortage.
116 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 141 | 141 | 0 | 0 | 0 | 0 |  |  | Gas shortage.
117 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282 | 282 | 282 | 0 | 0 | 0 | 0 | 282 |  | Gas shortage.
118 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 0 | 35
119 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
120 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 14 | 14 | 14
121 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
122 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
123 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 26 | 102 | 90 | 100
| Rajshahi Area Total |  |  |  |  | 1556 | 1546 | 419 | 664 | 619 | 754 | 563 | 20
124 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
125 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 149 | 149 | 149 | 125 |  | Coal shortage
126 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 17 | 17 | 0 | 17
127 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 18 | 18 | 0 | 15
| Rangpur Area Total |  |  |  |  | 564 | 484 | 184 | 184 | 149 | 181 | 125 | 170
| Total |  |  |  |  | 17685 | 17142 | 6444.5 | 8347 | 10691 | 12142 | 1623 | 1633
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6063.8676 | 7854 | 10059.556 | 11424.8554
A. |  | 2019-01-06 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 8347 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 4796 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8347 | MW
3 | Day peak Generation : |  |  | 6444.5 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7854 | MW
4 | Evening peak Generation : |  |  | 8347 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 153.6554 | MKWHr | By Solar | 0.14482 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 120.6315 | MKWHr |  | By Oil: | 14.5123 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.6479 | MKWHr |  | By Hydro: | 1.0368 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1623 | MW | Dhaka | 2812 | 2812 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1633 | MW | Chittagong | 816 | 816 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3256 | MW | Khulna | 999 | 999 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1032.48 | MMCFD |  |  | Rajshahi | 861 | 861 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 89094443.96 | ii) Oil : | Taka | 109093837.55 | Comilla | 694 | 694 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14080894 | Total | Taka | 212269175.51 | Mymensingh | 599 | 599 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 3.783 | MKWHr. | Sylhet | 311 | 311 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -420 | MW at | 19:00 | hrs | Barisal | 203 | 203 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -510 | MW at | 6:00 | hrs | Rangpur | 559 | 559 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 27.5° C |  |  | Total | 7854 | 7854 |  | 0
B. |  | 2019-01-07 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 26.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12142 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6700 | MW
4 | Reserve(Generation end) |  |  |  | 3642 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 156.4719 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 4973 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.5316 | MKWHr. | ii) HVDC Flow at Peak Time |  | 679 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1504 | MKWHr. | iii) Maximum HVDC Flow : |  | 679 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.14 |  | (b) Today: | 98.09 |  | (c) Rule Curve: |  | 101.86
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-01-06
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 0 | 0 | 250 | 12 | 20 | 360 | 321 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 120 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 33 | 33 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 100 | 100 | 0 | 327 | 198 | 8 | 100 | 10 | 5 | 5 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 15 | 76 | 194 | 0 | 0 | 0 | 56 | 62 | 5 | 0 | 100 | 259 | 40 | 5 | 5 | 78 | 0 | 6 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 435 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 19 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 14 | 5 | 0 | 0 | 148 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4090 | 1438 | 5528 | 3528 | 435 | 1266 | 32 | 148 | 43 | 0 | 76 | 0 | 0 | 98.15
2:00 | 35 | 0 | 0 | 0 | 250 | 12 | 20 | 355 | 303 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 33 | 33 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 100 | 100 | 0 | 305 | 184 | 8 | 100 | 10 | 5 | 5 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 15 | 74 | 194 | 0 | 0 | 0 | 56 | 62 | 5 | 0 | 100 | 255 | 40 | 5 | 5 | 77 | 0 | 6 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 233 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 19 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3999 | 1216 | 5215 | 3473 | 233 | 1228 | 15 | 149 | 43 | 0 | 74 | 0 | 0 | 98.15
3:00 | 35 | 0 | 0 | 0 | 240 | 12 | 20 | 345 | 280 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 120 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 33 | 33 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 100 | 100 | 0 | 305 | 184 | 8 | 100 | 10 | 5 | 5 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 15 | 70 | 157 | 0 | 0 | 0 | 56 | 62 | 5 | 0 | 100 | 259 | 40 | 5 | 5 | 79 | 0 | 6 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 233 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 18 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3876 | 1134 | 5010 | 3346 | 233 | 1154 | 15 | 149 | 43 | 0 | 70 | 0 | 0 | 98.15
4:00 | 35 | 0 | 0 | 0 | 240 | 12 | 20 | 345 | 254 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 120 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 33 | 33 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 100 | 100 | 0 | 294 | 194 | 8 | 100 | 10 | 5 | 5 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 15 | 70 | 158 | 0 | 0 | 0 | 56 | 62 | 5 | 0 | 100 | 262 | 40 | 5 | 5 | 76 | 0 | 6 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 232 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 18 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 3 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3800 | 1115 | 4915 | 3297 | 232 | 1109 | 15 | 149 | 43 | 0 | 70 | 0 | 0 | 98.14
5:00 | 35 | 0 | 0 | 0 | 240 | 12 | 20 | 345 | 249 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 33 | 33 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 100 | 100 | 0 | 264 | 185 | 8 | 100 | 10 | 5 | 5 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 15 | 70 | 157 | 0 | 0 | 0 | 56 | 62 | 5 | 0 | 100 | 254 | 40 | 5 | 5 | 77 | 0 | 6 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 232 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204 | 18 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 3 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3733 | 1063 | 4796 | 3193 | 232 | 1094 | 15 | 149 | 43 | 0 | 70 | 0 | 0 | 98.14
6:00 | 35 | 0 | 0 | 0 | 320 | 12 | 20 | 375 | 310 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 120 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 33 | 33 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 100 | 100 | 0 | 294 | 203 | 8 | 100 | 10 | 5 | 5 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 15 | 72 | 217 | 0 | 0 | 0 | 56 | 62 | 5 | 0 | 100 | 262 | 40 | 5 | 5 | 78 | 0 | 6 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 232 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 19 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 3 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4077 | 1108 | 5185 | 3469 | 232 | 1205 | 15 | 149 | 43 | 0 | 72 | 0 | 0 | 98.14
7:00 | 35 | 0 | 0 | 0 | 380 | 12 | 20 | 360 | 313 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 120 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 33 | 33 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 100 | 100 | 0 | 320 | 204 | 8 | 100 | 36 | 5 | 5 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 15 | 70 | 220 | 0 | 0 | 0 | 56 | 62 | 5 | 0 | 100 | 266 | 40 | 5 | 5 | 78 | 0 | 6 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 1.56 | 0 | 0 | 0 | 0 |  | 232 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 18 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 35 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4239.56 | 1288 | 5527.56 | 3747 | 232 | 1231 | 54 | 149 | 43 | 0 | 70 | 1.56 | 0 | 0
8:00 | 35 | 0 | 0 | 0 | 380 | 12 | 20 | 380 | 342 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 120 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 33 | 33 | 0 | 0 | 45 | 0 | 0 | 120 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 0 | 100 | 100 | 0 | 342 | 205 | 8 | 100 | 36 | 5 | 5 | 5 | 5 | 0 | 0 | 3 | 0 | 0 | 15 | 78 | 203 | 0 | 0 | 0.5 | 56 | 62 | 5 | 0 | 130 | 270 | 40 | 5 | 5 | 78 | 0 | 6 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 8.5 | 9 | 0 | 0 | 0 |  | 524 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 205 | 18 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 20 | 8 | 0 | 52 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 |  | 4384 | 1752 | 6136 | 3864 | 524 | 1296 | 171 | 149 | 45 | 0 | 78 | 9 | 0 | 0
9:00 | 35 | 0 | 0 | 0 | 300 | 12 | 20 | 352 | 310 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 120 | 0 | 97 | 0 | 0 | 5 | 0 | 0 | 8 | 0 | 0 | 18 | 4 | 0 | 19 | 25 | 25 | 33 | 33 | 25 | 0 | 45 | 0 | 0 | 120 | 0 | 0 | 0 | 120 | 0 | 0 | 19 | 0 | 0 | 0 | 10 | 1 | 20 | 5 | 0 | 80 | 80 | 0 | 305 | 183 | 8 | 100 | 37 | 5 | 5 | 5 | 30 | 0 | 0 | 19 | 5 | 4 | 15 | 84 | 185 | 5 | 22 | 0 | 56 | 62 | 5 | 0 | 100 | 260 | 40 | 30 | 47 | 77 | 0 | 37 | 9 | 280 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 14.14 | 80 | 1 | 0 | 0 |  | 525 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 16 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 52 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 17 | 18 | 187 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 35 |  | 4441.14 | 1803 | 6244.14 | 3639 | 525 | 1358 | 395 | 149 | 45 | 35 | 84 | 14.14 | 0 | 0
10:00 | 35 | 0 | 0 | 0 | 250 | 13 | 20 | 348 | 268 | 0 | 0 | 330 | 0 | 0 | 0 | 20 | 120 | 0 | 105 | 0 | 0 | 7 | 0 | 0 | 8 | 0 | 0 | 18 | 18 | 0 | 19 | 25 | 24 | 33 | 33 | 43 | 0 | 45 | 0 | 0 | 120 | 25 | 0 | 0 | 120 | 0 | 0 | 38 | 0 | 0 | 30 | 45 | 38 | 19 | 5 | 0 | 80 | 80 | 0 | 276 | 183 | 8 | 100 | 34 | 5 | 5 | 40 | 30 | 0 | 0 | 19 | 8 | 8 | 15 | 92 | 167 | 7 | 22 | 0 | 56 | 62 | 5 | 0 | 100 | 248 | 40 | 30 | 47 | 77 | 0 | 36 | 9 | 275 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 17.76 | 80 | 17 | 0 | 0 |  | 524 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 199 | 17 | 0 | 0 | 50 | 0 | 0 | 0 | 24 | 50 | 50 | 0 | 52 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 17 | 18 | 180 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 |  | 4515.76 | 1716 | 6231.76 | 3448 | 524 | 1311 | 586 | 149 | 45 | 59 | 92 | 17.76 | 0 | 98.2
11:00 | 35 | 0 | 0 | 0 | 250 | 12 | 20 | 350 | 268 | 0 | 0 | 330 | 0 | 0 | 0 | 15 | 120 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 18 | 18 | 0 | 19 | 25 | 24 | 33 | 33 | 43 | 0 | 45 | 0 | 0 | 100 | 25 | 0 | 0 | 120 | 0 | 0 | 40 | 0 | 0 | 50 | 46 | 45 | 19 | 4 | 0 | 80 | 80 | 0 | 272 | 198 | 8 | 100 | 37 | 5 | 5 | 51 | 30 | 0 | 0 | 19 | 8 | 8 | 15 | 92 | 169 | 7 | 22 | 2.3 | 56 | 62 | 5 | 0 | 130 | 259 | 46 | 30 | 47 | 78 | 0 | 38 | 9 | 285 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 20 | 80 | 17 | 0 | 0 |  | 524 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 197 | 16 | 0 | 0 | 50 | 0 | 0 | 0 | 26 | 50 | 8 | 0 | 52 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 17 | 18 | 184 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 |  | 4650.3 | 1639 | 6289.3 | 3481 | 524 | 1361 | 554 | 149 | 45 | 61 | 92 | 22.3 | 0 | 98.13
12:00 | 35 | 0 | 0 | 0 | 250 | 12 | 20 | 362 | 266 | 0 | 0 | 330 | 0 | 0 | 0 | 15 | 130 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 18 | 18 | 17 | 19 | 25 | 24 | 33 | 33 | 38 | 0 | 45 | 0 | 0 | 100 | 25 | 0 | 0 | 120 | 0 | 0 | 40 | 0 | 0 | 50 | 46 | 45 | 20 | 6 | 0 | 80 | 80 | 0 | 272 | 205 | 8 | 100 | 37 | 5 | 5 | 51 | 30 | 0 | 0 | 19 | 8 | 8 | 15 | 92 | 169 | 7 | 22 | 2.5 | 56 | 62 | 5 | 0 | 130 | 256 | 50 | 30 | 44 | 77 | 0 | 39 | 9 | 310 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 20 | 80 | 17 | 0 | 0 |  | 522 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 194 | 18 | 0 | 0 | 50 | 0 | 0 | 0 | 26 | 50 | 8 | 0 | 52 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 17 | 18 | 192 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 |  | 4750.5 | 1694 | 6444.5 | 3601 | 522 | 1386 | 566 | 149 | 45 | 61 | 92 | 22.5 | 0 | 98.19
13:00 | 35 | 0 | 0 | 0 | 250 | 12 | 20 | 360 | 294 | 0 | 0 | 360 | 0 | 0 | 0 | 15 | 174 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 18 | 18 | 17 | 19 | 25 | 24 | 33 | 33 | 32 | 0 | 45 | 0 | 0 | 100 | 25 | 0 | 0 | 100 | 0 | 0 | 40 | 0 | 0 | 50 | 46 | 46 | 20 | 12 | 0 | 80 | 80 | 0 | 264 | 190 | 8 | 100 | 37 | 5 | 5 | 51 | 30 | 0 | 0 | 19 | 8 | 8 | 15 | 96 | 148 | 7 | 22 | 2.1 | 56 | 62 | 5 | 10 | 163 | 255 | 50 | 30 | 47 | 77 | 0 | 41 | 9 | 325 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 19.1 | 80 | 17 | 0 | 0 |  | 521 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 192 | 19 | 0 | 0 | 50 | 0 | 0 | 0 | 26 | 50 | 8 | 0 | 52 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 0 | 18 | 195 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 17 |  | 4817.2 | 1677 | 6494.2 | 3544 | 521 | 1513 | 561 | 149 | 45 | 44 | 96 | 21.2 | 0 | 98.19
14:00 | 35 | 0 | 0 | 0 | 250 | 12 | 20 | 350 | 299 | 0 | 0 | 360 | 0 | 0 | 0 | 15 | 158 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 18 | 18 | 17 | 19 | 25 | 18 | 33 | 33 | 42 | 0 | 43 | 0 | 0 | 100 | 25 | 0 | 0 | 100 | 0 | 0 | 40 | 0 | 0 | 50 | 46 | 46 | 20 | 10 | 0 | 80 | 80 | 0 | 253 | 185 | 8 | 100 | 40 | 5 | 5 | 51 | 30 | 0 | 0 | 19 | 8 | 8 | 15 | 94 | 148 | 7 | 22 | 1.7 | 56 | 62 | 5 | 10 | 163 | 260 | 50 | 30 | 47 | 78 | 0 | 40 | 9 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 16.2 | 70 | 17 | 0 | 0 |  | 522 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 191 | 19 | 0 | 0 | 80 | 0 | 0 | 0 | 26 | 50 | 50 | 0 | 52 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 184 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 |  | 4665.9 | 1681 | 6346.9 | 3411 | 522 | 1481 | 603 | 149 | 43 | 26 | 94 | 17.9 | 0 | 98.22
15:00 | 35 | 0 | 0 | 0 | 250 | 12 | 20 | 348 | 299 | 0 | 0 | 360 | 0 | 0 | 0 | 15 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 18 | 18 | 17 | 19 | 25 | 25 | 33 | 33 | 42 | 0 | 40 | 0 | 0 | 100 | 25 | 0 | 0 | 100 | 0 | 0 | 40 | 0 | 0 | 50 | 46 | 46 | 20 | 4 | 0 | 80 | 80 | 0 | 257 | 185 | 8 | 100 | 40 | 5 | 5 | 51 | 30 | 0 | 0 | 19 | 11 | 8 | 13 | 94 | 148 | 7 | 22 | 1.3 | 53 | 61 | 5 | 10 | 163 | 255 | 54 | 30 | 47 | 78 | 0 | 40 | 9 | 300 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 12.9 | 70 | 17 | 0 | 0 |  | 522 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 204 | 16 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 50 | 24 | 0 | 52 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 181 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 |  | 4635.2 | 1626 | 6261.2 | 3383 | 522 | 1482 | 577 | 149 | 40 | 0 | 94 | 14.2 | 0 | 98.22
16:00 | 35 | 0 | 0 | 0 | 250 | 12 | 20 | 360 | 296 | 0 | 0 | 360 | 0 | 0 | 0 | 15 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 1 | 18 | 18 | 17 | 19 | 25 | 25 | 33 | 33 | 42 | 0 | 42 | 0 | 0 | 100 | 25 | 0 | 0 | 100 | 0 | 0 | 50 | 0 | 0 | 50 | 46 | 46 | 20 | 5 | 0 | 80 | 80 | 0 | 283 | 202 | 8 | 100 | 40 | 5 | 5 | 25 | 10 | 0 | 0 | 19 | 8 | 8 | 20 | 92 | 148 | 7 | 22 | 0.6 | 56 | 61 | 5 | 10 | 130 | 256 | 58 | 10 | 47 | 77 | 0 | 7 | 9 | 310 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7.65 | 70 | 17 | 0 | 0 |  | 534 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 8 | 202 | 16 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 25 | 8 | 0 | 25 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 189 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 |  | 4582.25 | 1582 | 6164.25 | 3455 | 534 | 1358 | 520 | 149 | 42 | 6 | 92 | 8.25 | 0 | 98.22
17:00 | 35 | 0 | 0 | 0 | 240 | 12 | 20 | 360 | 295 | 0 | 0 | 330 | 0 | 0 | 10 | 15 | 120 | 0 | 80 | 0 | 0 | 5 | 0 | 0 | 25 | 0 | 6 | 18 | 18 | 17 | 19 | 25 | 25 | 33 | 33 | 42 | 0 | 42 | 0 | 0 | 100 | 25 | 0 | 0 | 100 | 0 | 0 | 50 | 0 | 0 | 53 | 72 | 46 | 20 | 11 | 0 | 80 | 80 | 0 | 253 | 184 | 8 | 100 | 40 | 5 | 5 | 25 | 10 | 0 | 0 | 19 | 8 | 8 | 20 | 94 | 150 | 21 | 22 | 0 | 56 | 62 | 5 | 10 | 100 | 260 | 49 | 10 | 47 | 78 | 0 | 7 | 9 | 300 | 0 | 11 | 0 | 12 | 0 | 0 | 7 | 0 | 0 | 1 | 80 | 20 | 2 | 0 |  | 551 | 0 | 200 | 0 | 18 | 0 | 0 | 0 | 24 | 0 | 8 | 194 | 18 | 24 | 0 | 100 | 0 | 0 | 0 | 0 | 25 | 8 | 0 | 37 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 0 | 18 | 194 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 53 |  | 4560 | 1695 | 6255 | 3363 | 551 | 1296 | 717 | 149 | 42 | 42 | 94 | 1 | 0 | 98.22
18:00 | 35 | 0 | 0 | 0 | 280 | 12 | 20 | 345 | 308 | 0 | 0 | 370 | 0 | 1 | 15 | 28 | 136 | 0 | 160 | 0 | 0 | 7 | 0 | 0 | 46 | 0 | 40 | 54 | 36 | 17 | 19 | 25 | 18 | 33 | 33 | 42 | 0 | 42 | 0 | 0 | 100 | 25 | 0 | 0 | 120 | 0 | 0 | 50 | 34 | 68 | 64 | 93 | 46 | 20 | 19 | 0 | 80 | 80 | 0 | 268 | 228 | 8 | 100 | 40 | 5 | 5 | 25 | 50 | 8 | 0 | 19 | 11 | 16 | 22 | 120 | 147 | 81 | 22 | 0 | 56 | 62 | 16 | 18 | 130 | 256 | 65 | 86 | 49 | 107 | 0 | 45 | 9 | 285 | 25 | 11 | 0 | 40 | 0 | 0 | 7 | 0 | 28 | 0 | 80 | 78 | 18 | 0 |  | 679 | 0 | 300 | 0 | 33 | 0 | 0 | 0 | 43 | 0 | 40 | 198 | 24 | 48 | 0 | 100 | 0 | 50 | 0 | 51 | 50 | 24 | 19 | 52 | 32 | 22 | 14 | 11 | 0 | 0 | 149 | 17 | 18 | 177 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 105 |  | 5567 | 2331 | 7898 | 3725 | 679 | 1595 | 1248 | 149 | 42 | 340 | 120 | 0 | 0 | 98.22
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 0 | 0 | 280 | 12 | 20 | 348 | 305 | 0 | 0 | 370 | 0 | 7 | 32 | 30 | 175 | 0 | 112 | 0 | 0 | 7 | 0 | 0 | 46 | 0 | 47 | 54 | 55 | 17 | 19 | 25 | 30 | 33 | 33 | 43 | 0 | 43 | 0 | 0 | 100 | 25 | 0 | 0 | 100 | 0 | 0 | 50 | 49 | 68 | 64 | 51 | 46 | 20 | 28 | 0 | 80 | 80 | 0 | 272 | 184 | 8 | 100 | 40 | 5 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 16 | 21 | 118 | 146 | 81 | 22 | 0 | 56 | 62 | 22 | 49 | 130 | 256 | 40 | 86 | 49 | 108 | 0 | 43 | 10 | 290 | 25 | 11 | 0 | 84 | 0 | 0 | 100 | 0 | 56 | 0 | 80 | 140 | 62 | 0 |  | 679 | 0 | 340 | 0 | 32 | 0 | 0 | 0 | 40 | 0 | 40 | 178 | 26 | 80 | 0 | 70 | 0 | 50 | 0 | 102 | 50 | 50 | 32 | 52 | 31 | 22 | 14 | 11 | 0 | 0 | 149 | 17 | 18 | 180 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 105 |  | 5882 | 2465 | 8347 | 3638 | 679 | 1727 | 1586 | 149 | 43 | 407 | 118 | 0 | 0 | 98.22
19:30 | 35 | 0 | 0 | 0 | 280 | 12 | 20 | 350 | 307 | 0 | 0 | 370 | 0 | 7 | 48 | 30 | 150 | 0 | 115 | 0 | 0 | 7 | 0 | 0 | 46 | 0 | 47 | 54 | 55 | 17 | 19 | 25 | 32 | 33 | 33 | 43 | 0 | 43 | 0 | 0 | 100 | 25 | 0 | 0 | 90 | 0 | 0 | 50 | 49 | 68 | 64 | 26 | 46 | 20 | 33 | 0 | 80 | 80 | 0 | 272 | 185 | 8 | 95 | 40 | 5 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 16 | 21 | 116 | 145 | 81 | 22 | 0 | 56 | 62 | 22 | 49 | 130 | 258 | 44 | 86 | 49 | 108 | 0 | 44 | 10 | 285 | 25 | 11 | 0 | 100 | 0 | 0 | 100 | 0 | 56 | 0 | 80 | 120 | 62 | 0 |  | 679 | 0 | 340 | 0 | 32 | 0 | 0 | 0 | 32 | 0 | 40 | 187 | 26 | 80 | 0 | 70 | 0 | 50 | 0 | 102 | 50 | 50 | 32 | 52 | 31 | 22 | 14 | 11 | 0 | 0 | 149 | 17 | 18 | 177 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 105 |  | 5843 | 2462 | 8305 | 3617 | 679 | 1729 | 1573 | 149 | 43 | 399 | 116 | 0 | 0 | 0
20:00 | 35 | 0 | 0 | 0 | 280 | 12 | 20 | 345 | 304 | 0 | 0 | 370 | 0 | 7 | 48 | 30 | 150 | 0 | 112 | 0 | 0 | 7 | 0 | 0 | 46 | 0 | 47 | 54 | 55 | 17 | 19 | 25 | 32 | 33 | 33 | 43 | 0 | 43 | 0 | 0 | 100 | 25 | 0 | 0 | 90 | 0 | 0 | 50 | 49 | 68 | 64 | 26 | 46 | 20 | 37 | 0 | 80 | 80 | 0 | 272 | 185 | 8 | 96 | 40 | 5 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 16 | 21 | 110 | 145 | 81 | 22 | 0 | 56 | 62 | 22 | 49 | 100 | 258 | 40 | 86 | 49 | 78 | 0 | 44 | 10 | 285 | 25 | 11 | 0 | 103 | 0 | 0 | 100 | 0 | 54 | 0 | 80 | 125 | 62 | 0 |  | 677 | 0 | 340 | 0 | 32 | 0 | 0 | 0 | 37 | 0 | 40 | 173 | 26 | 80 | 0 | 70 | 0 | 50 | 0 | 102 | 50 | 50 | 31 | 52 | 31 | 22 | 14 | 11 | 0 | 0 | 149 | 17 | 18 | 177 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 105 |  | 5773 | 2450 | 8223 | 3562 | 677 | 1700 | 1579 | 149 | 43 | 403 | 110 | 0 | 0 | 98.21
21:00 | 35 | 0 | 0 | 0 | 280 | 12 | 20 | 347 | 280 | 0 | 0 | 370 | 0 | 0 | 48 | 0 | 120 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 47 | 54 | 55 | 0 | 19 | 25 | 32 | 33 | 33 | 42 | 0 | 43 | 0 | 0 | 100 | 25 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 46 | 20 | 38 | 0 | 80 | 80 | 0 | 305 | 185 | 8 | 100 | 40 | 5 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 16 | 21 | 112 | 139 | 80 | 22 | 0 | 56 | 62 | 22 | 49 | 100 | 256 | 59 | 86 | 49 | 77 | 0 | 45 | 10 | 280 | 25 | 11 | 0 | 107 | 0 | 0 | 80 | 0 | 49 | 0 | 80 | 95 | 62 | 0 |  | 678 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 40 | 198 | 26 | 80 | 0 | 80 | 0 | 50 | 0 | 60 | 50 | 50 | 0 | 52 | 23 | 22 | 14 | 11 | 0 | 0 | 149 | 17 | 0 | 180 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 105 |  | 5494 | 2358 | 7852 | 3667 | 678 | 1673 | 1343 | 149 | 43 | 187 | 112 | 0 | 0 | 98.21
22:00 | 35 | 0 | 0 | 0 | 280 | 12 | 20 | 347 | 280 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 47 | 55 | 36 | 0 | 19 | 25 | 32 | 33 | 33 | 26 | 0 | 44 | 0 | 0 | 100 | 0 | 0 | 0 | 120 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 42 | 20 | 38 | 0 | 80 | 80 | 0 | 305 | 185 | 8 | 100 | 40 | 5 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 16 | 21 | 100 | 139 | 81 | 22 | 0 | 56 | 62 | 22 | 49 | 100 | 256 | 52 | 86 | 49 | 78 | 0 | 45 | 10 | 290 | 25 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 80 | 80 | 0 | 0 |  | 678 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 40 | 192 | 23 | 0 | 0 | 80 | 0 | 0 | 0 | 15 | 50 | 0 | 0 | 52 | 23 | 22 | 14 | 11 | 0 | 0 | 149 | 0 | 0 | 180 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 0 |  | 5097 | 1996 | 7093 | 3645 | 678 | 1680 | 728 | 149 | 44 | 69 | 100 | 0 | 0 | 98.16
23:00 | 35 | 0 | 0 | 0 | 280 | 12 | 20 | 345 | 280 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 120 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 33 | 33 | 0 | 0 | 44 | 0 | 0 | 100 | 0 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 80 | 80 | 0 | 316 | 196 | 8 | 100 | 40 | 5 | 5 | 5 | 85 | 0 | 0 | 19 | 11 | 0 | 21 | 94 | 140 | 7 | 22 | 0 | 56 | 62 | 22 | 49 | 100 | 256 | 69 | 86 | 49 | 78 | 0 | 45 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 60 | 0 | 0 | 0 |  | 677 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 24 | 200 | 23 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 51 | 0 | 22 | 14 | 8 | 0 | 0 | 149 | 0 | 0 | 180 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 |  | 4584 | 1856 | 6440 | 3657 | 677 | 1592 | 223 | 149 | 44 | 4 | 94 | 0 | 0 | 98.16
24:00 | 35 | 0 | 0 | 0 | 280 | 12 | 20 | 358 | 280 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 120 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 33 | 33 | 0 | 0 | 45 | 0 | 0 | 100 | 0 | 0 | 0 | 120 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 19 | 41 | 0 | 80 | 80 | 0 | 334 | 202 | 8 | 0 | 40 | 5 | 5 | 5 | 85 | 0 | 0 | 19 | 11 | 0 | 21 | 84 | 140 | 0 | 22 | 0 | 56 | 62 | 22 | 49 | 100 | 258 | 69 | 86 | 49 | 79 | 0 | 45 | 0 | 325 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 60 | 0 | 0 | 0 |  | 281 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 20 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 52 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 193 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 |  | 4542 | 1446 | 5988 | 3612 | 281 | 1623 | 194 | 149 | 45 | 0 | 84 | 0 | 0 | 98.16
KWH | 730000 | 0 | 0 | 0 | 6605554 | 301090 | 601248 | 8560900 | 6991000 | 0 | 0 | 8541375 | 0 | 18240 | 188376 | 242160 | 3223765 | 0 | 2706000 | 0 | 0 | 50688 | 0 | 0 | 288000 | 0 | 246240 | 427680 | 380262 | 167266 | 277128 | 600000 | 668880 | 806900 | 820800 | 579660 | 0 | 1036800 | 0 | 0 | 2700000 | 323820 | 0 | 0 | 2591126 | 0 | 0 | 705600 | 125496 | 188397 | 570960 | 577920 | 603840 | 322656 | 479520 | 0 | 2097740 | 2103780 | 0 | 6989500 | 4652000 | 200727 | 2254950 | 728784 | 168000 | 120000 | 767811 | 807640 | 7144 | 0 | 304020 | 142560 | 158200 | 455090 | 2150400 | 3830120 | 504960 | 346500 | 12250 | 1305000 | 1480720 | 234000 | 362000 | 3176885 | 5857000 | 1140000 | 874560 | 801000 | 1995590 | 0 | 610480 | 129780 | 7743250 | 125856 | 151536 | 0 | 393930 | 0 | 0 | 544800 | 0 | 205920 | 132570 | 1194240 | 720960 | 274320 | 0 |  | 11531636 | 0 | 7734240 | 0 | 139200 | 0 | 0 | 0 | 208800 | 0 | 388875 | 4787089 | 459200 | 319872 | 0 | 1538000 | 0 | 190920 | 0 | 468596 | 729860 | 404464 | 83960 | 942720 | 144894 | 473520 | 339516 | 163080 | 0 | 0 | 3647900 | 145000 | 160000 | 4649536 | 0 | 0 | 0 | 844326 | 0 | 0 | 0 | 0 | 654240 |  | 112505920 | 41149444 | 153655364 | 85604600 | 11531636 | 35026928 | 12789073 | 3647900 | 1036800 | 1723207 | 2150400 | 144820 | 0
Fuel Cost | 627800 | 0 | 0 | 0 | 4227554.56 | 243882.9 | 565173.12 | 5222149 | 4264510 | 0 | 0 | 5722721.25 | 0 | 114547.2 | 1258351.68 | 1479597.6 | 2095447.25 | 0 | 3003660 | 0 | 0 | 334033.92 | 0 | 0 | 1725120 | 0 | 1642420.8 | 3049358.4 | 2376637.5 | 1048757.82 | 207846 | 450000 | 0 | 0 | 0 | 5483583.6 | 0 | 0 | 0 | 0 | 2970000 | 3066575.4 | 0 | 0 | 2979794.9 | 0 | 0 | 6202224 | 1351591.92 | 1833102.81 | 3534242.4 | 3733363.2 | 3949113.6 | 274257.6 | 0 | 0 | 1908943.4 | 1914439.8 | 0 | 4822755 | 3256400 | 138501.63 | 2164752 | 488285.28 | 144480 | 110400 | 629605.02 | 767258 | 77440.96 | 0 | 234095.4 | 106920 | 121814 | 341317.5 | 14708736 | 2872590 | 4640582.4 | 266805 | 0 | 1357200 | 1539948.8 | 224640 | 325800 | 2477970.3 | 4099900 | 1299600 | 935779.2 | 881100 | 2274972.6 | 0 | 567746.4 | 120695.4 | 4955680 | 94392 | 115167.36 | 0 | 2859931.8 | 0 | 0 | 3895320 | 0 | 0 | 0 | 0 | 6733766.4 | 2562148.8 | 0 |  | 58811343.6 | 0 | 5181940.8 | 0 | 1153968 | 0 | 0 | 0 | 2351088 | 0 | 3064335 | 3303091.41 | 454608 | 2367052.8 | 0 | 1614900 | 0 | 2186034 | 0 | 4198620.16 | 6313289 | 3599729.6 | 894174 | 9351782.4 | 1705402.38 | 520872 | 319145.04 | 123451.56 | 0 | 0 | 14080894 | 4673350 | 4283200 | 3161684.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 152075298.88 | 133713956.23 | 285789255.11 | 64723875.7 | 58811343.6 | 24370568.26 | 85539833.32 | 14080894 | 0 | 23554004.23 | 14708736 | 0 | 0
Yesterday Day Peak | 35 | 0 | 0 | 0 | 250 | 12 | 20 | 362 | 266 | 0 | 0 | 330 | 0 | 0 | 0 | 15 | 130 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 18 | 18 | 17 | 19 | 25 | 24 | 33 | 33 | 38 | 0 | 45 | 0 | 0 | 100 | 25 | 0 | 0 | 120 | 0 | 0 | 40 | 0 | 0 | 50 | 46 | 45 | 20 | 6 | 0 | 80 | 80 | 0 | 272 | 205 | 8 | 100 | 37 | 5 | 5 | 51 | 30 | 0 | 0 | 19 | 8 | 8 | 15 | 92 | 169 | 7 | 22 | 2.5 | 56 | 62 | 5 | 0 | 130 | 256 | 50 | 30 | 44 | 77 | 0 | 39 | 9 | 310 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 20 | 80 | 17 | 0 | 0 |  | 522 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 194 | 18 | 0 | 0 | 50 | 0 | 0 | 0 | 26 | 50 | 8 | 0 | 52 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 17 | 18 | 192 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 |  | 6444.5 | DayPeak
Yesterday Evening Peak | 35 | 0 | 0 | 0 | 280 | 12 | 20 | 348 | 305 | 0 | 0 | 370 | 0 | 7 | 32 | 30 | 175 | 0 | 112 | 0 | 0 | 7 | 0 | 0 | 46 | 0 | 47 | 54 | 55 | 17 | 19 | 25 | 30 | 33 | 33 | 43 | 0 | 43 | 0 | 0 | 100 | 25 | 0 | 0 | 100 | 0 | 0 | 50 | 49 | 68 | 64 | 51 | 46 | 20 | 28 | 0 | 80 | 80 | 0 | 272 | 184 | 8 | 100 | 40 | 5 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 16 | 21 | 118 | 146 | 81 | 22 | 0 | 56 | 62 | 22 | 49 | 130 | 256 | 40 | 86 | 49 | 108 | 0 | 43 | 10 | 290 | 25 | 11 | 0 | 84 | 0 | 0 | 100 | 0 | 56 | 0 | 80 | 140 | 62 | 0 |  | 679 | 0 | 340 | 0 | 32 | 0 | 0 | 0 | 40 | 0 | 40 | 178 | 26 | 80 | 0 | 70 | 0 | 50 | 0 | 102 | 50 | 50 | 32 | 52 | 31 | 22 | 14 | 11 | 0 | 0 | 149 | 17 | 18 | 180 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 105 |  | 8347 | EvPeak
Forecast for Evening | 35 | 0 | 0 | 0 | 380 | 100 | 40 | 412 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 170 | 0 | 130 | 100 | 100 | 102 | 149 | 100 | 46 | 0 | 47 | 54 | 55 | 36 | 22 | 25 | 33 | 33 | 33 | 43 | 0 | 45 | 30 | 0 | 150 | 25 | 0 | 0 | 140 | 0 | 0 | 50 | 70 | 68 | 90 | 100 | 50 | 22 | 20 | 0 | 100 | 100 | 0 | 360 | 210 | 16 | 100 | 40 | 5 | 5 | 51 | 85 | 40 | 52 | 22 | 11 | 33 | 22 | 112 | 200 | 80 | 22 | 0 | 56 | 63 | 51 | 21 | 163 | 280 | 66 | 86 | 50 | 140 | 20 | 50 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 130 | 0 | 100 | 180 | 150 | 0 |  | 678 | 46 | 410 | 0 | 115 | 0 | 0 | 0 | 40 | 80 | 40 | 194 | 25 | 110 | 30 | 80 | 0 | 50 | 40 | 100 | 50 | 50 | 50 | 52 | 35 | 22 | 14 | 11 | 0 | 0 | 149 | 17 | 15 | 200 | 0 | 0 | 0 | 95 | 100 | 0 | 0 | 0 | 105
Forecast for Day | 35 | 0 | 0 | 0 | 380 | 100 | 40 | 412 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 170 | 0 | 130 | 100 | 100 | 102 | 149 | 100 | 8 | 0 | 47 | 54 | 55 | 36 | 22 | 25 | 33 | 33 | 33 | 43 | 0 | 45 | 30 | 0 | 150 | 25 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 0 | 90 | 90 | 50 | 22 | 20 | 0 | 100 | 100 | 0 | 360 | 210 | 8 | 100 | 40 | 5 | 5 | 51 | 85 | 0 | 52 | 22 | 11 | 0 | 22 | 84 | 200 | 80 | 22 | 2 | 56 | 63 | 51 | 21 | 163 | 270 | 66 | 86 | 50 | 78 | 20 | 50 | 0 | 341 | 0 | 11 | 100 | 150 | 300 | 0 | 100 | 0 | 130 | 20 | 100 | 180 | 150 | 0 |  | 540 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 194 | 25 | 110 | 0 | 80 | 0 | 0 | 0 | 90 | 50 | 50 | 50 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 149 |  | 0 | 200 | 0 | 0 | 0 | 95 | 100 | 0 | 0 | 0 | 105
Generation at 08:00(Today) | 35 | 0 | 0 | 0 | 320 | 52 | 0 | 388 | 367 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 170 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 33 | 33 | 0 | 0 | 42 | 0 | 0 | 120 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 20 | 0 | 80 | 80 | 0 | 342 | 208 | 8 | 0 | 37 | 5 | 5 | 5 | 6 | 0 | 0 | 19 | 11 | 0 | 18 | 72 | 146 | 0 | 0 | 0.4 | 56 | 62 | 5 | 21 | 163 | 256 | 69 | 5 | 5 | 78 | 0 | 6 | 0 | 335 | 0 | 2 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7.6 | 35 | 0 | 0 | 0 | 0 | 540 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 203 | 18 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 43 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 200 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 17 | 0
199
| Minimum Generation |  | 4796 | 5:00
| Highest Generation |  | 8347 | 19:00
| Day Peak Generation |  | 6444.5 | 12:00
| Evening Peak Generation |  | 8347 | 19:00
| HVDC Max Flow |  | 679 | 18:00
| HVDC EvPeak Flow |  | 679 | 19:00
| Load factor L.F |  | 76.7%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-01-07
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2019-01-06 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6444.5 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 4973 | MW
Evening Peak Generation : |  | 8347 | MW Hour : | 19:00 | Available Max Generation : |  | 12142 | MW
E.P. Demand (at gen end) : |  | 8347 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8500 | MW
Maximum Generation : |  | 8347 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3642 | MW
Total Gen. (MKWH) : |  | 153.6554 | System Load Factor : | 76.7% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -510 | MW at | 6:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-01-07
Actual : | 98.09 | Ft.(MSL) , | Rule curve : | 101.86 | Ft.( MSL )
Gas Consumed : | Total = | 1032.48 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 89094443.96
|  | Coal : | 14080894 | Oil : | 109093837.55 | Total : | 212269175.51
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 2992.0267 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1010.5242 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 904.1613 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 816.5476 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 738.144 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 595.6386 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 341.9702 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 153.5969 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 459.3434 |  |  | 0 | 0%
Total | 0 |  | 8011.9529 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 8) Raozan # 01
| Nil |  |  | 2) Khulna ST 110 MW |  | 9) Sirajganj Unit-2,3,4
|  |  |  | 3) Ghorasal Unit-1,5 |  | 10) Ashuganj #3
|  |  |  | 4) Tongi GT |  | 11) Ashuganj North 360MW
5) Haripur GT-1,2
6) Siddhirganj ST 210 MW
7) Bhagabari 71 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Bashundhara 132/33 kV T3 transformer was under shut down from 08:55 to 15:24 for A/M.
b) Hathazari-BSRM 230 kV Ckt was under shut down from 09:11 to 20:20 for A/M.
c) Khulshi-Madunaghat 132 kV Ckt-1 was under shut down from 08:42 to 16:30 for A/M.
d) Kallyanpur 132/33 kV T3 transformer was under shut down from 09:12 to 16:15 for A/M.
e) Kabirpur-Kaliakoir 132 kV Ckt-1 was under shut down from 10:09 to 14:59 for A/M.
f) Ghorasal-Ishurdi 230 kV Ckt-2 was under shut down from 08:13 to 16:52 for A/M.
g) Cumilla(N) 230/132 kV T01 transformer was under shut down from 09:11 to 15:23 for A/M.
h) Kishoreganj-Mymensingh 132 kV Ckt-2 & Kishoreganj 132 kV bus-A were under shut down
from 09:42 to 15:43 for A/M.
i) Bibiyana-Shahjibazar 230 kV Ckt-2 was under shut down from 08:14 to 17:27 for A/M.
j) Madunaghat-TK Chemical 132 kV Ckt was under shut down from 11:26 to 12:30 for C/M.
k) Maniknagar-Matuail 132 kV Ckt was under shut down from 09:05 16:22 for C/M.
l) Haripur-Siddhirganj 230 kV Ckt-1 was under shut down from 09:49 to 15:30 for A/M.
m) Cumilla(S) 132/33 kV T4 transformer was shut down at 09:04 for D/W.
n) Baghabari 230/132 kV TR transformer was under shut down from 08:53 to 11:17 for A/M.
o) Goalpara-Bagerhat 132 kV Ckt-1 was under shut down from 08:04 to 18:15 for A/M.
p) Baghabari-Sirajganj 230 kV Ckt-1 was switched on at 11:19.
q) Baghabari-Sirajganj 230 kV Ckt-2 was shut down at 12:04 for D/W.
r) Barapukuria P/S-Barapukuria S/S 230 kV Ckt-2 was under shut down from 08:50 to 15:38 for D/W.
s) Bheramara HVDC-Bheramara S/S 230 kV Ckt-1 was under shut down from 08:08 to 20:25 for A/M.
t) Chandpur 150 MW GT was shut down at 23:14 for maintenance.
u) Hasnabad 230/132 kV T3 transformer was shut down at 07:35 (07/01/2019) for A/M.
v) Feni 132/33 kV T1 transformer was shut down at 05:48(07/01/2019) for D/W.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-01-06 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 35 | 730000 | #2 under maint.
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | On test
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | On test
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 280 | 6605554 | Frequency control
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 20 | 601248 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 12 | 301090 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 348 | 8560900 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 0 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 305 | 6991000 | Low demand
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 370 | 8541375 | Frequency control
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 7 | 18240 | Low demand
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Reserve
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 32 | 188376 | Low demand
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 30 | 242160 | Low demand
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 277128
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 112 | 2706000 | FGMO
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 175 | 3223765 | Low demand
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 7 | 50688 | Low demand
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 47 | 246240
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 427680
25 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 55 | 380262
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 17 | 167266 | Low demand
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 46 | 288000
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1268880 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 806900
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 820800
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 43 | 579660 | Engine problem
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 84 | 393930 | Low demand
35 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
38 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 56 | 205920 | Low demand
| Dhaka area Total |  |  |  | 5798 | 2275 | 44623062
39 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 100 | 2700000 | Gas shortage
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 323820
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 132570
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 46 | 603840 | Engine problem
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 43 | 1036800 | Low water lavel
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 100 | 2591126 | FGMO
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 50 | 705600
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 49 | 125496 | Low demand
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 68 | 188397
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 64 | 570960 | Low demand
| Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 80 | 1194240 | Engine problem
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 322656
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 28 | 479520
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 51 | 577920 | Low demand
| Chattogram area Total |  |  |  | 1681 | 724 | 11552945
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 2097740 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 2103780 | Gas shortage
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 184 | 4652000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Reserve
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 272 | 6989500 | FGMO
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 40 | 728784 | Engine problem
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 5 | 168000 | Gas shortage
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 51 | 767811
| Midland 150MW |  | IPP | 23*7.015 | 150 | 62 | 274320 | Low demand
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 807640
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 7144 | Reserve
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2254950 | ST Under maint.
| Chandpur Desh 200MW |  | IPP | 0 | 200 | 140 | 720960 | Low demand
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 19 | 304020
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 142560
** | Tripura |  | Imported power | 0 | 160 | 118 | 2150400
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 16 | 158200 | Engine problem
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
68 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 455090
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1297 | 25103626
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 146 | 3830120 | Gas shortage
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 346500
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 81 | 504960 | Engine problem
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 12250
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 100 | 544800 | Low demand
| Mymensingh Area Total |  |  |  | 522 | 349 | 5238630
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 56 | 1305000
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 62 | 1480720
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 130 | 3176885 | Frequency control
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 256 | 5857000 | FGMO
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 22 | 234000 | Low demand
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 49 | 362000
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 151536
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 40 | 1140000 | FGMO
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 874560
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 49 | 801000
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 108 | 1995590
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 43 | 610480 | Engine problem
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 25 | 125856
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 290 | 7743250 | FGMO
| Bibiyana-3 285MW |  | PDB | 285 MW | 0 | 0 | 0 | On test
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 129780
| Sylhet Area Total |  |  |  | 1549 | 1237 | 25987657
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 679 | 11531636
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 32 | 139200 | Low demand
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 40 | 208800
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 0 | 0 | Low demand
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 340 | 7734240 | Frequency control
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 388875
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
| Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 105 | 654240
| Khulna Area Total |  |  |  | 2209 | 1236 | 20656991
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 80 | 319872 | Low demand
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 26 | 459200 | Engine problem
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 178 | 4787089 | FGMO
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 97 | 844326
| Barisal Area Total |  |  |  | 462 | 381 | 6410487
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 70 | 1538000 | Gas shortage
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 50 | 190920
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 729860
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 404464
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 32 | 83960 | Reserve
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 180 | 4649536 | Gas shortage
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 141 | 0 | 0 | Gas shortage
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282 | 282 | 0 | 0 | Gas shortage
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 31 | 144894
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 473520
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 14 | 339516 | Engine problem
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 163080
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 52 | 942720
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 102 | 468596
| Rajshahi Area Total |  |  |  | 1546 | 664 | 10129066
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 149 | 3647900
122 | Rangpur GT |  | PDB | 1*20 | 20 | 17 | 145000
123 | Saidpur GT |  | PDB | 1*20 | 20 | 18 | 160000
| Rangpur Area Total |  |  |  | 484 | 184 | 3952900
| Total |  |  |  | 17142 | 8347 | 153655364
| Eastern Grid Total |  |  |  | 12441 | 5882 | 112505920
| Western Grid Total |  |  |  | 4701 | 2465 | 41149444
| National Grid Total |  |  |  | 17142 | 8347 | 153655364
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2019-01-06 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 5232 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2622 | MW
i) Dhaka area |  |  | 2812 | MW | i) Khulna area |  |  | 999 | MW
ii) Chittagong area |  |  | 816 | MW | ii) Rajshahi area |  |  | 861 | MW
iii) Comilla area |  |  | 694 | MW | iii) Barisal area |  |  | 203 | MW
iv) Mymensingh area |  |  | 599 | MW | iv) Rangpur area |  |  | 559 | MW
v) Sylhet area |  |  | 311 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 7854 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 90 | 1800 | Netrokona | 67 | 1830 | Goalpara | 26 | 1300
Munsiganj | 72 | 1930 | Jamalpur | 87 | 1830 | Central s/s | 60 | 1900
Sonargaon | 36 | 1900 | Sherpur | 74 | 1830 | Noapara | 74 | 1830
Shyampur | 120 | 100 | Srimongal | 22 | 1800 | Jessore | 112 | 1830
Bhulta | 147 | 1930 | Shahjibazar | 80 | 1800 | Jhenida | 80 | 1830
Madanganj | 43 | 1300 | Fenchuganj | 28 | 1800 | Bottail | 94 | 1830
Shitalakhya | 87 | 1000 | Kulawara | 25 | 1830 | G.K Project | 34 | 1830
Rahim steel | 4 | 700 | Sylhet | 89 | 1900 | Faridpur | 120 | 1830
Matuail | 74 | 1000 | Chatak | 20 | 1800 | Madaripur | 90 | 1930
Ghorasal | 61 | 1830 | Sunamganj | 24 | 1830 | Gopalganj | 60 | 1830
Narsingdi | 99 | 1930 | Biani Bazar | 28 | 1830 | Bagerhat | 63 | 1830
Haripur (SBU) | 73 | 1900 | Comilla (S) | 120 | 1800 | Mongla | 34 | 1000
Ullon | 53 | 1800 | Comilla(N) | 76 | 1900 | Satkhira | 68 | 1830
Hasnabad | 132 | 1900 | Chandpur | 74 | 1930 | Gallamari | 28 | 1300
Magbazar | 88 | 1300 | Feni | 88 | 1800 | Magura | 34 | 1800
Maniknagar | 76 | 1300 | Chowmuhani | 122 | 1830 | Chuadanga | 58 | 1830
Bangabhaban | 15 | 1300 | Ashuganj | 38 | 1900 | Barisal | 88 | 1930
Narinda | 64 | 1100 | Daudkandi | 82 | 1830 | Patuakhali | 62 | 1900
Dhanmondi | 75 | 1300 | B.Baria | 82 | 2000 | Bhandaria | 38 | 1930
Lalbag | 78 | 1300 | Ramganj | 24 | 1830 | Ishurdi | 40 | 1830
Madartek | 34 | 2000 | Madunaghat | 47.5 | 1800 | Ruppur Paromanobik | 1 | 100
Mirpur | 74 | 1800 | Hathazari | 69 | 1900 | Natore | 90 | 1830
Kalyanpur | 63 | 1900 | Khulshi | 126 | 1700 | Bogra | 172 | 1900
Gulshan | 78 | 2000 | Halishahar | 86 | 1800 | Noagaon | 94 | 1830
Uttara | 34 | 1800 | Baraulia | 154 | 100 | Rajshahi | 97 | 1900
Uttara(New) | 4 | 800 | Sikalbaha | 29 | 1800 | C.Nawabganj | 58 | 1200
Kamrangirchar | 53 | 1800 | Dohazari | 64 | 1800 | Amnura | 25 | 1830
Savar | 102 | 1800 | Cox'sbazar | 62 | 1900 | Pabna | 74 | 1900
Bhasantec | 90 | 1800 | Chandraghona | 20 | 1830 | Shahjadpur | 62 | 1800
Agargaon | 33 | 1800 | Kaptai | 4 | 1830 | Serajganj | 68 | 1900
Satmosjid | 60 | 1930 | A. Khaer Stl. | 16 | 1600 | Niyamatpur | 58 | 1930
Tongi | 124 | 1100 | Bakulia | 74 | 1800 | Joypurhat | 36 | 1830
Kabirpur | 127 | 1800 | Julda | 17 | 900 | Rangpur | 97 | 1830
Basundhara | 82 | 1900 | TK chemical | 0.6 | 100 | Lalmonirhat | 75 | 1830
Manikganj | 58 | 1900 | Modern Steel | 14 | 600 | Saidpur | 98 | 1830
Joydevpur | 191 | 1800 | Shahmirpur | 21.5 | 1800 | Purbasadipur | 80 | 1900
New Tongi | 81 | 1600 | Khagrachhari | 15 | 1830 | Thakurgaon | 58 | 1830
Korda | 188 | 1900 | Matarbari | 19.5 | 1830 | Palashbari | 82 | 1900
Dhamrai | 26 | 1830 | Baroiar Hat | 18 | 1800 | Barapukuria | 41 | 1930
Tangail | 129 | 1800 | Rangamati | 8 | 1800 | Panchagar | 34 | 1830
Mymensing | 183 | 1830 | Abul Khair 230 | 180 | 1600
Kishorganj | 70 | 1900 | BSRM | 100 | 100
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-01-06
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 407 | 2:00 | 400 | 19:30 | Kaliakoir | 400 | 2:00 | 389 | 12:00
Bheramara | 406 | 3:00 | 397 | 17:00 | Bhulta | 405 | 3:00 | 394 | 12:00
Ashuganj(N) | 403 | 5:00 | 394 | 13:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 238 | 1:00 | 238 | 1:00 | Hathazari | 224 | 19:30 | 217 | 8:00
Ishurdi | 240 | 4:00 | 230 | 13:00 | Megnaghat | 236 | 3:00 | 232 | 9:00
Ashuganj | 241 | 21:00 | 236 | 12:00 | Fenchuganj | 245 | 3:00 | 239 | 9:00
Serajganj | 235 | 4:00 | 228 | 8:00 | Siddhirganj | 236 | 3:00 | 230 | 10:00
Baghabari | 231 | 4:00 | 222 | 8:00 | Maniknagar | 234 | 4:00 | 228 | 15:00
Barapukuria | 237 | 3:00 | 225 | 18:00 | Old Airport | 236 | 3:00 | 228 | 12:00
Bogra | 234 | 5:00 | 223 | 18:30 | Barisal | 234 | 4:00 | 223 | 13:00
Khulna South | 241 | 3:00 | 203 | 19:00 | AKSML | 227 | 19:30 | 217 | 6:00
Rampura | 230 | 3:00 | 228 | 9:00 | BSRM | 233 | 19:00 | 21 | 6:00
Haripur | 232 | 3:00 | 229 | 13:00 | Bibiyana | 242 | 3:00 | 237 | 18:00
Hasnabad | 235 | 24:00 | 230 | 9:00 | Bhulta | 234 | 2:00 | 228 | 10:00
Aminbazar | 236 | 1:00 | 230 | 12:00 | Ashuganj (S) | 241 | 2:00 | 236 | 12:00
Tongi | 233 | 1:00 | 222 | 11:00 | Kaliakoir | 238 | 2:00 | 230 | 12:00
Comilla (N) | 239 | 20:00 | 236 | 3:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 137 | 2000 | 134 | 900 | Ramganj | 136 | 2100 | 132 | 700
Munsiganj | 139 | 1900 | 133 | 1200 | Madanhat | 137 | 1800 | 129 | 300
Megnaghat | 135 | 1830 | 132 | 1100 | Hathazari | 133 | 1000 | 129 | 700
Shyampur | 134 | 1930 | 128 | 1200 | Khulshi | 134 | 1930 | 125 | 800
Bhulta | 136 | 1400 | 132 | 1200 | Halishahar | 138 | 1830 | 127 | 600
Madanganj | 138 | 300 | 131 | 1100 | Baraulia | 135 | 2000 | 127 | 300
Shitalakhya | 140 | 100 | 135 | 1100 | Sikalbaha | 135 | 1830 | 126 | 300
Rahim steal | 137 | 100 | 134 | 1200 | Dohazari | 136 | 1930 | 128 | 300
Matuail | 137 | 1930 | 133 | 1100 | Cox'sbazar | 132 | 1930 | 123 | 400
Ghorasal | 140 | 100 | 140 | 200 | Chandraghona | 136 | 1830 | 129 | 300
Narsinghdi | 139 | 1400 | 134 | 800 | Kaptai | 136 | 2000 | 130 | 300
Haripur (SBU) | 137 | 1830 | 132 | 700 | A. Khaer Stl. | 134 | 2000 | 126 | 700
Ullon | 134 | 600 | 129 | 1200 | Bakulia | 134 | 1830 | 125 | 800
Hasnabad | 138 | 600 | 134 | 1500 | Julda | 135 | 1800 | 126 | 300
Magbazar | 137 | 600 | 129 | 1500 | TK Chemical | 138 | 1900 | 129 | 400
Maniknagar | 136 | 600 | 133 | 1200 | Modern Steel | 134 | 1930 | 126 | 300
Bangabhaban | 137 | 500 | 132 | 1200 | Shahmirpur | 134 | 1900 | 125 | 300
Narinda | 133 | 600 | 128 | 1300 | Khagrachhari | 135 | 1830 | 128 | 100
Dhanmondi | 134 | 600 | 129 | 1200 | Matarbari | 131 | 1830 | 125 | 600
Lalbag | 137 | 500 | 132 | 1200 | Baroiar Hat | 134 | 1800 | 132 | 300
Madartek | 133 | 600 | 128 | 1300 | Rangamati | 135 | 1830 | 128 | 100
Mirpur | 136 | 500 | 130 | 1200 | Goalpara | 136 | 200 | 127 | 700
Kalyanpur | 139 | 200 | 133 | 1300 | Central s/s | 138 | 500 | 126 | 1300
Gulshan | 133 | 400 | 128 | 1200 | Noapara | 136 | 400 | 124 | 1300
Uttara | 136 | 200 | 130 | 1200 | Jessore | 132 | 300 | 122 | 700
Uttara(New) | 134 | 200 | 130 | 1200 | Jhenida | 136 | 300 | 119 | 1300
Kamrangirchar | 136 | 400 | 132 | 600 | Bottail | 140 | 300 | 133 | 1830
Savar | 134 | 100 | 130 | 1000 | G.K.Project | 142 | 200 | 138 | 800
Bhasantec | 137 | 200 | 131 | 1200 | Faridpur | 136 | 600 | 130 | 800
Agargaon | 138 | 500 | 132 | 1200 | Madaripur | 135 | 600 | 128 | 1800
Satmosjid | 137 | 300 | 132 | 1200 | Gopalganj | 135 | 600 | 123 | 1800
Tongi | 138 | 100 | 131 | 1300 | Bagerhat | 135 | 100 | 123 | 1300
Kabirpur | 136 | 500 | 132 | 1800 | Mongla | 133 | 1700 | 124 | 1200
Basundhara | 130 | 400 | 124 | 1300 | Satkhira | 137 | 400 | 125 | 1300
Manikganj | 141 | 400 | 133 | 1100 | Gallamari | 137 | 1700 | 126 | 1300
Joydevpur | 140 | 2000 | 135 | 1200 | Magura | 135 | 200 | 126 | 1800
New Tongi | 137 | 100 | 130 | 1200 | Chuadanga | 134 | 100 | 122 | 1800
Kodda | 140 | 2000 | 136 | 1200 | Barisal | 136 | 300 | 129 | 1200
Dhamrai | 137 | 400 | 132 | 1800 | Patuakhali | 135 | 500 | 129 | 1300
Tangail | 139 | 600 | 135 | 800 | Bhandaria | 135 | 300 | 125 | 1300
Mymensing | 137 | 400 | 132 | 1300 | Ishurdi | 140 | 100 | 135 | 800
Kishorganj | 137 | 300 | 134 | 1800 | Ruppur Paromanobik | 141 | 100 | 136 | 1200
Netrokona | 136 | 100 | 130 | 1800 | Natore | 137 | 1400 | 128 | 800
Jamalpur | 138 | 1900 | 128 | 1200 | Bogra | 134 | 200 | 122 | 800
Sherpur | 137 | 1930 | 127 | 2300 | Noagaon | 131 | 300 | 120 | 800
Srimongal | 142 | 2100 | 139 | 1100 | Rajshahi | 136 | 1400 | 130 | 1200
Shahjibazar | 140 | 200 | 139 | 100 | C.Nawabganj | 135 | 1400 | 123 | 800
Fenchuganj | 139 | 200 | 138 | 100 | Amnura | 137 | 1930 | 125 | 800
Khulawara | 138 | 100 | 137 | 100 | Pabna | 136 | 200 | 130 | 800
Sylhet | 138 | 2100 | 136 | 800 | Shahjadpur | 143 | 100 | 137 | 1800
Chatak | 138 | 300 | 136 | 1600 | Serajganj | 138 | 200 | 127 | 900
Sunamganj | 137 | 200 | 135 | 1100 | Niyamatpur | 131 | 400 | 117 | 1100
Biani Bazar | 138 | 200 | 135 | 1800 | Joypurhat | 135 | 200 | 119 | 1100
Cumilla(s) | 130 | 700 | 128 | 1800 | Rangpur | 134 | 300 | 117 | 1830
Cumilla(n) | 141 | 1830 | 139 | 700 | Lalmonirhat | 131 | 600 | 110 | 1830
Chandpur | 143 | 1900 | 136 | 1300 | Saidpur | 135 | 500 | 116 | 1830
Feni | 137 | 2100 | 132 | 800 | Purbasadipur | 132 | 100 | 113 | 1830
Chowmuhani | 135 | 1800 | 131 | 1300 | Thakurgaon | 130 | 600 | 103 | 1830
Ashuganj | 142 | 700 | 140 | 1700 | Palashbari | 136 | 400 | 118 | 1800
Daudkandi | 138 | 2000 | 135 | 1000 | Barapukuria | 137 | 300 | 125 | 1830
B.Baria | 141 | 2100 | 138 | 100 | Panchagar | 129 | 500 | 100 | 1830

## L-Curve
Date | 2019-01-06
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 440 | 4542 | 1446 | 5988 |  |  |  | QF-LDC-12
0:30 | 390 | 4316 | 1442 | 5758 | Date: | 2019-01-06
1:00 | 340 | 4090 | 1438 | 5528
1:30 | 400 | 4044.5 | 1327 | 5371.5
2:00 | 460 | 3999 | 1216 | 5215
2:30 | 455 | 3937.5 | 1175 | 5112.5 | [5 empty] | Gen. at Eve. Peak | 8347 | 8347 MW (19:00 )
3:00 | 450 | 3876 | 1134 | 5010 | [6 empty] | 19:00
3:30 | 445 | 3838 | 1124.5 | 4962.5 | [5 empty] | Gen. at Day Peak | 6444.5 | 6444.5 MW (12:00 )
4:00 | 440 | 3800 | 1115 | 4915 | [6 empty] | 12:00
4:30 | 450 | 3766.5 | 1089 | 4855.5 | [5 empty] | Highest Generation | 8347
5:00 | 460 | 3733 | 1063 | 4796 | [6 empty] | 19:00
5:30 | 485 | 3905 | 1085.5 | 4990.5
6:00 | 510 | 4077 | 1108 | 5185
6:30 | 485 | 4158.28 | 1198 | 5356.28
7:00 | 460 | 4239.56 | 1288 | 5527.56
7:30 | 385 | 4311.78 | 1520 | 5831.78
8:00 | 310 | 4384 | 1752 | 6136
8:30 | 175 | 4412.57 | 1777.5 | 6190.07
9:00 | 40 | 4441.14 | 1803 | 6244.14
9:30 | 35 | 4478.45 | 1759.5 | 6237.95
10:00 | 30 | 4515.76 | 1716 | 6231.76
10:30 | 45 | 4583.03 | 1677.5 | 6260.53
11:00 | 60 | 4650.3 | 1639 | 6289.3
11:30 | 80 | 4700.4 | 1666.5 | 6366.9
12:00 | 100 | 4750.5 | 1694 | 6444.5
12:30 | 180 | 4783.85 | 1685.5 | 6469.35
13:00 | 260 | 4817.2 | 1677 | 6494.2
13:30 | 210 | 4741.55 | 1679 | 6420.55
14:00 | 160 | 4665.9 | 1681 | 6346.9
14:30 | 130 | 4650.55 | 1653.5 | 6304.05
15:00 | 100 | 4635.2 | 1626 | 6261.2
15:30 | 55 | 4608.725 | 1604 | 6212.725
16:00 | 10 | 4582.25 | 1582 | 6164.25
16:30 | 25 | 4571.125 | 1638.5 | 6209.625
17:00 | 40 | 4560 | 1695 | 6255
17:30 | 210 | 5063.5 | 2013 | 7076.5
18:00 | 380 | 5567 | 2331 | 7898
18:30 | 400 | 5724.5 | 2398 | 8122.5
19:00 | 420 | 5882 | 2465 | 8347
19:30 | 420 | 5843 | 2462 | 8305
20:00 | 410 | 5773 | 2450 | 8223 |  |  |  | Executive Engineer
20:30 | 385 | 5633.5 | 2404 | 8037.5 |  |  |  | Network Operation Division
21:00 | 360 | 5494 | 2358 | 7852
21:30 | 340 | 5295.5 | 2177 | 7472.5
22:00 | 320 | 5097 | 1996 | 7093 |  |  |  |  | Page 6 of 7
22:30 | 295 | 4840.5 | 1926 | 6766.5
23:00 | 270 | 4584 | 1856 | 6440
23:30 | 355 | 4563 | 1651 | 6214
24:00 | 440 | 4542 | 1446 | 5988
8347 MW (19:00 )
6444.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-01-06 |  | Energy | 153655364
[10 empty] | 2019-01-06 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3612 | 281 | 1623 | 194 | 149 | 45 | 0 | 0 | 84
0:30 | 3570 | 358 | 1444.5 | 113 | 148.5 | 44 | 0 | 0 | 80 | Date: | 2019-01-06
1:00 | 3528 | 435 | 1266 | 32 | 148 | 43 | 0 | 0 | 76
1:30 | 3500.5 | 334 | 1247 | 23.5 | 148.5 | 43 | 0 | 0 | 75 | [7 empty] | Total Energy | 153.6554 | Total Energy Gen 153.655 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 153.655 MKWHr
2:00 | 3473 | 233 | 1228 | 15 | 149 | 43 | 0 | 0 | 74 | [7 empty] | Energy not Served | 0
2:30 | 3409.5 | 233 | 1191 | 15 | 149 | 43 | 0 | 0 | 72 | [7 empty] | Energy Requirement | 153.6554
3:00 | 3346 | 233 | 1154 | 15 | 149 | 43 | 0 | 0 | 70
3:30 | 3321.5 | 232.5 | 1131.5 | 15 | 149 | 43 | 0 | 0 | 70 | [6 empty] | Shortage
4:00 | 3297 | 232 | 1109 | 15 | 149 | 43 | 0 | 0 | 70
4:30 | 3245 | 232 | 1101.5 | 15 | 149 | 43 | 0 | 0 | 70
5:00 | 3193 | 232 | 1094 | 15 | 149 | 43 | 0 | 0 | 70
5:30 | 3331 | 232 | 1149.5 | 15 | 149 | 43 | 0 | 0 | 71
6:00 | 3469 | 232 | 1205 | 15 | 149 | 43 | 0 | 0 | 72
6:30 | 3608 | 232 | 1218 | 34.5 | 149 | 43 | 0 | 0 | 71 |  |  |  |  | Coal
7:00 | 3747 | 232 | 1231 | 54 | 149 | 43 | 0 | 0 | 70
7:30 | 3805.5 | 378 | 1263.5 | 112.5 | 149 | 44 | 0 | 0 | 74 |  |  |  | Oil |  |  |  | ,
8:00 | 3864 | 524 | 1296 | 171 | 149 | 45 | 0 | 0 | 78
8:30 | 3751.5 | 524.5 | 1327 | 283 | 149 | 45 | 17.5 | 0 | 81
9:00 | 3639 | 525 | 1358 | 395 | 149 | 45 | 35 | 0 | 84
9:30 | 3543.5 | 524.5 | 1334.5 | 490.5 | 149 | 45 | 47 | 0 | 88
10:00 | 3448 | 524 | 1311 | 586 | 149 | 45 | 59 | 0 | 92
10:30 | 3464.5 | 524 | 1336 | 570 | 149 | 45 | 60 | 0 | 92
11:00 | 3481 | 524 | 1361 | 554 | 149 | 45 | 61 | 0 | 92
11:30 | 3541 | 523 | 1373.5 | 560 | 149 | 45 | 61 | 0 | 92
12:00 | 3601 | 522 | 1386 | 566 | 149 | 45 | 61 | 0 | 92
12:30 | 3572.5 | 521.5 | 1449.5 | 563.5 | 149 | 45 | 52.5 | 0 | 94
13:00 | 3544 | 521 | 1513 | 561 | 149 | 45 | 44 | 0 | 96
13:30 | 3544 | 521 | 1513 | 561 | 149 | 45 | 44 | 0 | 96
14:00 | 3544 | 521 | 1513 | 561 | 149 | 45 | 44 | 0 | 96
14:30 | 3463.5 | 521.5 | 1497.5 | 569 | 149 | 42.5 | 22 | 0 | 95
15:00 | 3383 | 522 | 1482 | 577 | 149 | 40 | 0 | 0 | 94
15:30 | 3419 | 528 | 1420 | 548.5 | 149 | 41 | 3 | 0 | 93
16:00 | 3455 | 534 | 1358 | 520 | 149 | 42 | 6 | 0 | 92
16:30 | 3409 | 542.5 | 1327 | 618.5 | 149 | 42 | 24 | 0 | 93
17:00 | 3363 | 551 | 1296 | 717 | 149 | 42 | 42 | 0 | 94
17:30 | 3544 | 615 | 1445.5 | 982.5 | 149 | 42 | 191 | 0 | 107
18:00 | 3725 | 679 | 1595 | 1248 | 149 | 42 | 340 | 0 | 120
18:30 | 3681.5 | 679 | 1661 | 1417 | 149 | 42.5 | 373.5 | 0 | 119
19:00 | 3638 | 679 | 1727 | 1586 | 149 | 43 | 407 | 0 | 118
19:30 | 3617 | 679 | 1729 | 1573 | 149 | 43 | 399 | 0 | 116
20:00 | 3562 | 677 | 1700 | 1579 | 149 | 43 | 403 | 0 | 110
20:30 | 3614.5 | 677.5 | 1686.5 | 1461 | 149 | 43 | 295 | 0 | 111
21:00 | 3667 | 678 | 1673 | 1343 | 149 | 43 | 187 | 0 | 112
21:30 | 3656 | 678 | 1676.5 | 1035.5 | 149 | 43.5 | 128 | 0 | 106
22:00 | 3645 | 678 | 1680 | 728 | 149 | 44 | 69 | 0 | 100
22:30 | 3651 | 677.5 | 1636 | 475.5 | 149 | 44 | 36.5 | 0 | 97
23:00 | 3657 | 677 | 1592 | 223 | 149 | 44 | 4 | 0 | 94
23:30 | 3634.5 | 479 | 1607.5 | 208.5 | 149 | 44.5 | 2 | 0 | 89 | Max Temp. in Dhaka |  | 27.5° C
24:00 | 3612 | 281 | 1623 | 194 | 149 | 45 | 0 | 0 | 84
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 153.655 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 153.655 MKWHr
Note on W13: Author:

## Generation
2019-01-06
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 45 | 45 | 45 | 45 | 45 | 45 | 43 | 40 | 42 | 42 | 42 |  | 43 | 43 | 43 | 43 | 44 | 44 | 45 | 1036800
2 | Kaptai Unit-4 & 5
3 | Chattogram ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2700000
5 | Raozan 25 MW (RPCL) | [8 empty] | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 0 |  |  | 323820
| Teknaf Solartech 20MW | [5 empty] | 0 | 1.56 | 8.5 | 14.14 | 17.76 | 20 | 20 | 19.1 | 16.2 | 12.9 | 7.65 | 1 | 0 | [8 empty] | 132570
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 120 | 120 | 120 | 70 | 70 | 70 | 120 | 120 | 120 | 120 | 120 | 120 | 100 | 100 | 100 | 100 | 100 | 120 |  | 100 | 90 | 90 | 120 | 120 | 120 | 120 | 2591126
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | [16 empty] | 0 | 68 |  | 68 | 68 | 68 | 0 | 0 |  |  | 188397
12 | Hathazari peaking | [16 empty] | 0 | 34 |  | 49 | 49 | 49 | 0 | 0 |  |  | 125496
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [16 empty] | 0 | 8 |  | 0 | [6 empty] | 7144
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 85 | 80 | 85 | 85 | 80 | 85 | 85 | 85 | 97 | 105 | 150 | 185 | 150 | 75 | 80 | 80 | 80 | 160 |  | 112 | 115 | 112 | 130 | 120 | 130 | 130 | 2706000
17 | Siddhirganj CCPP-335 MW | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 130 | 174 | 158 | 120 | 120 | 120 | 136 |  | 175 | 150 | 150 | 120 | 120 | 120 | 120 | 3223765
18 | Summit Gazipur -2 | [15 empty] | 0 | 12 | 40 |  | 84 | 100 | 103 | 107 | 0 |  |  | 393930
19 | Ashuganj 195MW Modular | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal ST: Unit-1,2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 730000
21 | Ghorasal GT: Unit-3
22 | Ghorasal GT: Unit-4
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 250 | 250 | 240 | 240 | 240 | 320 | 380 | 380 | 300 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 240 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6605554
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2097740
30 | Ashuganj ST: Unit- 5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2103780
32 | Ashuganj Engines TSK | 10 | 10 | 10 | 10 | 10 | 10 | 36 | 36 | 37 | 34 | 37 | 37 | 37 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 728784
33 | Ashuganj CCPP 225 MW | 198 | 184 | 184 | 194 | 185 | 203 | 204 | 205 | 183 | 183 | 198 | 205 | 190 | 185 | 185 | 202 | 184 | 228 |  | 184 | 185 | 185 | 185 | 185 | 196 | 202 | 4652000
34 | Ashuganj CCPP(South) | 327 | 305 | 305 | 294 | 264 | 294 | 320 | 342 | 305 | 276 | 272 | 272 | 264 | 253 | 257 | 283 | 253 | 268 |  | 272 | 272 | 272 | 305 | 305 | 316 | 334 | 6989500
Ashuganj CCPP(North)
35 | Ashuganj (Precision) 55MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 168000
36 | Chandpur CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 95 | 96 | 100 | 100 | 100 | 0 | 2254950
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 360 | 355 | 345 | 345 | 345 | 375 | 360 | 380 | 352 | 348 | 350 | 362 | 360 | 350 | 348 | 360 | 360 | 345 |  | 348 | 350 | 345 | 347 | 347 | 345 | 358 | 8560900
40 | Meghnaghat CCPP 450MW | 370 | 370 | 320 | 320 | 320 | 340 | 340 | 340 | 370 | 330 | 330 | 330 | 360 | 360 | 360 | 360 | 330 | 370 |  | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 8541375
41 | Haripur Power CCPP 360MW | 321 | 303 | 280 | 254 | 249 | 310 | 313 | 342 | 310 | 268 | 268 | 266 | 294 | 299 | 299 | 296 | 295 | 308 |  | 305 | 307 | 304 | 280 | 280 | 280 | 280 | 6991000
42 | Mymensingh RPCL 210MW | 194 | 194 | 157 | 158 | 157 | 217 | 220 | 203 | 185 | 167 | 169 | 169 | 148 | 148 | 148 | 148 | 150 | 147 |  | 146 | 145 | 145 | 139 | 139 | 140 | 140 | 3830120
43 | Haripur NEPC 110MW
44 | Fenchugonj CCPP-1 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 53 | 56 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 1305000
45 | Fenchugonj CCPP-2 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 61 | 61 | 62 | 62 |  | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 1480720
46 | Shajibazar 330 MW | 259 | 255 | 259 | 262 | 254 | 262 | 266 | 270 | 260 | 248 | 259 | 256 | 255 | 260 | 255 | 256 | 260 | 256 |  | 256 | 258 | 258 | 256 | 256 | 256 | 258 | 5857000
47 | Shahjibazar GT: Unit- 8, 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 46 | 50 | 50 | 50 | 54 | 58 | 49 | 65 |  | 40 | 44 | 40 | 59 | 52 | 69 | 69 | 1140000
48 | Shahjibazar 86MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 10 | 10 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 874560
49 | Shahjibazar (EPL) 50MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 47 | 47 | 47 | 44 | 47 | 47 | 47 | 47 | 47 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 801000
50 | Sylhet GT 150 MW | 78 | 77 | 79 | 76 | 77 | 78 | 78 | 78 | 77 | 77 | 78 | 77 | 77 | 78 | 78 | 77 | 78 | 107 |  | 108 | 108 | 78 | 77 | 78 | 78 | 79 | 1995590
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 37 | 36 | 38 | 39 | 41 | 40 | 40 | 7 | 7 | 45 |  | 43 | 44 | 44 | 45 | 45 | 45 | 45 | 610480
53 | Sylhet (Desh) 10MW | [8 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 129780
54 | Hobiganj 11MW | [7 empty] | 0 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 151536
55 | Fenchugonj (Barakatullah) 51MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 16 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 234000
56 | Shahjahanulla 25 MW | [16 empty] | 0 | 25 |  | 25 | 25 | 25 | 25 | 25 | 0 |  | 125856
57 | Summit Bibiana- 2 | 330 | 310 | 310 | 310 | 300 | 310 | 320 | 330 | 280 | 275 | 285 | 310 | 325 | 290 | 300 | 310 | 300 | 285 |  | 290 | 285 | 285 | 280 | 290 | 290 | 325 | 7743250
58 | Southern 55MW | [11 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 0 | 0 |  |  | 167266
59 | Sikalbaha (Energis) | [7 empty] | 0 | 19 | 38 | 40 | 40 | 40 | 40 | 40 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 51 | 50 | 51 | 705600
60 | Barabkunda (Regent) | [7 empty] | 20 | 20 | 19 | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 322656
61 | Narshingdi (Doreen) | [8 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 277128
62 | Tangail (Doreen) 22MW | [7 empty] | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 346500
63 | Tripura | 76 | 74 | 70 | 70 | 70 | 72 | 70 | 78 | 84 | 92 | 92 | 92 | 96 | 94 | 94 | 92 | 94 | 120 |  | 118 | 116 | 110 | 112 | 100 | 94 | 84 | 2150400
64 | Malancha, Ctg. EPZ (United) | 8 | 8 | 8 | 8 | 8 | 27 | 22 | 19 | 5 | 5 | 4 | 6 | 12 | 10 | 4 | 5 | 11 | 19 |  | 28 | 33 | 37 | 38 | 38 | 42 | 41 | 479520
65 | Feni (Doreen) 22MW | [7 empty] | 3 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 304020
66 | Feni, Mohipal (Doreen) | [8 empty] | 5 | 8 | 8 | 8 | 8 | 8 | 11 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 142560
67 | Jangalia (Summit) 33MW | [8 empty] | 4 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 |  | 16 | 16 | 16 | 16 | 16 | 0 |  | 158200
68 | Summit Cumilla 25MW | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 13 | 20 | 20 | 22 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 455090
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 24 | 24 | 24 | 24 | 18 | 25 | 25 | 25 | 18 |  | 30 | 32 | 32 | 32 | 32 | 32 | 32 | 668880
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 806900
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 820800
73 | Ghorashal (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 301090
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla)
78 | Gazipur (RPCL) | [8 empty] | 25 | 43 | 43 | 38 | 32 | 42 | 42 | 42 | 42 | 42 |  | 43 | 43 | 43 | 42 | 26 | 0 |  | 579660
79 | Kodda 149MW
80 | Jamalpur 95MW | [8 empty] | 5 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 21 | 81 |  | 81 | 81 | 81 | 80 | 81 | 7 | 0 | 504960
81 | Lakdhanvi 52 MW
82 | Madanganj 102MW | [15 empty] | 0 | 10 | 15 |  | 32 | 48 | 48 | 48 | 0 | 0 |  | 188376
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 10 | 10 | 50 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 807640
85 | Keraniganj (Powerpac) 100MW
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat (IEL) | [16 empty] | 0 | 1 |  | 7 | 7 | 7 | 0 | 0 |  |  | 18240
88 | Ghorashal 78MW (MAX) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 601248
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | [8 empty] | 0 | 30 | 50 | 50 | 50 | 50 | 50 | 50 | 53 | 64 |  | 64 | 64 | 64 | 0 | 0 |  |  | 570960
92 | Fenchuganj (EPL) 44MW | [12 empty] | 10 | 10 | 10 | 10 | 10 | 18 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 362000
93 | Ashuganj (Midland) 51MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 40 | 51 | 51 | 51 | 51 | 51 | 25 | 25 | 25 |  | 51 | 51 | 51 | 51 | 51 | 5 | 5 | 767811
94 | Gagnagar (Orion) | [8 empty] | 5 | 7 | 0 | 0 |  |  |  | 0 | 5 | 7 |  | 7 | 7 | 7 | 0 | 0 |  |  | 50688
95 | Patenga 50MW | [8 empty] | 1 | 38 | 45 | 45 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 42 | 0 |  | 603840
96 | Chattogram ECPV 108 MW | [8 empty] | 10 | 45 | 46 | 46 | 46 | 46 | 46 | 46 | 72 | 93 |  | 51 | 26 | 26 | 0 | 0 |  |  | 577920
97 | Katpotti 51 MW | [14 empty] | 0 | 1 | 6 | 40 |  | 47 | 47 | 47 | 47 | 47 | 0 | 0 | 246240
98 | Bosila 108MW | [8 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 46 |  | 46 | 46 | 46 | 46 | 38 | 0 |  | 288000
99 | Madanganj-55 MW | [8 empty] | 0 | 20 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 28 |  | 30 | 30 | 30 | 0 | 0 |  |  | 242160
100 | Northern 55 MW | [8 empty] | 4 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 36 |  | 55 | 55 | 55 | 55 | 36 | 0 |  | 380262
101 | Kushiara 163 MW CCPP GT | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 130 | 130 | 163 | 163 | 163 | 130 | 100 | 130 |  | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 3176885
102 | Sarishabari (Solar) | [7 empty] | 0.5 | 0 | 0 | 2.3 | 2.5 | 2.1 | 1.7 | 1.3 | 0.6 | 0 | [9 empty] | 12250
103 | Banco Energy 54MW | [8 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 54 |  | 54 | 54 | 54 | 54 | 55 | 0 |  | 427680
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 100 | 100 | 100 | 80 | 50 | 7 | 7 | 544800
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | [16 empty] | 0 | 28 |  | 56 | 56 | 54 | 49 | 0 |  |  | 205920
115 | Juldah 100 MW Unit-3 | [7 empty] | 9 | 80 | 80 | 80 | 80 | 80 | 70 | 70 | 70 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 60 | 60 | 1194240
116 | Chandpur Desh 200MW | [8 empty] | 1 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 78 |  | 140 | 120 | 125 | 95 | 80 | 0 |  | 720960
117 | Midland 150MW | [15 empty] | 0 | 2 | 18 |  | 62 | 62 | 62 | 62 | 0 | 0 |  | 274320
118 | Bibiyana-3 285MW
120 | Eastern Zone Total | 4090 | 3999 | 3876 | 3800 | 3733 | 4077 | 4239.56 | 4384 | 4441.14 | 4515.76 | 4650.3 | 4750.5 | 4817.2 | 4665.9 | 4635.2 | 4582.25 | 4560 | 5567 |  | 5882 | 5843 | 5773 | 5494 | 5097 | 4584 | 4542 | 112505920
121
122 | o
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | [15 empty] | 0 | 18 | 33 |  | 32 | 32 | 32 | 0 |  |  |  | 139200
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | [14 empty] | 0 | 6 | 24 | 43 |  | 40 | 32 | 37 | 37 | 31 | 4 | 0 | 208800
Khulna CCPP 225MW
129 | Labon Chora 105 MW | [7 empty] | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 53 | 105 |  | 105 | 105 | 105 | 105 | 0 |  |  | 654240
130
131
132
133
| Summit Barisal 110 MW | [15 empty] | 0 | 24 | 48 |  | 80 | 80 | 80 | 80 | 0 |  |  | 319872
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | [8 empty] | 28 | 32 | 32 | 32 | 31 | 32 | 32 | 32 | 33 | 75 |  | 97 | 96 | 96 | 96 | 96 | 60 | 60 | 844326
| Bhola CCPP 194MW | 206 | 205 | 205 | 206 | 204 | 208 | 208 | 205 | 180 | 199 | 197 | 194 | 192 | 191 | 204 | 202 | 194 | 198 |  | 178 | 187 | 173 | 198 | 192 | 200 | 206 | 4787089
140 | Bhola (Venture) 33MW | 19 | 19 | 18 | 18 | 18 | 19 | 18 | 18 | 16 | 17 | 16 | 18 | 19 | 19 | 16 | 16 | 18 | 24 |  | 26 | 26 | 26 | 26 | 23 | 23 | 20 | 459200
141 | Bangla Trak Noapara
142 | Noapara (KZA) 40MW | [7 empty] | 40 | 40 | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 40 |  | 40 | 40 | 40 | 40 | 40 | 24 | 0 | 388875
143 | Gopalganj Peaking
144 | Bheramara GT-1,2,3
145
146 | Bheramara HVDC | 435 | 233 | 233 | 232 | 232 | 232 | 232 | 524 | 525 | 524 | 524 | 522 | 521 | 522 | 522 | 534 | 551 | 679 |  | 679 | 679 | 677 | 678 | 678 | 677 | 281 | 11531636
147 | Bheramara 360 MW | 320 | 320 | 280 | 280 | 230 | 270 | 350 | 410 | 380 | 280 | 250 | 300 | 300 | 260 | 260 | 260 | 200 | 300 |  | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 7734240
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 148 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3647900
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 80 | 70 | 70 | 100 | 100 |  | 70 | 70 | 70 | 80 | 80 | 80 | 80 | 1538000
| Baghabari Peaking 50MW | [16 empty] | 0 | 50 |  | 50 | 50 | 50 | 50 | 0 |  |  | 190920
157 | Sirajgonj Unit-1 225MW (Gas) | 194 | 191 | 150 | 150 | 150 | 150 | 193 | 200 | 187 | 180 | 184 | 192 | 195 | 184 | 181 | 189 | 194 | 177 |  | 180 | 177 | 177 | 180 | 180 | 180 | 193 | 4649536
158 | Sirajgonj Unit-1 225MW (Oil)
Sirajgonj Unit-2 225MW (Gas)
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas)
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas)
161 | Bera Peaking
162 | Bogra (GBB) | 22 | 22 | 22 | 3 | 3 | 3 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 473520
163 | Bogra (EPL) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 339516
164 | Ullapara (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 | 5 | 163080
165 | Amnura 50MW | [5 empty] | 0 | 12 | 20 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 25 | 50 |  | 50 | 50 | 50 | 50 | 50 | 24 | 24 | 729860
166 | Katakhali (Northern) | [7 empty] | 8 | 35 | 50 | 8 | 8 | 8 | 50 | 24 | 8 | 8 | 24 |  | 50 | 50 | 50 | 50 | 0 |  |  | 404464
167 | Katakhali Peaking | [16 empty] | 0 | 19 |  | 32 | 32 | 31 | 0 | 0 |  |  | 83960
168 | Santahar Peaking | [16 empty] | 0 | 32 |  | 31 | 31 | 31 | 23 | 23 | 0 |  | 144894
169 | Rajlanka 52 MW | 25 | 8 | 8 | 8 | 8 | 8 | 35 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 25 | 37 | 52 |  | 52 | 52 | 52 | 52 | 52 | 51 | 52 | 942720
170 | Chapainawabganj-100 MW | [9 empty] | 24 | 26 | 26 | 26 | 26 | 0 |  | 0 | 51 |  | 102 | 102 | 102 | 60 | 15 | 0 |  | 468596
171
172
173 | Rangpur GT | [7 empty] | 0 | 17 | 17 | 17 | 17 | 0 |  |  |  | 0 | 17 |  | 17 | 17 | 17 | 17 |  |  |  | 145000
175 | Saidpur GT | [7 empty] | 0 | 18 | 18 | 18 | 18 | 18 | 0 |  | 0 | 18 | 18 |  | 18 | 18 | 18 | 0 |  |  |  | 160000
176
177
178
178 | Western Zone Total | 1438 | 1216 | 1134 | 1115 | 1063 | 1108 | 1288 | 1752 | 1803 | 1716 | 1639 | 1694 | 1677 | 1681 | 1626 | 1582 | 1695 | 2331 | 0 | 2465 | 2462 | 2450 | 2358 | 1996 | 1856 | 1446 | 41149444