## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 09-03-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-03-2026 | during | 09-03-2026 | during | 09-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 6 | 6 | 97.7 | 97.7 | 7 | 7 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 343 | 322 | 412 | 412 | 412 | 412 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 30 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 1 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 270 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 16 | 51.3 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 15 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 22.5 | 23 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 22 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 34 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 160 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 70 | 115 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 50 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 45 | 159 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 340 | 345 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 300 | 350 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 108 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1697.5 | 2172.3 | 5947.22 | 5915.22 | 3215.05 | 3240.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 80 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 226 | 220 | 225 | 220 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 32 | 103 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 23 | 0 | 0 | 56 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 68 | 68 | 68 | 68 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 25 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 26 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.21 | 0 | 3.31 | 0 | 3.31 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 68 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 15 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1224 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 8 | 0 | 1 | 0 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 720 | 830 | 830 | 830 | 720 | 720 | ps availability is less
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2220.21 | 2743 | 3682.17 | 3683.86 | 3186.81 | 3196.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 208 | 200 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 161 | 300 | 353.35 | 353.35 | 0 | 220 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 290 | 230 | 318.81 | 318.81 | 318.81 | 318.81 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 70 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 24 | 32 | 32 | 32 | 32 | Machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 93 | 89 | 163 | 163 | 100 | 100 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 50 | 153 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 136 | 146 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 16 | 115 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 69 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1094 | 1398 | 2736.51 | 2670.51 | 1572.01 | 1732.01
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-03-2026 | during | 09-03-2026 | during | 09-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 12 | 18 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 98 | 60 | 80 | 60 | 80 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 69 | 78 | 70 | 115 | 70 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 36.1 | 0 | 41 | 0 | 41 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 3 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 35 | 54.5 | 54.5 | 35 | 35 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 183.1 | 232 | 407.1 | 429 | 214.1 | 236
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 42 | 42 | 42 | 42 | 42 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 142 | 159 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 70 | 71 | 70 | 70 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 40 | 42 | 83 | 83 | 42 | 42 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 97 | 96 | 100 | 100 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 22 | 22 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 315 | 341 | 341 | 150 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 389 | 391 | 385 | 385 | 385 | 385 | Due to Air Filter DP High FGMO not available.
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1110 | 1138 | 1259 | 1259 | 904 | 1061
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 902 | 901 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 44 | 44 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 207 | 172 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 86.45 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1108 | 1115 | 0 | 0 | 1148.28 | 1148.28 | plant availability zero
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2303.45 | 2188 | 2370 | 2280 | 2547.38 | 2457.38
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 31 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 125 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 1085 | 1085 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 180 | 110 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150 | 15 | 15 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 279 | 307 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.62 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2700.36 | 1664.62 | 1712 | 2003.32 | 2002.32 | 1868.32 | 1867.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 47.54 | 0 | 40 | 0 | 40 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 48 | 48 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 182 | 180 | 220 | 220 | 220 | 220 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 378 | 414 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 21 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 40 | 40 | 40 | 40 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.08 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1371.92 | 1449.15 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 38.62 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 100 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2123.16 | 2134.15 | 3168.57 | 2961.87 | 2622.57 | 2415.87
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 53 | 53 | 55 | 55 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.3 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 28 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 142 | 0 | 167 | 0 | 167 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 228.3 | 193 | 505.2 | 303 | 430.2 | 228
System Total |  |  |  |  | 28823.2 | 28385.703 | 12624.34 | 13910.45 | 22079.09 | 21504.78 | 16560.44 | 16434.13
Forecast Scenario (09-03-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12700 |  | 0 |  | 12700
|  |  |  | 1:00 | 11940 |  | 0 |  | 11940
|  |  |  | 2:00 | 11610 |  | 0 |  | 11610
|  |  |  | 3:00 | 11710 |  | 0 |  | 11710
|  |  |  | 4:00 | 12400 |  | 0 |  | 12400
|  |  |  | 5:00 | 11350 |  | 0 |  | 11350
|  |  |  | 6:00 | 10480 |  | 0 |  | 10480
|  |  |  | 7:00 | 10580 |  | 0 |  | 10580
|  |  |  | 8:00 | 11140 |  | 0 |  | 11140
|  |  |  | 9:00 | 11900 |  | 0 |  | 11900
|  |  |  | 10:00 | 12430 |  | 0 |  | 12430
|  |  |  | 11:00 | 12640 |  | 0 |  | 12640
|  |  |  | 12:00 | 13000 |  | 0 |  | 13000
|  |  |  | 13:00 | 13500 |  | 0 |  | 13500
|  |  |  | 14:00 | 13550 |  | 0 |  | 13550
|  |  |  | 15:00 | 13530 |  | 0 |  | 13530
|  |  |  | 16:00 | 13320 |  | 0 |  | 13320
|  |  |  | 17:00 | 13600 |  | 0 |  | 13600
|  |  |  | 18:00 | 13460 |  | 0 |  | 13460
|  |  |  | 18:30 | 13550 |  | 0 |  | 13550
|  |  |  | 19:00 | 13740 |  | 0 |  | 13740
|  |  |  | 19:30 | 13990 |  | 0 |  | 13990
|  |  |  | 20:00 | 13730 |  | 0 |  | 13730
|  |  |  | 21:00 | 14010 |  | 0 |  | 14010
|  |  |  | 22:00 | 13780 |  | 0 |  | 13780
|  |  |  | 23:00 | 13200 |  | 0 |  | 13200
Probable Maximum Temperature: |  |  | 32.10°C
Probable Maximum Demand at Day Peak: |  |  | 13000.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14010.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13159.90 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 299.80667 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:54 hrs on 09-03-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 08-03-2026 | [28 empty] | Date: | 08-03-2026 | [28 empty] | Date: | 08-03-2026 | [28 empty] | Date: | 08-03-2026 | [28 empty] | Date: | 08-03-2026 | [17 empty] | Date: | 08-03-2026
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [17 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 6 | 313 | 0 | 0 | 45.5 | 17 | 114 | 0 | 15 | 15 | 35 | 147 | 0 | 0 | 0 | 314 | 0 | 17 | 250 | 0 | 0 | 0 | 108 | 24 | 22 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 38 | 12 | 0 | 80 | 20 | 20 | 515 | 0 | 0 | 50 | 0 | 51 | 226 | 0 | 0 | 0 | 1140 | 0 | 15 | 0 | 290 | 0 | 340 | 51 | 0 | 182 | 0 | 94 | 96 | 85 | 0 | 20 | 0 | 142 | 0 | 0 | 0 | 310 | 0 | 363 | 41 | 0 | 154 | 0 | 17 | 0 | 41 | 0 | 69 | 0 | 96 | 0 | 59 | 47 | 12 | 0 | 0 | 0 | 6496.5 | 902 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 1438.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 49 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 0 | 1085 | 0 | 6106.42 | 12602.92 | 90.1
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 310 | 0 | 0 | 34 | 17 | 100 | 0 | 0 | 0 | 17 | 117 | 0 | 0 | 0 | 265 | 0 | 0 | 250 | 0 | 0 | 0 | 90 | 23.5 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 24 | 12 | 0 | 80 | 6 | 26 | 515 | 0 | 0 | 30 | 0 | 17 | 227 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 220 | 0 | 300 | 51 | 0 | 187 | 0 | 47 | 96 | 34 | 0 | 20 | 0 | 142 | 0 | 0 | 0 | 305 | 0 | 374 | 41 | 0 | 154 | 0 | 17 | 0 | 41 | 0 | 70 | 0 | 94 | 0 | 58 | 48 | 12 | 0 | 0 | 0 | 5975.5 | 902 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 1359.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 48 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246 | 120 | 220 | 0 | 0 | 1020 | 0 | 5870.5 | 11846 | 90.09
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 311 | 0 | 0 | 23.3 | 17 | 78 | 0 | 0 | 0 | 17 | 83 | 0 | 0 | 0 | 255 | 0 | 0 | 250 | 0 | 0 | 0 | 70 | 23.5 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 515 | 0 | 0 | 19 | 0 | 15 | 227 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 220 | 0 | 300 | 51 | 0 | 205 | 0 | 22 | 96 | 17 | 0 | 20 | 0 | 132 | 0 | 0 | 0 | 305 | 0 | 388 | 41 | 0 | 155 | 0 | 17 | 0 | 41 | 0 | 71 | 0 | 96 | 0 | 59 | 48 | 12 | 0 | 0 | 0 | 5810.8 | 903 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1045 | 0 | 0 | 0 | 1250.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 48 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247 | 120 | 220 | 0 | 0 | 1010 | 0 | 5701.4 | 11512.2 | 90.08
03:00 | 0 | 3 | 2 | 0 | 0 | 0 | 0 | 6 | 324 | 0 | 0 | 15.8 | 0 | 79 | 0 | 0 | 0 | 17 | 98 | 0 | 0 | 0 | 255 | 0 | 0 | 250 | 0 | 0 | 0 | 90 | 23.5 | 22 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 515 | 0 | 0 | 19 | 0 | 15 | 227 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 220 | 0 | 342 | 51 | 0 | 208 | 0 | 15 | 96 | 16 | 0 | 20 | 0 | 138 | 0 | 0 | 0 | 300 | 0 | 390 | 41 | 0 | 142 | 0 | 17 | 0 | 41 | 0 | 71 | 0 | 97 | 0 | 67 | 57 | 12 | 0 | 0 | 0 | 5930.3 | 902 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 1268.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 48 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 120 | 220 | 0 | 0 | 1020 | 0 | 5679.68 | 11609.98 | 90.07
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 6 | 351 | 0 | 0 | 16.8 | 0 | 107 | 0 | 0 | 0 | 17 | 104 | 0 | 0 | 0 | 365 | 0 | 0 | 250 | 0 | 0 | 0 | 108 | 23.5 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 30 | 515 | 0 | 0 | 19 | 0 | 31 | 227 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 220 | 0 | 342 | 51 | 0 | 190 | 0 | 16 | 96 | 31 | 0 | 20 | 0 | 138 | 0 | 0 | 0 | 305 | 0 | 388 | 41 | 0 | 159 | 0 | 17 | 0 | 41 | 0 | 70 | 0 | 97 | 0 | 98 | 57 | 18 | 0 | 0 | 0 | 6270.3 | 902 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1122 | 0 | 0 | 0 | 1442.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 48 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 0 | 1020 | 0 | 6037.75 | 12308.05 | 90.06
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 336 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 250 | 0 | 0 | 0 | 52 | 23.5 | 22 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 30 | 515 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 1056 | 0 | 0 | 0 | 220 | 0 | 260 | 51 | 0 | 191 | 0 | 0 | 97 | 0 | 0 | 20 | 0 | 124 | 0 | 0 | 0 | 305 | 0 | 386 | 41 | 0 | 159 | 0 | 17 | 0 | 41 | 0 | 69 | 0 | 96 | 0 | 69 | 58 | 18 | 0 | 0 | 0 | 5524.5 | 902 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 0 | 0 | 1359.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 120 | 220 | 0 | 0 | 950 | 0 | 5732.67 | 11257.17 | 90.05
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 23.5 | 22 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 30 | 515 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 1030 | 0 | 0 | 0 | 215 | 52 | 230 | 51 | 0 | 127 | 0 | 0 | 96 | 0 | 0 | 20 | 0 | 114 | 0 | 0 | 0 | 300 | 0 | 366 | 41 | 0 | 156 | 0 | 17 | 0 | 41 | 0 | 69 | 0 | 96 | 0 | 67 | 45 | 18 | 0 | 0 | 0 | 5231.5 | 667 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 966 | 0 | 0 | 0 | 1227.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 120 | 220 | 0 | 0 | 940 | 0 | 5150.33 | 10381.83 | 90.04
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 250 | 0 | 0 | 1 | 0 | 23.8 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31 | 80 | 0 | 13 | 515 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 1058 | 2 | 0 | 0 | 215 | 21 | 230 | 51 | 0 | 127 | 0 | 0 | 97 | 0 | 0 | 8 | 0 | 100 | 0 | 6 | 0 | 300 | 0 | 356 | 41 | 0 | 137 | 0 | 17 | 0 | 41 | 0 | 69 | 0 | 96 | 0 | 67 | 45 | 18 | 0 | 3.3 | 4 | 5178.41 | 785 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 965 | 0 | 0 | 0 | 1236.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.42 | 4 | 0 | 0 | 2.37 | 0 | 0 | 185 | 0 | 0 | 0 | 381 | 0 | 0.17 | 0 | 48 | 0 | 2 | 0 | 0 | 0 | 0 | 0.2 | 11 | 0.05 | 0 | 230 | 120 | 180 | 0 | 0 | 935 | 0 | 5302.33 | 10480.74 | 90.03
08:00 | 0 | 5 | 16 | 0 | 0 | 0 | 0 | 6 | 335 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 250 | 0 | 0 | 3 | 35 | 23 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 80 | 0 | 8 | 515 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1200 | 5 | 0 | 0 | 215 | 27 | 230 | 51 | 0 | 128 | 0 | 0 | 97 | 0 | 0 | 20 | 0 | 116 | 0 | 19 | 0 | 310 | 0 | 408 | 41 | 0 | 161 | 2 | 17 | 0 | 41 | 0 | 70 | 0 | 97 | 0 | 69 | 58 | 18 | 0 | 11.41 | 6 | 5601.51 | 700 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 1013 | 0 | 0 | 0 | 1242.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.81 | 14 | 0 | 0 | 4.65 | 0 | 0 | 182 | 0 | 0 | 0 | 414 | 0 | 0.6 | 0 | 48 | 0 | 10 | 0 | 0 | 0 | 0 | 1.2 | 43 | 0.18 | 0 | 235 | 120 | 220 | 0 | 0 | 950 | 0 | 5444.38 | 11045.89 | 90.02
09:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 6 | 354 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 250 | 0 | 0 | 4 | 70 | 22.5 | 22 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.97 | 80 | 0 | 2 | 515 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1210 | 13 | 0 | 0 | 200 | 71 | 230 | 51 | 0 | 131 | 0 | 0 | 94 | 0 | 0 | 20 | 0 | 122 | 0 | 43 | 0 | 305 | 0 | 366 | 41 | 0 | 161 | 5 | 17 | 0 | 41 | 0 | 70 | 0 | 97 | 0 | 69 | 58 | 18 | 1 | 20.1 | 6 | 5761.57 | 902 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.88 | 1080 | 0 | 0 | 0 | 1302.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.19 | 25 | 0 | 0 | 22.28 | 0 | 0 | 181 | 0 | 0 | 0 | 414 | 0 | 2.23 | 0 | 48 | 0 | 16 | 0 | 0 | 0 | 0 | 2.5 | 86 | 0.35 | 0 | 307 | 120 | 220 | 0 | 0 | 990 | 0 | 5994.04 | 11755.61 | 90.01
10:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 5 | 349 | 0 | 0 | 12 | 0 | 70 | 0 | 0 | 0 | 30 | 48 | 0 | 0 | 0 | 305 | 0 | 20 | 300 | 0 | 0 | 9 | 70 | 22.5 | 22 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.42 | 80 | 0 | 3 | 515 | 0 | 0 | 0 | 0 | 5 | 223 | 0 | 0 | 0 | 1140 | 17 | 0 | 0 | 0 | 105 | 260 | 51 | 0 | 210 | 0 | 0 | 94 | 14 | 0 | 20 | 0 | 124 | 0 | 56 | 0 | 300 | 0 | 375 | 42 | 0 | 153 | 7 | 17 | 0 | 41 | 0 | 70 | 0 | 97 | 0 | 68 | 58 | 16 | 2 | 29.09 | 6 | 5806.01 | 902 | 211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.58 | 1114 | 0 | 0 | 0 | 1350.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.88 | 55 | 0 | 0 | 36 | 0 | 0 | 181 | 0 | 0 | 0 | 337 | 0 | 3.79 | 0 | 52 | 0 | 23 | 0 | 0 | 0 | 0 | 3.8 | 120 | 0.22 | 0 | 307 | 120 | 220 | 0 | 0 | 1085 | 0 | 6220.73 | 12026.74 | 90
11:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 6 | 330 | 0 | 0 | 15 | 0 | 70 | 0 | 0 | 25 | 35 | 47 | 0 | 0 | 0 | 290 | 0 | 35 | 300 | 0 | 0 | 29 | 70 | 22.5 | 22 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.66 | 80 | 0 | 6 | 565 | 0 | 0 | 0 | 0 | 33 | 220 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 0 | 131 | 260 | 51 | 0 | 199 | 0 | 15 | 94 | 47 | 0 | 20 | 0 | 134 | 0 | 57 | 0 | 295 | 0 | 377 | 42 | 0 | 135 | 6 | 20 | 0 | 40 | 0 | 71 | 0 | 97 | 0 | 69 | 58 | 16 | 2 | 35.1 | 6 | 5982.26 | 902 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.26 | 1094 | 0 | 0 | 0 | 1366.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.43 | 94 | 0 | 0 | 33.26 | 0 | 0 | 182 | 0 | 0 | 0 | 346 | 0 | 4.65 | 0 | 51 | 0 | 27 | 0 | 0 | 0 | 0 | 4.7 | 146 | 0.6 | 0 | 277 | 120 | 180 | 0 | 0 | 1085 | 0 | 6252.22 | 12234.48 | 89.99
12:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 6 | 343 | 0 | 0 | 16 | 0 | 70 | 0 | 0 | 30 | 35 | 45 | 0 | 0 | 0 | 300 | 0 | 35 | 300 | 0 | 0 | 31 | 70 | 22.5 | 21 | 0 | 340 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1.21 | 80 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 32 | 219 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 0 | 161 | 290 | 51 | 0 | 208 | 0 | 16 | 93 | 50 | 0 | 20 | 0 | 136 | 0 | 69 | 0 | 305 | 0 | 389 | 41 | 0 | 142 | 4 | 22 | 0 | 40 | 0 | 70 | 0 | 97 | 0 | 69 | 58 | 12 | 2 | 36.1 | 6 | 6304.81 | 902 | 207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.45 | 1108 | 0 | 0 | 0 | 1371.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.54 | 100 | 0 | 0 | 38.62 | 0 | 0 | 182 | 0 | 0 | 0 | 378 | 0 | 5.08 | 0 | 53 | 0 | 28 | 0 | 0 | 0 | 0 | 5.3 | 142 | 0.62 | 0 | 279 | 120 | 180 | 0 | 0 | 1085 | 0 | 6319.53 | 12624.34 | 89.98
13:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 6 | 355 | 0 | 0 | 25.5 | 0 | 70 | 0 | 55 | 30 | 35 | 48 | 0 | 0 | 0 | 310 | 0 | 35 | 300 | 0 | 0 | 30 | 70 | 22.5 | 21 | 0 | 300 | 3 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 2.3 | 80 | 7 | 15 | 825 | 0 | 0 | 0 | 0 | 41 | 220 | 0 | 0 | 0 | 1140 | 18 | 15 | 0 | 0 | 220 | 345 | 51 | 0 | 188 | 0 | 23 | 93 | 51 | 0 | 20 | 0 | 144 | 0 | 65 | 0 | 310 | 0 | 361 | 42 | 0 | 152 | 8 | 22 | 0 | 40 | 0 | 71 | 0 | 95 | 0 | 69 | 58 | 12 | 1 | 22.08 | 6 | 6598.38 | 902 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 1115 | 0 | 0 | 0 | 1456.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.68 | 91 | 0 | 0 | 32.19 | 0 | 0 | 182 | 0 | 0 | 0 | 402 | 0 | 5.2 | 0 | 53 | 0 | 25 | 34 | 0 | 0 | 0 | 5.2 | 128 | 0.6 | 0 | 275 | 120 | 220 | 0 | 0 | 1085 | 0 | 6462.33 | 13060.71 | 89.98
14:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 5 | 329 | 0 | 0 | 32.7 | 0 | 95 | 0 | 60 | 30 | 35 | 50 | 0 | 0 | 0 | 305 | 0 | 35 | 300 | 0 | 0 | 25 | 70 | 22.5 | 21 | 0 | 300 | 15 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 1.39 | 80 | 34 | 7 | 830 | 0 | 0 | 0 | 0 | 50 | 219 | 0 | 0 | 0 | 1173 | 17 | 50 | 0 | 0 | 355 | 300 | 51 | 0 | 209 | 0 | 31 | 90 | 50 | 0 | 20 | 0 | 156 | 0 | 47 | 0 | 315 | 0 | 356 | 42 | 0 | 146 | 6 | 22 | 0 | 41 | 0 | 71 | 0 | 96 | 0 | 65 | 58 | 8 | 1 | 22.29 | 6 | 6811.88 | 902 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 1044 | 0 | 0 | 0 | 1448.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.76 | 88 | 0 | 0 | 50.23 | 0 | 0 | 182 | 0 | 0 | 0 | 414 | 0 | 4.65 | 0 | 53 | 0 | 24 | 34 | 0 | 0 | 0 | 2.4 | 115 | 0.52 | 0 | 277 | 120 | 220 | 0 | 0 | 1085 | 0 | 6376.64 | 13188.52 | 89.97
15:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 6 | 359 | 0 | 0 | 33.3 | 0 | 96 | 0 | 60 | 30 | 35 | 53 | 0 | 0 | 0 | 315 | 0 | 35 | 300 | 0 | 0 | 19 | 90 | 22.5 | 21 | 0 | 300 | 16 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 1.27 | 80 | 33 | 0 | 830 | 0 | 0 | 13 | 0 | 49 | 219 | 0 | 0 | 0 | 1202 | 13 | 50 | 0 | 0 | 354 | 280 | 51 | 0 | 198 | 0 | 33 | 90 | 51 | 0 | 20 | 0 | 150 | 0 | 44 | 0 | 320 | 0 | 359 | 42 | 0 | 154 | 3 | 22 | 0 | 41 | 0 | 70 | 0 | 96 | 0 | 65 | 58 | 5 | 1 | 9.16 | 6 | 6877.23 | 902 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.24 | 1079 | 0 | 0 | 0 | 1449.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.28 | 65 | 0 | 0 | 13.77 | 0 | 0 | 182 | 0 | 0 | 0 | 414 | 0 | 2.29 | 0 | 54 | 0 | 19 | 34 | 0 | 0 | 0 | 2 | 96 | 0.4 | 0 | 307 | 120 | 220 | 0 | 0 | 1085 | 0 | 6305.78 | 13183.01 | 89.97
16:00 | 0 | 40 | 16 | 0 | 0 | 0 | 0 | 6 | 351 | 0 | 0 | 40 | 2 | 97 | 30 | 95 | 30 | 35 | 84 | 0 | 0 | 0 | 310 | 0 | 35 | 300 | 0 | 0 | 11 | 90 | 22.5 | 21 | 0 | 300 | 17 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 12 | 24 | 0.34 | 80 | 33 | 3 | 830 | 0 | 0 | 18 | 0 | 57 | 220 | 0 | 0 | 0 | 1224 | 8 | 50 | 0 | 0 | 355 | 230 | 51 | 0 | 162 | 0 | 39 | 90 | 59 | 0 | 20 | 0 | 144 | 0 | 28 | 0 | 305 | 0 | 346 | 42 | 0 | 153 | 2 | 22 | 0 | 41 | 0 | 70 | 0 | 96 | 0 | 65 | 58 | 5 | 1 | 1.3 | 6 | 6899.14 | 902 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 1114 | 0 | 0 | 0 | 1450.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.93 | 40 | 0 | 0 | 19.56 | 0 | 0 | 182 | 0 | 0 | 0 | 414 | 0 | 1.92 | 0 | 54 | 35 | 12 | 50 | 0 | 0 | 0 | 0.9 | 59 | 0.25 | 0 | 307 | 120 | 220 | 0 | 0 | 1085 | 0 | 6284.51 | 13183.65 | 89.96
17:00 | 0 | 50 | 30 | 0 | 0 | 0 | 0 | 6 | 342 | 0 | 0 | 51.6 | 17 | 114 | 30 | 145 | 55 | 35 | 87 | 0 | 0 | 0 | 305 | 0 | 35 | 300 | 0 | 0 | 4 | 108 | 22.5 | 21 | 0 | 300 | 32 | 20 | 0 | 0 | 5 | 34 | 14 | 0 | 12 | 24 | 0.36 | 80 | 32 | 16 | 830 | 0 | 0 | 23 | 0 | 68 | 221 | 0 | 0 | 0 | 1224 | 2 | 73 | 0 | 0 | 320 | 230 | 51 | 0 | 175 | 0 | 56 | 90 | 94 | 0 | 20 | 0 | 150 | 0 | 9 | 5 | 310 | 0 | 359 | 42 | 0 | 154 | 1 | 22 | 0 | 41 | 0 | 69 | 0 | 97 | 10 | 62 | 87 | 5 | 0 | 0.83 | 6 | 7234.29 | 902 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.61 | 1125 | 0 | 0 | 0 | 1447.92 | 0 | 0 | 0 | 10 | 20 | 0 | 0 | 0 | 0 | 7.03 | 16 | 5 | 0 | 6.63 | 0 | 0 | 182 | 0 | 0 | 0 | 402 | 0 | 0.72 | 0 | 54 | 70 | 4 | 85 | 0 | 0 | 0 | 0.4 | 19 | 0.09 | 0 | 307 | 120 | 220 | 0 | 0 | 1085 | 2 | 6271.4 | 13505.69 | 89.96
18:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 6 | 340 | 0 | 0 | 49.5 | 17 | 115 | 15 | 180 | 30 | 35 | 120 | 0 | 0 | 0 | 305 | 0 | 45 | 260 | 0 | 0 | 0 | 108 | 20 | 21 | 0 | 310 | 31 | 45 | 12 | 0 | 12 | 51 | 23 | 0 | 24 | 24 | 0 | 80 | 32 | 24 | 830 | 0 | 0 | 32 | 0 | 76 | 196 | 0 | 0 | 0 | 1110 | 0 | 97 | 0 | 0 | 320 | 230 | 20 | 0 | 180 | 0 | 75 | 90 | 109 | 0 | 20 | 0 | 154 | 7 | 0 | 32 | 305 | 0 | 375 | 42 | 0 | 152 | 0 | 22 | 0 | 50 | 0 | 69 | 0 | 96 | 17 | 75 | 96 | 5 | 0 | 0 | 0 | 7284.5 | 902 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 1115 | 0 | 0 | 0 | 1453.89 | 0 | 0 | 0 | 35 | 45 | 0 | 0 | 0 | 0 | 0.1 | 0 | 15 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 350 | 0 | 0.03 | 0 | 53 | 110 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 232 | 110 | 180 | 0 | 0 | 1050 | 17 | 6078.27 | 13362.77 | 89.95
19:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 6 | 350 | 0 | 0 | 36.5 | 17 | 115 | 15 | 180 | 30 | 35 | 158 | 0 | 0 | 0 | 325 | 0 | 55 | 240 | 0 | 0 | 0 | 120 | 25 | 21 | 0 | 345 | 31 | 45 | 12 | 0 | 7 | 34 | 16 | 0 | 25 | 30 | 0 | 80 | 35 | 19 | 830 | 0 | 0 | 33 | 0 | 86 | 224 | 0 | 0 | 0 | 1176 | 0 | 95 | 0 | 0 | 300 | 230 | 43 | 0 | 200 | 0 | 71 | 87 | 106 | 0 | 20 | 0 | 148 | 20 | 0 | 32 | 275 | 0 | 373 | 42 | 0 | 148 | 0 | 22 | 0 | 42 | 0 | 70 | 0 | 96 | 17 | 75 | 97 | 11 | 0 | 0 | 0 | 7444.5 | 902 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1086 | 0 | 0 | 0 | 1441.31 | 0 | 0 | 0 | 60 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 53 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 288 | 120 | 110 | 0 | 0 | 1058 | 17 | 6195.31 | 13639.81 | 89.94
19:30 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 6 | 290 | 0 | 0 | 43 | 35 | 149 | 45 | 210 | 55 | 35 | 147 | 0 | 0 | 0 | 305 | 0 | 55 | 240 | 0 | 0 | 0 | 108 | 25 | 21 | 0 | 340 | 45 | 65 | 24 | 0 | 2 | 34 | 23 | 0 | 38 | 38 | 0 | 80 | 50 | 22 | 830 | 0 | 0 | 45 | 0 | 90 | 226 | 0 | 0 | 0 | 1180 | 0 | 120 | 0 | 0 | 300 | 230 | 51 | 0 | 200 | 0 | 115 | 88 | 141 | 0 | 20 | 0 | 146 | 16 | 0 | 32 | 305 | 0 | 390 | 42 | 0 | 150 | 0 | 22 | 0 | 42 | 0 | 71 | 0 | 96 | 20 | 75 | 97 | 12 | 0 | 0 | 0 | 7766 | 902 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1115 | 0 | 0 | 0 | 1426.98 | 0 | 0 | 0 | 70 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 53 | 70 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 231 | 125 | 110 | 0 | 0 | 1085 | 54 | 6127.98 | 13893.98
20:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 6 | 304 | 0 | 0 | 46.3 | 35 | 130 | 15 | 145 | 55 | 35 | 149 | 0 | 0 | 0 | 320 | 0 | 17 | 240 | 0 | 0 | 0 | 108 | 25 | 22 | 0 | 350 | 45 | 15 | 24 | 0 | 0 | 34 | 23 | 0 | 12 | 12 | 0 | 80 | 65 | 22 | 830 | 0 | 0 | 48 | 0 | 93 | 226 | 0 | 0 | 0 | 1184 | 0 | 70 | 0 | 0 | 300 | 230 | 51 | 0 | 200 | 0 | 109 | 90 | 147 | 0 | 20 | 0 | 152 | 16 | 0 | 32 | 315 | 0 | 390 | 42 | 0 | 152 | 0 | 22 | 0 | 42 | 0 | 71 | 0 | 96 | 28 | 78 | 98 | 12 | 0 | 0 | 0 | 7562.3 | 902 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1084 | 0 | 0 | 0 | 1416.58 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 53 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 277 | 125 | 110 | 0 | 0 | 1085 | 54 | 6069.58 | 13631.88 | 89.93
21:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 6 | 322 | 0 | 0 | 51.3 | 35 | 115 | 15 | 160 | 55 | 35 | 159 | 0 | 0 | 0 | 350 | 0 | 17 | 270 | 0 | 0 | 0 | 108 | 23 | 22 | 0 | 345 | 15 | 15 | 26 | 0 | 0 | 34 | 23 | 0 | 12 | 12 | 0 | 80 | 68 | 25 | 830 | 0 | 0 | 50 | 0 | 103 | 226 | 0 | 0 | 0 | 1224 | 0 | 70 | 0 | 0 | 300 | 230 | 51 | 0 | 200 | 0 | 115 | 89 | 153 | 0 | 20 | 0 | 146 | 0 | 0 | 24 | 315 | 0 | 391 | 42 | 0 | 159 | 0 | 22 | 0 | 42 | 0 | 71 | 0 | 96 | 35 | 78 | 98 | 18 | 0 | 0 | 3 | 7683.3 | 901 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1115 | 0 | 0 | 0 | 1449.15 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 53 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 307 | 125 | 110 | 0 | 0 | 1085 | 54 | 6227.15 | 13910.45 | 89.92
22:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 6 | 314 | 0 | 0 | 49.6 | 35 | 115 | 15 | 110 | 55 | 35 | 158 | 0 | 0 | 0 | 345 | 0 | 17 | 270 | 0 | 0 | 0 | 108 | 23 | 22 | 0 | 340 | 15 | 15 | 24 | 0 | 0 | 17 | 0 | 0 | 12 | 12 | 0 | 80 | 67 | 21 | 830 | 0 | 0 | 50 | 0 | 100 | 227 | 0 | 0 | 0 | 1224 | 0 | 70 | 0 | 0 | 300 | 230 | 51 | 0 | 202 | 0 | 115 | 88 | 150 | 0 | 20 | 0 | 158 | 0 | 0 | 24 | 305 | 0 | 377 | 42 | 0 | 157 | 0 | 22 | 0 | 42 | 0 | 69 | 0 | 96 | 35 | 49 | 59 | 16 | 0 | 0 | 6 | 7478.6 | 902 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1113 | 0 | 0 | 0 | 1461.66 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 53 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 307 | 125 | 110 | 0 | 0 | 1080 | 54 | 6210.66 | 13689.26 | 89.91
23:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 6 | 314 | 0 | 0 | 47.8 | 35 | 115 | 15 | 60 | 15 | 35 | 153 | 0 | 0 | 0 | 355 | 0 | 0 | 270 | 0 | 0 | 0 | 70 | 23 | 22 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 24 | 25 | 0 | 80 | 66 | 27 | 830 | 0 | 0 | 50 | 0 | 97 | 227 | 0 | 0 | 0 | 1224 | 0 | 30 | 0 | 0 | 280 | 230 | 51 | 0 | 211 | 0 | 103 | 90 | 100 | 0 | 20 | 0 | 158 | 0 | 0 | 24 | 305 | 0 | 390 | 42 | 0 | 156 | 0 | 22 | 0 | 42 | 0 | 69 | 0 | 96 | 35 | 49 | 58 | 9 | 0 | 0 | 0 | 7123.8 | 902 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 0 | 0 | 0 | 1451.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 53 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 125 | 110 | 0 | 0 | 1085 | 35 | 6011.35 | 13135.15 | 89.9
Total KWH | 0 | 585600 | 405600 | 0 | 0 | 0 | 0 | 152636.36 | 8078400 | 0 | 0 | 644400 | 255240 | 2046672 | 156960 | 1314011 | 553163 | 601279 | 1938240 | 0 | 0 | 0 | 7586839 | 0 | 453940 | 6500012 | 0 | 0 | 170773 | 1872000 | 543600 | 519120 | 0 | 7740454.55 | 244636 | 190691 | 114240 | 0 | 112800 | 390117 | 100343 | 0 | 168960 | 195840 | 16684 | 1921980 | 581270 | 421920 | 16276363.64 | 0 | 0 | 488640 | 0 | 1119891 | 5469897 | 0 | 0 | 0 | 28052725 | 105975 | 809600 | 0 | 2037500 | 4322800 | 6452000 | 1244536 | 0 | 4537000 | 0 | 1015680 | 2262260 | 1431360 | 0 | 477700 | 0 | 3377280 | 52109 | 447873 | 186752 | 7387000 | 0 | 9230000 | 982000 | 0 | 3669545.45 | 47192 | 489336 | 0 | 998400 | 0 | 1679000 | 0 | 2316500 | 218520 | 1638000 | 1531200 | 284160 | 9700 | 191280 | 78240 | 157496436 | 21214545 | 4846176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 537120 | 25825450 | 0 | 0 | 0 | 33192866 | 0 | 0 | 0 | 245952 | 327168 | 0 | 0 | 0 | 0 | 278336 | 616230 | 67629 | 0 | 268496 | 0 | 0 | 4607809 | 0 | 0 | 0 | 9608145 | 0 | 29760 | 0 | 1174254 | 618316 | 190065 | 919468 | 0 | 0 | 0 | 27519.12 | 1008720 | 3963 | 125280 | 6676000 | 2895000 | 4760810 | 0 | 0 | 25688727.27 | 256800 | 146010604.39 | 303507040.39

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 08-03-2026
Power Supply Scenario
| Day Peak Generation |  |  | 12624.34 | MW | 12:00 Hr. | Energy Generated |  |  | 303.507 |  | MKWHr.
| Day Peak Demand |  |  | 12903.34 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.766 |  | MKWHr.
| Evening Peak Generation |  |  | 13910.45 | MW | 21:00 Hr. | Energy Demand |  |  | 305.273 |  | MKWHr.
| Evening Peak Demand |  |  | 13910.45 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32.9 |  | °C
| Minimum Generation of the Day |  |  | 10381.83 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 817.59 |  | MMCFD
| Maximum Generation of the Day |  |  | 13910.45 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.0981 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 31.1211 | 0 | 10.8271 | 0 | 0 | 0.17077 | 0 | 0 | 42.1189 | Gas | 112.1006 | Gas | 384420338.7035
| Chattogram Zone |  |  | 5.8918 | 44.3291 | 3.5946 | 0 | 1.922 | 0.12266 | 0 | 0.1128 | 55.973 | Coal | 103.6935 | Coal | 677012732.3958
| Cumilla Zone |  |  | 21.3338 | 0 | 3.4955 | 0 | 0 | 0.44787 | 3.3773 | 0 | 28.6545 | HFO | 23.9438 | HFO | 391958029.66
| Mymensingh Zone |  |  | 0.28416 | 0 | 3.466 | 0 | 0 | 0.20098 | 0 | 0 | 3.9511 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.7518 | 0 | 0 | 0 | 0 | 0.047192 | 0 | 0 | 26.799 | Hydro | 1.922 | Hydro | 192198
| Khulna Zone |  |  | 4.8462 | 25.8255 | 0 | 0 | 0 | 0.53712 | 21.2145 | 0 | 52.4233 | Solar | 3.9497 | Solar | 62977152.584
| Barishal Zone |  |  | 7.6558 | 32.3647 | 0.38208 | 0 | 0 | 0.003963 | 0 | 0 | 40.4066 | Import | 57.7847 | Import | 332608739.04
| Rajshahi Zone |  |  | 14.216 | 0 | 0.64075 | 0 | 0 | 1.1928 | 33.1929 | 0 | 49.2424 | Wind | 0.1128 | Wind | 1659288
| Rangpur Zone |  |  | 0 | 1.1743 | 1.5378 | 0 | 0 | 1.2263 | 0 | 0 | 3.9383
| Total |  |  | 112.1006 | 103.6935 | 23.9438 | 0 | 1.922 | 3.9497 | 57.7847 | 0.1128 | 303.507
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 384420338.7035 |  | Hydro | 192198
|  |  |  | Coal | 677012732.3958 |  | Solar | 62977152.584
|  |  |  | HFO | 391958029.66 |  | Import | 332608739.04
|  |  |  | HSD | 0 |  | Wind | 1659288
[5 empty] | Total: | 185,08,28,478 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.2145 | Peak Hr Flow | 901.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 48100272.73 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 33.1929 | Peak Hr Flow | 1449.15 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1986 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.3773 | Peak Hr Flow | 146.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2655 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 57.7847 | Peak Hr Flow | 2496.15 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5195
|  |  |  | Chattogram |  | 0 |  | 1240
|  |  |  | Cumilla |  | 0 |  | 1263
|  |  |  | Mymensingh |  | 0 |  | 1107
|  |  |  | Sylhet |  | 0 |  | 534
|  |  |  | Khulna |  | 0 |  | 1542
|  |  |  | Barishal |  | 0 |  | 399
|  |  |  | Rajshahi |  | 0 |  | 1322
|  |  |  | Rangpur |  | 0 |  | 770
|  |  |  | Total |  | 0 |  | 13372
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:46 | 15:49 | Aminbazar-Meghnaghat 400kV Ckt-1 Scheduled S/D from Meghnaghat 400/230kV end Due to
Shutdown instructed by NLDC
| 08:47 | 14:56 | Chowmuhani 230/132/33kV S/S ATR-02 LT Scheduled S/D Due to Outside painting Final work.
| 08:48 | 14:55 | Chowmuhani 230/132/33kV S/S ATR-02 HT Scheduled S/D Due to Outside painting Final work.
| 09:11 | 15:00 | Chandraghona-Kaptai 132 kV Ckt-2 Scheduled S/D from Chandraghona 132/33kV end.
|  | 09:35 | Shahjibazar-Sreemangal 132kV Ckt-1 is restored.
| 09:42 | 10:33 | Ashuganj-Brahmanbaria 132kV Ckt-2 Forced S/D from Brahmanbaria 132/33kV end.
| 09:43 |  | Dhamrai 132/33kV S/S Main Bus-1 Scheduled S/D Due to Project work
|  | 10:12 | Muktagacha 132/33kV S/S T-3(424T) HT is restored.
|  | 10:13 | Muktagacha 132/33kV S/S T-3(424T) LT is restored.
| 10:34 | 16:32 | Goalpara-Labanchura 132kV Ckt-2 Scheduled S/D from Goalpara 132/33kV end Due to Boring
work for Earthing
| 11:27 |  | Kishoreganj 132/33kV S/S Tr-1 (404T) HT Project Work S/D Due to schedule shutdown
| 14:45 | 15:48 | Halishahar 132/33kV S/S 415T(TR-2) HT Forced S/D Due to Due to emergency maintenance work
at t-2 secondary B-phase Isolator contact.
| 16:05 | 16:53 | Halishahar 132/33kV S/S 405T(TR-1) HT Forced S/D Due to Due to 33Kv side CT unbalanced
problem to B phase CT Protection core Short.
| 21:00 |  | Evening peak generation is 13910 MW.
| 04:00 |  | Sehri peak generation 12403 MW
| 04:39 |  | BIPTC S/S 20DF24 Tripped showing PSD relays Due to CB pole discrepancy.
| 05:32 |  | Meghnaghat-Shyampur 230kV Ckt-1 Tripped from Meghnaghat 400/230kV end showing 86.1, 86.2
relays Due to Meghnaghat -Shyampur 230kV ckt 1 SOTF Operated Fault Distance: 9.9 km
and from Shyampur 230/132kV end showing Distance relay. zone-01 relays.
| 06:00 |  | Minimum generation 10439 MW
| 06:34 |  | Magura 132/33kV S/S T-3 (425T) LT Scheduled S/D Due to 33kV Bus, section - 3 bay | [7 empty] | 20.0MW load
|  |  | extention. | [7 empty] | interrup.
| 06:35 |  | Magura 132/33kV S/S T-3 (425T) HT Scheduled S/D Due to 33kV Bus, section - 3 bay | [7 empty] | 20.0MW load
|  |  | extention. | [7 empty] | interrup.
| 06:47 | 07:02 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing Ph-Y, Zone-1, Dist. Send
relays.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 08-03-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 6 | 152636.36 | Demand "0"MW due to gas restriction by Titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 322 | 8078400 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 553163 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 270 | 6500012 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 51.3 | 644400 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 15 | 156960 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 601279 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 453940 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 543600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 519120 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 34 | 405600 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 160 | 1314011 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 115 | 2046672 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 50 | 585600 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 159 | 1938240 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 170773 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 255240 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 345 | 7740454.55 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 350 | 7586839 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 108 | 1872000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2172.3 | 42118939.91
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 105975 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 488640 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1921980 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 226 | 5469897 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 103 | 1119891 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 23 | 100343 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 390117 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 168960 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 25 | 421920 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 26 | 114240 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 16684 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 190691 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 68 | 581270 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 195840 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 15 | 244636 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28052725 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 112800 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 830 | 16276363.64 | ps availability is less
Chattogram Area Total |  |  |  |  | 4898.863 | 2743 | 55972972.64
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 200 | 4537000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 300 | 4322800 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 230 | 6452000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 2037500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1244536 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 70 | 809600 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 24 | 186752 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 89 | 2262260 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 153 | 1431360 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 146 | 3377280 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 52109 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 477700 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1015680 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 447873 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1398 | 28654450
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 18 | 284160 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9700 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 98 | 1531200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 1638000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 191280 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 3 | 78240 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 218520 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 232 | 3951100
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 47192 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 982000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 159 | 3669545.45 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 71 | 1679000 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 42 | 998400 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 96 | 2316500 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 22 | 489336 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7387000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 391 | 9230000 | -
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2325 | 1138 | 26798973.45
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 901 | 21214545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 172 | 4846176 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 537120 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1115 | 25825450 | plant availability zero
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2188 | 52423291
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 31 | 125280 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 125 | 2895000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 1085 | 25688727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 110 | 4760810 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 256800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6676000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3963 | -
Barishal Area Total |  |  |  |  | 2700.36 | 1712 | 40406580.27
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 278336 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 180 | 4607809 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9608145 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 67629 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 327168 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 245952 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 29760 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1449.15 | 33192866 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 268496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 616230 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2134.15 | 49242391
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 53 | 1174254 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 919468 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 27519.12 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 618316 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 190065 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1008720 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 193 | 3938342.12
Eastern Grid Total |  |  |  |  | 17400.108 | 7683.3 | 157496436
Western Grid Total |  |  |  |  | 10985.595 | 6227.15 | 146010604.39
National Grid Total |  |  |  |  | 28385.703 | 13910.45 | 303507040.39
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 08-03-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9338.05 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4031.9 | MW
i) Dhaka area |  |  | 5194.55 |  | MW | i) Khulna area |  |  |  | 1541.7 | MW
ii) Chattogram area |  |  | 1239.5 |  | MW | ii) Barishal area |  |  |  | 398.6 | MW
iii) Cumilla area |  |  | 1263 |  | MW | iii) Rajshahi area |  |  |  | 1321.6 | MW
iv) Mymensingh area |  |  | 1107 |  | MW | iv) Rangpur area |  |  |  | 770 | MW
v) Sylhet area |  |  | 534 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13369.95 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 82 | 20:00 | 133 | Nawabganj | 46.6 | 18:30
2 | AKSML | 19 | 01:00 | 68 | Hathazari | 72 | 22:00 | 134 | Netrakona | 156 | 18:00
3 | Aftabnagar | 34 | 13:00 | 69 | Hatirjheel | 39 | 13:00 | 135 | New | 72 | 12:00
4 | Agargaon | 99 | 14:00 | 70 | Ishurdi | 66 | 13:00 | 136 | Niamatpur | 98 | 13:00
5 | Agrabad | 50 | 12:00 | 71 | Jaldhaka | 78 | 18:00 | 137 | Noapara | 42 | 19:00
6 | Amnura | 36 | 13:00 | 72 | Jamalpur | 117 | 03:00 | 138 | PHP | 9 | 14:00
7 | Ashuganj | 76 | 00:00 | 73 | Jashore | 128 | 18:30 | 139 | Pabna | 79 | 16:00
8 | BSRM | 197 | 17:00 | 74 | Jhenaidah | 90 | 19:00 | 140 | Palashbari | 102 | 18:00
9 | Bagerhat | 76 | 19:00 | 75 | Joydebpur | 141 | 17:00 | 141 | Panchagarh | 52 | 18:00
10 | Bajitpur | 78 | 21:00 | 76 | Joypurhat | 61 | 22:00 | 142 | Patiya | 8 | 19:00
11 | Bakerganj | 12.1 | 21:00 | 77 | Juldah | 15 | 14:00 | 143 | Patuakhali | 53.5 | 21:00
12 | Bakulia | 85 | 19:30 | 78 | KSRM | 15 | 18:00 | 144 | Payra | 32 | 19:30
13 | Banani | 53 | 14:00 | 79 | Kabirpur | 253 | 19:00 | 145 | Postogola | 48 | 13:00
14 | Bangabhaban | 16 | 10:00 | 80 | Kachua | 80 | 16:00 | 146 | Pubail | N/A | N/A
15 | Barapukuria | 63 | 09:00 | 81 | Kaliganj | 26 | 19:30 | 147 | Purbachal | 27 | 13:00
16 | Barguna | 14 | 00:00 | 82 | Kallyanpur | 102 | 19:30 | 148 | Purbasadipur | 133 | 17:00
17 | Barishal | 90 | 20:00 | 83 | Kalurghat | 38 | 14:00 | 149 | Rahanpur | 27 | 19:00
18 | Barishal-230 | 78 | 18:30 | 84 | Kamrangirchar | 79 | 13:00 | 150 | Rahim | 34 | 17:00
19 | Baroaulia | 63 | 12:00 | 85 | Kaptai | N/A | N/A | 151 | Rajbari | 65 | 19:30
20 | Baroirhat | 49 | 19:00 | 86 | Kasba | 32 | 04:00 | 152 | Rajendrapur | 128 | 16:00
21 | Bashundhara | 186 | 13:00 | 87 | Kazla | 95 | 00:00 | 153 | Rajshahi | 104 | 04:00
22 | BashundharaCement | 8 | 15:00 | 88 | Keranigonj | 86 | 13:00 | 154 | Rajshahi-230 | 72 | 18:00
23 | Beanibazar | 60 | 18:30 | 89 | Khagrachori | 28 | 18:00 | 155 | Ramganj | 84 | 18:00
24 | Benapole | 60 | 19:30 | 90 | Khulna | 55 | 14:00 | 156 | Rampur | 35 | 19:00
25 | Bhaluka | 132 | 10:00 | 91 | Khulshi | 186 | 19:00 | 157 | Rangamati | 16 | 18:30
26 | Bhandaria | 44 | 21:00 | 92 | Kishoreganj | 119 | 22:00 | 158 | Rangpur | 143 | 18:00
27 | Bhangura | 40 | 14:00 | 93 | Kodda | 292 | 10:00 | 159 | Ruppur | 2.8 | 15:00
28 | Bheramara(GK) | 52 | 19:00 | 94 | Kulaura | 38 | 18:30 | 160 | SSM | 2 | 02:00
29 | Bhulta | 219 | 15:00 | 95 | Kurigram | 70 | 17:00 | 161 | Saidpur | 108 | 17:00
30 | Bog-Sherpur | 70 | 04:00 | 96 | Kushtia | 122 | 03:00 | 162 | Satkhira | 121 | 19:00
31 | Bogura | 151 | 18:00 | 97 | Laksam | 28 | 21:00 | 163 | Satmasjid | 94 | 19:30
32 | Borhanuddin | 81 | 21:00 | 98 | Lakshmipur | 30 | 21:00 | 164 | Savar | 220 | 12:00
33 | Brahmanbaria | 124 | 18:30 | 99 | Lalbag | 72 | 13:00 | 165 | SevenRings | 18.98 | 17:00
34 | Cantonment | 94 | 17:00 | 100 | Lalmonirhat | 55 | 17:00 | 166 | ShahCement | 30 | 11:00
35 | Chandina | 12 | 19:00 | 101 | MI_Cement | 18.3 | 17:00 | 167 | Shahjadpur | 73 | 17:00
36 | Chandpur | 66 | 16:00 | 102 | Madanganj | 52 | 17:00 | 168 | Shahjibazar | 112 | 21:00
37 | Chandraghona | 31 | 19:00 | 103 | Madaripur | 91 | 20:00 | 169 | Shahmirpur | 56 | 00:00
38 | Chapai | 61 | 19:30 | 104 | Madartek | 70 | 20:00 | 170 | Shariatpur | 69 | 21:00
39 | Charsaidpur | 44 | 00:00 | 105 | Madunaghat | 45 | 19:00 | 171 | Sherpur | 156 | 18:00
40 | Chauddagram | 64 | 17:00 | 106 | Magura | 56 | 19:00 | 172 | Shikalbaha | 23 | 23:00
41 | Chhatak | 29 | 23:00 | 107 | Mahasthangarh | 74 | 21:00 | 173 | Shitalakhya | 80.9 | 14:00
42 | Chowmuhani | 111 | 18:30 | 108 | Maijdee | 40 | 22:00 | 174 | Sholosohor | 40 | 10:00
43 | Chuadanga | 91 | 19:00 | 109 | Manikganj | 115 | 19:00 | 175 | Shyampur | 180 | 14:00
44 | Coxsbazar | 126 | 14:00 | 110 | Maniknagar | 70 | 15:00 | 176 | Siddhirganj | 126 | 12:00
45 | Cumilla(N) | 109 | 19:00 | 111 | Matarbari | 49 | 22:00 | 177 | Sirajganj | 108 | 17:00
46 | Cumilla(S) | 158 | 18:00 | 112 | Matuail | 70 | 00:00 | 178 | Sonargaon | 150 | 23:00
47 | Daganbhuiyan | 27 | 18:30 | 113 | Metrorail_Motijheel | 36 | 14:00 | 179 | Sreemongol | 67 | 21:00
48 | Daudkandi | 134 | 13:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sreepur | 116 | 17:00
49 | DhakaUniversity | 70 | 13:00 | 115 | Millgate | 90 | 10:00 | 181 | Srinagar | 40 | 21:00
50 | Dhamrai | 132 | 08:00 | 116 | Mirpur | 135 | 19:00 | 182 | Sunamganj | 53 | 21:00
51 | Dhanmondi | 111 | 13:00 | 117 | Mirsorai | 51 | 06:00 | 183 | Sylhet | 51 | 22:00
52 | Dohazari | 96 | 20:00 | 118 | Mirzapur | 47 | 10:00 | 184 | Sylhet-132 | 99 | 19:30
53 | Faridpur | 135 | 19:30 | 119 | Mithapukur | 56 | 04:00 | 185 | TK | 21 | 19:00
54 | Fatullah | 90 | 10:00 | 120 | Modern | N/A | N/A | 186 | Tangail | 170 | 18:00
55 | Fenchuganj | 31 | 18:30 | 121 | Mogbazar | 87.5 | 14:00 | 187 | Taraganj | 23 | 13:00
56 | Feni | 86 | 21:00 | 122 | Mongla | 40 | 18:00 | 188 | Tasnim | 32 | 17:00
57 | GPH | 2 | 00:00 | 123 | Motijheel | 43 | 13:00 | 189 | Thakurgaon | 89 | 18:00
58 | Ghatail | 90 | 03:00 | 124 | Muktagacha | 40 | 03:00 | 190 | Tongi | 164 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 93 | 19:00 | 191 | Ullahpara | 35 | 03:00
60 | Ghorashal-230 | 109 | 21:00 | 126 | Muradnagar | 35 | 18:30 | 192 | Ullon | 41 | 21:00
61 | Goalpara | 33 | 18:00 | 127 | Mymensingh | 200 | 17:00 | 193 | Uttara | 77 | 14:00
62 | Gollamari | 92 | 19:00 | 128 | Naogaon | 118 | 21:00 | 194 | UttaraNew | 28 | 22:00
63 | Gopalganj | 91.6 | 19:00 | 129 | Narail | 52.5 | 19:30 | 195 | Zigatola | 74 | 20:00
64 | Gulshan | 100 | 12:00 | 130 | Narinda | 66 | 15:00
65 | Halishahar | 80 | 15:00 | 131 | Narshingdi | 166 | 20:00
66 | HaripurSBU | 125 | 22:00 | 132 | Natore | 134 | 04:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 08-03-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 12602.92 | 0 |  | 12602.92
1:00 | 11846 | 0 |  | 11846
2:00 | 11512.2 | 0 |  | 11512.2
3:00 | 11609.98 | 0 |  | 11609.98
4:00 | 12308.05 | 0 |  | 12308.05
5:00 | 11257.17 | 0 |  | 11257.17
6:00 | 10381.83 | 0 |  | 10381.83
7:00 | 10480.74 | 0 |  | 10480.74
8:00 | 11045.89 | 0 |  | 11045.89
9:00 | 11755.61 | 47 |  | 11804.61
10:00 | 12026.74 | 294 |  | 12333.74
11:00 | 12234.48 | 296 |  | 12543.48
12:00 | 12624.34 | 267 |  | 12903.34
13:00 | 13060.71 | 328 |  | 13403.71
14:00 | 13188.52 | 254 |  | 13453.52
15:00 | 13183.01 | 240 |  | 13434.01
16:00 | 13183.65 | 40 |  | 13225.65
17:00 | 13505.69 | 0 |  | 13505.69
18:00 | 13362.77 | 0 |  | 13362.77
19:00 | 13639.81 | 0 |  | 13639.81
19:30 | 13893.98 | 0 |  | 13893.98
20:00 | 13631.88 | 0 |  | 13631.88
21:00 | 13910.45 | 0 |  | 13910.45
22:00 | 13689.26 | 0 |  | 13689.26
23:00 | 13135.15 | 0 |  | 13135.15
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 08-03-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6496.5 | 6106.42 | 12602.92 | DAILY GENERATION CURVE
00:30 | 6236 | 5988.46 | 12224.46
01:00 | 5975.5 | 5870.5 | 11846 | 08-03-2026
01:30 | 5893.15 | 5785.95 | 11679.1
02:00 | 5810.8 | 5701.4 | 11512.2
02:30 | 5870.55 | 5690.54 | 11561.09
03:00 | 5930.3 | 5679.68 | 11609.98
03:30 | 6100.3 | 5858.715 | 11959.015
04:00 | 6270.3 | 6037.75 | 12308.05
04:30 | 5897.4 | 5885.21 | 11782.61
05:00 | 5524.5 | 5732.67 | 11257.17
05:30 | 5378 | 5441.5 | 10819.5
06:00 | 5231.5 | 5150.33 | 10381.83
06:30 | 5204.955 | 5226.33 | 10431.285
07:00 | 5178.41 | 5302.33 | 10480.74
07:30 | 5389.96 | 5373.355 | 10763.315
08:00 | 5601.51 | 5444.38 | 11045.89
08:30 | 5681.54 | 5719.21 | 11400.75
09:00 | 5761.57 | 5994.04 | 11755.61
09:30 | 5783.79 | 6107.385 | 11891.175
10:00 | 5806.01 | 6220.73 | 12026.74
10:30 | 5894.135 | 6236.475 | 12130.61
11:00 | 5982.26 | 6252.22 | 12234.48
11:30 | 6143.535 | 6285.875 | 12429.41
12:00 | 6304.81 | 6319.53 | 12624.34
12:30 | 6451.595 | 6390.93 | 12842.525
13:00 | 6598.38 | 6462.33 | 13060.71
13:30 | 6705.13 | 6419.485 | 13124.615
14:00 | 6811.88 | 6376.64 | 13188.52
14:30 | 6844.555 | 6341.21 | 13185.765
15:00 | 6877.23 | 6305.78 | 13183.01
15:30 | 6888.185 | 6295.145 | 13183.33
16:00 | 6899.14 | 6284.51 | 13183.65
16:30 | 7066.715 | 6277.955 | 13344.67
17:00 | 7234.29 | 6271.4 | 13505.69
17:30 | 7259.395 | 6174.835 | 13434.23
18:00 | 7284.5 | 6078.27 | 13362.77
18:30 | 7364.5 | 6136.79 | 13501.29
19:00 | 7444.5 | 6195.31 | 13639.81
19:30 | 7766 | 6127.98 | 13893.98
20:00 | 7562.3 | 6069.58 | 13631.88
20:30 | 7622.8 | 6148.365 | 13771.165 |  | Executive Engineer
21:00 | 7683.3 | 6227.15 | 13910.45 |  | Network Operation Division
21:30 | 7580.95 | 6218.905 | 13799.855
22:00 | 7478.6 | 6210.66 | 13689.26
22:30 | 7301.2 | 6111.005 | 13412.205
23:00 | 7123.8 | 6011.35 | 13135.15

## En-Curve
QF-LDC-12
Date | 08-03-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3214 | 1509 | 902 | 0 | 142 | 1438.42 | 80 | 4196 | 0 | 176 | 945.5 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3168 | 1469.75 | 902 | 0 | 142 | 1398.96 | 80 | 4142.5 | 0 | 151 | 770.25 | 0 | 0 | 0 | 0 | 08-03-2026
01:00 | 3122 | 1430.5 | 902 | 0 | 142 | 1359.5 | 80 | 4089 | 0 | 126 | 595 | 0 | 0 | 0 | 0
01:30 | 3141.5 | 1427.5 | 902.5 | 0 | 137 | 1304.95 | 80 | 4057 | 0 | 115 | 513.65 | 0 | 0 | 0 | 0 | Energy Generated | 303.507 |  | MKWHr
02:00 | 3161 | 1424.5 | 903 | 0 | 132 | 1250.4 | 80 | 4025 | 0 | 104 | 432.3 | 0 | 0 | 0 | 0 | Energy not Served | 1.766 |  | MKWHr
02:30 | 3174 | 1438 | 902.5 | 0 | 135 | 1259.54 | 80 | 4023 | 0 | 116.5 | 432.55 | 0 | 0 | 0 | 0 | Total Energy Requirement | 305.273 |  | MKWHr
03:00 | 3187 | 1451.5 | 902 | 0 | 138 | 1268.68 | 80 | 4021 | 0 | 129 | 432.8 | 0 | 0 | 0 | 0
03:30 | 3209.5 | 1515.5 | 902 | 0 | 138 | 1355.715 | 80 | 4128.5 | 0 | 148 | 481.8 | 0 | 0 | 0 | 0
04:00 | 3232 | 1579.5 | 902 | 0 | 138 | 1442.75 | 80 | 4236 | 0 | 167 | 530.8 | 0 | 0 | 0 | 0
04:30 | 3176.5 | 1554.5 | 902 | 0 | 131 | 1401.21 | 80 | 4064 | 0 | 109.5 | 363.9 | 0 | 0 | 0 | 0
05:00 | 3121 | 1529.5 | 902 | 0 | 124 | 1359.67 | 80 | 3892 | 0 | 52 | 197 | 0 | 0 | 0 | 0
05:30 | 3046 | 1508 | 784.5 | 0 | 119 | 1293.5 | 80 | 3808 | 0 | 26 | 154.5 | 0 | 0 | 0 | 0
06:00 | 2971 | 1486.5 | 667 | 0 | 114 | 1227.33 | 80 | 3724 | 0 | 0 | 112 | 0 | 0 | 0 | 0
06:30 | 2959.5 | 1455.15 | 726 | 0 | 107 | 1231.725 | 80 | 3737.5 | 20.41 | 0 | 114 | 0 | 0 | 0 | 0
07:00 | 2948 | 1423.8 | 785 | 0 | 100 | 1236.12 | 80 | 3751 | 40.82 | 0 | 116 | 0 | 0 | 0 | 0
07:30 | 3010 | 1476.4 | 742.5 | 0 | 108 | 1239.53 | 80 | 3856 | 93.885 | 28 | 129 | 0 | 0 | 0 | 0
08:00 | 3072 | 1529 | 700 | 0 | 116 | 1242.94 | 80 | 3961 | 146.95 | 56 | 142 | 0 | 0 | 0 | 0
08:30 | 3073 | 1528.25 | 801 | 0 | 119 | 1272.775 | 80 | 4055.5 | 225.225 | 79.5 | 166.5 | 0 | 0 | 0 | 23.5
09:00 | 3074 | 1527.5 | 902 | 0 | 122 | 1302.61 | 80 | 4150 | 303.5 | 103 | 191 | 0 | 0 | 0 | 47
09:30 | 3032 | 1498.5 | 902 | 0 | 123 | 1326.535 | 80 | 4181.5 | 383.64 | 103 | 261 | 0 | 0 | 0 | 170.5
10:00 | 2990 | 1469.5 | 902 | 0 | 124 | 1350.46 | 80 | 4213 | 463.78 | 103 | 331 | 0 | 0 | 0 | 294
10:30 | 2990.5 | 1433.5 | 902 | 0 | 129 | 1358.39 | 80 | 4222.5 | 518.72 | 103 | 393 | 0 | 0 | 0 | 295
11:00 | 2991 | 1397.5 | 902 | 0 | 134 | 1366.32 | 80 | 4232 | 573.66 | 103 | 455 | 0 | 0 | 0 | 296
11:30 | 3050.5 | 1423.5 | 902 | 0 | 135 | 1369.12 | 80 | 4318.5 | 585.29 | 103 | 458.5 | 0 | 0 | 4 | 281.5
12:00 | 3110 | 1449.5 | 902 | 0 | 136 | 1371.92 | 80 | 4405 | 596.92 | 103 | 462 | 0 | 0 | 8 | 267
12:30 | 3156.5 | 1469.5 | 902 | 0 | 140 | 1414.19 | 80 | 4449 | 582.085 | 103 | 533.75 | 0 | 0 | 12.5 | 297.5
13:00 | 3203 | 1489.5 | 902 | 0 | 144 | 1456.46 | 80 | 4493 | 567.25 | 103 | 605.5 | 0 | 0 | 17 | 328
13:30 | 3245.5 | 1482.5 | 902 | 0 | 150 | 1452.27 | 80 | 4477.5 | 543.745 | 103 | 668.1 | 0 | 0 | 20 | 291
14:00 | 3288 | 1475.5 | 902 | 0 | 156 | 1448.08 | 80 | 4462 | 520.24 | 103 | 730.7 | 0 | 0 | 23 | 254
14:30 | 3282.5 | 1484 | 902 | 0 | 153 | 1448.94 | 80 | 4509.5 | 440.325 | 121.5 | 740.5 | 0 | 0 | 23.5 | 247
15:00 | 3277 | 1492.5 | 902 | 0 | 150 | 1449.8 | 80 | 4557 | 360.41 | 140 | 750.3 | 0 | 0 | 24 | 240
15:30 | 3221 | 1483.5 | 902 | 0 | 147 | 1450.375 | 80 | 4585.5 | 290.305 | 158 | 845.65 | 0 | 0 | 20 | 140
16:00 | 3165 | 1474.5 | 902 | 0 | 144 | 1450.95 | 80 | 4614 | 220.2 | 176 | 941 | 0 | 0 | 16 | 40
16:30 | 3149 | 1481.5 | 902 | 0 | 147 | 1449.435 | 80 | 4619.5 | 146.435 | 226 | 1133.3 | 0 | 0 | 10.5 | 20
17:00 | 3133 | 1488.5 | 902 | 0 | 150 | 1447.92 | 80 | 4625 | 72.67 | 276 | 1325.6 | 0 | 0 | 5 | 0
17:30 | 3051 | 1461.75 | 902 | 0 | 152 | 1450.905 | 80 | 4507.5 | 36.525 | 294 | 1490.05 | 0 | 0 | 8.5 | 0
18:00 | 2969 | 1435 | 902 | 0 | 154 | 1453.89 | 80 | 4390 | 0.38 | 312 | 1654.5 | 0 | 0 | 12 | 0
18:30 | 3036 | 1418 | 902 | 0 | 151 | 1447.6 | 80 | 4440.5 | 0.19 | 304.5 | 1712 | 0 | 0 | 9.5 | 0
19:00 | 3103 | 1401 | 902 | 0 | 148 | 1441.31 | 80 | 4491 | 0 | 297 | 1769.5 | 0 | 0 | 7 | 0
19:30 | 2977 | 1419 | 902 | 0 | 146 | 1426.98 | 80 | 4494 | 0 | 341 | 2106 | 0 | 0 | 2 | 0
20:00 | 3035 | 1457 | 902 | 0 | 152 | 1416.58 | 80 | 4513 | 0 | 316 | 1760.3 | 0 | 0 | 0 | 0
20:30 | 3090.5 | 1473.5 | 901.5 | 0 | 149 | 1432.865 | 80 | 4563.5 | 0 | 312.5 | 1767.8 | 0 | 0 | 0 | 0
21:00 | 3146 | 1490 | 901 | 0 | 146 | 1449.15 | 80 | 4614 | 0 | 309 | 1775.3 | 0 | 0 | 0 | 0
21:30 | 3133.5 | 1477 | 901.5 | 0 | 152 | 1455.405 | 80 | 4610.5 | 0 | 278.5 | 1711.45 | 0 | 0 | 0 | 0
22:00 | 3121 | 1464 | 902 | 0 | 158 | 1461.66 | 80 | 4607 | 0 | 248 | 1647.6 | 0 | 0 | 0 | 0
22:30 | 3119 | 1456.5 | 902 | 0 | 158 | 1456.505 | 80 | 4608 | 0 | 207.5 | 1424.7 | 0 | 0 | 0 | 0
23:00 | 3117 | 1449 | 902 | 0 | 158 | 1451.35 | 80 | 4609 | 0 | 167 | 1201.8 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 08-03-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 390 | 19:30 | 349 | 18:30 | Madunaghat | 403 | 06:00 | 391 | 14:00
Amtali | 415 | 08:00 | 406 | 12:00 | Meghnaghat | 395 | 18:30 | 376 | 13:00
Ashuganj | 403 | 18:30 | 376 | 12:00 | Payra | 416 | 05:00 | 408 | 15:00
Bhulta | 399 | 18:00 | 372 | 12:00 | Rahanpur | 410 | 06:00 | 396 | 16:00
Bibiana | 405 | 05:00 | 395 | 12:00 | Rampal | 406 | 06:00 | 394 | 12:00
BIPTC | 405 | 06:00 | 391 | 12:00
Bogura | 399 | 06:00 | 381 | 12:00
Gopalganj | 404 | 06:00 | 369 | 19:00
Kaliakoir | 390 | 18:00 | 367 | 12:00
Korerhat | 402 | 06:00 | 388 | 14:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 234 | 18:30 | 219 | 15:00 | Jhenaidah | 234 | 05:00 | 221 | 12:00
AKSML | 229 | 18:00 | 221 | 12:00 | Kachua | 230 | 00:00 | 220 | 16:00
Aminbazar | 233 | 06:00 | 220 | 12:00 | Kaliakoir | 237 | 18:00 | 220 | 12:00
Ashuganj | 230 | 18:00 | 219 | 13:00 | Keranigonj | 232 | 06:00 | 217 | 15:00
Ashuganj-400 | 232 | 18:30 | 216 | 12:00 | Khulna(S) | 237 | 06:00 | 224 | 12:00
Baghabari | 233 | 02:00 | 223 | 09:00 | Korerhat | 229 | 06:00 | 220 | 14:00
Barapukuria | 221 | 06:00 | 210 | 08:00 | Madunaghat | 229 | 06:00 | 222 | 12:00
Barapukuria-230 | 221 | 6:00 | 212 | 9:00 | Madunaghat-400 | 230 | 07:00 | 223 | 13:00
Barishal | 231 | 06:00 | 223 | 15:00 | Maniknagar | 230 | 18:30 | 216 | 15:00
Bheramara | 234 | 02:00 | 221 | 09:00 | Meghnaghat | 238 | 00:00 | 228 | 11:00
Bhulta | 232 | 18:00 | 217 | 12:00 | Meghnaghat-400 | 233 | 06:00 | 221 | 12:00
Bibiana | 234 | 22:00 | 228 | 15:00 | Mirsorai | 236 | 18:30 | 228 | 15:00
BIPTC | 237 | 02:00 | 221 | 09:00 | Rajshahi | 233 | 03:00 | 221 | 09:00
Bogura | 236 | 02:00 | 225 | 09:00 | Rampal | 235 | 06:00 | 227 | 09:00
Bogura-400 | 236 | 06:00 | 225 | 09:00 | Rampur | N/A | N/A | N/A | N/A
Borhanuddin | 236 | 06:00 | 230 | 19:00 | Rampura | 230 | 18:30 | 214 | 13:00
BSRM | 229 | 06:00 | 219 | 16:00 | Shikalbaha | 230 | 19:00 | 221 | 12:00
Chowmuhani | 229 | 06:00 | 224 | 09:00 | Shyampur | 232 | 18:30 | 218 | 15:00
Cumilla(N) | 229 | 19:30 | 220 | 15:00 | Siddhirganj | 229 | 03:00 | 219 | 15:00
Faridpur | 227 | 05:00 | 217 | 15:00 | Sirajgonj | 237 | 02:00 | 229 | 09:00
Fenchuganj | 237 | 18:30 | 231 | 14:00 | Sreepur | 225 | 02:00 | 213 | 16:00
Feni | 231 | 06:00 | 221 | 14:00 | Tongi | 230 | 23:00 | 216 | 11:00
Ghorashal | 230 | 00:00 | 220 | 11:00
Ghorashal-230 | 231 | 18:30 | 214 | 15:00
Gopalganj | 227 | 06:00 | 218 | 12:00
GPH | 230 | 21:00 | 220 | 06:00
Haripur | 232 | 18:30 | 218 | 15:00
Hasnabad | 232 | 18:30 | 218 | 15:00
Hathazari | 228 | 03:00 | 217 | 14:00
Ishurdi | 236 | 01:00 | 223 | 09:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 18:30 | 127 | 15:00 | Magura | 135 | 06:00 | 123 | 12:00
Agargaon | 137 | 02:00 | 129 | 12:00 | Mahasthangarh | 134 | 18:30 | 124 | 09:00
Agrabad | 132 | 19:30 | 124 | 14:00 | Maijdee | 128 | 06:00 | 122 | 16:00
AKS | 130 | 18:00 | 125 | 11:00 | Manikganj | 129 | 05:00 | 119 | 15:00
Aminbazar | 136 | 00:00 | 126 | 09:00 | Maniknagar | 133 | 18:30 | 118 | 15:00
Amnura | 135 | 02:00 | 127 | 09:00 | Matarbari | 121 | 21:00 | 111 | 14:00
Ashuganj | 140 | 06:00 | 133 | 12:00 | Matuail | 132 | 18:00 | 123 | 15:00
Bagerhat | 133 | 06:00 | 118 | 15:00 | Metrorail_Motijheel | 133 | 18:30 | 118 | 15:00
Bajitpur | 130 | 05:00 | 124 | 11:00 | Metrorail_Uttara | 134 | 06:00 | 123 | 12:00
Bakerganj | 135 | 06:00 | 130 | 12:00 | Millgate | 134 | 06:00 | 123 | 09:00
Bakulia | 132 | 19:30 | 126 | 14:00 | Mirpur | 134 | 00:00 | 124 | 15:00
Banani | 137 | 18:30 | 127 | 12:00 | Mirzapur | 133 | 19:30 | 124 | 11:00
Bangabhaban | 131 | 18:30 | 118 | 15:00 | Mithapukur | 134 | 18:30 | 122 | 09:00
Barapukuria | 137 | 06:00 | 126 | 08:00 | MI_Cement | 134 | 02:00 | 122 | 12:00
Barguna | 135 | 06:00 | 130 | 12:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 133 | 01:00 | 128 | 15:00 | Mogbazar | 136 | 02:00 | 127 | 15:00
Barishal-230 | 135 | 06:00 | 129 | 14:00 | Mongla | 133 | 05:00 | 118 | 16:00
Baroaulia | 133 | 18:00 | 128 | 09:00 | Motijheel | 131 | 18:30 | 118 | 15:00
Baroirhat | 131 | 01:00 | 125 | 15:00 | Muktagacha | 129 | 17:00 | 117 | 11:00
Bashundhara | 135 | 05:00 | 126 | 13:00 | Munshiganj | 129 | 19:30 | 122 | 09:00
BashundharaCement | 131 | 00:00 | 124 | 09:00 | Muradnagar | 131 | 18:00 | 122 | 13:00
Beanibazar | 129 | 05:00 | 123 | 13:00 | Mymensingh | 128 | 18:30 | 114 | 17:00
Benapole | 132 | 06:00 | 120 | 12:00 | Naogaon | 133 | 06:00 | 122 | 09:00
Bhaluka | 135 | 18:30 | 124 | 14:00 | Narail | 134 | 06:00 | 122 | 14:00
Bhandaria | 134 | 05:00 | 126 | 15:00 | Narinda | 133 | 18:30 | 118 | 15:00
Bhangura | 134 | 05:00 | 126 | 08:00 | Narshingdi | 127 | 18:30 | 117 | 09:00
Bheramara | 136 | 01:00 | 131 | 10:00 | Natore | 134 | 05:00 | 127 | 08:00
Bheramara(GK) | 136 | 03:00 | 131 | 09:00 | Nawabganj | 136 | 06:00 | 126 | 12:00
Bhulta | 127 | 18:30 | 118 | 15:00 | Netrakona | 125 | 01:00 | 111 | 16:00
Bog-Sherpur | 135 | 02:00 | 126 | 09:00 | New | 136 | 18:00 | 124 | 09:00
Bogura | 136 | 06:00 | 128 | 09:00 | Niamatpur | 135 | 05:00 | 130 | 09:00
Bogura-230 | 136 | 02:00 | 128 | 09:00 | Noapara | 135 | 05:00 | 124 | 12:00
Brahmanbaria | 135 | 06:00 | 127 | 12:00 | Pabna | 135 | 01:00 | 128 | 12:00
Cantonment | 137 | 01:00 | 128 | 15:00 | Palashbari | 132 | 18:30 | 120 | 09:00
Chandina | 133 | 06:00 | 126 | 15:00 | Panchagarh | 137 | 18:00 | 122 | 09:00
Chandpur | 134 | 20:00 | 127 | 09:00 | Patiya | 131 | 18:00 | 124 | 14:00
Chandraghona | 133 | 00:00 | 128 | 14:00 | Patuakhali | 133 | 19:30 | 129 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 135 | 05:00 | 130 | 16:00 | Payra | 136 | 07:00 | 133 | 12:00
Charsaidpur | 130 | 01:00 | 122 | 13:00 | PHP | 131 | 06:00 | 125 | 13:00
Chauddagram | 130 | 06:00 | 124 | 14:00 | Postogola | 134 | 06:00 | 125 | 21:00
Chhatak | 128 | 04:00 | 122 | 13:00 | Pubail | N/A | N/A | N/A | N/A
Chowmuhani | 128 | 18:00 | 123 | 15:00 | Purbachal | 135 | 06:00 | 127 | 09:00
Chuadanga | 134 | 05:00 | 123 | 09:00 | Purbasadipur | 132 | 18:30 | 120 | 09:00
Coxsbazar | 118 | 19:30 | 112 | 14:00 | Rahanpur | 137 | 05:00 | 132 | 09:00
Cumilla(N) | 132 | 00:00 | 126 | 14:00 | Rahanpur-400 | 137 | 02:00 | 132 | 12:00
Cumilla(S) | 132 | 06:00 | 119 | 14:00 | Rahim | 130 | 06:00 | 122 | 13:00
Daganbhuiyan | 130 | 06:00 | 124 | 14:00 | Rajbari | 130 | 05:00 | 123 | 15:00
Daudkandi | 127 | 18:30 | 119 | 15:00 | Rajendrapur | 135 | 03:00 | 124 | 16:00
DhakaUniversity | 135 | 05:00 | 127 | 15:00 | Rajshahi | 134 | 01:00 | 126 | 09:00
Dhamrai | 139 | 18:30 | 128 | 15:00 | Rajshahi-230 | 134 | 02:00 | 126 | 12:00
Dhanmondi | 136 | 06:00 | 127 | 12:00 | Ramganj | 129 | 22:00 | 123 | 14:00
Dohazari | 128 | 18:00 | 122 | 14:00 | Rampur | 132 | 18:00 | 125 | 14:00
Faridpur | 132 | 06:00 | 125 | 15:00 | Rampura | 137 | 18:30 | 126 | 13:00
Fatullah | 136 | 11:00 | 123 | 12:00 | Rangamati | 135 | 07:00 | 127 | 14:00
Fenchuganj | 134 | 06:00 | 130 | 14:00 | Rangpur | 133 | 00:00 | 123 | 09:00
Feni | 127 | 00:00 | 123 | 14:00 | Ruppur | 137 | 05:00 | 131 | 09:00
Feni-230 | 130 | 06:00 | 124 | 14:00 | Saidpur | 134 | 06:00 | 123 | 09:00
Ghatail | 128 | 17:00 | 116 | 11:00 | Satkhira | 134 | 06:00 | 121 | 19:00
Ghorashal | 137 | 19:00 | 128 | 13:00 | Satmasjid | 137 | 02:00 | 127 | 13:00
Goalpara | 137 | 06:00 | 127 | 12:00 | Savar | 137 | 18:00 | 124 | 09:00
Gollamari | 136 | 06:00 | 127 | 15:00 | SevenRings | 138 | 18:30 | 127 | 13:00
Gopalganj | 134 | 06:00 | 127 | 14:00 | ShahCement | 130 | 01:00 | 122 | 13:00
Gopalganj-400 | 135 | 06:00 | 129 | 12:00 | Shahjadpur | 138 | 05:00 | 130 | 10:00
Gulshan | 137 | 18:30 | 127 | 12:00 | Shahjibazar | 134 | 06:00 | 124 | 14:00
Halishahar | 133 | 19:30 | 125 | 14:00 | Shahmirpur | 133 | 19:00 | 126 | 15:00
Haripur | 132 | 18:30 | 123 | 15:00 | Shariatpur | 131 | 10:00 | 126 | 15:00
HaripurSBU | 132 | 18:30 | 124 | 12:00 | Sherpur | 127 | 04:00 | 112 | 11:00
Hasnabad | 133 | 01:00 | 125 | 15:00 | Shikalbaha | 122 | 20:00 | 118 | 14:00
Hathazari | 134 | 18:00 | 127 | 14:00 | Shikalbaha-230 | 132 | 01:00 | 128 | 12:00
Hatirjheel | 136 | 06:00 | 127 | 15:00 | Shitalakhya | 133 | 06:00 | 122 | 15:00
Ishurdi | 138 | 02:00 | 132 | 09:00 | Sholosohor | 133 | 06:00 | 127 | 14:00
Jaldhaka | 131 | 06:00 | 122 | 09:00 | Shyampur | 134 | 18:00 | 123 | 12:00
Jamalpur | 131 | 17:00 | 116 | 11:00 | Shyampur-230 | 134 | 18:30 | 125 | 12:00
Jashore | 134 | 06:00 | 121 | 15:00 | Siddhirganj | 131 | 18:00 | 124 | 12:00
Jhenaidah | 135 | 04:00 | 116 | 12:00 | Sirajganj | 133 | 01:00 | 124 | 09:00
Jhenaidah-230 | 136 | 05:00 | 126 | 12:00 | Sonargaon | 129 | 18:00 | 122 | 12:00
Joydebpur | 133 | 18:00 | 123 | 09:00 | Sreemongol | 129 | 06:00 | 124 | 14:00
Joypurhat | 130 | 03:00 | 117 | 09:00 | Sreepur | 137 | 04:00 | 127 | 16:00
Juldah | 133 | 19:30 | 126 | 14:00 | Srinagar | 136 | 06:00 | 127 | 12:00
Kabirpur | 138 | 19:30 | 120 | 15:00 | SSM | 136 | 18:00 | 130 | 13:00
Kachua | 131 | 00:00 | 126 | 14:00 | Sunamganj | 127 | 07:00 | 120 | 13:00
Kaliakoir | 141 | 18:00 | 131 | 12:00 | Sylhet | 130 | 06:00 | 124 | 14:00
Kaliganj | 138 | 04:00 | 125 | 12:00 | Sylhet-132 | 130 | 05:00 | 126 | 13:00
Kallyanpur | 136 | 00:00 | 125 | 09:00 | Tangail | 128 | 06:00 | 119 | 11:00
Kalurghat | 133 | 18:00 | 128 | 12:00 | Taraganj | 132 | 06:00 | 121 | 09:00
Kamrangirchar | 136 | 06:00 | 123 | 15:00 | Tasnim | 129 | 06:00 | 122 | 12:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 136 | 18:30 | 120 | 09:00
Kasba | 130 | 06:00 | 122 | 13:00 | TK | 133 | 18:00 | 128 | 12:00
Kazla | 131 | 18:30 | 118 | 13:00 | Tongi | 135 | 04:00 | 126 | 11:00
Keranigonj | 136 | 06:00 | 126 | 15:00 | Ullahpara | 134 | 01:00 | 126 | 09:00
Khagrachori | 132 | 19:30 | 126 | 12:00 | Ullon | 135 | 06:00 | 127 | 12:00
Khulna | 136 | 06:00 | 126 | 12:00 | Uttara | 135 | 03:00 | 124 | 15:00
Khulna(S) | 137 | 06:00 | 127 | 15:00 | UttaraNew | 134 | 06:00 | 123 | 12:00
Khulshi | 131 | 19:30 | 124 | 15:00 | Zigatola | 136 | 06:00 | 126 | 13:00
Kishoreganj | 130 | 02:00 | 120 | 14:00
Kodda | 138 | 18:30 | 121 | 16:00
Korerhat | 133 | 06:00 | 127 | 14:00
KSRM | 133 | 19:00 | 126 | 14:00
Kulaura | 134 | 06:00 | 129 | 14:00
Kurigram | 130 | 06:00 | 118 | 08:00
Kushtia | 127 | 00:00 | 122 | 12:00
Laksam | 131 | 19:30 | 125 | 16:00
Lakshmipur | 128 | 06:00 | 122 | 16:00
Lalbag | 135 | 02:00 | 126 | 12:00
Lalmonirhat | 129 | 00:00 | 121 | 17:00
Madanganj | 131 | 00:00 | 124 | 09:00
Madaripur | 134 | 06:00 | 128 | 14:00
Madartek | 135 | 18:30 | 126 | 15:00
Madunaghat | 133 | 02:00 | 128 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division