## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 11-03-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-03-2026 | during | 11-03-2026 | during | 11-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 6 | 6 | 97.7 | 97.7 | 7 | 7 | Demand "05"MW due to gas restiction by Titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 348 | 292 | 412 | 412 | 412 | 412 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 9 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 328 | 260 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 16.5 | 48.8 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 62 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 24 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 34 | 33 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 300 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 70 | 145 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 75 | 148 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 28 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 330 | 350 | 584 | 584 | 300 | 300 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 250 | 320 | 583 | 583 | 300 | 300 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 75 | 125 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1734.5 | 2401.8 | 5945.22 | 5915.22 | 2704.05 | 2692.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 80 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 150 | 220 | 220 | 220 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 27 | 29 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 38 | 0 | 0 | 56 | 64 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 47 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 28 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 87 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.29 | 0 | 3.28 | 0 | 3.28 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 33 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 38 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 107 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1049 | 1200 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 830 | 830 | 830 | 830 | 840 | 840 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2226.29 | 2793.5 | 3663.14 | 3656.86 | 3483.78 | 3485.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 209 | 205 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 280 | 280 | 353.35 | 353.35 | 300 | 300 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 318.81 | 318.81 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 225 | 260 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 1 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 150 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 15 | 32 | 32 | 32 | 32 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 163 | 163 | 100 | 100 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 178 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 172 | 176 | 84 | 80 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 17 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 36 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 13 | 96 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 65 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1134 | 1589 | 2736.51 | 2672.51 | 1946.2 | 1886.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-03-2026 | during | 11-03-2026 | during | 11-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 10 | 11 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.4 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 78 | 60 | 80 | 60 | 80 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 69 | 99 | 70 | 115 | 70 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 42.46 | 0 | 45.12 | 0 | 45.12 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 1 | 0 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 35 | 54.5 | 54.5 | 17 | 35 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 181.86 | 223 | 411.12 | 429 | 200.12 | 236
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 41 | 41 | 41 | 42 | 42 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 150 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 70 | 71 | 70 | 70 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 41 | 41 | 83 | 83 | 42 | 42 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 97 | 95 | 100 | 100 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 20 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 305 | 341 | 341 | 150 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 406 | 357 | 385 | 385 | 385 | 385
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1158 | 1080 | 1258 | 1258 | 904 | 1061
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 902 | 713 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 161 | 151 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 63 | 0 | 86 | 0 | 86 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1112 | 1070 | 0 | 0 | 1148.28 | 1148.28
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2238 | 1934 | 2364 | 2278 | 2541.38 | 2455.38
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 80 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 125 | 120 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 1050 | 1080 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 103 | 150 | 150 | 15 | 15 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.55 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2700.36 | 1702.55 | 1910 | 2003.32 | 2002.32 | 1868.32 | 1867.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 43.67 | 0 | 48 | 0 | 48 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 15 | 48 | 48 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 180 | 172 | 220 | 220 | 180 | 180 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 19 | 21 | 21 | 21 | 21 | Machine problem and fuel shortage
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 32 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 26 | 34 | 34 | 34 | 34 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.02 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1449 | 1453 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 18.6 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 96 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2204.29 | 2357 | 3163.57 | 2948.87 | 2609.57 | 2394.87
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 52 | 55 | 55 | 55 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 107 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.8 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 25 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 150 | 0 | 162.84 | 0 | 162.84 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 266.8 | 277 | 515.04 | 317 | 426.04 | 228
System Total |  |  |  |  | 28823.2 | 28385.703 | 12846.29 | 14565.3 | 22059.92 | 21477.78 | 16683.46 | 16306.32
Forecast Scenario (11-03-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13230 |  | 0 |  | 13230
|  |  |  | 1:00 | 12705 |  | 0 |  | 12705
|  |  |  | 2:00 | 12407 |  | 0 |  | 12407
|  |  |  | 3:00 | 12306 |  | 0 |  | 12306
|  |  |  | 4:00 | 13028 |  | 0 |  | 13028
|  |  |  | 5:00 | 11758 |  | 0 |  | 11758
|  |  |  | 6:00 | 10847 |  | 0 |  | 10847
|  |  |  | 7:00 | 11010 |  | 0 |  | 11010
|  |  |  | 8:00 | 11705 |  | 0 |  | 11705
|  |  |  | 9:00 | 12302 |  | 0 |  | 12302
|  |  |  | 10:00 | 12833 |  | 0 |  | 12833
|  |  |  | 11:00 | 13303 |  | 0 |  | 13303
|  |  |  | 12:00 | 13553 |  | 0 |  | 13553
|  |  |  | 13:00 | 13702 |  | 0 |  | 13702
|  |  |  | 14:00 | 13954 |  | 0 |  | 13954
|  |  |  | 15:00 | 14005 |  | 0 |  | 14005
|  |  |  | 16:00 | 13953 |  | 0 |  | 13953
|  |  |  | 17:00 | 14464 |  | 0 |  | 14464
|  |  |  | 18:00 | 14300 |  | 0 |  | 14300
|  |  |  | 18:30 | 14600 |  | 0 |  | 14600
|  |  |  | 19:00 | 14755 |  | 0 |  | 14755
|  |  |  | 19:30 | 14965 |  | 0 |  | 14965
|  |  |  | 20:00 | 14847 |  | 0 |  | 14847
|  |  |  | 21:00 | 14951 |  | 0 |  | 14951
|  |  |  | 22:00 | 14650 |  | 0 |  | 14650
|  |  |  | 23:00 | 13900 |  | 0 |  | 13900
Probable Maximum Temperature: |  |  | 32.20°C
Probable Maximum Demand at Day Peak: |  |  | 13553.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14965.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14965.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 309.83966 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:13 hrs on 11-03-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 10-03-2026 | [28 empty] | Date: | 10-03-2026 | [28 empty] | Date: | 10-03-2026 | [28 empty] | Date: | 10-03-2026 | [28 empty] | Date: | 10-03-2026 | [17 empty] | Date: | 10-03-2026
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [17 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 6 | 295 | 0 | 0 | 45 | 17 | 113 | 0 | 15 | 30 | 35 | 125 | 0 | 0 | 0 | 305 | 0 | 35 | 300 | 0 | 0 | 0 | 70 | 22 | 21 | 0 | 320 | 15 | 16 | 0 | 0 | 0 | 51 | 0 | 0 | 12 | 12 | 0 | 80 | 82 | 26 | 830 | 0 | 0 | 50 | 0 | 89 | 226 | 0 | 0 | 0 | 1162 | 0 | 30 | 0 | 0 | 280 | 230 | 51 | 0 | 206 | 0 | 94 | 90 | 100 | 0 | 20 | 0 | 154 | 0 | 0 | 0 | 310 | 0 | 381 | 41 | 0 | 153 | 0 | 22 | 0 | 42 | 0 | 70 | 0 | 96 | 0 | 59 | 48 | 6 | 0 | 0 | 2 | 6907 | 900 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1096 | 0 | 0 | 0 | 1451.37 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 54 | 35 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 125 | 110 | 0 | 0 | 1030 | 0 | 5923.37 | 12830.37 | 89.69
01:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 9 | 293 | 0 | 0 | 33.4 | 17 | 97 | 0 | 15 | 30 | 35 | 111 | 0 | 0 | 0 | 305 | 0 | 17 | 300 | 0 | 0 | 0 | 52 | 22 | 0 | 0 | 320 | 15 | 16 | 0 | 0 | 0 | 51 | 0 | 0 | 12 | 12 | 0 | 80 | 34 | 29 | 830 | 0 | 0 | 50 | 0 | 90 | 227 | 0 | 0 | 0 | 1065 | 0 | 12 | 0 | 0 | 280 | 230 | 51 | 0 | 140 | 0 | 61 | 90 | 34 | 0 | 20 | 0 | 154 | 0 | 0 | 0 | 305 | 0 | 362 | 41 | 0 | 152 | 0 | 22 | 0 | 42 | 0 | 70 | 0 | 96 | 0 | 59 | 48 | 9 | 0 | 0 | 0 | 6462.4 | 900 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1093 | 0 | 0 | 0 | 1450.62 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 52 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 125 | 130 | 0 | 0 | 1035 | 0 | 5842.62 | 12305.02 | 89.68
02:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 7 | 289 | 0 | 0 | 29.4 | 17 | 97 | 0 | 15 | 30 | 17 | 109 | 0 | 0 | 0 | 305 | 0 | 17 | 300 | 0 | 0 | 0 | 52 | 21 | 21 | 0 | 320 | 13 | 16 | 0 | 0 | 0 | 51 | 0 | 0 | 12 | 12 | 0 | 80 | 34 | 29 | 830 | 0 | 0 | 50 | 0 | 67 | 227 | 0 | 0 | 0 | 1000 | 0 | 12 | 0 | 0 | 280 | 230 | 51 | 0 | 140 | 0 | 58 | 90 | 32 | 0 | 20 | 0 | 144 | 0 | 0 | 0 | 310 | 0 | 376 | 41 | 0 | 151 | 0 | 17 | 0 | 42 | 0 | 72 | 0 | 96 | 0 | 59 | 48 | 10 | 0 | 0 | 0 | 6363.4 | 899 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1017 | 0 | 0 | 0 | 1320.88 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 50 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 125 | 220 | 0 | 0 | 1030 | 0 | 5643.88 | 12007.28 | 89.67
03:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 7 | 319 | 0 | 0 | 32.7 | 0 | 97 | 0 | 15 | 30 | 17 | 120 | 0 | 0 | 0 | 330 | 0 | 17 | 300 | 0 | 0 | 0 | 70 | 21 | 21 | 0 | 345 | 15 | 16 | 0 | 0 | 0 | 51 | 0 | 0 | 12 | 12 | 0 | 80 | 33 | 24 | 830 | 0 | 0 | 50 | 0 | 66 | 226 | 0 | 0 | 0 | 612 | 0 | 12 | 0 | 0 | 280 | 230 | 51 | 0 | 140 | 0 | 65 | 91 | 33 | 0 | 20 | 0 | 140 | 0 | 0 | 0 | 305 | 0 | 411 | 41 | 0 | 160 | 0 | 17 | 0 | 42 | 0 | 70 | 0 | 96 | 0 | 96 | 58 | 10 | 0 | 0 | 0 | 6153.7 | 900 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1014 | 0 | 0 | 0 | 1335.08 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 52 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 125 | 220 | 0 | 0 | 1070 | 0 | 5752.08 | 11905.78 | 89.66
04:00 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 7 | 316 | 0 | 0 | 40.6 | 0 | 102 | 30 | 80 | 40 | 22 | 154 | 0 | 0 | 0 | 385 | 0 | 35 | 310 | 0 | 0 | 0 | 108 | 14 | 22 | 0 | 300 | 28 | 16 | 0 | 0 | 0 | 33 | 0 | 0 | 38 | 38 | 0 | 80 | 60 | 24 | 830 | 0 | 0 | 50 | 0 | 83 | 226 | 0 | 0 | 0 | 612 | 0 | 36 | 0 | 0 | 280 | 230 | 51 | 0 | 140 | 0 | 79 | 91 | 64 | 0 | 20 | 0 | 148 | 0 | 0 | 0 | 305 | 0 | 359 | 41 | 0 | 157 | 0 | 17 | 0 | 42 | 0 | 70 | 0 | 96 | 0 | 98 | 58 | 10 | 0 | 0 | 0 | 6505.6 | 899 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1082 | 0 | 0 | 0 | 1447.84 | 0 | 0 | 0 | 20 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 51 | 113 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254 | 125 | 220 | 0 | 0 | 1085 | 0 | 6122.84 | 12628.44 | 89.65
05:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 303 | 0 | 0 | 41.7 | 0 | 111 | 0 | 0 | 15 | 17 | 90 | 0 | 0 | 0 | 295 | 0 | 0 | 280 | 0 | 0 | 0 | 52 | 14 | 22 | 0 | 315 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 92 | 24 | 830 | 0 | 0 | 19 | 0 | 85 | 226 | 0 | 0 | 0 | 612 | 0 | 30 | 0 | 0 | 280 | 230 | 51 | 0 | 140 | 0 | 62 | 91 | 17 | 0 | 20 | 0 | 138 | 0 | 0 | 0 | 300 | 0 | 330 | 41 | 0 | 157 | 0 | 17 | 0 | 42 | 0 | 70 | 0 | 96 | 0 | 60 | 58 | 10 | 0 | 0 | 0 | 5780.7 | 900 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998 | 0 | 0 | 0 | 1452.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 52 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 125 | 220 | 0 | 0 | 1000 | 0 | 5577.74 | 11358.44 | 89.64
06:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 5 | 311 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 19 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 21 | 830 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 0 | 280 | 230 | 51 | 0 | 140 | 0 | 0 | 91 | 0 | 0 | 20 | 0 | 124 | 0 | 0 | 0 | 305 | 0 | 371 | 41 | 0 | 158 | 0 | 17 | 0 | 42 | 0 | 70 | 0 | 96 | 0 | 45 | 35 | 10 | 0 | 0 | 0 | 5158 | 618 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 0 | 0 | 0 | 1452.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 125 | 220 | 0 | 0 | 1000 | 0 | 5288.75 | 10446.75 | 89.63
07:00 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 6 | 310 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 300 | 0 | 0 | 2 | 0 | 24 | 22 | 0 | 315 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0.29 | 80 | 0 | 13 | 830 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 621 | 1 | 0 | 0 | 25 | 280 | 230 | 51 | 0 | 207 | 0 | 0 | 91 | 0 | 0 | 20 | 0 | 126 | 0 | 6 | 0 | 310 | 0 | 371 | 41 | 0 | 158 | 1 | 17 | 0 | 42 | 0 | 70 | 0 | 96 | 0 | 50 | 41 | 10 | 0 | 3.31 | 0 | 5330.6 | 620 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.59 | 1000 | 0 | 0 | 0 | 1356.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.62 | 5 | 0 | 0 | 3.3 | 0 | 0 | 140 | 0 | 0 | 0 | 350 | 0 | 0.32 | 0 | 52 | 0 | 1 | 0 | 0 | 0 | 0 | 0.4 | 10 | 0 | 0 | 222 | 125 | 220 | 0 | 0 | 1000 | 0 | 5279.76 | 10610.36 | 89.62
08:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 6 | 312 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 300 | 0 | 0 | 8 | 17 | 22 | 22 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99 | 80 | 0 | 7 | 830 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 860 | 3 | 0 | 0 | 25 | 280 | 230 | 51 | 0 | 140 | 0 | 0 | 91 | 0 | 0 | 17 | 0 | 134 | 0 | 21 | 0 | 305 | 0 | 390 | 41 | 0 | 157 | 3 | 17 | 0 | 42 | 0 | 70 | 0 | 97 | 0 | 69 | 57 | 10 | 1 | 12.49 | 0 | 5669.48 | 618 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 1035 | 0 | 0 | 0 | 1370.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.98 | 23 | 0 | 0 | 12.7 | 0 | 0 | 170 | 0 | 0 | 0 | 414 | 0 | 1.19 | 0 | 52 | 0 | 6 | 0 | 0 | 0 | 0 | 1.5 | 45 | 0.11 | 0 | 307 | 125 | 220 | 0 | 0 | 1029 | 0 | 5635.27 | 11304.75 | 89.61
09:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 6 | 324 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 300 | 0 | 0 | 13 | 35 | 0 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.82 | 80 | 0 | 5 | 830 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 920 | 12 | 0 | 0 | 50 | 280 | 160 | 51 | 0 | 130 | 0 | 0 | 90 | 0 | 0 | 17 | 0 | 140 | 0 | 39 | 0 | 310 | 0 | 407 | 41 | 0 | 159 | 5 | 0 | 0 | 42 | 0 | 70 | 0 | 97 | 0 | 69 | 58 | 10 | 1 | 23.03 | 0.5 | 5791.35 | 902 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 1062 | 0 | 0 | 0 | 1364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.32 | 46 | 0 | 0 | 15.07 | 0 | 0 | 173 | 0 | 0 | 0 | 414 | 0 | 1.35 | 0 | 52 | 0 | 13 | 0 | 0 | 0 | 0 | 3 | 74 | 0.23 | 0 | 307 | 125 | 220 | 0 | 0 | 1043 | 0 | 6039.97 | 11831.32 | 89.6
10:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 6 | 320 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 300 | 0 | 0 | 20 | 70 | 21 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.62 | 80 | 0 | 4 | 830 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1016 | 10 | 0 | 0 | 90 | 280 | 50 | 51 | 0 | 130 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 148 | 0 | 52 | 0 | 310 | 0 | 390 | 41 | 0 | 158 | 7 | 17 | 0 | 42 | 0 | 71 | 0 | 96 | 0 | 69 | 57 | 10 | 1.5 | 32.94 | 0 | 5861.06 | 902 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 1100 | 0 | 0 | 0 | 1458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.96 | 68 | 0 | 0 | 32.15 | 0 | 0 | 183 | 0 | 0 | 0 | 414 | 0 | 3.44 | 0 | 52 | 0 | 19 | 0 | 0 | 0 | 0 | 4.2 | 110 | 0.36 | 0 | 307 | 125 | 220 | 0 | 0 | 1050 | 0 | 6312.11 | 12173.17 | 89.59
11:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 6 | 325 | 0 | 0 | 12 | 9 | 70 | 0 | 0 | 0 | 4 | 25 | 0 | 0 | 0 | 305 | 0 | 45 | 329 | 0 | 0 | 26 | 70 | 21 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.08 | 80 | 0 | 4 | 830 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1180 | 18 | 0 | 0 | 140 | 280 | 0 | 51 | 0 | 130 | 0 | 0 | 91 | 0 | 0 | 12 | 0 | 154 | 0 | 61 | 0 | 320 | 0 | 405 | 42 | 0 | 159 | 9 | 17 | 0 | 42 | 0 | 70 | 0 | 97 | 0 | 69 | 58 | 10 | 2 | 39.59 | 0 | 6259.67 | 902 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 1110 | 0 | 0 | 0 | 1450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.43 | 84 | 0 | 0 | 33.74 | 0 | 0 | 181 | 0 | 0 | 0 | 391 | 0 | 4.07 | 0 | 52 | 0 | 24 | 0 | 0 | 0 | 0 | 5.3 | 139 | 0.51 | 0 | 307 | 125 | 220 | 0 | 0 | 1050 | 0 | 6343.05 | 12602.72 | 89.58
12:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 6 | 348 | 0 | 0 | 16.5 | 17 | 70 | 0 | 0 | 9 | 17 | 75 | 0 | 0 | 0 | 250 | 0 | 55 | 328 | 0 | 0 | 28 | 75 | 21 | 21 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.29 | 80 | 0 | 2 | 830 | 0 | 0 | 0 | 0 | 27 | 217 | 0 | 0 | 0 | 1049 | 18 | 0 | 0 | 225 | 280 | 0 | 51 | 0 | 209 | 0 | 13 | 90 | 17 | 0 | 12 | 0 | 172 | 0 | 65 | 0 | 320 | 0 | 406 | 42 | 0 | 155 | 10 | 17 | 0 | 41 | 0 | 70 | 0 | 97 | 0 | 69 | 58 | 10 | 1.4 | 42.46 | 1 | 6434.65 | 902 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 1112 | 0 | 0 | 0 | 1449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.67 | 96 | 0 | 0 | 18.6 | 0 | 0 | 180 | 0 | 0 | 0 | 414 | 0 | 3.02 | 0 | 52 | 0 | 25 | 34 | 0 | 0 | 0 | 5.8 | 150 | 0.55 | 0 | 307 | 125 | 220 | 0 | 0 | 1050 | 0 | 6411.64 | 12846.29 | 89.57
13:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 6 | 350 | 0 | 0 | 32.7 | 17 | 70 | 0 | 0 | 28 | 35 | 101 | 0 | 0 | 0 | 250 | 0 | 55 | 328 | 0 | 0 | 27 | 90 | 21 | 21 | 0 | 325 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 3.05 | 80 | 33 | 8 | 830 | 0 | 0 | 6 | 0 | 62 | 0 | 0 | 0 | 0 | 1138 | 18 | 0 | 0 | 293 | 280 | 0 | 51 | 0 | 208 | 0 | 36 | 90 | 70 | 0 | 15 | 0 | 170 | 0 | 62 | 0 | 320 | 0 | 396 | 42 | 0 | 154 | 10 | 17 | 0 | 41 | 0 | 70 | 0 | 97 | 0 | 69 | 58 | 8 | 2 | 40.34 | 6 | 6610.09 | 902 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 1100 | 0 | 0 | 0 | 1456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.39 | 90 | 0 | 0 | 23.06 | 0 | 0 | 180 | 0 | 0 | 0 | 414 | 0 | 4.07 | 0 | 52 | 0 | 18 | 34 | 0 | 0 | 0 | 5.7 | 110 | 0.53 | 0 | 307 | 125 | 220 | 0 | 0 | 1045 | 0 | 6360.75 | 12970.84 | 89.56
14:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 6 | 356 | 0 | 0 | 33.8 | 17 | 70 | 0 | 0 | 30 | 35 | 146 | 0 | 0 | 0 | 250 | 0 | 55 | 326 | 0 | 0 | 24 | 90 | 21 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 24 | 10 | 2.42 | 80 | 51 | 2 | 830 | 0 | 0 | 42 | 0 | 67 | 0 | 0 | 0 | 0 | 1210 | 17 | 1 | 0 | 360 | 280 | 0 | 51 | 0 | 200 | 0 | 50 | 90 | 86 | 0 | 15 | 0 | 184 | 0 | 52 | 0 | 315 | 0 | 392 | 42 | 0 | 153 | 9 | 17 | 0 | 41 | 0 | 70 | 0 | 96 | 0 | 69 | 58 | 6 | 2 | 37.06 | 0 | 6866.28 | 902 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 1120 | 0 | 0 | 0 | 1457 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 36.28 | 57 | 0 | 0 | 30.77 | 0 | 0 | 173 | 0 | 0 | 0 | 414 | 0 | 2.01 | 0 | 52 | 35 | 21 | 34 | 0 | 0 | 0 | 4.9 | 111 | 0.45 | 0 | 307 | 120 | 220 | 0 | 0 | 1045 | 0 | 6368.41 | 13234.69 | 89.55
15:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 6 | 351 | 0 | 0 | 34.8 | 17 | 70 | 8 | 105 | 30 | 35 | 152 | 0 | 0 | 0 | 250 | 0 | 55 | 326 | 0 | 0 | 17 | 90 | 21 | 21 | 0 | 290 | 11 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 38 | 38 | 1.98 | 80 | 50 | 0 | 830 | 0 | 0 | 50 | 0 | 68 | 0 | 0 | 0 | 0 | 1200 | 9 | 40 | 0 | 260 | 280 | 0 | 51 | 0 | 207 | 0 | 73 | 90 | 100 | 0 | 17 | 0 | 184 | 0 | 39 | 0 | 320 | 0 | 382 | 42 | 0 | 153 | 6 | 17 | 0 | 41 | 0 | 70 | 0 | 95 | 0 | 69 | 59 | 6 | 1 | 25.35 | 0 | 6976.13 | 902 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 1112 | 0 | 0 | 0 | 1454 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 26.55 | 47 | 0 | 0 | 26.52 | 0 | 0 | 172 | 0 | 0 | 0 | 414 | 0 | 2.4 | 0 | 54 | 35 | 17 | 34 | 0 | 0 | 0 | 3.8 | 95 | 0.35 | 0 | 307 | 120 | 220 | 0 | 0 | 1052 | 0 | 6334.62 | 13310.75 | 89.54
16:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 6 | 353 | 0 | 0 | 48.1 | 17 | 84 | 15 | 110 | 55 | 35 | 155 | 0 | 0 | 0 | 295 | 0 | 55 | 326 | 0 | 0 | 10 | 90 | 21 | 21 | 0 | 320 | 17 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 38 | 38 | 1.11 | 80 | 51 | 0 | 830 | 0 | 0 | 50 | 1 | 66 | 0 | 0 | 0 | 0 | 1190 | 6 | 60 | 0 | 260 | 280 | 0 | 51 | 0 | 210 | 1 | 104 | 90 | 108 | 0 | 19 | 0 | 176 | 0 | 22 | 0 | 310 | 0 | 394 | 42 | 0 | 153 | 3 | 13 | 0 | 41 | 0 | 71 | 0 | 95 | 0 | 72 | 58 | 6 | 1 | 13.39 | 0 | 7147.6 | 901 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 1118 | 0 | 0 | 0 | 1448 | 0 | 0 | 0 | 20 | 40 | 0 | 0 | 0 | 0 | 15.28 | 28 | 0 | 0 | 15.66 | 0 | 0 | 174 | 0 | 0 | 0 | 414 | 0 | 1.58 | 0 | 54 | 70 | 10 | 62 | 0 | 0 | 0 | 2.8 | 48 | 0.19 | 0 | 307 | 120 | 220 | 0 | 0 | 1085 | 5 | 6336.51 | 13484.11 | 89.53
17:00 | 0 | 70 | 32 | 0 | 0 | 0 | 0 | 6 | 338 | 0 | 0 | 51 | 17 | 98 | 78 | 175 | 55 | 35 | 157 | 0 | 0 | 0 | 310 | 0 | 55 | 328 | 0 | 0 | 3 | 90 | 21 | 21 | 0 | 290 | 16 | 16 | 1 | 0 | 2 | 0 | 35 | 0 | 41 | 38 | 0.36 | 80 | 51 | 12 | 830 | 40 | 0 | 50 | 13 | 67 | 40 | 0 | 0 | 0 | 1194 | 1 | 85 | 0 | 260 | 280 | 0 | 51 | 0 | 212 | 1 | 106 | 90 | 140 | 0 | 19 | 17 | 168 | 9 | 7 | 0 | 315 | 0 | 392 | 42 | 0 | 153 | 1 | 13 | 0 | 41 | 0 | 70 | 0 | 95 | 31 | 102 | 77 | 8 | 0 | 4.37 | 0 | 7546.73 | 901 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 1123 | 0 | 0 | 0 | 1444 | 0 | 0 | 0 | 60 | 70 | 0 | 0 | 0 | 4 | 4.94 | 9 | 15 | 0 | 5.49 | 0 | 0 | 174 | 0 | 0 | 0 | 414 | 0 | 0.57 | 0 | 54 | 110 | 4 | 100 | 0 | 0 | 0 | 1.7 | 17 | 0.07 | 18 | 307 | 120 | 220 | 0 | 0 | 1085 | 47 | 6470.77 | 14017.5 | 89.52
18:00 | 0 | 70 | 32 | 0 | 0 | 0 | 0 | 6 | 324 | 0 | 0 | 49.2 | 17 | 113 | 62 | 230 | 55 | 35 | 153 | 0 | 0 | 0 | 305 | 0 | 55 | 300 | 0 | 0 | 0 | 125 | 22 | 21 | 0 | 350 | 15 | 16 | 57 | 0 | 0 | 34 | 38 | 0 | 43 | 38 | 0 | 80 | 34 | 19 | 830 | 51 | 0 | 50 | 17 | 34 | 80 | 0 | 0 | 0 | 1114 | 0 | 115 | 0 | 260 | 280 | 0 | 20 | 0 | 206 | 1 | 102 | 90 | 158 | 0 | 19 | 17 | 164 | 16 | 0 | 9 | 315 | 0 | 391 | 42 | 0 | 155 | 0 | 13 | 0 | 41 | 0 | 69 | 0 | 95 | 35 | 101 | 78 | 7 | 0 | 0.02 | 0 | 7673.22 | 807 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1108 | 0 | 0 | 0 | 1453 | 0 | 0 | 0 | 70 | 70 | 0 | 18 | 4 | 8 | 0.12 | 0 | 19 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 350 | 0 | 0.01 | 0 | 53 | 115 | 0 | 106 | 0 | 0 | 0 | 0.1 | 0 | 0 | 48 | 262 | 110 | 180 | 0 | 0 | 1085 | 49 | 6202.23 | 13875.45 | 89.51
19:00 | 0 | 90 | 33 | 0 | 0 | 0 | 0 | 6 | 326 | 0 | 0 | 48.8 | 17 | 113 | 68 | 280 | 55 | 35 | 157 | 0 | 0 | 0 | 320 | 0 | 55 | 260 | 0 | 0 | 0 | 125 | 24 | 21 | 0 | 380 | 0 | 0 | 85 | 0 | 0 | 51 | 38 | 0 | 46 | 38 | 0 | 80 | 34 | 24 | 830 | 92 | 0 | 50 | 19 | 32 | 125 | 0 | 0 | 0 | 1200 | 0 | 138 | 0 | 260 | 280 | 0 | 37 | 0 | 210 | 1 | 103 | 90 | 171 | 0 | 17 | 57 | 170 | 16 | 0 | 9 | 310 | 0 | 357 | 42 | 0 | 148 | 0 | 20 | 0 | 41 | 0 | 70 | 0 | 95 | 35 | 106 | 78 | 11 | 0 | 0 | 0 | 8029.8 | 724 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1037 | 0 | 0 | 0 | 1438 | 0 | 0 | 0 | 100 | 80 | 0 | 25 | 5 | 16 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 51 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 307 | 120 | 220 | 0 | 0 | 1085 | 96 | 6325 | 14354.8 | 89.5
19:30 | 0 | 105 | 33 | 0 | 0 | 0 | 0 | 6 | 292 | 0 | 0 | 48.8 | 17 | 145 | 62 | 300 | 55 | 35 | 148 | 0 | 0 | 0 | 320 | 0 | 55 | 260 | 0 | 0 | 0 | 125 | 24 | 21 | 0 | 350 | 0 | 0 | 87 | 0 | 0 | 51 | 38 | 0 | 47 | 38 | 0 | 80 | 33 | 28 | 830 | 107 | 0 | 50 | 25.5 | 29 | 150 | 0 | 0 | 0 | 1200 | 0 | 150 | 0 | 260 | 280 | 0 | 51 | 0 | 205 | 1 | 96 | 90 | 178 | 0 | 17 | 36 | 176 | 34 | 0 | 15 | 305 | 0 | 357 | 41 | 0 | 150 | 0 | 20 | 0 | 41 | 0 | 71 | 0 | 95 | 35 | 99 | 78 | 11 | 0 | 0 | 0 | 8087.3 | 713 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1070 | 0 | 0 | 0 | 1453 | 0 | 15 | 0 | 113 | 113 | 0 | 26 | 0 | 32 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 307 | 120 | 220 | 0 | 0 | 1080 | 103 | 6478 | 14565.3
20:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 6 | 305 | 0 | 0 | 48.8 | 17 | 149 | 30 | 300 | 55 | 35 | 149 | 0 | 0 | 0 | 330 | 0 | 55 | 260 | 0 | 0 | 0 | 125 | 24 | 21 | 0 | 350 | 0 | 0 | 92 | 0 | 0 | 51 | 38 | 0 | 48 | 38 | 0 | 80 | 17 | 29 | 830 | 77 | 0 | 50 | 25.5 | 29 | 121 | 0 | 0 | 0 | 1205 | 0 | 150 | 0 | 260 | 280 | 0 | 51 | 0 | 205 | 1 | 98 | 90 | 178 | 0 | 19 | 32 | 168 | 16 | 0 | 17 | 305 | 0 | 387 | 41 | 0 | 151 | 0 | 22 | 0 | 41 | 0 | 70 | 0 | 95 | 35 | 102 | 78 | 11 | 0 | 0 | 0 | 7996.3 | 713 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 0 | 0 | 0 | 1445 | 0 | 20 | 0 | 113 | 113 | 0 | 26 | 0 | 16 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 273 | 120 | 220 | 0 | 0 | 1085 | 104 | 6451 | 14447.3 | 89.49
21:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 6 | 317 | 0 | 0 | 46.6 | 17 | 149 | 30 | 300 | 55 | 35 | 151 | 0 | 0 | 0 | 340 | 0 | 55 | 260 | 0 | 0 | 0 | 108 | 24 | 21 | 0 | 350 | 0 | 0 | 85 | 0 | 0 | 51 | 38 | 0 | 50 | 38 | 0 | 80 | 0 | 29 | 830 | 80 | 0 | 50 | 25.5 | 0 | 151 | 0 | 0 | 0 | 1212 | 0 | 148 | 0 | 250 | 280 | 0 | 51 | 0 | 205 | 1 | 99 | 90 | 178 | 0 | 19 | 33 | 170 | 16 | 0 | 17 | 305 | 0 | 385 | 41 | 0 | 155 | 0 | 22 | 0 | 41 | 0 | 70 | 0 | 95 | 35 | 97 | 78 | 11 | 0 | 0 | 0 | 7979.1 | 759 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1109 | 0 | 0 | 0 | 1460 | 0 | 22 | 0 | 113 | 113 | 0 | 26 | 10 | 16 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 124 | 220 | 0 | 0 | 1085 | 107 | 6572 | 14551.1 | 89.48
22:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 6 | 317 | 0 | 0 | 48.5 | 17 | 149 | 15 | 300 | 55 | 35 | 156 | 0 | 0 | 0 | 340 | 0 | 55 | 260 | 0 | 0 | 0 | 108 | 22 | 21 | 0 | 350 | 0 | 0 | 88 | 0 | 0 | 51 | 38 | 0 | 50 | 38 | 0 | 80 | 0 | 29 | 830 | 0 | 0 | 50 | 25.5 | 0 | 151 | 0 | 0 | 0 | 1212 | 0 | 137 | 0 | 250 | 280 | 0 | 51 | 0 | 209 | 0 | 100 | 90 | 177 | 0 | 19 | 0 | 172 | 0 | 0 | 17 | 315 | 0 | 355 | 41 | 0 | 155 | 0 | 22 | 0 | 41 | 0 | 70 | 0 | 96 | 35 | 57 | 48 | 9 | 0 | 0 | 0 | 7710 | 902 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1106 | 0 | 0 | 0 | 1454 | 0 | 34 | 0 | 35 | 113 | 0 | 26 | 31 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 124 | 220 | 0 | 0 | 1085 | 46 | 6540 | 14250 | 89.47
23:00 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 5 | 310 | 0 | 0 | 46 | 17 | 149 | 0 | 95 | 55 | 35 | 152 | 0 | 0 | 0 | 335 | 0 | 55 | 260 | 0 | 0 | 0 | 108 | 22 | 22 | 0 | 350 | 0 | 0 | 91 | 0 | 0 | 51 | 31 | 0 | 50 | 38 | 0 | 80 | 0 | 29 | 830 | 0 | 0 | 50 | 25.5 | 0 | 151 | 0 | 0 | 0 | 1217 | 0 | 80 | 0 | 250 | 280 | 0 | 51 | 0 | 216 | 0 | 99 | 90 | 178 | 0 | 19 | 0 | 168 | 0 | 0 | 17 | 310 | 0 | 399 | 41 | 0 | 154 | 0 | 22 | 0 | 41 | 0 | 68 | 0 | 96 | 35 | 58 | 48 | 9 | 0 | 0 | 0 | 7438.5 | 901 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1102 | 0 | 0 | 0 | 1466 | 0 | 40 | 0 | 0 | 35 | 0 | 26 | 31 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 54 | 90 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 124 | 220 | 0 | 0 | 1085 | 0 | 6350 | 13788.5 | 89.46
Total KWH | 0 | 894720 | 594720 | 0 | 0 | 0 | 0 | 168318.18 | 7880400 | 0 | 0 | 750960 | 282240 | 2284416 | 334560 | 2132476 | 768858 | 592523 | 2521440 | 0 | 0 | 0 | 7447514 | 0 | 829318 | 7186039 | 0 | 0 | 180162 | 1836000 | 504000 | 470880 | 0 | 8047272.73 | 179400 | 127964 | 594240 | 0 | 36000 | 515085 | 260016 | 0 | 525120 | 450240 | 20879 | 1924860 | 702542 | 386880 | 19978181.82 | 334545 | 0 | 816480 | 179118 | 959309 | 3877409 | 0 | 0 | 0 | 24098180 | 115830 | 1201018 | 0 | 3825000 | 7074500 | 2236000 | 1225450 | 0 | 4396000 | 8064 | 1468800 | 2142026 | 2010720 | 0 | 420160 | 142500 | 3767040 | 94982 | 426964 | 96784 | 7525000 | 0 | 9349000 | 982000 | 0 | 3737290.91 | 64744 | 420696 | 0 | 992640 | 0 | 1681000 | 0 | 2305110 | 255600 | 1794000 | 1404000 | 209280 | 11350 | 275590 | 14880 | 163347284.64 | 20453818 | 3848544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 472320 | 25949090 | 0 | 0 | 0 | 34388354 | 0 | 136365 | 0 | 586464 | 922752 | 0 | 138448 | 76181 | 68074 | 267740 | 570641 | 129750 | 0 | 236256 | 0 | 0 | 4282682 | 0 | 0 | 0 | 9656654 | 0 | 23820 | 0 | 1234472 | 1216872 | 159696 | 1255555 | 0 | 0 | 0 | 38632.2 | 898560 | 3397 | 320832 | 6742000 | 2967000 | 5271800 | 0 | 0 | 25717818.18 | 481200 | 148515787.38 | 311863072.02

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 10-03-2026
Power Supply Scenario
| Day Peak Generation |  |  | 12846.29 | MW | 12:00 Hr. | Energy Generated |  |  | 311.8631 |  | MKWHr.
| Day Peak Demand |  |  | 13153.29 | MW | 12:00 Hr. | Energy Unserverd |  |  | 2.024 |  | MKWHr.
| Evening Peak Generation |  |  | 14565.3 | MW | 19:30 Hr. | Energy Demand |  |  | 313.8871 |  | MKWHr.
| Evening Peak Demand |  |  | 14565.3 | MW | 19:30 Hr. | Maximum Temperature |  |  | 32.7 |  | °C
| Minimum Generation of the Day |  |  | 10446.75 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 816.44 |  | MMCFD
| Maximum Generation of the Day |  |  | 14565.3 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.457 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 31.7044 | 0 | 13.8222 | 0 | 0 | 0.18016 | 0 | 0 | 45.7068 | Gas | 110.5246 | Gas | 378839537.0943
| Chattogram Zone |  |  | 4.2643 | 44.0764 | 5.6441 | 0 | 1.9249 | 0.13671 | 0 | 0.036 | 56.0823 | Coal | 103.7197 | Coal | 680200116.429
| Cumilla Zone |  |  | 21.3272 | 0 | 5.0148 | 0 | 0 | 0.42696 | 3.767 | 0 | 30.536 | HFO | 33.2821 | HFO | 552232546.64
| Mymensingh Zone |  |  | 0.20928 | 0 | 3.4685 | 0 | 0 | 0.28694 | 0 | 0 | 3.9647 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.9927 | 0 | 0 | 0 | 0 | 0.064744 | 0 | 0 | 27.0575 | Hydro | 1.9249 | Hydro | 192486
| Khulna Zone |  |  | 3.8485 | 25.9491 | 0 | 0 | 0 | 0.47232 | 20.4538 | 0 | 50.7238 | Solar | 3.7666 | Solar | 60328276.55
| Barishal Zone |  |  | 8.2388 | 32.4598 | 0.80203 | 0 | 0 | 0.003397 | 0 | 0 | 41.504 | Import | 58.6092 | Import | 341362817.18
| Rajshahi Zone |  |  | 13.9393 | 0 | 2.058 | 0 | 0 | 1.0985 | 34.3884 | 0 | 51.4842 | Wind | 0.036 | Wind | 529560
| Rangpur Zone |  |  | 0 | 1.2345 | 2.4724 | 0 | 0 | 1.0969 | 0 | 0 | 4.8038
| Total |  |  | 110.5246 | 103.7197 | 33.2821 | 0 | 1.9249 | 3.7666 | 58.6092 | 0.036 | 311.8631
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 378839537.0943 |  | Hydro | 192486
|  |  |  | Coal | 680200116.429 |  | Solar | 60328276.55
|  |  |  | HFO | 552232546.64 |  | Import | 341362817.18
|  |  |  | HSD | 0 |  | Wind | 529560
[5 empty] | Total: | 201,36,85,339 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.4538 | Peak Hr Flow | 713.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 46424763.63 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 34.3884 | Peak Hr Flow | 1453.00 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1946 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.767 | Peak Hr Flow | 176.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2626 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 58.6092 | Peak Hr Flow | 2342.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5255
|  |  |  | Chattogram |  | 0 |  | 1432
|  |  |  | Cumilla |  | 0 |  | 1297
|  |  |  | Mymensingh |  | 0 |  | 1152
|  |  |  | Sylhet |  | 0 |  | 522
|  |  |  | Khulna |  | 0 |  | 1636
|  |  |  | Barishal |  | 0 |  | 405
|  |  |  | Rajshahi |  | 0 |  | 1379
|  |  |  | Rangpur |  | 0 |  | 880
|  |  |  | Total |  | 0 |  | 13958
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:13 | 16:31 | Matuail-Siddhirganj 132kV Ckt-1 Tripped from Siddhirganj 132/33kV end showing Distance | [7 empty] | 70.0MW load
|  |  | Relay Trip relays Due to Unknown | [7 empty] | interrup.
Siddhirganj
132/33kV end
| 08:32 |  | Aminbazar-Kaliakoir 230kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to By
NLDC and from Aminbazar 400/230/132kV end Due to Disc cleaning
| 08:39 | 12:03 | Kallyanpur 132/33kV S/S GT-2 (132kV) HT Scheduled S/D
| 08:40 |  | Kaliakoir 400/230/132kV S/S Bibiyana1 Scheduled S/D Due to By NLDC
| 08:42 | 15:16 | Bibiyana-Kaliakoir 400 kV Ckt-1 Scheduled S/D from Bibiana 400/230kV end Due to line
maintenance
| 09:15 | 12:20 | Narshingdi 132/33kV S/S T-2 LT Scheduled S/D Due to Oil leakage maintenance
| 09:16 | 12:20 | Narshingdi 132/33kV S/S T-2 HT Scheduled S/D Due to Oil leakage maintenance
| 09:47 | 16:43 | Gopalganj 132/33kV S/S Gallamari-1 Scheduled S/D Due to ALDC
| 09:47 | 16:43 | Gopalganj 132/33kV S/S Gallamari-2 Scheduled S/D Due to ALDC
| 09:50 | 16:44 | Gollamari 132/33kV S/S E01 Gollamari-Gopalgonj Line - 1 Project Work S/D Due to Rupsha -
khulna south 230kv line Lilo work.
| 09:50 | 16:45 | Gollamari 132/33kV S/S E07 Gollamari-Gopalgonj Line - 2 Project Work S/D Due to Rupsha -
khulna south 230kv line Lilo work.
| 09:52 | 10:28 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T LT Forced S/D Due to Emergency
maintenance work.
| 09:54 | 10:24 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T HT Forced S/D Due to Emergency
maintenance work.
| 10:50 | 17:16 | BSRM-GPH 230 kV Ckt-1 Scheduled S/D from BSRM 230/33kV end Due to GPH works
| 10:50 | 17:15 | BSRM-GPH 230 kV Ckt-2 Scheduled S/D from GPH 230/33kV end Due to OPGW String repair and
maintenance
| 10:56 | 15:14 | Kachua 230/132/33kV S/S ATR-2 LT Project Work S/D Due to DFDR Test.
| 10:58 | 15:14 | Kachua 230/132/33kV S/S ATR-2 HT Project Work S/D Due to DFDR Test
| 11:30 | 16:31 | Matuail-Siddhirganj 132kV Ckt-1 Forced S/D from Siddhirganj 132/33kV end Due to Under
ground cable test
| 12:00 |  | Day Peak Generation: 12842 MW.
|  | 12:03 | Kallyanpur 132/33kV S/S GT-2 (132kV) HT is restored.
| 12:28 | 12:48 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Tripped showing Lockout Relay K862 trip | [7 empty] | 28.0MW load
|  |  | relays. | [7 empty] | interrup.
| 12:56 |  | Bogura 400/230kV S/S ATR-01 HT Scheduled S/D Due to Oil centrifuging
| 12:56 |  | Bogura 400/230kV S/S ATR-01 LT Scheduled S/D Due to Oil centrifuging
|  | 13:31 | Barapukuria-Bogura 230 kV Ckt-2 is restored.
| 15:42 | 15:55 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Tripped showing Lockout Relay K862 trip | [7 empty] | 24.0MW load
|  |  | relays. | [7 empty] | interrup.
|  | 16:19 | Meghnaghat-Shyampur 230kV Ckt-1 is restored.
| 16:43 |  | Sikalbaha 225 MW CCPP GT was sync.
|  | 17:54 | Khulna(S) 230/132kV S/S Rupsha Ckt-1 is restored.
| 04:00 |  | Sehri peak generation: 12871 MW
| 07:45 |  | Sreemongol 132/33kV S/S 132/33kv T-3 HT Tripped showing over current relays Due to 33kv | [7 empty] | 45.0MW load
|  |  | Tr-3 circuit breaker is burst | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 10-03-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 6 | 168318.18 | Demand "05"MW due to gas restiction by Titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 292 | 7880400 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 768858 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 260 | 7186039 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 48.8 | 750960 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 62 | 334560 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 592523 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 829318 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 24 | 504000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 470880 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 33 | 594720 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 300 | 2132476 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 145 | 2284416 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 894720 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 148 | 2521440 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 180162 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 282240 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 350 | 8047272.73 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 320 | 7447514 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 125 | 1836000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2401.8 | 45706816.91
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 179118 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 115830 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 816480 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1924860 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 150 | 3877409 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 29 | 959309 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 38 | 260016 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 515085 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 47 | 525120 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 28 | 386880 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 87 | 594240 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20879 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 127964 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 33 | 702542 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 38 | 450240 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 179400 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 107 | 334545 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1200 | 24098180 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 36000 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 830 | 19978181.82 | ps availability is less
Chattogram Area Total |  |  |  |  | 4898.863 | 2793.5 | 56082278.82
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 205 | 4396000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 280 | 7074500 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 2236000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 260 | 3825000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 1 | 8064 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1225450 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 1201018 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 15 | 96784 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2142026 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 178 | 2010720 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 176 | 3767040 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 34 | 94982 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 420160 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 36 | 142500 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 96 | 1468800 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 426964 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1589 | 30536008
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 11 | 209280 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11350 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 78 | 1404000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 99 | 1794000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 275590 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 14880 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 255600 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 223 | 3964700
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 64744 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 982000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 150 | 3737290.91 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 71 | 1681000 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 41 | 992640 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 95 | 2305110 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 20 | 420696 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7525000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 357 | 9349000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1080 | 27057480.91
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 713 | 20453818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 151 | 3848544 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 472320 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1070 | 25949090 | plant availability zero
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1934 | 50723772
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 80 | 320832 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2967000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 1080 | 25717818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5271800 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 103 | 481200 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6742000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3397 | -
Barishal Area Total |  |  |  |  | 2700.36 | 1910 | 41504047.18
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 267740 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 15 | 136365 | Under Maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 76181 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 172 | 4282682 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9656654 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 19 | 129750 | Machine problem and fuel shortage
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 32 | 68074 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 26 | 138448 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 922752 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 586464 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 23820 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1453 | 34388354 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 236256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 570641 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2357 | 51484181
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 55 | 1234472 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 1255555 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 38632.2 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1216872 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 159696 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 898560 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 277 | 4803787.2
Eastern Grid Total |  |  |  |  | 17400.108 | 8087.3 | 163347284.64
Western Grid Total |  |  |  |  | 10985.595 | 6478 | 148515787.38
National Grid Total |  |  |  |  | 28385.703 | 14565.3 | 311863072.02
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 10-03-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9658.44 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4299.7 | MW
i) Dhaka area |  |  | 5255.44 |  | MW | i) Khulna area |  |  |  | 1636 | MW
ii) Chattogram area |  |  | 1432 |  | MW | ii) Barishal area |  |  |  | 404.7 | MW
iii) Cumilla area |  |  | 1297 |  | MW | iii) Rajshahi area |  |  |  | 1379 | MW
iv) Mymensingh area |  |  | 1152 |  | MW | iv) Rangpur area |  |  |  | 880 | MW
v) Sylhet area |  |  | 522 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13958.14 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 12 | 14:00 | 67 | Hasnabad | 88 | 21:00 | 133 | Nawabganj | 51.8 | 21:00
2 | AKSML | 9.7 | 17:00 | 68 | Hathazari | 74 | 21:00 | 134 | Netrakona | 155 | 20:00
3 | Aftabnagar | 38 | 21:00 | 69 | Hatirjheel | 41 | 14:00 | 135 | New | 74 | 14:00
4 | Agargaon | 101 | 13:00 | 70 | Ishurdi | 68 | 19:00 | 136 | Niamatpur | 94 | 13:00
5 | Agrabad | 52 | 12:00 | 71 | Jaldhaka | 76 | 17:00 | 137 | Noapara | 44.5 | 19:00
6 | Amnura | 35 | 07:00 | 72 | Jamalpur | 109 | 17:00 | 138 | PHP | 9 | 12:00
7 | Ashuganj | 79 | 23:00 | 73 | Jashore | 138 | 19:00 | 139 | Pabna | 86 | 18:00
8 | BSRM | 208 | 23:00 | 74 | Jhenaidah | 96 | 18:30 | 140 | Palashbari | 108 | 18:00
9 | Bagerhat | 79 | 19:00 | 75 | Joydebpur | 134 | 17:00 | 141 | Panchagarh | 56 | 18:00
10 | Bajitpur | 81 | 18:00 | 76 | Joypurhat | 63 | 09:00 | 142 | Patiya | 9 | 18:30
11 | Bakerganj | 12.38 | 21:00 | 77 | Juldah | 17 | 12:00 | 143 | Patuakhali | 50 | 21:00
12 | Bakulia | 82 | 12:00 | 78 | KSRM | 12 | 13:00 | 144 | Payra | 34 | 20:00
13 | Banani | 53.2 | 14:00 | 79 | Kabirpur | 249 | 18:30 | 145 | Postogola | 51 | 13:00
14 | Bangabhaban | 16 | 10:00 | 80 | Kachua | 84 | 21:00 | 146 | Pubail | N/A | N/A
15 | Barapukuria | 69 | 21:00 | 81 | Kaliganj | 26 | 18:30 | 147 | Purbachal | 27 | 13:00
16 | Barguna | 18 | 19:30 | 82 | Kallyanpur | 108 | 22:00 | 148 | Purbasadipur | 134 | 17:00
17 | Barishal | 89 | 19:00 | 83 | Kalurghat | 55 | 14:00 | 149 | Rahanpur | 35 | 03:00
18 | Barishal-230 | 90 | 19:00 | 84 | Kamrangirchar | 82 | 17:00 | 150 | Rahim | 37 | 13:00
19 | Baroaulia | 59 | 09:00 | 85 | Kaptai | N/A | N/A | 151 | Rajbari | 69 | 19:00
20 | Baroirhat | 52 | 19:00 | 86 | Kasba | 35 | 21:00 | 152 | Rajendrapur | 125 | 17:00
21 | Bashundhara | 183 | 14:00 | 87 | Kazla | 103 | 16:00 | 153 | Rajshahi | 101 | 04:00
22 | BashundharaCement | 7 | 07:00 | 88 | Keranigonj | 82 | 17:00 | 154 | Rajshahi-230 | 76 | 18:00
23 | Beanibazar | 64 | 18:00 | 89 | Khagrachori | 32 | 18:00 | 155 | Ramganj | 96 | 22:00
24 | Benapole | 64 | 21:00 | 90 | Khulna | 54 | 20:00 | 156 | Rampur | 38 | 23:00
25 | Bhaluka | 134 | 17:00 | 91 | Khulshi | 190 | 19:30 | 157 | Rangamati | 16 | 18:30
26 | Bhandaria | 46 | 21:00 | 92 | Kishoreganj | 120 | 20:00 | 158 | Rangpur | 148 | 18:00
27 | Bhangura | 41 | 14:00 | 93 | Kodda | 304 | 09:00 | 159 | Ruppur | 3.4 | 11:00
28 | Bheramara(GK) | 52 | 19:00 | 94 | Kulaura | 41 | 18:00 | 160 | SSM | 0 | 00:00
29 | Bhulta | 228 | 16:00 | 95 | Kurigram | 74 | 17:00 | 161 | Saidpur | 107 | 17:00
30 | Bog-Sherpur | 72 | 04:00 | 96 | Kushtia | 132 | 20:00 | 162 | Satkhira | 131 | 19:00
31 | Bogura | 154 | 18:00 | 97 | Laksam | 19 | 18:30 | 163 | Satmasjid | 97 | 19:30
32 | Borhanuddin | 86 | 21:00 | 98 | Lakshmipur | 33 | 19:30 | 164 | Savar | 216 | 16:00
33 | Brahmanbaria | 123 | 19:00 | 99 | Lalbag | 75 | 17:00 | 165 | SevenRings | 17.88 | 03:00
34 | Cantonment | 95 | 21:00 | 100 | Lalmonirhat | 57 | 17:00 | 166 | ShahCement | 31 | 03:00
35 | Chandina | 20 | 01:00 | 101 | MI_Cement | 18.5 | 11:00 | 167 | Shahjadpur | 80 | 17:00
36 | Chandpur | 68 | 20:00 | 102 | Madanganj | 52 | 16:00 | 168 | Shahjibazar | 118 | 23:00
37 | Chandraghona | 34 | 18:30 | 103 | Madaripur | 94 | 18:30 | 169 | Shahmirpur | 56 | 03:00
38 | Chapai | 68 | 13:00 | 104 | Madartek | 71 | 22:00 | 170 | Shariatpur | 75 | 21:00
39 | Charsaidpur | 45 | 02:00 | 105 | Madunaghat | 48 | 19:00 | 171 | Sherpur | 170 | 18:00
40 | Chauddagram | 70 | 22:00 | 106 | Magura | 60 | 19:00 | 172 | Shikalbaha | 28 | 21:00
41 | Chhatak | 34 | 22:00 | 107 | Mahasthangarh | 76 | 03:00 | 173 | Shitalakhya | 80.2 | 15:00
42 | Chowmuhani | 130 | 19:00 | 108 | Maijdee | 42 | 19:00 | 174 | Sholosohor | 45 | 18:30
43 | Chuadanga | 103 | 21:00 | 109 | Manikganj | 121 | 20:00 | 175 | Shyampur | 180 | 13:00
44 | Coxsbazar | 139 | 21:00 | 110 | Maniknagar | 70 | 14:00 | 176 | Siddhirganj | 129 | 12:00
45 | Cumilla(N) | 117 | 18:30 | 111 | Matarbari | 53 | 18:00 | 177 | Sirajganj | 110 | 17:00
46 | Cumilla(S) | 184 | 15:00 | 112 | Matuail | 68 | 00:00 | 178 | Sonargaon | 153 | 17:00
47 | Daganbhuiyan | 31 | 22:00 | 113 | Metrorail_Motijheel | 25 | 16:00 | 179 | Sreemongol | 69 | 18:30
48 | Daudkandi | 134 | 21:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sreepur | 119 | 17:00
49 | DhakaUniversity | 68 | 14:00 | 115 | Millgate | 94 | 15:00 | 181 | Srinagar | 42.22 | 21:00
50 | Dhamrai | 132 | 19:00 | 116 | Mirpur | 141 | 14:00 | 182 | Sunamganj | 52 | 21:00
51 | Dhanmondi | 109 | 13:00 | 117 | Mirsorai | 44 | 08:00 | 183 | Sylhet | 52 | 19:00
52 | Dohazari | 110 | 18:00 | 118 | Mirzapur | 45 | 19:00 | 184 | Sylhet-132 | 97 | 21:00
53 | Faridpur | 150 | 20:00 | 119 | Mithapukur | 60 | 04:00 | 185 | TK | 22.5 | 18:30
54 | Fatullah | 104 | 15:00 | 120 | Modern | N/A | N/A | 186 | Tangail | 170 | 21:00
55 | Fenchuganj | 33 | 19:00 | 121 | Mogbazar | 86.6 | 13:00 | 187 | Taraganj | 24 | 17:00
56 | Feni | 96 | 19:00 | 122 | Mongla | 37 | 10:00 | 188 | Tasnim | 17 | 16:00
57 | GPH | 2 | 15:00 | 123 | Motijheel | 43 | 13:00 | 189 | Thakurgaon | 96 | 19:00
58 | Ghatail | 88 | 17:00 | 124 | Muktagacha | 39 | 18:00 | 190 | Tongi | 173 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 101 | 16:00 | 191 | Ullahpara | 40 | 03:00
60 | Ghorashal-230 | 117 | 22:00 | 126 | Muradnagar | 36 | 20:00 | 192 | Ullon | 52 | 19:30
61 | Goalpara | 36 | 19:00 | 127 | Mymensingh | 212 | 18:00 | 193 | Uttara | 78 | 13:00
62 | Gollamari | 98 | 19:00 | 128 | Naogaon | 126 | 21:00 | 194 | UttaraNew | 30 | 18:00
63 | Gopalganj | 94 | 19:00 | 129 | Narail | 57 | 19:00 | 195 | Zigatola | 78 | 21:00
64 | Gulshan | 102 | 12:00 | 130 | Narinda | 68 | 14:00
65 | Halishahar | 79 | 15:00 | 131 | Narshingdi | 163 | 19:30
66 | HaripurSBU | 128 | 17:00 | 132 | Natore | 135 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 10-03-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 12830.37 | 0 |  | 12830.37
1:00 | 12305.02 | 0 |  | 12305.02
2:00 | 12007.28 | 0 |  | 12007.28
3:00 | 11905.78 | 0 |  | 11905.78
4:00 | 12628.44 | 0 |  | 12628.44
5:00 | 11358.44 | 0 |  | 11358.44
6:00 | 10446.75 | 0 |  | 10446.75
7:00 | 10610.36 | 0 |  | 10610.36
8:00 | 11304.75 | 0 |  | 11304.75
9:00 | 11831.32 | 68 |  | 11902.32
10:00 | 12173.17 | 249 |  | 12433.17
11:00 | 12602.72 | 287 |  | 12902.72
12:00 | 12846.29 | 294 |  | 13153.29
13:00 | 12970.84 | 317 |  | 13301.84
14:00 | 13234.69 | 305 |  | 13553.69
15:00 | 13310.75 | 281 |  | 13604.75
16:00 | 13484.11 | 66 |  | 13553.08
17:00 | 14017.5 | 44 |  | 14063.5
18:00 | 13875.45 | 24 |  | 13900.45
19:00 | 14354.8 | 0 |  | 14354.8
19:30 | 14565.3 | 0 |  | 14565.3
20:00 | 14447.3 | 0 |  | 14447.3
21:00 | 14551.1 | 0 |  | 14551.1
22:00 | 14250 | 49 |  | 14301
23:00 | 13788.5 | 40 |  | 13830.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 10-03-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6907 | 5923.37 | 12830.37 | DAILY GENERATION CURVE
00:30 | 6684.7 | 5882.995 | 12567.695
01:00 | 6462.4 | 5842.62 | 12305.02 | 10-03-2026
01:30 | 6412.9 | 5743.25 | 12156.15
02:00 | 6363.4 | 5643.88 | 12007.28
02:30 | 6258.55 | 5697.98 | 11956.53
03:00 | 6153.7 | 5752.08 | 11905.78
03:30 | 6329.65 | 5937.46 | 12267.11
04:00 | 6505.6 | 6122.84 | 12628.44
04:30 | 6143.15 | 5850.29 | 11993.44
05:00 | 5780.7 | 5577.74 | 11358.44
05:30 | 5469.35 | 5433.245 | 10902.595
06:00 | 5158 | 5288.75 | 10446.75
06:30 | 5244.3 | 5284.255 | 10528.555
07:00 | 5330.6 | 5279.76 | 10610.36
07:30 | 5500.04 | 5457.515 | 10957.555
08:00 | 5669.48 | 5635.27 | 11304.75
08:30 | 5730.415 | 5837.62 | 11568.035
09:00 | 5791.35 | 6039.97 | 11831.32
09:30 | 5826.205 | 6176.04 | 12002.245
10:00 | 5861.06 | 6312.11 | 12173.17
10:30 | 6060.365 | 6327.58 | 12387.945
11:00 | 6259.67 | 6343.05 | 12602.72
11:30 | 6347.16 | 6377.345 | 12724.505
12:00 | 6434.65 | 6411.64 | 12846.29
12:30 | 6522.37 | 6386.195 | 12908.565
13:00 | 6610.09 | 6360.75 | 12970.84
13:30 | 6738.185 | 6364.58 | 13102.765
14:00 | 6866.28 | 6368.41 | 13234.69
14:30 | 6921.205 | 6351.515 | 13272.72
15:00 | 6976.13 | 6334.62 | 13310.75
15:30 | 7061.865 | 6335.565 | 13397.43
16:00 | 7147.6 | 6336.51 | 13484.11
16:30 | 7347.165 | 6403.64 | 13750.805
17:00 | 7546.73 | 6470.77 | 14017.5
17:30 | 7609.975 | 6336.5 | 13946.475
18:00 | 7673.22 | 6202.23 | 13875.45
18:30 | 7851.51 | 6263.615 | 14115.125
19:00 | 8029.8 | 6325 | 14354.8
19:30 | 8087.3 | 6478 | 14565.3
20:00 | 7996.3 | 6451 | 14447.3
20:30 | 7987.7 | 6511.5 | 14499.2 |  | Executive Engineer
21:00 | 7979.1 | 6572 | 14551.1 |  | Network Operation Division
21:30 | 7844.55 | 6556 | 14400.55
22:00 | 7710 | 6540 | 14250
22:30 | 7574.25 | 6445 | 14019.25
23:00 | 7438.5 | 6350 | 13788.5

## En-Curve
QF-LDC-12
Date | 10-03-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3076 | 1408 | 900 | 0 | 154 | 1451.37 | 80 | 4445 | 0 | 138 | 1178 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3012.5 | 1407.5 | 900 | 0 | 154 | 1450.995 | 80 | 4393.5 | 0 | 129 | 1040.2 | 0 | 0 | 0 | 0 | 10-03-2026
01:00 | 2949 | 1407 | 900 | 0 | 154 | 1450.62 | 80 | 4342 | 0 | 120 | 902.4 | 0 | 0 | 0 | 0
01:30 | 2956 | 1460.5 | 899.5 | 0 | 149 | 1385.75 | 80 | 4230 | 0 | 120 | 875.4 | 0 | 0 | 0 | 0 | Energy Generated | 311.8631 |  | MKWHr
02:00 | 2963 | 1514 | 899 | 0 | 144 | 1320.88 | 80 | 4118 | 0 | 120 | 848.4 | 0 | 0 | 0 | 0 | Energy not Served | 2.024 |  | MKWHr
02:30 | 3016 | 1538.5 | 899.5 | 0 | 142 | 1327.98 | 80 | 3949 | 0 | 129 | 874.55 | 0 | 0 | 0 | 0 | Total Energy Requirement | 313.8871 |  | MKWHr
03:00 | 3069 | 1563 | 900 | 0 | 140 | 1335.08 | 80 | 3780 | 0 | 138 | 900.7 | 0 | 0 | 0 | 0
03:30 | 3024.5 | 1563.5 | 899.5 | 0 | 144 | 1391.46 | 80 | 3847 | 0 | 169.5 | 1147.65 | 0 | 0 | 0 | 0
04:00 | 2980 | 1564 | 899 | 0 | 148 | 1447.84 | 80 | 3914 | 0 | 201 | 1394.6 | 0 | 0 | 0 | 0
04:30 | 2898 | 1524 | 899.5 | 0 | 143 | 1450.29 | 80 | 3813 | 0 | 130.5 | 1054.15 | 0 | 0 | 1 | 0
05:00 | 2816 | 1484 | 900 | 0 | 138 | 1452.74 | 80 | 3712 | 0 | 60 | 713.7 | 0 | 0 | 2 | 0
05:30 | 2853 | 1481.5 | 759 | 0 | 131 | 1452.745 | 80 | 3698 | 0 | 34 | 411.85 | 0 | 0 | 1.5 | 0
06:00 | 2890 | 1479 | 618 | 0 | 124 | 1452.75 | 80 | 3684 | 0 | 8 | 110 | 0 | 0 | 1 | 0
06:30 | 2962.5 | 1488.5 | 619 | 0 | 125 | 1404.64 | 80 | 3704.5 | 21.915 | 10 | 109 | 0 | 0 | 3.5 | 0
07:00 | 3035 | 1498 | 620 | 0 | 126 | 1356.53 | 80 | 3725 | 43.83 | 12 | 108 | 0 | 0 | 6 | 0
07:30 | 3063 | 1477 | 619 | 0 | 130 | 1363.66 | 80 | 3919 | 108.895 | 48.5 | 145.5 | 0 | 0 | 3 | 0
08:00 | 3091 | 1456 | 618 | 0 | 134 | 1370.79 | 80 | 4113 | 173.96 | 85 | 183 | 0 | 0 | 0 | 0
08:30 | 3078 | 1464 | 760 | 0 | 137 | 1367.395 | 80 | 4163.5 | 238.39 | 94 | 185.75 | 0 | 0 | 0 | 34
09:00 | 3065 | 1472 | 902 | 0 | 140 | 1364 | 80 | 4214 | 302.82 | 103 | 188.5 | 0 | 0 | 0 | 68
09:30 | 3023 | 1464 | 902 | 0 | 144 | 1411 | 80 | 4284.5 | 380.995 | 120.5 | 192.25 | 0 | 0 | 0 | 158.5
10:00 | 2981 | 1456 | 902 | 0 | 148 | 1458 | 80 | 4355 | 459.17 | 138 | 196 | 0 | 0 | 0 | 249
10:30 | 2990 | 1482.5 | 902 | 0 | 151 | 1454 | 80 | 4442 | 504.445 | 138 | 244 | 0 | 0 | 0 | 268
11:00 | 2999 | 1509 | 902 | 0 | 154 | 1450 | 80 | 4529 | 549.72 | 138 | 292 | 0 | 0 | 0 | 287
11:30 | 3100.5 | 1477.5 | 902 | 0 | 163 | 1449.5 | 80 | 4464.5 | 561.755 | 140.5 | 385.25 | 0 | 0 | 0 | 290.5
12:00 | 3202 | 1446 | 902 | 0 | 172 | 1449 | 80 | 4400 | 573.79 | 143 | 478.5 | 0 | 0 | 0 | 294
12:30 | 3120.5 | 1447.5 | 902 | 0 | 171 | 1452.5 | 80 | 4436 | 551.965 | 150.5 | 595.6 | 0 | 0 | 1 | 305.5
13:00 | 3039 | 1449 | 902 | 0 | 170 | 1456 | 80 | 4472 | 530.14 | 158 | 712.7 | 0 | 0 | 2 | 317
13:30 | 3060.5 | 1430 | 902 | 0 | 177 | 1456.5 | 80 | 4518 | 502.515 | 158 | 813.75 | 0 | 0 | 4.5 | 311
14:00 | 3082 | 1411 | 902 | 0 | 184 | 1457 | 80 | 4564 | 474.89 | 158 | 914.8 | 0 | 0 | 7 | 305
14:30 | 3027 | 1409 | 902 | 0 | 184 | 1455.5 | 80 | 4559.5 | 420.42 | 162 | 1064.8 | 0 | 0 | 8.5 | 293
15:00 | 2972 | 1407 | 902 | 0 | 184 | 1454 | 80 | 4555 | 365.95 | 166 | 1214.8 | 0 | 0 | 10 | 281
15:30 | 2980 | 1438.5 | 901.5 | 0 | 180 | 1451 | 80 | 4569.5 | 284.48 | 177.5 | 1324.95 | 0 | 0 | 10 | 173.5
16:00 | 2988 | 1470 | 901 | 0 | 176 | 1448 | 80 | 4584 | 203.01 | 189 | 1435.1 | 0 | 0 | 10 | 66
16:30 | 3002 | 1471 | 901 | 0 | 172 | 1446 | 80 | 4588.5 | 136.255 | 254.5 | 1693.55 | 0 | 0 | 6 | 55
17:00 | 3016 | 1472 | 901 | 0 | 168 | 1444 | 80 | 4593 | 69.5 | 320 | 1952 | 0 | 0 | 2 | 44
17:30 | 2953.5 | 1469 | 854 | 0 | 166 | 1448.5 | 80 | 4522.5 | 35.375 | 365.5 | 2051.1 | 0 | 0 | 1 | 34
18:00 | 2891 | 1466 | 807 | 0 | 164 | 1453 | 80 | 4452 | 1.25 | 411 | 2150.2 | 0 | 0 | 0 | 24
18:30 | 2937 | 1517 | 765.5 | 0 | 167 | 1445.5 | 80 | 4481 | 0.625 | 434.5 | 2287 | 0 | 0 | 0 | 12
19:00 | 2983 | 1568 | 724 | 0 | 170 | 1438 | 80 | 4510 | 0 | 458 | 2423.8 | 0 | 0 | 0 | 0
19:30 | 2970 | 1553 | 713 | 0 | 176 | 1453 | 80 | 4542 | 0 | 489 | 2589.3 | 0 | 0 | 0 | 0
20:00 | 2983 | 1569 | 713 | 0 | 168 | 1445 | 80 | 4553 | 0 | 430 | 2506.3 | 0 | 0 | 0 | 0
20:30 | 3001.5 | 1576 | 736 | 0 | 169 | 1452.5 | 80 | 4575.5 | 0 | 428 | 2480.7 | 0 | 0 | 0 | 0
21:00 | 3020 | 1583 | 759 | 0 | 170 | 1460 | 80 | 4598 | 0 | 426 | 2455.1 | 0 | 0 | 0 | 0
21:30 | 3007.5 | 1587 | 830.5 | 0 | 171 | 1457 | 80 | 4596.5 | 0 | 417 | 2254.05 | 0 | 0 | 0 | 24.5
22:00 | 2995 | 1591 | 902 | 0 | 172 | 1454 | 80 | 4595 | 0 | 408 | 2053 | 0 | 0 | 0 | 49
22:30 | 3015.5 | 1585.5 | 901.5 | 0 | 170 | 1460 | 80 | 4595 | 0 | 391.5 | 1820.25 | 0 | 0 | 0 | 44.5
23:00 | 3036 | 1580 | 901 | 0 | 168 | 1466 | 80 | 4595 | 0 | 375 | 1587.5 | 0 | 0 | 0 | 40
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 10-03-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 396 | 04:00 | 367 | 11:00 | Madunaghat | 403 | 05:00 | 386 | 11:00
Amtali | 414 | 05:00 | 403 | 12:00 | Meghnaghat | 397 | 04:00 | 370 | 11:00
Ashuganj | 399 | 4:00 | 372 | 16:00 | Payra | 416 | 05:00 | 407 | 11:00
Bhulta | 397 | 04:00 | 367 | 16:00 | Rahanpur | 407 | 02:00 | 391 | 13:00
Bibiana | 407 | 04:00 | 394 | 16:00 | Rampal | 407 | 05:00 | 391 | 15:00
BIPTC | 407 | 06:00 | 387 | 13:00
Bogura | 396 | 18:30 | 374 | 12:00
Gopalganj | 403 | 04:00 | 384 | 11:00
Kaliakoir | 392 | 04:00 | 355 | 12:00
Korerhat | 406 | 04:00 | 383 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 235 | 04:00 | 213 | 11:00 | Jhenaidah | 234 | 06:00 | 218 | 13:00
AKSML | 233 | 04:00 | 218 | 11:00 | Kachua | 231 | 03:00 | 217 | 11:00
Aminbazar | 234 | 03:00 | 214 | 10:00 | Kaliakoir | 238 | 04:00 | 216 | 12:00
Ashuganj | 232 | 05:00 | 216 | 12:00 | Keranigonj | 233 | 04:00 | 211 | 11:00
Ashuganj-400 | 232 | 05:00 | 216 | 12:00 | Khulna(S) | 235 | 05:00 | 221 | 13:00
Baghabari | 233 | 02:00 | 221 | 11:00 | Korerhat | 229 | 03:00 | 216 | 02:00
Barapukuria | 222 | 03:00 | 197 | 13:00 | Madunaghat | 231 | 04:00 | 219 | 11:00
Barapukuria-230 | 222 | 03:00 | 197 | 13:00 | Madunaghat-400 | 232 | 19:00 | 220 | 11:00
Barishal | 230 | 05:00 | 222 | 15:00 | Maniknagar | 231 | 03:00 | 213 | 11:00
Bheramara | 235 | 06:00 | 221 | 11:00 | Meghnaghat | 241 | 04:00 | 222 | 11:00
Bhulta | 233 | 04:00 | 213 | 16:00 | Meghnaghat-400 | 236 | 04:00 | 218 | 11:00
Bibiana | 237 | 03:00 | 226 | 16:00 | Mirsorai | 238 | 04:00 | 224 | 11:00
BIPTC | 237 | 06:00 | 222 | 09:00 | Rajshahi | 233 | 06:00 | 219 | 09:00
Bogura | 234 | 02:00 | 218 | 13:00 | Rampal | 232 | 03:00 | 220 | 15:00
Bogura-400 | 233 | 02:00 | 220 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Borhanuddin | 235 | 06:00 | 229 | 13:00 | Rampura | 232 | 04:00 | 211 | 16:00
BSRM | 231 | 04:00 | 216 | 11:00 | Shikalbaha | 232 | 18:00 | 218 | 11:00
Chowmuhani | 231 | 04:00 | 215 | 11:00 | Shyampur | 233 | 04:00 | 212 | 11:00
Cumilla(N) | 232 | 04:00 | 217 | 11:00 | Siddhirganj | 233 | 05:00 | 216 | 11:00
Faridpur | 227 | 06:00 | 215 | 13:00 | Sirajgonj | 236 | 02:00 | 227 | 11:00
Fenchuganj | 239 | 04:00 | 230 | 16:00 | Sreepur | 229 | 03:00 | 211 | 16:00
Feni | 230 | 02:00 | 217 | 11:00 | Tongi | 232 | 04:00 | 212 | 11:00
Ghorashal | 240 | 06:00 | 215 | 12:00
Ghorashal-230 | 231 | 04:00 | 212 | 12:00
Gopalganj | 226 | 04:00 | 216 | 11:00
GPH | 231 | 18:30 | 217 | 11:00
Haripur | 234 | 04:00 | 216 | 11:00
Hasnabad | 234 | 04:00 | 211 | 11:00
Hathazari | 230 | 03:00 | 217 | 11:00
Ishurdi | 238 | 05:00 | 223 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 01:00 | 126 | 11:00 | Magura | 134 | 04:00 | 121 | 13:00
Agargaon | 139 | 04:00 | 125 | 11:00 | Mahasthangarh | 135 | 02:00 | 123 | 13:00
Agrabad | 132 | 04:00 | 120 | 22:00 | Maijdee | 129 | 04:00 | 120 | 11:00
AKS | 130 | 18:00 | 123 | 11:00 | Manikganj | 130 | 04:00 | 116 | 16:00
Aminbazar | 137 | 03:00 | 122 | 10:00 | Maniknagar | 138 | 00:00 | 119 | 12:00
Amnura | 137 | 03:00 | 126 | 11:00 | Matarbari | 121 | 13:00 | 110 | 11:00
Ashuganj | 141 | 07:00 | 131 | 14:00 | Matuail | 132 | 03:00 | 116.4 | 14:00
Bagerhat | 132 | 06:00 | 117 | 19:00 | Metrorail_Motijheel | 134 | 02:00 | 119 | 12:00
Bajitpur | 132 | 04:00 | 121 | 16:00 | Metrorail_Uttara | 136 | 02:00 | 121 | 10:00
Bakerganj | 135 | 06:00 | 129 | 12:00 | Millgate | 136 | 04:00 | 121 | 11:00
Bakulia | 134 | 04:00 | 123 | 11:00 | Mirpur | 135 | 03:00 | 120 | 11:00
Banani | 139 | 03:00 | 123 | 11:00 | Mirzapur | 135 | 04:00 | 121 | 14:00
Bangabhaban | 133 | 04:00 | 119 | 11:00 | Mithapukur | 134 | 04:00 | 120 | 13:00
Barapukuria | 137 | 02:00 | 121 | 13:00 | MI_Cement | 133 | 03:00 | 117 | 11:00
Barguna | 134 | 05:00 | 129 | 12:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 133 | 05:00 | 127 | 12:00 | Mogbazar | 139 | 04:00 | 125 | 11:00
Barishal-230 | 134 | 07:00 | 128 | 13:00 | Mongla | 131 | 06:00 | 119 | 19:00
Baroaulia | 131 | 17:00 | 124 | 11:00 | Motijheel | 133 | 04:00 | 119 | 11:00
Baroirhat | 132 | 05:00 | 123 | 11:00 | Muktagacha | 128 | 04:00 | 116 | 12:00
Bashundhara | 138 | 03:00 | 124 | 16:00 | Munshiganj | 130 | 18:00 | 121 | 10:00
BashundharaCement | 133 | 09:00 | 123 | 10:00 | Muradnagar | 130 | 04:00 | 120 | 14:00
Beanibazar | 130 | 04:00 | 121 | 16:00 | Mymensingh | 128 | 05:00 | 114 | 16:00
Benapole | 131 | 06:00 | 116 | 13:00 | Naogaon | 134 | 01:00 | 121 | 13:00
Bhaluka | 134 | 05:00 | 122 | 17:00 | Narail | 135 | 06:00 | 121 | 13:00
Bhandaria | 132 | 04:00 | 125 | 13:00 | Narinda | 138 | 00:00 | 119 | 12:00
Bhangura | 154 | 15:00 | 124 | 10:00 | Narshingdi | 127 | 06:00 | 117 | 12:00
Bheramara | 136 | 06:00 | 129 | 13:00 | Natore | 135 | 04:00 | 125 | 13:00
Bheramara(GK) | 135 | 05:00 | 128 | 16:00 | Nawabganj | 137 | 04:00 | 122 | 11:00
Bhulta | 125 | 03:00 | 120 | 11:00 | Netrakona | 124 | 05:00 | 111 | 14:00
Bog-Sherpur | 136 | 02:00 | 126 | 12:00 | New | 135 | 05:00 | 122 | 11:00
Bogura | 138 | 19:30 | 127 | 13:00 | Niamatpur | 134 | 02:00 | 128 | 10:00
Bogura-230 | 138 | 02:00 | 127 | 13:00 | Noapara | 133 | 05:00 | 121 | 15:00
Brahmanbaria | 135 | 05:00 | 124 | 16:00 | Pabna | 135 | 05:00 | 127 | 12:00
Cantonment | 138 | 04:00 | 124 | 12:00 | Palashbari | 133 | 04:00 | 119 | 13:00
Chandina | 134 | 04:00 | 124 | 11:00 | Panchagarh | 139 | 04:00 | 118 | 13:00
Chandpur | 136 | 04:00 | 123 | 11:00 | Patiya | 130 | 16:00 | 124 | 11:00
Chandraghona | 135 | 04:00 | 127 | 10:00 | Patuakhali | 134 | 19:30 | 128 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 134 | 05:00 | 128 | 11:00 | Payra | 135 | 00:00 | 132 | 12:00
Charsaidpur | 132 | 03:00 | 121 | 11:00 | PHP | 132 | 04:00 | 123 | 11:00
Chauddagram | 131 | 04:00 | 122 | 11:00 | Postogola | 137 | 18:00 | 120 | 11:00
Chhatak | 129 | 06:00 | 121 | 15:00 | Pubail | N/A | N/A | N/A | N/A
Chowmuhani | 130 | 02:00 | 120 | 10:00 | Purbachal | 138 | 02:00 | 124 | 16:00
Chuadanga | 132 | 05:00 | 119 | 13:00 | Purbasadipur | 133 | 04:00 | 117 | 13:00
Coxsbazar | 121 | 13:00 | 110 | 11:00 | Rahanpur | 136 | 04:00 | 130 | 13:00
Cumilla(N) | 133 | 03:00 | 124 | 11:00 | Rahanpur-400 | 137 | 02:00 | 131 | 10:00
Cumilla(S) | 134 | 04:00 | 115 | 14:00 | Rahim | 132 | 05:00 | 122 | 11:00
Daganbhuiyan | 131 | 04:00 | 122 | 11:00 | Rajbari | 130 | 04:00 | 122 | 15:00
Daudkandi | 129 | 04:00 | 117 | 11:00 | Rajendrapur | 135 | 05:00 | 123 | 17:00
DhakaUniversity | 139 | 04:00 | 125 | 13:00 | Rajshahi | 134 | 06:00 | 124 | 12:00
Dhamrai | 139 | 04:00 | 127 | 11:00 | Rajshahi-230 | 134 | 06:00 | 126 | 09:00
Dhanmondi | 138.6 | 04:00 | 125.5 | 16:00 | Ramganj | 131 | 04:00 | 120 | 11:00
Dohazari | 127 | 06:00 | 120 | 11:00 | Rampur | 131 | 02:00 | 122 | 11:00
Faridpur | 131 | 03:00 | 125 | 11:00 | Rampura | 139 | 04:00 | 125 | 16:00
Fatullah | 135 | 18:30 | 118 | 11:00 | Rangamati | 133 | 04:00 | 126 | 11:00
Fenchuganj | 135 | 06:00 | 129 | 16:00 | Rangpur | 135 | 02:00 | 121 | 13:00
Feni | 128 | 04:00 | 121 | 11:00 | Ruppur | 136 | 02:00 | 129 | 16:00
Feni-230 | 130 | 04:00 | 122 | 11:00 | Saidpur | 133 | 02:00 | 120 | 13:00
Ghatail | 128 | 04:00 | 116 | 12:00 | Satkhira | 132 | 06:00 | 118 | 19:00
Ghorashal | 140 | 03:00 | 129 | 11:00 | Satmasjid | 139 | 04:00 | 125 | 12:00
Goalpara | 136 | 06:00 | 124 | 13:00 | Savar | 137 | 04:00 | 120 | 10:00
Gollamari | 135 | 06:00 | 125 | 15:00 | SevenRings | 140 | 04:00 | 127 | 14:00
Gopalganj | 133 | 05:00 | 125 | 12:00 | ShahCement | 132 | 03:00 | 121 | 11:00
Gopalganj-400 | 134 | 04:00 | 127 | 12:00 | Shahjadpur | 136 | 01:00 | 130 | 10:00
Gulshan | 137 | 02:00 | 125 | 12:00 | Shahjibazar | 135 | 04:00 | 121 | 16:00
Halishahar | 134 | 04:00 | 123 | 11:00 | Shahmirpur | 132 | 03:00 | 126 | 11:00
Haripur | 132 | 04:00 | 122 | 11:00 | Shariatpur | 133 | 04:00 | 125 | 13:00
HaripurSBU | 131 | 04:00 | 122 | 11:00 | Sherpur | 125 | 17:00 | 110 | 12:00
Hasnabad | 134 | 05:00 | 120 | 11:00 | Shikalbaha | 124 | 05:00 | 115 | 11:00
Hathazari | 135 | 02:00 | 129 | 10:00 | Shikalbaha-230 | 134 | 04:00 | 126 | 11:00
Hatirjheel | 139 | 04:00 | 125 | 14:00 | Shitalakhya | 133 | 03:00 | 117 | 11:00
Ishurdi | 138 | 06:00 | 130 | 16:00 | Sholosohor | 134 | 04:00 | 126 | 11:00
Jaldhaka | 131 | 04:00 | 116 | 13:00 | Shyampur | 132 | 04:00 | 120 | 11:00
Jamalpur | 130 | 03:00 | 115 | 12:00 | Shyampur-230 | 134 | 04:00 | 121 | 11:00
Jashore | 132 | 06:00 | 118 | 13:00 | Siddhirganj | 133 | 04:00 | 122 | 11:00
Jhenaidah | 134 | 05:00 | 115 | 12:00 | Sirajganj | 134 | 06:00 | 124 | 09:00
Jhenaidah-230 | 135 | 05:00 | 124 | 13:00 | Sonargaon | 129 | 18:00 | 121 | 16:00
Joydebpur | 133 | 03:00 | 120 | 16:00 | Sreemongol | 130 | 06:00 | 123 | 14:00
Joypurhat | 131 | 01:00 | 117 | 13:00 | Sreepur | 138 | 03:00 | 126 | 16:00
Juldah | 134 | 02:00 | 124 | 11:00 | Srinagar | 136 | 03:00 | 123 | 11:00
Kabirpur | 139 | 04:00 | 118 | 11:00 | SSM | 135 | 00:00 | 130 | 11:00
Kachua | 132 | 03:00 | 123 | 11:00 | Sunamganj | 126 | 06:00 | 120 | 16:00
Kaliakoir | 142 | 04:00 | 128 | 12:00 | Sylhet | 131 | 06:00 | 123 | 16:00
Kaliganj | 135 | 03:00 | 122 | 13:00 | Sylhet-132 | 129 | 04:00 | 125 | 13:00
Kallyanpur | 136 | 05:00 | 121 | 10:00 | Tangail | 128 | 04:00 | 117 | 12:00
Kalurghat | 134 | 04:00 | 127 | 11:00 | Taraganj | 132 | 00:00 | 121 | 13:00
Kamrangirchar | 136 | 04:00 | 119 | 11:00 | Tasnim | 130 | 04:00 | 121 | 12:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 136 | 18:30 | 116 | 13:00
Kasba | 130 | 06:00 | 120 | 11:00 | TK | 134 | 18:00 | 126 | 11:00
Kazla | 133 | 05:00 | 118 | 12:00 | Tongi | 136 | 04:00 | 124 | 11:00
Keranigonj | 137 | 04:00 | 123 | 11:00 | Ullahpara | 134 | 04:00 | 124 | 13:00
Khagrachori | 133 | 04:00 | 125 | 11:00 | Ullon | 138 | 04:00 | 125 | 14:00
Khulna | 134 | 05:00 | 123 | 13:00 | Uttara | 136 | 03:00 | 121 | 11:00
Khulna(S) | 135 | 06:00 | 125 | 13:00 | UttaraNew | 136 | 02:00 | 121 | 10:00
Khulshi | 131 | 04:00 | 122 | 11:00 | Zigatola | 137 | 05:00 | 123 | 11:00
Kishoreganj | 132 | 06:00 | 120 | 15:00
Kodda | 138 | 04:00 | 121 | 07:00
Korerhat | 133 | 03:00 | 126 | 11:00
KSRM | 132 | 02:00 | 124 | 11:00
Kulaura | 134 | 06:00 | 128 | 14:00
Kurigram | 132 | 00:00 | 117 | 13:00
Kushtia | 131 | 05:00 | 121 | 13:00
Laksam | 133 | 04:00 | 124 | 11:00
Lakshmipur | 129 | 04:00 | 120 | 11:00
Lalbag | 136 | 05:00 | 123 | 11:00
Lalmonirhat | 131 | 00:00 | 117 | 13:00
Madanganj | 133 | 09:00 | 123 | 10:00
Madaripur | 134 | 06:00 | 127 | 15:00
Madartek | 136 | 03:00 | 124 | 16:00
Madunaghat | 134 | 03:00 | 128 | 10:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division