## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 11-03-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 13372.5 | 0 |  | 13372.5
1:00 | 12913.7 | 0 |  | 12913.7
2:00 | 12366.5 | 0 |  | 12366.5
3:00 | 12570.1 | 0 |  | 12570.1
4:00 | 12871.6 | 0 |  | 12871.6
5:00 | 11783.4 | 0 |  | 11783.4
6:00 | 10953.5 | 0 |  | 10953.5
7:00 | 10933.81 | 38 |  | 10973.52
8:00 | 11456.37 | 53 |  | 11511.37
9:00 | 12249.57 | 71 |  | 12323.57
10:00 | 12660.76 | 316 |  | 12990.76
11:00 | 13077.95 | 206 |  | 13292.95
12:00 | 13333.42 | 278 |  | 13624.42
13:00 | 13619.66 | 320 |  | 13953.66
14:00 | 13822.07 | 496 |  | 14340.07
15:00 | 13581.53 | 499 |  | 14102.53
16:00 | 13664.81 | 467 |  | 14152.81
17:00 | 13977.91 | 197 |  | 14183.91
18:00 | 14155.64 | 111 |  | 14271.64
19:00 | 14567.25 | 99 |  | 14670.25
19:30 | 14785.74 | 139 |  | 14930.74
20:00 | 14780.96 | 125 |  | 14911.96
21:00 | 14856.09 | 100 |  | 14960.09
22:00 | 14740.22 | 116 |  | 14861.22
23:00 | 14256.53 | 90 |  | 14350.53
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## En-Curve
QF-LDC-12
Date | 11-03-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3018 | 1599 | 902 | 0 | 168 | 1447 | 80 | 4609 | 0 | 348 | 1201.5 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3019 | 1576 | 901.5 | 0 | 163 | 1377 | 80 | 4537.5 | 0 | 319 | 1170.1 | 0 | 0 | 0 | 0 | 11-03-2026
01:00 | 3020 | 1553 | 901 | 0 | 158 | 1307 | 80 | 4466 | 0 | 290 | 1138.7 | 0 | 0 | 0 | 0
01:30 | 2911 | 1505 | 901 | 0 | 157 | 1265 | 80 | 4393.5 | 0 | 280 | 1147.6 | 0 | 0 | 0 | 0 | Energy Generated | 320.2188 |  | MKWHr
02:00 | 2802 | 1457 | 901 | 0 | 156 | 1223 | 80 | 4321 | 0 | 270 | 1156.5 | 0 | 0 | 0 | 0 | Energy not Served | 3.582 |  | MKWHr
02:30 | 2771 | 1446 | 901 | 0 | 155 | 1273.5 | 80 | 4349 | 0 | 291.5 | 1201.3 | 0 | 0 | 0 | 0 | Total Energy Requirement | 323.8008 |  | MKWHr
03:00 | 2740 | 1435 | 901 | 0 | 154 | 1324 | 80 | 4377 | 0 | 313 | 1246.1 | 0 | 0 | 0 | 0
03:30 | 2874.5 | 1465 | 901 | 0 | 154 | 1387.5 | 80 | 4457 | 0 | 274.5 | 1127.35 | 0 | 0 | 0 | 0
04:00 | 3009 | 1495 | 901 | 0 | 154 | 1451 | 80 | 4537 | 0 | 236 | 1008.6 | 0 | 0 | 0 | 0
04:30 | 3020.5 | 1509.5 | 901 | 0 | 150 | 1390.5 | 80 | 4407 | 0 | 144 | 725 | 0 | 0 | 0 | 0
05:00 | 3032 | 1524 | 901 | 0 | 146 | 1330 | 80 | 4277 | 0 | 52 | 441.4 | 0 | 0 | 0 | 0
05:30 | 2973 | 1506.5 | 830.5 | 0 | 141 | 1246.5 | 80 | 4175 | 0 | 43 | 372.95 | 0 | 0 | 0 | 0
06:00 | 2914 | 1489 | 760 | 0 | 136 | 1163 | 80 | 4073 | 0 | 34 | 304.5 | 0 | 0 | 0 | 0
06:30 | 2938 | 1499.5 | 755 | 0 | 133 | 1171.5 | 80 | 4049 | 20.405 | 25.5 | 271.75 | 0 | 0 | 0 | 19
07:00 | 2962 | 1510 | 750 | 0 | 130 | 1180 | 80 | 4025 | 40.81 | 17 | 239 | 0 | 0 | 0 | 38
07:30 | 3011.5 | 1517.5 | 684 | 0 | 129 | 1252 | 80 | 4121.5 | 99.09 | 43 | 257.5 | 0 | 0 | 0 | 45.5
08:00 | 3061 | 1525 | 618 | 0 | 128 | 1324 | 80 | 4218 | 157.37 | 69 | 276 | 0 | 0 | 0 | 53
08:30 | 3043 | 1526 | 760 | 0 | 137 | 1388.87 | 80 | 4291 | 233.6 | 101 | 292.5 | 0 | 0 | 0 | 62
09:00 | 3025 | 1527 | 902 | 0 | 146 | 1453.74 | 80 | 4364 | 309.83 | 133 | 309 | 0 | 0 | 0 | 71
09:30 | 2998 | 1506.5 | 902.5 | 0 | 144 | 1449.92 | 80 | 4406 | 381.245 | 145.5 | 441.5 | 0 | 0 | 0 | 193.5
10:00 | 2971 | 1486 | 903 | 0 | 142 | 1446.1 | 80 | 4448 | 452.66 | 158 | 574 | 0 | 0 | 0 | 316
10:30 | 2997.5 | 1476.5 | 903 | 0 | 153 | 1447.825 | 80 | 4473.5 | 500.78 | 176 | 661.25 | 0 | 0 | 0 | 261
11:00 | 3024 | 1467 | 903 | 0 | 164 | 1449.55 | 80 | 4499 | 548.9 | 194 | 748.5 | 0 | 0 | 0 | 206
11:30 | 3053 | 1491.5 | 903 | 0 | 164 | 1452.025 | 80 | 4483 | 565.51 | 199 | 814.65 | 0 | 0 | 0 | 242
12:00 | 3082 | 1516 | 903 | 0 | 164 | 1454.5 | 80 | 4467 | 582.12 | 204 | 880.8 | 0 | 0 | 0 | 278
12:30 | 3113.5 | 1536 | 903 | 0 | 171 | 1455.71 | 80 | 4469 | 558.83 | 221 | 968.5 | 0 | 0 | 0 | 299
13:00 | 3145 | 1556 | 903 | 0 | 178 | 1456.92 | 80 | 4471 | 535.54 | 238 | 1056.2 | 0 | 0 | 0 | 320
13:30 | 3152 | 1550 | 903 | 0 | 185 | 1459.33 | 80 | 4524 | 505.385 | 228.5 | 1132.15 | 0 | 0 | 1.5 | 408
14:00 | 3159 | 1544 | 903 | 0 | 192 | 1461.74 | 80 | 4577 | 475.23 | 219 | 1208.1 | 0 | 0 | 3 | 496
14:30 | 3069 | 1496.5 | 902.5 | 0 | 189 | 1454.375 | 80 | 4506 | 406.775 | 225.5 | 1369.65 | 0 | 0 | 2.5 | 497.5
15:00 | 2979 | 1449 | 902 | 0 | 186 | 1447.01 | 80 | 4435 | 338.32 | 232 | 1531.2 | 0 | 0 | 2 | 499
15:30 | 2972.5 | 1419 | 902 | 0 | 185 | 1453.185 | 80 | 4446 | 263.035 | 232 | 1664.95 | 0 | 0 | 5.5 | 483
16:00 | 2966 | 1389 | 902 | 0 | 184 | 1459.36 | 80 | 4457 | 187.75 | 232 | 1798.7 | 0 | 0 | 9 | 467
16:30 | 3025 | 1445 | 902.5 | 0 | 177 | 1452.325 | 80 | 4455.5 | 129.685 | 266 | 1879.35 | 0 | 0 | 9 | 332
17:00 | 3084 | 1501 | 903 | 0 | 170 | 1445.29 | 80 | 4454 | 71.62 | 300 | 1960 | 0 | 0 | 9 | 197
17:30 | 3099 | 1513.5 | 903 | 0 | 165 | 1445.465 | 80 | 4412 | 36.31 | 326.5 | 2079.5 | 0 | 0 | 6.5 | 154
18:00 | 3114 | 1526 | 903 | 0 | 160 | 1445.64 | 80 | 4370 | 1 | 353 | 2199 | 0 | 0 | 4 | 111
18:30 | 3124.5 | 1532.5 | 902.5 | 0 | 171 | 1445.545 | 80 | 4390.5 | 0.5 | 410.5 | 2301.4 | 0 | 0 | 2.5 | 105
19:00 | 3135 | 1539 | 902 | 0 | 182 | 1445.45 | 80 | 4411 | 0 | 468 | 2403.8 | 0 | 0 | 1 | 99
19:30 | 3120 | 1567 | 764 | 0 | 174 | 1444.94 | 80 | 4527 | 0 | 613 | 2495.8 | 0 | 0 | 0 | 139
20:00 | 3126 | 1566 | 666 | 0 | 170 | 1451.56 | 80 | 4583 | 0 | 643 | 2495.4 | 0 | 0 | 0 | 125
20:30 | 3113.5 | 1567 | 729.5 | 0 | 173 | 1450.375 | 80 | 4583 | 0 | 643.5 | 2478.65 | 0 | 0 | 0 | 112.5
21:00 | 3101 | 1568 | 793 | 0 | 176 | 1449.19 | 80 | 4583 | 0 | 644 | 2461.9 | 0 | 0 | 0 | 100
21:30 | 3084 | 1559 | 847.5 | 0 | 175 | 1444.105 | 80 | 4571.5 | 0 | 650 | 2387.05 | 0 | 0 | 0 | 108
22:00 | 3067 | 1550 | 902 | 0 | 174 | 1439.02 | 80 | 4560 | 0 | 656 | 2312.2 | 0 | 0 | 0 | 116
22:30 | 3065 | 1547 | 901.5 | 0 | 173 | 1438.275 | 80 | 4555 | 0 | 615.5 | 2123.1 | 0 | 0 | 0 | 103
23:00 | 3063 | 1544 | 901 | 0 | 172 | 1437.53 | 80 | 4550 | 0 | 575 | 1934 | 0 | 0 | 0 | 90
Executive Engineer
Network Operation Division

## L-Curve
QF-LDC-11
Date | 11-03-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7174.5 | 6198 | 13372.5 | DAILY GENERATION CURVE
00:30 | 7091.1 | 6052 | 13143.1
01:00 | 7007.7 | 5906 | 12913.7 | 11-03-2026
01:30 | 6940.6 | 5699.5 | 12640.1
02:00 | 6873.5 | 5493 | 12366.5
02:30 | 6893.8 | 5574.5 | 12468.3
03:00 | 6914.1 | 5656 | 12570.1
03:30 | 6862.35 | 5858.5 | 12720.85
04:00 | 6810.6 | 6061 | 12871.6
04:30 | 6449 | 5878.5 | 12327.5
05:00 | 6087.4 | 5696 | 11783.4
05:30 | 5935.45 | 5433 | 11368.45
06:00 | 5783.5 | 5170 | 10953.5
06:30 | 5770.15 | 5173.505 | 10943.655
07:00 | 5756.8 | 5177.01 | 10933.81
07:30 | 5929.85 | 5265.24 | 11195.09
08:00 | 6102.9 | 5353.47 | 11456.37
08:30 | 6153.375 | 5699.595 | 11852.97
09:00 | 6203.85 | 6045.72 | 12249.57
09:30 | 6280.185 | 6174.98 | 12455.165
10:00 | 6356.52 | 6304.24 | 12660.76
10:30 | 6509.525 | 6359.83 | 12869.355
11:00 | 6662.53 | 6415.42 | 13077.95
11:30 | 6768.53 | 6437.155 | 13205.685
12:00 | 6874.53 | 6458.89 | 13333.42
12:30 | 7028.46 | 6448.08 | 13476.54
13:00 | 7182.39 | 6437.27 | 13619.66
13:30 | 7256.455 | 6464.41 | 13720.865
14:00 | 7330.52 | 6491.55 | 13822.07
14:30 | 7356.65 | 6345.15 | 13701.8
15:00 | 7382.78 | 6198.75 | 13581.53
15:30 | 7440.755 | 6182.415 | 13623.17
16:00 | 7498.73 | 6166.08 | 13664.81
16:30 | 7606.435 | 6214.925 | 13821.36
17:00 | 7714.14 | 6263.77 | 13977.91
17:30 | 7763.57 | 6303.205 | 14066.775
18:00 | 7813 | 6342.64 | 14155.64
18:30 | 7920.9 | 6440.545 | 14361.445
19:00 | 8028.8 | 6538.45 | 14567.25
19:30 | 8205.8 | 6579.94 | 14785.74
20:00 | 8211.4 | 6569.56 | 14780.96
20:30 | 8167.65 | 6650.875 | 14818.525 |  | Executive Engineer
21:00 | 8123.9 | 6732.19 | 14856.09 |  | Network Operation Division
21:30 | 8018.95 | 6779.205 | 14798.155
22:00 | 7914 | 6826.22 | 14740.22
22:30 | 7753.5 | 6744.875 | 14498.375
23:00 | 7593 | 6663.53 | 14256.53

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 11-03-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13333.42 | MW | 12:00 Hr. | Energy Generated |  |  | 320.2188 |  | MKWHr.
| Day Peak Demand |  |  | 13624.42 | MW | 12:00 Hr. | Energy Unserverd |  |  | 3.582 |  | MKWHr.
| Evening Peak Generation |  |  | 14856.09 | MW | 21:00 Hr. | Energy Demand |  |  | 323.8008 |  | MKWHr.
| Evening Peak Demand |  |  | 14960.09 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32.1 |  | °C
| Minimum Generation of the Day |  |  | 10933.81 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 814.73 |  | MMCFD
| Maximum Generation of the Day |  |  | 14856.09 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.6629 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 31.1072 | 0 | 17.087 | 0 | 0 | 0.17144 | 0 | 0 | 48.3656 | Gas | 110.7504 | Gas | 379549868.7264
| Chattogram Zone |  |  | 4.337 | 47.4709 | 5.3681 | 0 | 1.9197 | 0.1178 | 0 | 0.0264 | 59.24 | Coal | 106.8561 | Coal | 697585597.4515
| Cumilla Zone |  |  | 22.5066 | 0 | 6.0552 | 0 | 0 | 0.39435 | 3.8909 | 0 | 32.847 | HFO | 38.555 | HFO | 657030009.02
| Mymensingh Zone |  |  | 0.21312 | 0 | 3.7678 | 0 | 0 | 0.23865 | 0 | 0 | 4.2195 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.5344 | 0 | 0 | 0 | 0 | 0.054461 | 0 | 0 | 26.5889 | Hydro | 1.9197 | Hydro | 191970
| Khulna Zone |  |  | 4.3212 | 26.3927 | 0.2135 | 0 | 0 | 0.5076 | 20.8989 | 0 | 52.3339 | Solar | 3.7571 | Solar | 60178541.992
| Barishal Zone |  |  | 8.206 | 32.31 | 0.81547 | 0 | 0 | 0.002854 | 0 | 0 | 41.3343 | Import | 58.354 | Import | 338658061.89
| Rajshahi Zone |  |  | 13.5249 | 0 | 2.3376 | 0 | 0 | 1.1196 | 33.5642 | 0 | 50.5462 | Wind | 0.0264 | Wind | 388344
| Rangpur Zone |  |  | 0 | 0.68247 | 2.9105 | 0 | 0 | 1.1504 | 0 | 0 | 4.7434
| Total |  |  | 110.7504 | 106.8561 | 38.555 | 0 | 1.9197 | 3.7571 | 58.354 | 0.0264 | 320.2188
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 379549868.7264 |  | Hydro | 191970
|  |  |  | Coal | 697585597.4515 |  | Solar | 60178541.992
|  |  |  | HFO | 657030009.02 |  | Import | 338658061.89
|  |  |  | HSD | 0 |  | Wind | 388344
[5 empty] | Total: | 213,35,82,393 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.8989 | Peak Hr Flow | 793.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 44510709.09 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 33.5642 | Peak Hr Flow | 1449.19 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2122 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.8909 | Peak Hr Flow | 176.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2605 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 58.354 | Peak Hr Flow | 2418.19 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5463
|  |  |  | Chattogram |  | 40 |  | 1416
|  |  |  | Cumilla |  | 15 |  | 1370
|  |  |  | Mymensingh |  | 25 |  | 1217
|  |  |  | Sylhet |  | 10 |  | 570
|  |  |  | Khulna |  | 10 |  | 1672
|  |  |  | Barishal |  | 0 |  | 414
|  |  |  | Rajshahi |  | 0 |  | 1459
|  |  |  | Rangpur |  | 0 |  | 892
|  |  |  | Total |  | 100 |  | 14473
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:20 | 14:37 | Gallamari- Khulna (S) 132kV Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end. and from
Gollamari 132/33kV end Due to OPGW inspection work.
|  | 08:22 | Sreemongol 132/33kV S/S 132/33kv T-3 HT is restored.
| 08:25 | 16:46 | Chowmuhani 230/132/33kV S/S Korerhat-04 Scheduled S/D Due to Painting and Silicon work
| 08:31 | 15:11 | Chowmuhani 230/132/33kV S/S ATR-02 LT Scheduled S/D Due to Shield wire and PI
resplendent.
| 08:31 | 15:11 | Chowmuhani 230/132/33kV S/S ATR-02 HT Scheduled S/D Due to Shield wire and PI
resplendent.
| 08:33 |  | Aminbazar-Keraniganj 230kV Ckt-2 Scheduled S/D from Keranigonj 230/132/33kV end Due to
Line disk insulator cleaning from Aminbazar end. Shut-down according to NLDC instraction.
and from Aminbazar 400/230/132kV end Due to Disc cleaning
| 09:06 | 16:26 | Sylhet-Sylhet (South) 132KV Ckt-2 Scheduled S/D from Sylhet 132/33kV end Due to Work of
Sylhet (South) end
| 09:15 | 16:05 | Baroirhat-Hathazari 132 kV Ckt-1 Scheduled S/D from Hathazari 230/132/33kV end.
| 09:33 |  | Khulna(S) 230/132kV S/S Rupsha Ckt-2 Project Work S/D Due to Project work at Transmission
line.
| 09:56 |  | Bhulta-Haripur 230 kV Ckt-1 Scheduled S/D from Bhulta 400/230kV end Due to OPGW Stringing
by EEGBPSP and from Haripur 230/132kV end Due to QPGW Changing work.
| 11:45 |  | Chandina 132/33kV S/S TR-2 LT Forced S/D Due to For isolator changing work by PDB.
Clearance by Md. Motiur Rahman (SAE) PDB.
| 12:06 |  | Baghabari 230/132kV S/S T-1 LT Scheduled S/D Due to Maintenance work
| 12:06 |  | Baghabari 230/132kV S/S T-1 HT Scheduled S/D Due to Maintenance work
| 12:24 | 12:35 | Bakerganj 132/33kV S/S T1 LT Scheduled S/D Due to 33 kV incoming 1 CT connection change.
| 12:25 | 12:35 | Bakerganj 132/33kV S/S T1 HT Scheduled S/D Due to 33 kV incoming 1 CT connection change
| 12:28 | 13:58 | BIPTC S/S 20DF31 Tripped showing 87 Differential Relay relays Due to Tripped by Capacitor
Unbalance R PH Stage 3 Operated
| 13:14 | 13:58 | BIPTC S/S 20DF31 Scheduled S/D Due to Tripped by Capacitor Unbalance R PH Stage 3
Operated.
|  | 13:30 | Jashore 132/33kV S/S JH-2(L1) is restored.
| 14:18 | 14:56 | Jashore-Noapara 132kV Ckt-1 Scheduled S/D from Noapara 132/33kV end Due to By the
instruction of ALDC.
| 14:18 | 14:56 | Jashore-Noapara 132kV Ckt-2 Scheduled S/D from Noapara 132/33kV end Due to By the
instruction of ALDC.
| 21:00 |  | Evening Peak Generation: 14855 MW.
| 23:14 |  | Barapukuria unit-1 was sync.
| 23:31 |  | Rampur 230/132/33 S/S Khulshi-1 Forced S/D Due to by the order of NLDC
| 06:36 |  | Mymensingh-Netrokona 132kV Ckt-2 Scheduled S/D from Mymensingh 132/33kV end Due to High
temperature maintenance work
| 07:20 |  | Ramganj 132/33kV S/S 132 Kv Bus-B Scheduled S/D Due to Hot spot maintenance.
| 07:21 |  | Ramganj 132/33kV S/S Transformer-01 LT Scheduled S/D Due to Hot spot maintenance.
| 07:22 |  | Ramganj 132/33kV S/S Transformer-01 HT Scheduled S/D Due to Hot spot maintenance
| 07:36 |  | Mymensingh 132/33kV S/S Bus B Scheduled S/D Due to Netrakona 2 ar B BUS loop high
temperature maintenance work.
| 07:39 |  | Kabirpur -Tongi 132kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Shutdown
taken by kabirpur via nldc
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 11-03-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 6 | 156818.18 | Demand "05"MW due to gas restiction by Titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 313 | 7822800 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 680706 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 250 | 6289039 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 49.2 | 867240 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 78 | 584160 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 817438 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 616431 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 494400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 493920 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 51 | 734880 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 292 | 3426164 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2883312 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1165440 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 166080 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 155 | 2404800 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 171442 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 335520 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 320 | 8001818.18 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 350 | 7848395 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 2404800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2482.2 | 48365603.36
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 487513.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 100035 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 664320 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1919700 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 225 | 3935259 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 46 | 393984 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 39 | 563201 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 448320 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 29 | 401760 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 104 | 1955520 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 17762 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 504000 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 50 | 351272 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1160 | 27725452 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 26400 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 830 | 19745454.55 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 2662.5 | 59239953.35
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 195 | 4993000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 290 | 7472200 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 250 | 6191000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1249806 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 143 | 1428509 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 17 | 212480 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2150431 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 181 | 2323200 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 176 | 3890880 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 301483 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 450170 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 63 | 249660 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 33600 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 101 | 1506240 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 394345 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1628.2 | 32847004
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 16 | 213120 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10650 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 77 | 1432800 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 98 | 1777200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 228000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 136560 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 421200 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 238 | 4219530
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 54461 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 987000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 157 | 3590509.09 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 70 | 1645000 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 41 | 965760 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 95 | 2307340 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 450840 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7536000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 377 | 9052000 | Due to Air Filter DP High FGMO not available.
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1113 | 26588910.09
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 793 | 20898909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 25 | 124800 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 30 | 88704 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 172 | 4321152 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 507600 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1229 | 26392720 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2249 | 52333885
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 45 | 312672 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2892000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1085 | 25808000 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5314020 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 78 | 502800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 279 | 6502000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2854 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1827 | 41334346
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 270244 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 41 | 217121 | Under Maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 23 | 184306 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 191 | 4435264 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 405 | 9089600 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 183980 | Machine problem and fuel shortage
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52 | 201816 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 26 | 155952 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 718176 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 676224 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 26100 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1449.19 | 33564187 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 277504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 545710 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2434.19 | 50546184
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 682472 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 1503974 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 32579.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1406478 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 160249 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 957600 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 222 | 4743352.16
Eastern Grid Total |  |  |  |  | 17400.108 | 8123.9 | 171261000.8
Western Grid Total |  |  |  |  | 11852.195 | 6732.19 | 148957767.16
National Grid Total |  |  |  |  | 29252.303 | 14856.09 | 320218767.96
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 12-03-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-03-2026 | during | 12-03-2026 | during | 12-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 6 | 6 | 97.7 | 97.7 | 7 | 7 | Demand "05"MW due to gas restiction by Titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 331 | 313 | 412 | 412 | 412 | 412 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 1 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 250 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 32.3 | 49.2 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 78 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 22 | 23 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 34 | 51 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 95 | 292 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 88 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 1 | 16 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 67 | 155 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 27 | 0 | 29 | 0 | 29 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 320 | 320 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 350 | 350 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 108 | 142 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1926.3 | 2482.2 | 5944.22 | 5915.22 | 3250.05 | 3222.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 7 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 46 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 80 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 221 | 225 | 220 | 225 | 220 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 46 | 0 | 0 | 56 | 64 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 39 | 34 | 34 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 50 | 50 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 29 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 98 | 104 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3 | 0 | 3.28 | 0 | 3.28 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 38 | 38 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 50 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1160 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 3 | 0 | 3 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 830 | 830 | 830 | 830 | 830 | 830 | Plant availability less
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2496.5 | 2662.5 | 3649.14 | 3649.86 | 3240.78 | 3249.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 207 | 195 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 290 | 290 | 353.35 | 353.35 | 353.35 | 353.35 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 318.81 | 318.81 | 282.81 | 282.81 | FGMO ON
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 250 | 250 | 393 | 393 | 340 | 340 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 143 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 10 | 17 | 32 | 32 | 32 | 32 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 163 | 163 | 100 | 100 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 18 | 181 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 164 | 176 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 19 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 63 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 15 | 101 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 60 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1172 | 1628.2 | 2736.51 | 2670.51 | 2218.36 | 2158.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-03-2026 | during | 12-03-2026 | during | 12-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 10 | 16 | 157.5 | 157.5 | 10 | 10 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 77 | 60 | 80 | 60 | 80 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 69 | 98 | 70 | 115 | 70 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 36.73 | 0 | 45.12 | 0 | 45.12 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 12 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 35 | 54.5 | 54.5 | 17 | 35 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 198.73 | 238 | 411.12 | 429 | 210.12 | 246
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 41 | 41 | 41 | 41 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 140 | 157 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 70 | 70 | 70 | 70 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 40 | 41 | 86 | 86 | 42 | 42 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 96 | 95 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 21 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 357 | 377 | 385 | 385 | 385 | 385 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1081 | 1113 | 1261 | 1261 | 1094 | 1094
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 903 | 793 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 25 | 44 | 44 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 30 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 184 | 172 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 80 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1115 | 1229 | 1234.2 | 1234.2 | 1148.28 | 1148.28 | plant availability zero
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2282 | 2249 | 3599.2 | 3514.2 | 2540.38 | 2455.38
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 45 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1085 | 1085 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 78 | 150 | 150 | 15 | 15 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 277 | 279 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.55 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1702.55 | 1827 | 2003.32 | 2002.32 | 1868.32 | 1867.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 41.93 | 0 | 48 | 0 | 48 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 41 | 47 | 47 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 23 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 200 | 191 | 220 | 220 | 220 | 220 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 364 | 405 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 21 | 21 | 21 | 21 | 21 | machine problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 26 | 34 | 34 | 34 | 34 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.26 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1454.5 | 1449.19 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 42.45 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 88 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2195.14 | 2434.19 | 3162.57 | 2947.87 | 2649.57 | 2434.87
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 50 | 50 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 49 | 107 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.2 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 50 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 25 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 150 | 0 | 159.6 | 0 | 159.6 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 279.2 | 222 | 506.8 | 312 | 422.8 | 228
System Total |  |  |  |  | 28823.2 | 29252.303 | 13333.42 | 14856.09 | 23273.88 | 22701.98 | 17494.38 | 16955.48
Forecast Scenario (12-03-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13570 |  | 0 |  | 13570
|  |  |  | 1:00 | 13110 |  | 0 |  | 13110
|  |  |  | 2:00 | 12560 |  | 0 |  | 12560
|  |  |  | 3:00 | 12770 |  | 0 |  | 12770
|  |  |  | 4:00 | 13070 |  | 0 |  | 13070
|  |  |  | 5:00 | 11980 |  | 0 |  | 11980
|  |  |  | 6:00 | 11150 |  | 0 |  | 11150
|  |  |  | 7:00 | 11170 |  | 0 |  | 11170
|  |  |  | 8:00 | 11710 |  | 0 |  | 11710
|  |  |  | 9:00 | 12520 |  | 0 |  | 12520
|  |  |  | 10:00 | 13190 |  | 0 |  | 13190
|  |  |  | 11:00 | 13490 |  | 0 |  | 13490
|  |  |  | 12:00 | 13820 |  | 0 |  | 13820
|  |  |  | 13:00 | 14150 |  | 0 |  | 14150
|  |  |  | 14:00 | 14540 |  | 0 |  | 14540
|  |  |  | 15:00 | 14300 |  | 0 |  | 14300
|  |  |  | 16:00 | 14350 |  | 0 |  | 14350
|  |  |  | 17:00 | 14380 |  | 0 |  | 14380
|  |  |  | 18:00 | 14470 |  | 0 |  | 14470
|  |  |  | 18:30 | 14600 |  | 0 |  | 14600
|  |  |  | 19:00 | 14870 |  | 0 |  | 14870
|  |  |  | 19:30 | 15130 |  | 0 |  | 15130
|  |  |  | 20:00 | 15110 |  | 0 |  | 15110
|  |  |  | 21:00 | 15160 |  | 0 |  | 15160
|  |  |  | 22:00 | 14940 |  | 0 |  | 14940
|  |  |  | 23:00 | 14300 |  | 0 |  | 14300
Probable Maximum Temperature: |  |  | 32.20°C
Probable Maximum Demand at Day Peak: |  |  | 13820.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15160.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13259.90 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 311.33362 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:14 hrs on 12-03-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 11-03-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9946.1 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4427.48 | MW
i) Dhaka area |  |  | 5463.1 |  | MW | i) Khulna area |  |  |  | 1662 | MW
ii) Chattogram area |  |  | 1376 |  | MW | ii) Barishal area |  |  |  | 414.48 | MW
iii) Cumilla area |  |  | 1355 |  | MW | iii) Rajshahi area |  |  |  | 1459 | MW
iv) Mymensingh area |  |  | 1192 |  | MW | iv) Rangpur area |  |  |  | 892 | MW
v) Sylhet area |  |  | 560 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14373.58 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 10 | 11:00 | 67 | Hasnabad | 86 | 18:00 | 133 | Nawabganj | 53 | 21:00
2 | AKSML | 10.3 | 14:00 | 68 | Hathazari | 74 | 19:00 | 134 | Netrakona | 140 | 20:00
3 | Aftabnagar | 36 | 21:00 | 69 | Hatirjheel | 44 | 15:00 | 135 | New | 77 | 14:00
4 | Agargaon | 108 | 14:00 | 70 | Ishurdi | 68 | 19:30 | 136 | Niamatpur | 93 | 22:00
5 | Agrabad | 56 | 15:00 | 71 | Jaldhaka | 78 | 18:00 | 137 | Noapara | 45 | 19:30
6 | Amnura | 36 | 20:00 | 72 | Jamalpur | 112 | 18:00 | 138 | PHP | 8 | 12:00
7 | Ashuganj | 114 | 00:00 | 73 | Jashore | 133 | 19:00 | 139 | Pabna | 88 | 19:30
8 | BSRM | 193 | 01:00 | 74 | Jhenaidah | 102 | 19:30 | 140 | Palashbari | 108 | 18:30
9 | Bagerhat | 83 | 22:00 | 75 | Joydebpur | 142 | 17:00 | 141 | Panchagarh | 56 | 18:00
10 | Bajitpur | 83 | 20:00 | 76 | Joypurhat | 66 | 21:00 | 142 | Patiya | 8 | 00:00
11 | Bakerganj | 12.48 | 21:00 | 77 | Juldah | 19 | 23:00 | 143 | Patuakhali | 49.7 | 22:00
12 | Bakulia | 74 | 22:00 | 78 | KSRM | 16 | 04:00 | 144 | Payra | 34 | 21:00
13 | Banani | 55.6 | 15:00 | 79 | Kabirpur | 257 | 14:00 | 145 | Postogola | 51 | 13:00
14 | Bangabhaban | 17 | 10:00 | 80 | Kachua | 87 | 18:00 | 146 | Pubail | 19 | 18:00
15 | Barapukuria | 69 | 22:00 | 81 | Kaliganj | 26 | 18:30 | 147 | Purbachal | 28 | 19:30
16 | Barguna | 16 | 00:00 | 82 | Kallyanpur | 108 | 19:00 | 148 | Purbasadipur | 132 | 17:00
17 | Barishal | 93 | 19:30 | 83 | Kalurghat | 53 | 12:00 | 149 | Rahanpur | 42 | 04:00
18 | Barishal-230 | 88 | 18:30 | 84 | Kamrangirchar | 83 | 17:00 | 150 | Rahim | 40 | 15:00
19 | Baroaulia | 67 | 12:00 | 85 | Kaptai | N/A | N/A | 151 | Rajbari | 70.5 | 19:00
20 | Baroirhat | 55 | 19:00 | 86 | Kasba | 38 | 21:00 | 152 | Rajendrapur | 129 | 19:30
21 | Bashundhara | 198 | 14:00 | 87 | Kazla | 113 | 15:00 | 153 | Rajshahi | 97 | 22:00
22 | BashundharaCement | 8 | 15:00 | 88 | Keranigonj | 82 | 21:00 | 154 | Rajshahi-230 | 78 | 22:00
23 | Beanibazar | 62 | 18:30 | 89 | Khagrachori | 34 | 18:30 | 155 | Ramganj | 96 | 19:00
24 | Benapole | 70 | 22:00 | 90 | Khulna | 58 | 19:00 | 156 | Rampur | 38 | 19:00
25 | Bhaluka | 135 | 19:30 | 91 | Khulshi | 191 | 19:30 | 157 | Rangamati | 16 | 18:30
26 | Bhandaria | 55 | 21:00 | 92 | Kishoreganj | 128 | 21:00 | 158 | Rangpur | 134 | 17:00
27 | Bhangura | 41 | 14:00 | 93 | Kodda | 312 | 21:00 | 159 | Ruppur | 3.6 | 10:00
28 | Bheramara(GK) | 55 | 19:30 | 94 | Kulaura | 43 | 18:30 | 160 | SSM | 8 | 23:00
29 | Bhulta | 220 | 11:00 | 95 | Kurigram | 72 | 18:00 | 161 | Saidpur | 107 | 17:00
30 | Bog-Sherpur | 74 | 22:00 | 96 | Kushtia | 134 | 20:00 | 162 | Satkhira | 136 | 21:00
31 | Bogura | 159 | 18:00 | 97 | Laksam | 20 | 22:00 | 163 | Satmasjid | 100 | 19:30
32 | Borhanuddin | 86 | 21:00 | 98 | Lakshmipur | 35 | 19:30 | 164 | Savar | 234 | 14:00
33 | Brahmanbaria | 124 | 16:00 | 99 | Lalbag | 74 | 12:00 | 165 | SevenRings | 18.67 | 07:00
34 | Cantonment | 98 | 14:00 | 100 | Lalmonirhat | 58 | 18:00 | 166 | ShahCement | 33 | 16:00
35 | Chandina | 20 | 04:00 | 101 | MI_Cement | 18.8 | 07:00 | 167 | Shahjadpur | 78 | 12:00
36 | Chandpur | 72 | 21:00 | 102 | Madanganj | 52 | 09:00 | 168 | Shahjibazar | 118 | 19:00
37 | Chandraghona | 34 | 20:00 | 103 | Madaripur | 101 | 21:00 | 169 | Shahmirpur | 59 | 00:00
38 | Chapai | 73 | 22:00 | 104 | Madartek | 73 | 21:00 | 170 | Shariatpur | 77 | 21:00
39 | Charsaidpur | 47 | 12:00 | 105 | Madunaghat | 49 | 14:00 | 171 | Sherpur | 162 | 18:00
40 | Chauddagram | 71 | 18:30 | 106 | Magura | 60 | 19:30 | 172 | Shikalbaha | 32 | 15:00
41 | Chhatak | 36 | 21:00 | 107 | Mahasthangarh | 80 | 21:00 | 173 | Shitalakhya | 83.6 | 16:00
42 | Chowmuhani | 125 | 19:30 | 108 | Maijdee | 43 | 21:00 | 174 | Sholosohor | 45 | 14:00
43 | Chuadanga | 114 | 19:00 | 109 | Manikganj | 126 | 19:00 | 175 | Shyampur | 174 | 12:00
44 | Coxsbazar | 136 | 21:00 | 110 | Maniknagar | 71 | 14:00 | 176 | Siddhirganj | 125 | 15:00
45 | Cumilla(N) | 125 | 23:00 | 111 | Matarbari | 47 | 04:00 | 177 | Sirajganj | 114 | 21:00
46 | Cumilla(S) | 187 | 14:00 | 112 | Matuail | 66 | 13:00 | 178 | Sonargaon | 150 | 08:00
47 | Daganbhuiyan | 31 | 19:00 | 113 | Metrorail_Motijheel | 46 | 16:00 | 179 | Sreemongol | 75 | 22:00
48 | Daudkandi | 152 | 20:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sreepur | 118 | 19:30
49 | DhakaUniversity | 74 | 13:00 | 115 | Millgate | 96 | 14:00 | 181 | Srinagar | 43.4 | 21:00
50 | Dhamrai | 130 | 08:00 | 116 | Mirpur | 141 | 14:00 | 182 | Sunamganj | 55 | 21:00
51 | Dhanmondi | 113 | 13:00 | 117 | Mirsorai | 49 | 09:00 | 183 | Sylhet | 53 | 19:00
52 | Dohazari | 91 | 00:00 | 118 | Mirzapur | 48 | 19:30 | 184 | Sylhet-132 | 98 | 21:00
53 | Faridpur | 150 | 20:00 | 119 | Mithapukur | 58 | 04:00 | 185 | TK | 21 | 19:00
54 | Fatullah | 102 | 15:00 | 120 | Modern | N/A | N/A | 186 | Tangail | 182 | 20:00
55 | Fenchuganj | 35 | 18:30 | 121 | Mogbazar | 79.7 | 15:00 | 187 | Taraganj | 24 | 17:00
56 | Feni | 99 | 21:00 | 122 | Mongla | 40 | 10:00 | 188 | Tasnim | 16 | 10:00
57 | GPH | 1 | 00:00 | 123 | Motijheel | 45 | 13:00 | 189 | Thakurgaon | 100 | 19:00
58 | Ghatail | 88 | 03:00 | 124 | Muktagacha | 39 | 17:00 | 190 | Tongi | 172 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 102 | 21:00 | 191 | Ullahpara | 41 | 19:30
60 | Ghorashal-230 | 109 | 00:00 | 126 | Muradnagar | 33 | 14:00 | 192 | Ullon | 54 | 21:00
61 | Goalpara | 42 | 19:00 | 127 | Mymensingh | 223 | 18:00 | 193 | Uttara | 81 | 13:00
62 | Gollamari | 92 | 19:30 | 128 | Naogaon | 136 | 22:00 | 194 | UttaraNew | 29 | 18:00
63 | Gopalganj | 96 | 21:00 | 129 | Narail | 57 | 20:00 | 195 | Zigatola | 78 | 18:00
64 | Gulshan | 112 | 15:00 | 130 | Narinda | 68 | 15:00
65 | Halishahar | 93 | 15:00 | 131 | Narshingdi | 174 | 21:00
66 | HaripurSBU | 128 | 01:00 | 132 | Natore | 143 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 11-03-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 390 | 02:00 | 366 | 12:00 | Madunaghat | 398 | 03:00 | 388 | 12:00
Amtali | 413 | 06:00 | 404 | 12:00 | Meghnaghat | 391 | 03:00 | 369 | 12:00
Ashuganj | 398 | 3:00 | 360 | 13:00 | Payra | 415 | 06:00 | 406 | 13:00
Bhulta | 397 | 01:00 | 357 | 12:00 | Rahanpur | 409 | 06:00 | 390 | 13:00
Bibiana | 404 | 18:30 | 396 | 10:00 | Rampal | 404 | 06:00 | 390 | 12:00
BIPTC | 403 | 08:00 | 387 | 12:00
Bogura | 397 | 06:00 | 370 | 17:00
Gopalganj | 401 | 06:00 | 383 | 12:00
Kaliakoir | 385 | 02:00 | 355 | 11:00
Korerhat | 400 | 02:00 | 383 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 231 | 03:00 | 213 | 11:00 | Jhenaidah | 231 | 06:00 | 217 | 19:00
AKSML | 234 | 18:00 | 223 | 12:00 | Kachua | 230 | 19:30 | 218 | 14:00
Aminbazar | 230 | 18:00 | 213 | 12:00 | Kaliakoir | 234 | 18:00 | 214 | 11:00
Ashuganj | 226 | 05:00 | 209 | 13:00 | Keranigonj | 229 | 03:00 | 210 | 12:00
Ashuganj-400 | 226 | 05:00 | 209 | 13:00 | Khulna(S) | 234 | 06:00 | 218 | 19:00
Baghabari | 231 | 06:00 | 220 | 11:00 | Korerhat | 229 | 19:30 | 220 | 10:00
Barapukuria | 220 | 06:00 | 197 | 17:00 | Madunaghat | 233 | 18:00 | 225 | 11:00
Barapukuria-230 | 220 | 06:00 | 197 | 17:00 | Madunaghat-400 | 232 | 03:00 | 226 | 12:00
Barishal | 229 | 06:00 | 223 | 11:00 | Maniknagar | 226 | 18:30 | 210 | 12:00
Bheramara | 234 | 20:00 | 221 | 09:00 | Meghnaghat | 235 | 18:00 | 219 | 14:00
Bhulta | 232 | 01:00 | 205 | 12:00 | Meghnaghat-400 | 230 | 02:00 | 215 | 12:00
Bibiana | 233 | 04:00 | 227 | 11:00 | Mirsorai | 237 | 19:30 | 225 | 13:00
BIPTC | 235 | 06:00 | 221 | 09:00 | Purbasadipur | 219 | 23:00 | 196 | 17:00
Bogura | 232 | 06:00 | 216 | 17:00 | Rajshahi | 232 | 19:30 | 220 | 09:00
Bogura-400 | 232 | 06:00 | 214 | 17:00 | Rampal | 232 | 06:00 | 219 | 19:00
Borhanuddin | 234 | 07:00 | 230 | 11:00 | Rampur | N/A | N/A | N/A | N/A
BSRM | 229 | 02:00 | 218 | 13:00 | Rampura | 229 | 01:00 | 200 | 13:00
Chowmuhani | 229 | 18:30 | 220 | 10:00 | Shikalbaha | 231 | 03:00 | 225 | 12:00
Cumilla(N) | 229 | 18:30 | 215 | 12:00 | Shyampur | 228 | 02:00 | 212 | 14:00
Faridpur | 226 | 06:00 | 215 | 12:00 | Siddhirganj | 229 | 01:00 | 212 | 11:00
Fenchuganj | 236 | 06:00 | 229 | 14:00 | Sirajgonj | 235 | 06:00 | 224 | 12:00
Feni | 229 | 02:00 | 217 | 12:00 | Sreepur | 223 | 03:00 | 206 | 12:00
Ghorashal | 230 | 01:00 | 218 | 17:00 | Tongi | 232 | 04:00 | 207 | 11:00
Ghorashal-230 | 227 | 03:00 | 205 | 13:00
Gopalganj | 225 | 06:00 | 215 | 12:00
GPH | 231 | 02:00 | 222 | 12:00
Haripur | 227 | 06:00 | 212 | 12:00
Hasnabad | 226 | 02:00 | 211 | 11:00
Hathazari | 228 | 02:00 | 221 | 15:00
Ishurdi | 236 | 06:00 | 223 | 09:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 01:00 | 121 | 12:00 | Madunaghat | 134 | 02:00 | 130 | 11:00
Agargaon | 136 | 02:00 | 124 | 12:00 | Magura | 133 | 06:00 | 119 | 19:00
Agrabad | 131 | 01:00 | 126 | 13:00 | Mahasthangarh | 134 | 06:00 | 124 | 13:00
AKS | 130 | 06:00 | 125 | 12:00 | Maijdee | 127 | 02:00 | 121 | 11:00
Aminbazar | 135 | 18:00 | 121 | 11:00 | Manikganj | 127 | 06:00 | 113 | 12:00
Amnura | 135 | 19:30 | 126 | 09:00 | Maniknagar | 132 | 18:30 | 120 | 11:00
Ashuganj | 138 | 04:00 | 128 | 12:00 | Matarbari | 120 | 15:00 | 112 | 00:00
Ashuganj-230 | 138 | 04:00 | 128 | 12:00 | Matuail | 134 | 18:30 | 119 | 13:00
Bagerhat | 131 | 06:00 | 117 | 19:00 | Metrorail_Motijheel | 132 | 18:30 | 120 | 11:00
Bajitpur | 131 | 02:00 | 121 | 11:00 | Metrorail_Uttara | 133 | 03:00 | 120 | 11:00
Bakerganj | 134 | 20:00 | 129 | 13:00 | Millgate | 136 | 18:30 | 118 | 12:00
Bakulia | 132 | 03:00 | 127 | 13:00 | Mirpur | 133 | 02:00 | 121 | 11:00
Banani | 138 | 18:00 | 118 | 12:00 | Mirzapur | 133 | 02:00 | 121 | 12:00
Bangabhaban | 132 | 18:30 | 120 | 11:00 | Mithapukur | 133 | 22:00 | 120 | 13:00
Barapukuria | 135 | 22:00 | 120 | 13:00 | MI_Cement | 134 | 02:00 | 120 | 14:00
Barguna | 134 | 07:00 | 128 | 13:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 133 | 20:00 | 128 | 12:00 | Mogbazar | 138 | 18:00 | 120 | 12:00
Barishal-230 | 133 | 06:00 | 128 | 12:00 | Mongla | 131 | 06:00 | 119 | 19:00
Baroaulia | 132 | 01:00 | 128 | 12:00 | Motijheel | 132 | 18:30 | 120 | 11:00
Baroirhat | 130 | 18:30 | 123 | 13:00 | Muktagacha | 127 | 10:00 | 118 | 12:00
Bashundhara | 136 | 02:00 | 118 | 12:00 | Munshiganj | 131 | 18:30 | 117 | 11:00
BashundharaCement | 132 | 18:30 | 119 | 12:00 | Muradnagar | 129 | 18:30 | 119 | 11:00
Beanibazar | 128 | 05:00 | 123 | 12:00 | Mymensingh | 127 | 10:00 | 111 | 13:00
Benapole | 129 | 06:00 | 117 | 14:00 | Naogaon | 133 | 02:00 | 122 | 13:00
Bhaluka | 132 | 03:00 | 120 | 13:00 | Narail | 134 | 06:00 | 119 | 19:00
Bhandaria | 130 | 06:00 | 124 | 12:00 | Narinda | 132 | 18:30 | 120 | 11:00
Bhangura | 130 | 01:00 | 122 | 12:00 | Narshingdi | 127 | 18:00 | 113 | 12:00
Bheramara | 134 | 20:00 | 129 | 09:00 | Natore | 133 | 04:00 | 126 | 12:00
Bheramara(GK) | 134 | 06:00 | 129 | 12:00 | Nawabganj | 133 | 02:00 | 121 | 12:00
Bhulta | 126 | 18:00 | 115 | 12:00 | Netrakona | 122 | 05:00 | 111 | 13:00
Bog-Sherpur | 134 | 02:00 | 123 | 17:00 | New | 136 | 07:00 | 119 | 11:00
Bogura | 137 | 19:30 | 126 | 13:00 | Niamatpur | 135 | 05:00 | 127 | 13:00
Bogura-230 | 138 | 22:00 | 128 | 09:00 | Noapara | 133 | 06:00 | 121 | 13:00
Brahmanbaria | 132 | 05:00 | 120 | 12:00 | Pabna | 132 | 00:00 | 127 | 09:00
Cantonment | 136 | 02:00 | 124 | 12:00 | Palashbari | 132 | 05:00 | 116 | 17:00
Chandina | 132 | 18:30 | 123 | 12:00 | Panchagarh | 138 | 23:00 | 124 | 09:00
Chandpur | 135 | 20:00 | 125 | 11:00 | Patiya | 131 | 03:00 | 126 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 134 | 03:00 | 130 | 11:00 | Patuakhali | 135 | 21:00 | 128 | 12:00
Chapai | 135 | 06:00 | 127 | 13:00 | Payra | 136 | 03:00 | 132 | 14:00
Charsaidpur | 134 | 18:30 | 118 | 12:00 | PHP | 130 | 03:00 | 123 | 12:00
Chauddagram | 129 | 02:00 | 122 | 12:00 | Postogola | 135 | 01:00 | 123 | 11:00
Chhatak | 128 | 05:00 | 121 | 19:00 | Pubail | 136 | 18:00 | 133 | 19:00
Chowmuhani | 128 | 18:30 | 122 | 12:00 | Purbachal | 138 | 18:00 | 118 | 12:00
Chuadanga | 132 | 06:00 | 116 | 19:00 | Purbasadipur | 132 | 23:00 | 118 | 17:00
Coxsbazar | 118 | 07:00 | 111 | 00:00 | Rahanpur | 137 | 06:00 | 129 | 17:00
Cumilla(N) | 132 | 18:30 | 123 | 13:00 | Rahanpur-400 | 137 | 06:00 | 130 | 17:00
Cumilla(S) | 132 | 18:00 | 116 | 14:00 | Rahim | 131 | 18:00 | 119 | 12:00
Daganbhuiyan | 128 | 02:00 | 122 | 12:00 | Rajbari | 129 | 06:00 | 122 | 12:00
Daudkandi | 126 | 19:30 | 116 | 12:00 | Rajendrapur | 134 | 06:00 | 121 | 12:00
DhakaUniversity | 139 | 18:00 | 120 | 12:00 | Rajshahi | 132 | 06:00 | 124 | 12:00
Dhamrai | 138 | 18:00 | 124 | 11:00 | Rajshahi-230 | 133 | 03:00 | 126 | 09:00
Dhanmondi | 138 | 01:00 | 120 | 12:00 | Ramganj | 130 | 01:00 | 121 | 13:00
Dohazari | 128 | 18:00 | 123 | 00:00 | Rampur | 132 | 02:00 | 126 | 12:00
Faridpur | 130 | 02:00 | 125 | 17:00 | Rampura | 137 | 01:00 | 120 | 12:00
Fatullah | 134 | 03:00 | 121 | 11:00 | Rangamati | 133 | 02:00 | 128 | 12:00
Fenchuganj | 133 | 05:00 | 129 | 14:00 | Rangpur | 134 | 23:00 | 118 | 17:00
Feni | 128 | 18:00 | 121 | 14:00 | Ruppur | 135 | 06:00 | 130 | 09:00
Feni-230 | 129 | 03:00 | 122 | 12:00 | Saidpur | 132 | 22:00 | 119 | 17:00
Ghatail | 125 | 06:00 | 113 | 13:00 | Satkhira | 131 | 06:00 | 118 | 19:00
Ghorashal | 136 | 21:00 | 125 | 12:00 | Satmasjid | 135 | 02:00 | 124 | 12:00
Goalpara | 135 | 06:00 | 125 | 12:00 | Savar | 135 | 18:30 | 120 | 11:00
Gollamari | 135 | 06:00 | 125 | 12:00 | SevenRings | 138 | 20:00 | 124 | 12:00
Gopalganj | 133 | 06:00 | 125 | 12:00 | ShahCement | 134 | 18:30 | 118 | 12:00
Gopalganj-400 | 134 | 06:00 | 127 | 12:00 | Shahjadpur | 136 | 02:00 | 129 | 13:00
Gulshan | 140 | 18:00 | 120 | 12:00 | Shahjibazar | 132 | 06:00 | 119 | 12:00
Halishahar | 133 | 02:00 | 126 | 14:00 | Shahmirpur | 133 | 03:00 | 127 | 12:00
Haripur | 134 | 18:30 | 119 | 12:00 | Shariatpur | 132 | 06:00 | 125 | 13:00
HaripurSBU | 134 | 18:30 | 119 | 12:00 | Sherpur | 126 | 10:00 | 109 | 22:00
Hasnabad | 136 | 03:00 | 123 | 11:00 | Shikalbaha | 121 | 00:00 | 117 | 14:00
Hathazari | 133 | 00:00 | 129 | 12:00 | Shikalbaha-230 | 133 | 03:00 | 128 | 13:00
Hatirjheel | 137 | 18:00 | 119 | 12:00 | Shitalakhya | 134 | 02:00 | 120.6 | 12:00
Ishurdi | 136 | 06:00 | 131 | 09:00 | Sholosohor | 134 | 03:00 | 129 | 12:00
Jaldhaka | 132 | 23:00 | 114 | 17:00 | Shyampur | 130 | 18:00 | 119 | 11:00
Jamalpur | 126 | 17:00 | 114 | 13:00 | Shyampur-230 | 132 | 03:00 | 122 | 11:00
Jashore | 131 | 06:00 | 119 | 19:00 | Siddhirganj | 134 | 18:00 | 120 | 11:00
Jhenaidah | 134 | 05:00 | 116 | 14:00 | Sirajganj | 132 | 02:00 | 116 | 17:00
Jhenaidah-230 | 135 | 06:00 | 123 | 14:00 | Sonargaon | 130 | 18:00 | 117 | 12:00
Joydebpur | 132 | 18:00 | 117 | 12:00 | Sreemongol | 128 | 05:00 | 121 | 20:00
Joypurhat | 129 | 06:00 | 117 | 09:00 | Sreepur | 136 | 02:00 | 125 | 12:00
Juldah | 132 | 01:00 | 126 | 14:00 | Srinagar | 134 | 02:00 | 122 | 12:00
Kabirpur | 137 | 00:00 | 115 | 11:00 | SSM | 136 | 00:00 | 130 | 13:00
Kachua | 131 | 01:00 | 124 | 13:00 | Sunamganj | 127 | 06:00 | 119 | 21:00
Kaliakoir | 141 | 18:00 | 127 | 11:00 | Sylhet | 130 | 08:00 | 123 | 14:00
Kaliganj | 134 | 06:00 | 121 | 19:00 | Sylhet-132 | 129 | 03:00 | 126 | 11:00
Kallyanpur | 135 | 18:00 | 122 | 11:00 | Tangail | 127 | 04:00 | 115 | 13:00
Kalurghat | 134 | 02:00 | 129 | 12:00 | Taraganj | 133 | 23:00 | 114 | 17:00
Kamrangirchar | 134 | 02:00 | 119 | 11:00 | Tasnim | 131 | 18:00 | 117 | 12:00
Kaptai | 135 | 7:00 | 129 | 11:00 | Thakurgaon | 137 | 23:00 | 121 | 09:00
Kasba | 128 | 18:30 | 119 | 11:00 | TK | 133 | 03:00 | 130 | 09:00
Kazla | 131 | 19:00 | 121 | 11:00 | Tongi | 136 | 04:00 | 122 | 11:00
Keranigonj | 134 | 02:00 | 122 | 12:00 | Ullahpara | 133 | 02:00 | 124 | 13:00
Khagrachori | 132 | 01:00 | 127 | 12:00 | Ullon | 138 | 18:00 | 120 | 12:00
Khulna | 134 | 05:00 | 124 | 12:00 | Uttara | 135 | 03:00 | 119 | 12:00
Khulna(S) | 135 | 06:00 | 125 | 13:00 | UttaraNew | 133 | 02:00 | 120 | 11:00
Khulshi | 130 | 03:00 | 126 | 12:00 | Zigatola | 135 | 03:00 | 122 | 12:00
Kishoreganj | 130 | 05:00 | 118 | 13:00
Kodda | 137 | 02:00 | 118 | 11:00
Korerhat | 132 | 02:00 | 125 | 10:00
KSRM | 132 | 00:00 | 128 | 12:00
Kulaura | 133 | 06:00 | 128 | 12:00
Kurigram | 130 | 06:00 | 115 | 17:00
Kushtia | 129 | 06:00 | 121 | 14:00
Laksam | 131 | 18:00 | 124 | 12:00
Lakshmipur | 127 | 02:00 | 120 | 13:00
Lalbag | 134 | 06:00 | 121 | 12:00
Lalmonirhat | 130 | 02:00 | 118 | 09:00
Madanganj | 132 | 18:30 | 119 | 12:00
Madaripur | 130 | 00:00 | 127 | 13:00
Madartek | 137 | 18:00 | 119 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 11-03-2026 | [28 empty] | Date: | 11-03-2026 | [28 empty] | Date: | 11-03-2026 | [28 empty] | Date: | 11-03-2026 | [28 empty] | Date: | 11-03-2026 | [17 empty] | Date: | 11-03-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [17 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 8 | 329 | 0 | 0 | 51 | 17 | 149 | 0 | 45 | 15 | 35 | 160 | 0 | 0 | 0 | 350 | 0 | 17 | 260 | 0 | 0 | 0 | 108 | 16 | 21 | 0 | 340 | 0 | 0 | 92 | 0 | 0 | 51 | 31 | 0 | 37 | 38 | 0 | 80 | 0 | 29 | 830 | 0 | 0 | 50 | 25.5 | 0 | 151 | 0 | 0 | 0 | 1214 | 0 | 35 | 0 | 250 | 280 | 0 | 51 | 0 | 209 | 0 | 103 | 90 | 120 | 0 | 20 | 0 | 168 | 0 | 0 | 17 | 320 | 0 | 365 | 41 | 0 | 161 | 0 | 22 | 0 | 41 | 0 | 70 | 0 | 96 | 0 | 59 | 48 | 9 | 0 | 0 | 0 | 7174.5 | 902 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 0 | 0 | 0 | 1447 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 53 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 125 | 220 | 0 | 0 | 1085 | 0 | 6198 | 13372.5 | 89.45
01:00 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 6 | 316 | 0 | 0 | 48.2 | 17 | 144 | 0 | 45 | 15 | 35 | 155 | 0 | 0 | 0 | 340 | 0 | 17 | 260 | 0 | 0 | 0 | 90 | 15 | 22 | 0 | 320 | 0 | 0 | 92 | 0 | 0 | 51 | 31 | 0 | 37 | 38 | 0 | 80 | 0 | 29 | 830 | 0 | 0 | 50 | 25.5 | 0 | 151 | 0 | 0 | 0 | 1161 | 0 | 12 | 0 | 280 | 280 | 0 | 51 | 0 | 202 | 0 | 100 | 90 | 117 | 0 | 19 | 0 | 158 | 0 | 0 | 17 | 315 | 0 | 355 | 41 | 0 | 153 | 0 | 22 | 0 | 41 | 0 | 70 | 0 | 98 | 0 | 59 | 48 | 9 | 0 | 0 | 0 | 7007.7 | 901 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 0 | 0 | 1307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 52 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 125 | 220 | 0 | 0 | 1050 | 0 | 5906 | 12913.7 | 89.38
02:00 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 7 | 319 | 0 | 0 | 50 | 17 | 149 | 0 | 45 | 15 | 35 | 159 | 0 | 0 | 0 | 305 | 0 | 17 | 260 | 0 | 0 | 0 | 70 | 15 | 22 | 0 | 320 | 0 | 0 | 92 | 0 | 0 | 51 | 31 | 0 | 37 | 38 | 0 | 80 | 0 | 29 | 830 | 0 | 0 | 50 | 25.5 | 0 | 116 | 0 | 0 | 0 | 1103 | 0 | 12 | 0 | 250 | 315 | 0 | 51 | 0 | 211 | 0 | 104 | 90 | 118 | 0 | 19 | 0 | 156 | 0 | 0 | 17 | 305 | 0 | 355 | 41 | 0 | 141 | 0 | 22 | 0 | 41 | 0 | 71 | 0 | 98 | 0 | 59 | 48 | 9 | 0 | 0 | 3 | 6873.5 | 901 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1055 | 0 | 0 | 0 | 1223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 52 | 35 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 100 | 180 | 0 | 0 | 1050 | 0 | 5493 | 12366.5 | 89.38
03:00 | 0 | 24 | 33 | 0 | 0 | 0 | 0 | 6 | 319 | 0 | 0 | 49.6 | 17 | 149 | 0 | 45 | 15 | 35 | 158 | 0 | 0 | 0 | 300 | 0 | 17 | 250 | 0 | 0 | 0 | 108 | 15 | 22 | 0 | 320 | 0 | 0 | 93 | 0 | 0 | 51 | 31 | 0 | 37 | 38 | 0 | 80 | 0 | 29 | 830 | 0 | 0 | 50 | 25.5 | 0 | 101 | 0 | 0 | 0 | 1150 | 0 | 12 | 0 | 220 | 310 | 0 | 51 | 0 | 221 | 0 | 102 | 90 | 115 | 0 | 19 | 0 | 154 | 0 | 0 | 17 | 295 | 0 | 354 | 41 | 0 | 140 | 0 | 17 | 0 | 41 | 0 | 69 | 0 | 98 | 0 | 97 | 53 | 0 | 0 | 0 | 0 | 6914.1 | 901 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1055 | 0 | 0 | 0 | 1324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 51 | 70 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241 | 100 | 180 | 0 | 0 | 1050 | 0 | 5656 | 12570.1 | 89.38
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 6 | 332 | 0 | 0 | 47.1 | 17 | 144 | 0 | 60 | 0 | 0 | 108 | 0 | 0 | 0 | 295 | 0 | 0 | 280 | 0 | 0 | 0 | 108 | 15 | 22 | 0 | 320 | 0 | 0 | 92 | 0 | 0 | 51 | 31 | 0 | 37 | 38 | 0 | 80 | 0 | 29 | 770 | 0 | 0 | 50 | 25.5 | 0 | 151 | 0 | 0 | 0 | 1224 | 0 | 10 | 0 | 220 | 315 | 0 | 51 | 0 | 201 | 0 | 84 | 90 | 51 | 0 | 19 | 0 | 154 | 0 | 0 | 0 | 305 | 0 | 376 | 41 | 0 | 155 | 0 | 17 | 0 | 41 | 0 | 70 | 0 | 97 | 0 | 98 | 58 | 0 | 0 | 0 | 0 | 6810.6 | 901 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 0 | 0 | 0 | 1451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 51 | 35 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 125 | 220 | 0 | 0 | 1080 | 0 | 6061 | 12871.6 | 89.38
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 336 | 0 | 0 | 25.9 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 280 | 0 | 0 | 0 | 35 | 16 | 22 | 0 | 340 | 0 | 0 | 49 | 0 | 0 | 17 | 0 | 0 | 37 | 38 | 0 | 80 | 0 | 29 | 770 | 0 | 0 | 50 | 25.5 | 0 | 151 | 0 | 0 | 0 | 1103 | 0 | 0 | 0 | 220 | 325 | 0 | 51 | 0 | 204 | 0 | 0 | 90 | 0 | 0 | 19 | 0 | 146 | 0 | 0 | 0 | 310 | 0 | 377 | 41 | 0 | 158 | 0 | 17 | 0 | 41 | 0 | 70 | 0 | 97 | 0 | 60 | 58 | 0 | 0 | 0 | 0 | 6087.4 | 901 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1082 | 0 | 0 | 0 | 1330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241 | 125 | 220 | 0 | 0 | 1030 | 0 | 5696 | 11783.4 | 89.38
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 320 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 16 | 22 | 0 | 320 | 0 | 0 | 12 | 0 | 0 | 17 | 0 | 0 | 37 | 38 | 0 | 80 | 0 | 29 | 770 | 0 | 0 | 24 | 25.5 | 0 | 71 | 0 | 0 | 0 | 1102 | 0 | 0 | 0 | 220 | 315 | 0 | 51 | 0 | 199 | 0 | 0 | 90 | 0 | 0 | 19 | 0 | 136 | 0 | 0 | 0 | 310 | 0 | 385 | 41 | 0 | 143 | 0 | 17 | 0 | 41 | 0 | 70 | 0 | 97 | 0 | 69 | 58 | 0 | 0 | 0 | 1 | 5783.5 | 760 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 957 | 0 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 125 | 220 | 0 | 0 | 960 | 0 | 5170 | 10953.5 | 89.38
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 315 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 280 | 0 | 0 | 2 | 17 | 19 | 22 | 0 | 350 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 12 | 38 | 0.1 | 80 | 0 | 10 | 770 | 0 | 0 | 19 | 8 | 0 | 61 | 0 | 0 | 0 | 1106 | 1 | 0 | 0 | 230 | 330 | 0 | 51 | 0 | 208 | 0 | 0 | 90 | 0 | 0 | 19 | 0 | 130 | 0 | 5 | 0 | 310 | 0 | 391 | 41 | 0 | 140 | 1 | 17 | 0 | 41 | 0 | 70 | 0 | 97 | 0 | 69 | 58 | 0 | 0 | 2.7 | 6 | 5756.8 | 750 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6 | 912 | 0 | 0 | 0 | 1180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.79 | 5 | 0 | 0 | 2.91 | 0 | 0 | 161 | 0 | 0 | 0 | 384 | 0 | 0.27 | 0 | 55 | 0 | 1 | 0 | 0 | 0 | 0 | 0.4 | 10 | 0.04 | 0 | 232 | 125 | 220 | 0 | 0 | 950 | 0 | 5177.01 | 10933.81 | 89.38
08:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 6 | 320 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 280 | 0 | 0 | 7 | 35 | 22 | 22 | 0 | 350 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 12 | 38 | 0.82 | 80 | 0 | 6 | 830 | 0 | 0 | 28 | 8 | 0 | 70 | 0 | 0 | 0 | 1155 | 3 | 0 | 0 | 320 | 325 | 0 | 51 | 0 | 204 | 0 | 0 | 91 | 0 | 0 | 14 | 0 | 128 | 0 | 17 | 0 | 320 | 0 | 401 | 41 | 0 | 146 | 2 | 17 | 0 | 41 | 0 | 70 | 0 | 97 | 0 | 69 | 57 | 0 | 1 | 10.08 | 6 | 6102.9 | 618 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 922 | 0 | 0 | 0 | 1324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.5 | 22 | 0 | 0 | 11.09 | 0 | 0 | 156 | 0 | 0 | 0 | 376 | 0 | 1.03 | 0 | 55 | 0 | 6 | 0 | 0 | 0 | 0 | 1.7 | 40 | 0.15 | 0 | 266 | 125 | 220 | 0 | 0 | 990 | 0 | 5353.47 | 11456.37 | 89.37
09:00 | 0 | 34 | 29 | 0 | 0 | 0 | 0 | 6 | 327 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 280 | 0 | 0 | 14 | 70 | 22 | 22 | 0 | 340 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 1.59 | 80 | 0 | 3 | 830 | 0 | 0 | 50 | 0 | 0 | 71 | 0 | 0 | 0 | 1155 | 9 | 0 | 0 | 280 | 290 | 0 | 51 | 0 | 210 | 0 | 0 | 91 | 0 | 0 | 19 | 0 | 146 | 0 | 32 | 0 | 310 | 0 | 385 | 41 | 0 | 161 | 5 | 17 | 0 | 41 | 0 | 70 | 0 | 97 | 0 | 69 | 57 | 20 | 1 | 19.26 | 6 | 6203.85 | 902 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 970 | 0 | 0 | 0 | 1453.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.96 | 45 | 0 | 0 | 20 | 0 | 0 | 179 | 0 | 0 | 0 | 372 | 0 | 2.06 | 0 | 55 | 0 | 13 | 0 | 0 | 0 | 0 | 2.7 | 78 | 0.26 | 0 | 278 | 125 | 220 | 0 | 0 | 1076 | 0 | 6045.72 | 12249.57 | 89.36
10:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 6 | 321 | 0 | 0 | 17 | 6 | 106 | 0 | 25 | 0 | 25 | 28 | 0 | 0 | 0 | 305 | 0 | 30 | 300 | 0 | 0 | 20 | 90 | 22 | 22 | 0 | 320 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 2.22 | 80 | 0 | 2 | 830 | 0 | 0 | 50 | 1 | 0 | 86 | 0 | 0 | 0 | 1130 | 14 | 2 | 0 | 280 | 290 | 0 | 51 | 0 | 200 | 0 | 0 | 91 | 4 | 0 | 17 | 0 | 142 | 0 | 46 | 0 | 305 | 0 | 330 | 42 | 0 | 158 | 7 | 17 | 0 | 41 | 0 | 70 | 0 | 97 | 0 | 69 | 58 | 20 | 1 | 28.3 | 6 | 6356.52 | 903 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 1080 | 0 | 0 | 0 | 1446.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.28 | 66 | 0 | 0 | 32.32 | 0 | 0 | 196 | 0 | 0 | 0 | 338 | 0 | 3.03 | 0 | 53 | 35 | 18 | 34 | 0 | 0 | 0 | 4.1 | 111 | 0.41 | 0 | 270 | 125 | 220 | 0 | 0 | 1085 | 0 | 6304.24 | 12660.76 | 89.35
11:00 | 0 | 52 | 34 | 0 | 0 | 0 | 0 | 6 | 305 | 0 | 0 | 30.5 | 17 | 93 | 0 | 45 | 15 | 35 | 34 | 0 | 0 | 0 | 300 | 0 | 35 | 250 | 0 | 0 | 25 | 108 | 22 | 22 | 0 | 320 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 2.73 | 80 | 0 | 2 | 830 | 0 | 0 | 48 | 24 | 0 | 222 | 0 | 0 | 0 | 1155 | 16 | 0 | 0 | 250 | 290 | 0 | 51 | 0 | 203 | 0 | 17 | 90 | 17 | 0 | 20 | 0 | 164 | 0 | 57 | 0 | 310 | 0 | 331 | 42 | 0 | 136 | 9 | 17 | 0 | 41 | 0 | 70 | 0 | 97 | 17 | 69 | 58 | 17 | 2 | 34.3 | 6 | 6662.53 | 903 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 1102 | 0 | 0 | 0 | 1449.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.14 | 82 | 0 | 0 | 39.45 | 0 | 0 | 200 | 0 | 0 | 0 | 347 | 0 | 3.08 | 0 | 53 | 35 | 23 | 34 | 0 | 0 | 0 | 4.7 | 133 | 0.5 | 0 | 274 | 125 | 220 | 0 | 0 | 1085 | 0 | 6415.42 | 13077.95 | 89.34
12:00 | 0 | 52 | 34 | 0 | 0 | 0 | 0 | 6 | 331 | 0 | 0 | 32.3 | 17 | 88 | 0 | 95 | 15 | 55 | 67 | 1 | 0 | 0 | 350 | 0 | 35 | 250 | 0 | 0 | 27 | 108 | 22 | 21 | 0 | 320 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 3 | 80 | 0 | 2 | 830 | 0 | 0 | 46 | 25.5 | 0 | 221 | 0 | 0 | 0 | 1160 | 7 | 0 | 0 | 250 | 290 | 0 | 51 | 0 | 207 | 0 | 15 | 90 | 18 | 0 | 17 | 0 | 164 | 0 | 60 | 10 | 310 | 0 | 357 | 42 | 0 | 140 | 9 | 17 | 0 | 40 | 0 | 70 | 0 | 96 | 17 | 69 | 58 | 10 | 2 | 36.73 | 6 | 6874.53 | 903 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 1115 | 0 | 0 | 0 | 1454.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.93 | 88 | 0 | 0 | 42.45 | 0 | 0 | 200 | 0 | 0 | 0 | 364 | 0 | 4.26 | 0 | 0 | 50 | 25 | 49 | 0 | 0 | 0 | 5.2 | 150 | 0.55 | 0 | 277 | 120 | 220 | 0 | 0 | 1085 | 0 | 6458.89 | 13333.42 | 89.33
13:00 | 0 | 52 | 34 | 0 | 0 | 0 | 0 | 6 | 345 | 0 | 0 | 48.2 | 17 | 97 | 30 | 195 | 15 | 35 | 65 | 8 | 0 | 0 | 355 | 0 | 35 | 250 | 0 | 0 | 27 | 108 | 22 | 21 | 0 | 330 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 3.11 | 80 | 0 | 8 | 830 | 0 | 0 | 46.5 | 25.5 | 0 | 218 | 0 | 0 | 0 | 1157 | 12 | 0 | 0 | 250 | 290 | 0 | 51 | 0 | 207 | 0 | 45 | 91 | 49 | 9 | 17 | 0 | 178 | 0 | 58 | 14 | 320 | 0 | 399 | 42 | 0 | 148 | 5 | 17 | 0 | 41 | 0 | 71 | 0 | 96 | 17 | 69 | 58 | 10 | 2 | 30.08 | 0 | 7182.39 | 903 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 1120 | 0 | 0 | 0 | 1456.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.8 | 83 | 0 | 0 | 42.45 | 0 | 0 | 196 | 0 | 0 | 0 | 379 | 0 | 4.41 | 0 | 0 | 50 | 21 | 49 | 0 | 0 | 0 | 5.2 | 141 | 0.49 | 0 | 279 | 120 | 220 | 0 | 0 | 1085 | 0 | 6437.27 | 13619.66 | 89.32
14:00 | 0 | 52 | 33 | 0 | 0 | 0 | 0 | 6 | 352 | 0 | 0 | 50.6 | 17 | 122 | 17 | 240 | 15 | 35 | 106 | 15 | 0 | 0 | 360 | 0 | 35 | 250 | 0 | 0 | 23 | 108 | 22 | 21 | 0 | 320 | 0 | 0 | 91 | 0 | 3 | 0 | 0 | 0 | 12 | 12 | 1.29 | 80 | 0 | 3 | 830 | 0 | 0 | 50 | 25.5 | 0 | 218 | 0 | 0 | 0 | 1210 | 12 | 8 | 0 | 250 | 290 | 0 | 51 | 0 | 205 | 0 | 51 | 90 | 57 | 9 | 12 | 0 | 192 | 0 | 49 | 9 | 320 | 0 | 380 | 42 | 0 | 152 | 8 | 17 | 0 | 40 | 0 | 70 | 0 | 96 | 17 | 68 | 58 | 10 | 2 | 30.13 | 0 | 7330.52 | 903 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 1135 | 0 | 0 | 0 | 1461.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.48 | 68 | 0 | 0 | 39.53 | 0 | 0 | 193 | 0 | 0 | 0 | 414 | 0 | 3.02 | 0 | 40 | 50 | 23 | 64 | 0 | 0 | 0 | 3.5 | 132 | 0.28 | 0 | 277 | 120 | 220 | 0 | 0 | 1085 | 0 | 6491.55 | 13822.07 | 89.31
15:00 | 0 | 52 | 33 | 0 | 0 | 0 | 0 | 6 | 312 | 0 | 0 | 45.2 | 17 | 134 | 30 | 260 | 44 | 35 | 147 | 16 | 0 | 0 | 325 | 0 | 35 | 250 | 0 | 0 | 16 | 108 | 22 | 21 | 0 | 320 | 0 | 0 | 95 | 0 | 2 | 0 | 0 | 0 | 12 | 12 | 1.73 | 80 | 0 | 2 | 830 | 15 | 0 | 50 | 19 | 0 | 217 | 0 | 0 | 0 | 1155 | 10 | 88 | 0 | 250 | 290 | 0 | 51 | 0 | 205 | 0 | 77 | 90 | 108 | 9 | 12 | 0 | 186 | 2 | 35 | 9 | 305 | 0 | 337 | 42 | 0 | 148 | 5 | 17 | 0 | 40 | 0 | 71 | 0 | 94 | 27 | 68 | 57 | 10 | 1 | 19.85 | 0 | 7382.78 | 902 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 1090 | 0 | 0 | 0 | 1447.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.89 | 38 | 0 | 0 | 28.53 | 0 | 0 | 170 | 0 | 0 | 0 | 347 | 0 | 3.15 | 0 | 0 | 70 | 16 | 84 | 0 | 0 | 0 | 2.9 | 96 | 0.27 | 5 | 275 | 120 | 180 | 0 | 0 | 1085 | 0 | 6198.75 | 13581.53 | 89.3
16:00 | 0 | 52 | 33 | 0 | 0 | 0 | 0 | 6 | 304 | 0 | 0 | 45.2 | 17 | 149 | 30 | 276 | 55 | 35 | 146 | 20 | 0 | 0 | 290 | 0 | 35 | 250 | 0 | 0 | 9 | 108 | 22 | 0 | 0 | 320 | 0 | 0 | 98 | 0 | 9 | 0 | 0 | 0 | 12 | 12 | 0.88 | 80 | 0 | 2 | 830 | 15 | 0 | 50 | 25.5 | 0 | 217 | 0 | 0 | 0 | 1160 | 5 | 150 | 0 | 250 | 290 | 0 | 51 | 0 | 208 | 0 | 97 | 90 | 166 | 0 | 19 | 0 | 184 | 16 | 23 | 9 | 310 | 0 | 337 | 42 | 0 | 135 | 4 | 13 | 0 | 41 | 0 | 70 | 0 | 94 | 35 | 68 | 57 | 10 | 1 | 10.15 | 0 | 7498.73 | 902 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 1106 | 0 | 0 | 0 | 1459.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.25 | 22 | 0 | 0 | 16.06 | 0 | 0 | 160 | 0 | 0 | 0 | 350 | 0 | 1.39 | 0 | 0 | 70 | 8 | 106 | 0 | 0 | 0 | 1.9 | 53 | 0.12 | 26 | 276 | 120 | 180 | 0 | 0 | 1085 | 17 | 6166.08 | 13664.81 | 89.29
17:00 | 0 | 52 | 33 | 0 | 0 | 0 | 0 | 6 | 321 | 0 | 0 | 48.5 | 17 | 149 | 30 | 276 | 55 | 37 | 151 | 22 | 0 | 0 | 315 | 0 | 35 | 250 | 0 | 0 | 4 | 142 | 22 | 21 | 0 | 320 | 0 | 0 | 102 | 0 | 9 | 34 | 0 | 0 | 12 | 12 | 0.27 | 80 | 0 | 10 | 830 | 15 | 0 | 50 | 25.5 | 0 | 217 | 0 | 0 | 0 | 1155 | 2 | 142 | 0 | 250 | 290 | 0 | 51 | 0 | 209 | 0 | 101 | 90 | 179 | 0 | 19 | 0 | 170 | 16 | 8 | 9 | 310 | 0 | 380 | 42 | 0 | 145 | 0 | 21 | 0 | 41 | 0 | 70 | 0 | 95 | 35 | 96 | 65 | 10 | 0 | 3.87 | 6 | 7714.14 | 903 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1108 | 0 | 0 | 0 | 1445.29 | 0 | 0 | 0 | 25 | 13 | 0 | 0 | 0 | 0 | 5.07 | 11 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 406 | 0 | 0.55 | 0 | 0 | 109 | 5 | 106 | 0 | 0 | 0 | 0.8 | 19 | 0.06 | 29 | 276 | 120 | 220 | 0 | 0 | 1085 | 31 | 6263.77 | 13977.91 | 89.28
18:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 6 | 346 | 0 | 0 | 49.5 | 17 | 149 | 30 | 276 | 55 | 55 | 155 | 16 | 0 | 0 | 350 | 0 | 35 | 250 | 0 | 0 | 0 | 142 | 20 | 21 | 0 | 320 | 0 | 0 | 104 | 0 | 4 | 34 | 5 | 0 | 12 | 12 | 0 | 80 | 0 | 18 | 830 | 16 | 0 | 50 | 25.5 | 0 | 221 | 0 | 0 | 0 | 1099 | 0 | 142 | 0 | 250 | 290 | 0 | 51 | 0 | 212 | 0 | 102 | 90 | 179 | 0 | 19 | 30 | 160 | 25 | 0 | 9 | 325 | 0 | 356 | 42 | 0 | 154 | 0 | 21 | 0 | 41 | 0 | 71 | 0 | 94 | 35 | 97 | 76 | 10 | 0 | 0 | 8 | 7813 | 903 | 170 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1154 | 0 | 0 | 0 | 1445.64 | 0 | 0 | 0 | 100 | 75 | 0 | 9 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 227 | 120 | 180 | 0 | 0 | 1060 | 31 | 6342.64 | 14155.64 | 89.27
19:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 6 | 325 | 0 | 0 | 48.1 | 17 | 149 | 62 | 276 | 55 | 55 | 151 | 16 | 0 | 0 | 330 | 0 | 35 | 250 | 0 | 0 | 0 | 142 | 24 | 21 | 0 | 350 | 0 | 0 | 104 | 0 | 1 | 34 | 38 | 0 | 12 | 12 | 0 | 80 | 0 | 20 | 830 | 75 | 0 | 50 | 25.5 | 0 | 221 | 0 | 0 | 0 | 1160 | 0 | 140 | 0 | 250 | 290 | 0 | 51 | 0 | 208 | 0 | 101 | 90 | 180 | 0 | 19 | 31 | 182 | 52.2 | 0 | 9 | 290 | 0 | 391 | 42 | 0 | 146 | 0 | 21 | 0 | 41 | 0 | 70 | 0 | 95 | 35 | 98 | 77 | 12 | 0 | 0 | 12 | 8028.8 | 902 | 170 | 0 | 16 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1142 | 0 | 0 | 0 | 1445.45 | 0 | 0 | 0 | 113 | 112 | 0 | 26 | 4 | 34 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 279 | 120 | 220 | 0 | 0 | 1000 | 86 | 6538.45 | 14567.25 | 89.26
19:30 | 0 | 105 | 51 | 0 | 0 | 0 | 0 | 6 | 317 | 0 | 0 | 48.1 | 17 | 149 | 100 | 276 | 55 | 55 | 156 | 26 | 0 | 0 | 350 | 0 | 35 | 250 | 0 | 0 | 0 | 142 | 24 | 21 | 0 | 320 | 0 | 0 | 104 | 0 | 0 | 34 | 46 | 0 | 12 | 12 | 0 | 80 | 0 | 24 | 830 | 108 | 0 | 50 | 25.5 | 0 | 224 | 0 | 0 | 0 | 1160 | 0 | 140 | 0 | 250 | 290 | 0 | 51 | 0 | 196 | 0 | 100 | 90 | 180 | 0 | 19 | 70 | 174 | 52.2 | 0 | 17 | 315 | 0 | 392 | 42 | 0 | 155 | 0 | 21 | 0 | 41 | 0 | 69 | 0 | 95 | 35 | 98 | 77 | 12 | 0 | 0 | 12 | 8205.8 | 764 | 171 | 0 | 30 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1211 | 0 | 0 | 0 | 1444.94 | 0 | 29 | 0 | 113 | 113 | 0 | 26 | 5 | 43 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 276 | 120 | 220 | 0 | 0 | 1050 | 82 | 6579.94 | 14785.74
20:00 | 0 | 105 | 51 | 0 | 0 | 0 | 0 | 6 | 314 | 0 | 0 | 47.7 | 17 | 149 | 110 | 278 | 55 | 55 | 153 | 26 | 0 | 0 | 345 | 0 | 35 | 250 | 0 | 0 | 0 | 142 | 23 | 21 | 0 | 320 | 0 | 0 | 104 | 0 | 0 | 34 | 46 | 0 | 12 | 12 | 0 | 80 | 0 | 28 | 830 | 113 | 0 | 50 | 25.5 | 0 | 224 | 0 | 0 | 0 | 1163 | 0 | 140 | 0 | 250 | 290 | 0 | 51 | 0 | 201 | 0 | 100 | 90 | 179 | 0 | 19 | 61 | 170 | 52.2 | 0 | 17 | 315 | 0 | 393 | 42 | 0 | 156 | 0 | 21 | 0 | 41 | 0 | 70 | 0 | 95 | 35 | 98 | 77 | 12 | 0 | 0 | 12 | 8211.4 | 666 | 172 | 0 | 25 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1228 | 0 | 0 | 0 | 1451.56 | 0 | 40 | 0 | 113 | 113 | 0 | 26 | 8 | 43 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 277 | 120 | 220 | 0 | 0 | 1085 | 82 | 6569.56 | 14780.96 | 89.25
21:00 | 0 | 105 | 51 | 0 | 0 | 0 | 0 | 6 | 313 | 0 | 0 | 49.2 | 17 | 149 | 78 | 292 | 55 | 55 | 155 | 16 | 0 | 0 | 350 | 0 | 35 | 250 | 0 | 0 | 0 | 142 | 23 | 21 | 0 | 320 | 0 | 0 | 104 | 0 | 0 | 39 | 46 | 0 | 12 | 12 | 0 | 80 | 0 | 29 | 830 | 50 | 0 | 50 | 25.5 | 0 | 225 | 0 | 0 | 0 | 1160 | 0 | 143 | 0 | 250 | 290 | 0 | 51 | 0 | 195 | 0 | 101 | 90 | 181 | 0 | 19 | 63 | 176 | 52.2 | 0 | 17 | 310 | 0 | 377 | 42 | 0 | 157 | 0 | 21 | 0 | 41 | 0 | 70 | 0 | 95 | 35 | 98 | 77 | 16 | 0 | 0 | 12 | 8123.9 | 793 | 172 | 0 | 25 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1229 | 0 | 0 | 0 | 1449.19 | 0 | 41 | 0 | 113 | 113 | 0 | 26 | 23 | 52 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 279 | 120 | 220 | 0 | 0 | 1085 | 78 | 6732.19 | 14856.09 | 89.24
22:00 | 0 | 88 | 51 | 0 | 0 | 0 | 0 | 6 | 301 | 0 | 0 | 45.3 | 17 | 149 | 78 | 292 | 55 | 55 | 144 | 0 | 0 | 0 | 340 | 0 | 35 | 250 | 0 | 0 | 0 | 142 | 22 | 21 | 0 | 320 | 0 | 0 | 104 | 0 | 0 | 51 | 46 | 0 | 12 | 12 | 0 | 80 | 0 | 29 | 830 | 45 | 0 | 50 | 25.5 | 0 | 226 | 0 | 0 | 0 | 1150 | 0 | 142 | 0 | 250 | 290 | 0 | 51 | 0 | 190 | 0 | 97 | 90 | 177 | 0 | 19 | 30 | 174 | 52.2 | 0 | 17 | 305 | 0 | 368 | 42 | 0 | 155 | 0 | 21 | 0 | 41 | 0 | 70 | 0 | 95 | 35 | 59 | 48 | 12 | 0 | 0 | 12 | 7914 | 902 | 172 | 0 | 25 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 1439.02 | 0 | 41 | 0 | 113 | 113 | 0 | 26 | 30 | 52.2 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 271 | 120 | 220 | 0 | 0 | 1085 | 76 | 6826.22 | 14740.22 | 89.23
23:00 | 0 | 70 | 51 | 0 | 0 | 0 | 0 | 6 | 295 | 0 | 0 | 45 | 17 | 135 | 46 | 230 | 55 | 55 | 142 | 0 | 0 | 0 | 335 | 0 | 55 | 250 | 0 | 0 | 0 | 125 | 22 | 22 | 0 | 320 | 0 | 0 | 105 | 0 | 0 | 51 | 46 | 0 | 12 | 12 | 0 | 80 | 0 | 23 | 830 | 0 | 0 | 50 | 8 | 0 | 226 | 0 | 0 | 0 | 1150 | 0 | 100 | 0 | 250 | 290 | 0 | 51 | 0 | 191 | 0 | 77 | 90 | 176 | 0 | 19 | 0 | 172 | 24 | 0 | 17 | 310 | 0 | 369 | 42 | 0 | 154 | 0 | 21 | 0 | 41 | 0 | 70 | 0 | 95 | 35 | 58 | 48 | 12 | 0 | 0 | 12 | 7593 | 901 | 171 | 0 | 28 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1217 | 0 | 0 | 0 | 1437.53 | 0 | 41 | 0 | 70 | 70 | 0 | 26 | 28 | 8 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 115 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 273 | 120 | 220 | 0 | 0 | 1080 | 76 | 6663.53 | 14256.53 | 89.22
Total KWH | 0 | 1165440 | 734880 | 0 | 0 | 0 | 0 | 156818.18 | 7822800 | 0 | 0 | 867240 | 335520 | 2883312 | 584160 | 3426164 | 680706 | 817438 | 2404800 | 166080 | 0 | 0 | 7848395 | 0 | 616431 | 6289039 | 0 | 0 | 171442 | 2404800 | 494400 | 493920 | 0 | 8001818.18 | 0 | 0 | 1955520 | 0 | 26400 | 563201 | 393984 | 0 | 448320 | 504000 | 17762 | 1919700 | 0 | 401760 | 19745454.55 | 351272 | 0 | 664320 | 487513.8 | 0 | 3935259 | 0 | 0 | 0 | 27725452 | 100035 | 1428509 | 0 | 6191000 | 7472200 | 0 | 1249806 | 0 | 4993000 | 0 | 1506240 | 2150431 | 2323200 | 33600 | 450170 | 249660 | 3890880 | 301483 | 394345 | 212480 | 7536000 | 0 | 9052000 | 987000 | 0 | 3590509.09 | 54461 | 450840 | 0 | 965760 | 0 | 1645000 | 0 | 2307340 | 421200 | 1777200 | 1432800 | 213120 | 10650 | 228000 | 136560 | 171261000.8 | 20898909 | 4321152 | 0 | 124800 | 88704 | 0 | 0 | 0 | 0 | 0 | 0 | 507600 | 26392720 | 0 | 0 | 0 | 33564187 | 0 | 217121 | 0 | 676224 | 718176 | 0 | 155952 | 184306 | 201816 | 270244 | 545710 | 183980 | 0 | 277504 | 0 | 0 | 4435264 | 0 | 0 | 0 | 9089600 | 0 | 26100 | 0 | 682472 | 1406478 | 160249 | 1503974 | 0 | 0 | 0 | 32579.16 | 957600 | 2854 | 312672 | 6502000 | 2892000 | 5314020 | 0 | 0 | 25808000 | 502800 | 148957767.16 | 320218767.96