## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 13-03-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 12-03-2026 | during | 13-03-2026 | during | 13-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 6 | 6 | 97.7 | 97.7 | 7 | 7 | Demand "05"MW due to gas restiction by Titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 412 | 338 | 412 | 412 | 412 | 412
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 1 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 270 | 270 | 335 | 335 | 335 | 335
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 12 | 47.4 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 60 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23 | 24 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 42 | 33 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 145 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 113 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 2 | 34 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 16 | 30 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 147 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 13 | 0 | 26 | 0 | 26 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 300 | 340 | 584 | 584 | 320 | 320 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 305 | 350 | 583 | 583 | 320 | 320 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 125 | 108 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1788 | 2224.4 | 5941.22 | 5915.22 | 2720.05 | 2695.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 16 | 0 | 15 | 0 | 15 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 33 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 80 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 218 | 186 | 220 | 225 | 220 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 24 | 56 | 64 | 56 | 64 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 17 | 51 | 51 | 51 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 50 | 50 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 4 | 22 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 70 | 84 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.16 | 0 | 3.25 | 0 | 3.25 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 38 | 38 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1152 | 1224 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 3 | 5 | 28 | 2 | 28 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 830 | 875 | 675 | 675 | 675 | 675 | Plant availability less
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2450.16 | 2650.5 | 3589.11 | 3577.86 | 3107.75 | 3096.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 182 | 201 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 290 | 320 | 353.35 | 353.35 | 353.35 | 353.35 | FGMO
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 318.81 | 318.81 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 250 | 260 | 393 | 393 | 300 | 300 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 20 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 50 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 17 | 32 | 32 | 32 | 32 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 91 | 90 | 163 | 163 | 100 | 100 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 188 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 168 | 176 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 19 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 115 | 100 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 62 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1246 | 1472 | 2736.51 | 2670.51 | 1895.55 | 1835.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 12-03-2026 | during | 13-03-2026 | during | 13-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 11 | 15 | 157.5 | 157.5 | 10 | 10 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.6 | 0 | 1.6 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 35 | 108 | 70 | 80 | 60 | 80 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 69 | 70 | 115 | 70 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 14.22 | 0 | 45.12 | 0 | 45.12 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 5 | 12 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 35 | 54.5 | 54.5 | 17 | 35 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 134.22 | 239 | 420.72 | 429 | 209.72 | 246
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 41 | 41 | 41 | 41 | 41 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 157 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 72 | 70 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 41 | 41 | 86 | 86 | 42 | 42 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 96 | 95 | 0 | 0 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 23 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 315 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 396 | 393 | 385 | 385 | 385 | 385
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1137 | 1135 | 1091 | 1091 | 1094 | 1094
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 887 | 886 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 20 | 44 | 44 | 44 | 44 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 190 | 169 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 53 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 946 | 1234.2 | 1234.2 | 1234.2 | 1148.28 | 1148.28
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2076 | 2309.2 | 3594.2 | 3514.2 | 2537.38 | 2457.38
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 65 | 65 | 130 | 130 | GT-02 Offline Waterwash
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 900 | 1085.32 | 1085 | 1085 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 15 | 15 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 265 | 307 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.27 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1505.27 | 1732.32 | 1938 | 1937 | 1868.32 | 1867.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 18.42 | 0 | 48 | 0 | 48 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 185 | 190 | 220 | 220 | 200 | 200 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 21 | 21 | 21 | 21 | Machine problem and fuel shortage
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 32 | 32 | 34 | 34 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.17 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 963.33 | 1458.17 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 22.78 | 0 | 59 | 0 | 59 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 58 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1662.7 | 2062.17 | 3158.57 | 2945.87 | 2627.57 | 2414.87
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 55 | 55 | 55 | 55 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 106 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.8 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 167 | 0 | 191.71 | 0 | 191.71 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 258.8 | 276 | 543.91 | 317 | 454.91 | 228
System Total |  |  |  |  | 28823.2 | 29252.303 | 12258.15 | 14100.59 | 23013.24 | 22397.66 | 16515.25 | 15934.67
Forecast Scenario (13-03-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13610 |  | 0 |  | 13610
|  |  |  | 1:00 | 12950 |  | 0 |  | 12950
|  |  |  | 2:00 | 12530 |  | 0 |  | 12530
|  |  |  | 3:00 | 12740 |  | 0 |  | 12740
|  |  |  | 4:00 | 12900 |  | 0 |  | 12900
|  |  |  | 5:00 | 12290 |  | 0 |  | 12290
|  |  |  | 6:00 | 11180 |  | 0 |  | 11180
|  |  |  | 7:00 | 11010 |  | 0 |  | 11010
|  |  |  | 8:00 | 11380 |  | 0 |  | 11380
|  |  |  | 9:00 | 11930 |  | 0 |  | 11930
|  |  |  | 10:00 | 12200 |  | 0 |  | 12200
|  |  |  | 11:00 | 12520 |  | 0 |  | 12520
|  |  |  | 12:00 | 12970 |  | 0 |  | 12970
|  |  |  | 13:00 | 13670 |  | 0 |  | 13670
|  |  |  | 14:00 | 12790 |  | 0 |  | 12790
|  |  |  | 15:00 | 13080 |  | 0 |  | 13080
|  |  |  | 16:00 | 13140 |  | 0 |  | 13140
|  |  |  | 17:00 | 13460 |  | 0 |  | 13460
|  |  |  | 18:00 | 13650 |  | 0 |  | 13650
|  |  |  | 18:30 | 13700 |  | 0 |  | 13700
|  |  |  | 19:00 | 13880 |  | 0 |  | 13880
|  |  |  | 19:30 | 13910 |  | 0 |  | 13910
|  |  |  | 20:00 | 13950 |  | 0 |  | 13950
|  |  |  | 21:00 | 14240 |  | 0 |  | 14240
|  |  |  | 22:00 | 13970 |  | 0 |  | 13970
|  |  |  | 23:00 | 13630 |  | 0 |  | 13630
Probable Maximum Temperature: |  |  | 29.50°C
Probable Maximum Demand at Day Peak: |  |  | 12970.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14240.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14240.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 305.37276 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:02 hrs on 13-03-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 12-03-2026 | [28 empty] | Date: | 12-03-2026 | [28 empty] | Date: | 12-03-2026 | [28 empty] | Date: | 12-03-2026 | [28 empty] | Date: | 12-03-2026 | [17 empty] | Date: | 12-03-2026
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [17 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 6 | 309 | 0 | 0 | 46 | 17 | 133 | 46 | 195 | 55 | 55 | 122 | 0 | 0 | 0 | 345 | 0 | 55 | 250 | 0 | 0 | 0 | 108 | 22 | 22 | 0 | 320 | 0 | 0 | 102 | 0 | 0 | 51 | 24 | 0 | 12 | 12 | 0 | 80 | 0 | 21 | 830 | 0 | 0 | 50 | 0 | 0 | 226 | 0 | 0 | 0 | 1154 | 0 | 100 | 0 | 250 | 290 | 0 | 51 | 0 | 194 | 0 | 69 | 90 | 136 | 0 | 20 | 0 | 174 | 0 | 0 | 17 | 310 | 0 | 373 | 42 | 0 | 157 | 0 | 21 | 0 | 42 | 0 | 69 | 0 | 95 | 35 | 58 | 48 | 10 | 0 | 0 | 12 | 7406 | 901 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1190 | 0 | 0 | 0 | 1455.04 | 0 | 41 | 0 | 35 | 70 | 0 | 0 | 21 | 8 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 50 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 274 | 120 | 220 | 0 | 0 | 1085 | 47 | 6464.04 | 13870.04 | 89.21
01:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 6 | 293 | 0 | 0 | 44.6 | 17 | 133 | 46 | 195 | 55 | 55 | 109 | 0 | 0 | 0 | 335 | 0 | 55 | 250 | 0 | 0 | 0 | 108 | 22 | 22 | 0 | 320 | 0 | 0 | 90 | 0 | 0 | 51 | 24 | 0 | 12 | 12 | 0 | 80 | 0 | 21 | 830 | 0 | 0 | 50 | 0 | 0 | 226 | 0 | 0 | 0 | 1156 | 0 | 100 | 0 | 250 | 290 | 0 | 51 | 0 | 195 | 0 | 69 | 91 | 100 | 0 | 19 | 0 | 162 | 0 | 0 | 17 | 305 | 0 | 379 | 41 | 0 | 149 | 0 | 21 | 0 | 42 | 0 | 71 | 0 | 95 | 35 | 58 | 48 | 10 | 0 | 0 | 12 | 7302.6 | 666 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1134 | 0 | 0 | 0 | 1371.26 | 0 | 41 | 0 | 35 | 35 | 0 | 0 | 21 | 8 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 52 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 274 | 100 | 180 | 0 | 0 | 1085 | 47 | 5926.26 | 13228.86 | 89.2
02:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 6 | 299 | 0 | 0 | 45.3 | 17 | 133 | 46 | 195 | 55 | 55 | 111 | 0 | 0 | 0 | 295 | 0 | 55 | 250 | 0 | 0 | 0 | 108 | 20 | 22 | 0 | 320 | 0 | 0 | 96 | 0 | 0 | 51 | 23 | 0 | 12 | 12 | 0 | 80 | 0 | 21 | 830 | 0 | 0 | 50 | 0 | 0 | 186 | 0 | 0 | 0 | 1025 | 0 | 100 | 0 | 250 | 290 | 0 | 51 | 0 | 192 | 0 | 69 | 90 | 100 | 0 | 19 | 0 | 150 | 0 | 0 | 17 | 310 | 0 | 322 | 41 | 0 | 138 | 0 | 21 | 0 | 42 | 0 | 70 | 0 | 96 | 35 | 58 | 48 | 10 | 0 | 0 | 12 | 7024.3 | 744 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1058 | 0 | 0 | 0 | 1361.28 | 0 | 41 | 0 | 35 | 35 | 0 | 0 | 21 | 8 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 52 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 216 | 100 | 180 | 0 | 0 | 1085 | 46 | 5801.28 | 12825.58 | 89.19
03:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 6 | 292 | 0 | 0 | 45 | 17 | 140 | 46 | 195 | 55 | 55 | 108 | 0 | 0 | 0 | 285 | 0 | 55 | 250 | 0 | 0 | 0 | 125 | 20 | 22 | 0 | 320 | 0 | 0 | 103 | 0 | 0 | 51 | 23 | 0 | 12 | 12 | 0 | 80 | 0 | 21 | 830 | 0 | 0 | 50 | 0 | 0 | 186 | 0 | 0 | 0 | 1040 | 0 | 100 | 0 | 250 | 290 | 0 | 51 | 0 | 192 | 0 | 68 | 90 | 89 | 0 | 19 | 0 | 148 | 0 | 0 | 17 | 240 | 0 | 320 | 41 | 0 | 136 | 0 | 21 | 0 | 42 | 0 | 70 | 0 | 95 | 35 | 96 | 57 | 12 | 0 | 0 | 12 | 7010 | 745 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1035 | 0 | 0 | 0 | 1347.69 | 0 | 41 | 0 | 35 | 35 | 0 | 0 | 21 | 8 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 54 | 70 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 215 | 100 | 180 | 0 | 0 | 1085 | 46 | 5770.69 | 12780.69 | 89.18
04:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 6 | 305 | 0 | 0 | 45.6 | 17 | 149 | 30 | 95 | 55 | 55 | 113 | 0 | 0 | 0 | 310 | 0 | 55 | 250 | 0 | 0 | 0 | 125 | 20 | 22 | 0 | 320 | 0 | 0 | 101 | 0 | 0 | 51 | 23 | 0 | 12 | 12 | 0 | 80 | 0 | 25 | 830 | 0 | 0 | 50 | 0 | 0 | 226 | 0 | 0 | 0 | 1150 | 0 | 50 | 0 | 280 | 290 | 0 | 51 | 0 | 192 | 0 | 67 | 90 | 94 | 0 | 19 | 0 | 154 | 0 | 0 | 0 | 290 | 0 | 362 | 41 | 0 | 143 | 0 | 21 | 0 | 42 | 0 | 70 | 0 | 95 | 0 | 97 | 57 | 12 | 0 | 0 | 12 | 7120.6 | 745 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1081 | 0 | 0 | 0 | 1370.47 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 54 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 125 | 220 | 0 | 0 | 1085 | 14 | 5912.47 | 13033.07 | 89.17
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 6 | 300 | 0 | 0 | 31.9 | 17 | 113 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 250 | 0 | 0 | 0 | 90 | 18 | 22 | 0 | 320 | 0 | 0 | 99 | 0 | 0 | 51 | 0 | 0 | 12 | 12 | 0 | 80 | 0 | 25 | 830 | 0 | 0 | 50 | 0 | 0 | 227 | 0 | 0 | 0 | 954 | 0 | 0 | 0 | 280 | 290 | 0 | 51 | 0 | 196 | 0 | 34 | 90 | 0 | 0 | 19 | 0 | 152 | 0 | 0 | 0 | 310 | 0 | 372 | 41 | 0 | 153 | 0 | 17 | 0 | 42 | 0 | 71 | 0 | 95 | 0 | 69 | 58 | 12 | 0 | 0 | 12 | 6251.9 | 886 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024 | 0 | 0 | 0 | 1362.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 125 | 180 | 0 | 0 | 1030 | 0 | 5662.42 | 11914.32 | 89.16
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 6 | 306 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 250 | 0 | 0 | 0 | 70 | 18 | 22 | 0 | 320 | 0 | 0 | 74 | 0 | 0 | 34 | 0 | 0 | 12 | 12 | 0 | 80 | 0 | 25 | 830 | 0 | 0 | 33 | 0 | 0 | 186 | 0 | 0 | 0 | 910 | 0 | 0 | 0 | 280 | 290 | 0 | 51 | 0 | 189 | 0 | 30 | 91 | 0 | 0 | 19 | 0 | 144 | 0 | 0 | 0 | 310 | 0 | 348 | 41 | 0 | 151 | 0 | 17 | 0 | 42 | 0 | 70 | 0 | 96 | 0 | 68 | 58 | 12 | 0 | 0 | 12 | 5914 | 886 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 863 | 0 | 0 | 0 | 1173.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 100 | 180 | 0 | 0 | 860 | 0 | 5003.96 | 10917.96 | 89.15
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 6 | 315 | 0 | 0 | 0 | 0 | 34 | 15 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 320 | 0 | 0 | 250 | 0 | 0 | 2 | 90 | 24 | 21 | 0 | 350 | 0 | 0 | 70 | 0 | 0 | 34 | 0 | 0 | 12 | 12 | 0.17 | 80 | 0 | 10 | 830 | 0 | 0 | 33 | 0 | 0 | 186 | 0 | 0 | 0 | 904 | 1 | 0 | 0 | 280 | 290 | 0 | 51 | 0 | 163 | 0 | 86 | 90 | 0 | 0 | 19 | 0 | 140 | 0 | 5 | 0 | 315 | 0 | 348 | 41 | 0 | 143 | 1 | 17 | 0 | 41 | 0 | 71 | 0 | 96 | 0 | 69 | 58 | 0 | 0 | 1.55 | 12 | 5968.72 | 886 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 853 | 0 | 0 | 0 | 1012.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.14 | 4 | 0 | 0 | 1.89 | 0 | 0 | 172 | 0 | 0 | 0 | 384 | 0 | 0.26 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 170 | 100 | 180 | 0 | 0 | 850 | 0 | 4867.87 | 10836.59 | 89.14
08:00 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 6 | 316 | 0 | 0 | 0 | 0 | 65 | 60 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 325 | 0 | 0 | 250 | 0 | 0 | 8 | 125 | 23 | 21 | 0 | 320 | 0 | 0 | 70 | 0 | 0 | 34 | 0 | 0 | 12 | 12 | 0.42 | 80 | 0 | 6 | 830 | 0 | 0 | 33 | 0 | 0 | 186 | 0 | 0 | 0 | 902 | 5 | 0 | 0 | 320 | 290 | 0 | 51 | 0 | 161 | 18 | 115 | 90 | 0 | 0 | 19 | 0 | 144 | 0 | 12 | 0 | 315 | 0 | 341 | 41 | 0 | 145 | 2 | 17 | 0 | 41 | 0 | 70 | 0 | 96 | 0 | 69 | 58 | 0 | 0 | 3.18 | 12 | 6153.6 | 887 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 852 | 0 | 0 | 0 | 1030.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.03 | 15 | 0 | 0 | 1.77 | 0 | 0 | 178 | 0 | 0 | 0 | 352 | 0 | 0.19 | 0 | 54 | 0 | 1 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0.11 | 0 | 168 | 100 | 180 | 0 | 0 | 850 | 0 | 4899.37 | 11052.97 | 89.13
09:00 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 6 | 327 | 0 | 0 | 0 | 0 | 110 | 60 | 0 | 0 | 12 | 0 | 16 | 0 | 0 | 330 | 0 | 0 | 250 | 0 | 0 | 14 | 125 | 23.5 | 21 | 0 | 350 | 0 | 0 | 70 | 0 | 0 | 34 | 0 | 0 | 12 | 12 | 1.87 | 80 | 0 | 4 | 830 | 0 | 0 | 33 | 0 | 0 | 200 | 0 | 0 | 0 | 1010 | 11 | 0 | 0 | 320 | 290 | 0 | 51 | 0 | 189 | 20 | 115 | 90 | 0 | 0 | 19 | 0 | 142 | 0 | 32 | 0 | 325 | 0 | 377 | 42 | 0 | 150 | 5 | 17 | 0 | 41 | 0 | 70 | 0 | 96 | 0 | 68 | 58 | 10 | 0 | 6.28 | 12 | 6525.65 | 886 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 864 | 0 | 0 | 0 | 1015.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.87 | 41 | 0 | 0 | 5.22 | 0 | 0 | 180 | 0 | 0 | 0 | 414 | 0 | 0.55 | 0 | 54 | 0 | 6 | 0 | 0 | 0 | 0 | 2.8 | 12 | 0.22 | 0 | 166 | 125 | 220 | 0 | 0 | 840 | 0 | 5081.7 | 11607.35 | 89.12
10:00 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 6 | 317 | 0 | 0 | 0 | 12 | 113 | 60 | 0 | 0 | 17 | 14 | 16 | 0 | 0 | 325 | 0 | 5 | 250 | 0 | 0 | 19 | 125 | 23 | 16 | 0 | 350 | 0 | 0 | 71 | 0 | 0 | 34 | 0 | 0 | 12 | 12 | 2.14 | 80 | 0 | 3 | 830 | 0 | 0 | 33 | 0 | 0 | 199 | 0 | 0 | 0 | 1010 | 12 | 0 | 0 | 310 | 290 | 0 | 51 | 0 | 205 | 20 | 115 | 90 | 0 | 0 | 19 | 0 | 142 | 0 | 44 | 0 | 315 | 0 | 377 | 42 | 0 | 159 | 7 | 17 | 0 | 41 | 0 | 71 | 0 | 96 | 0 | 68 | 58 | 11 | 0 | 12.43 | 12 | 6580.57 | 886 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 853 | 0 | 0 | 0 | 1026.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.64 | 28 | 0 | 0 | 1.59 | 0 | 0 | 181 | 0 | 0 | 0 | 414 | 0 | 0.21 | 0 | 55 | 0 | 23 | 0 | 0 | 0 | 0 | 3.7 | 37 | 0.2 | 0 | 168 | 125 | 220 | 0 | 0 | 840 | 0 | 5135.94 | 11716.51 | 89.11
11:00 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 6 | 331 | 0 | 0 | 0 | 17 | 113 | 60 | 0 | 0 | 17 | 16 | 16 | 0 | 0 | 330 | 0 | 17 | 250 | 0 | 0 | 10 | 125 | 23 | 21 | 0 | 300 | 0 | 0 | 70 | 0 | 0 | 17 | 0 | 0 | 12 | 12 | 3.18 | 80 | 0 | 3 | 830 | 0 | 0 | 33 | 0 | 0 | 199 | 0 | 0 | 0 | 1100 | 6 | 0 | 0 | 260 | 290 | 0 | 51 | 0 | 196 | 20 | 115 | 91 | 0 | 0 | 19 | 0 | 154 | 0 | 58 | 0 | 310 | 0 | 377 | 42 | 0 | 159 | 5 | 17 | 0 | 41 | 0 | 70 | 0 | 96 | 0 | 68 | 58 | 11 | 0 | 15.45 | 12 | 6594.63 | 887 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 863 | 0 | 0 | 0 | 1022.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.64 | 26 | 0 | 0 | 8 | 0 | 0 | 185 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 0 | 29 | 0 | 0 | 0 | 0 | 4.6 | 97 | 0.37 | 0 | 167 | 125 | 220 | 0 | 0 | 855 | 0 | 5223.06 | 11817.69 | 89.1
12:00 | 0 | 2 | 42 | 0 | 0 | 0 | 0 | 6 | 412 | 0 | 0 | 12 | 17 | 113 | 60 | 0 | 0 | 17 | 17 | 16 | 0 | 0 | 305 | 0 | 17 | 270 | 0 | 0 | 13 | 125 | 23 | 21 | 0 | 300 | 0 | 0 | 70 | 0 | 3 | 17 | 0 | 0 | 12 | 12 | 3.16 | 80 | 0 | 4 | 830 | 0 | 0 | 33 | 0 | 0 | 218 | 0 | 0 | 0 | 1152 | 16 | 0 | 0 | 250 | 290 | 0 | 51 | 0 | 182 | 20 | 115 | 91 | 0 | 0 | 17 | 0 | 168 | 0 | 62 | 0 | 310 | 0 | 396 | 42 | 0 | 157 | 6 | 17 | 0 | 41 | 0 | 72 | 0 | 96 | 0 | 68 | 35 | 11 | 1 | 14.22 | 5 | 6755.38 | 887 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 946 | 0 | 0 | 0 | 963.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.42 | 58 | 0 | 0 | 22.78 | 0 | 0 | 185 | 0 | 0 | 0 | 414 | 0 | 1.17 | 0 | 55 | 0 | 32 | 0 | 0 | 0 | 0 | 4.8 | 167 | 0.27 | 0 | 265 | 120 | 220 | 0 | 0 | 900 | 0 | 5502.77 | 12258.15 | 89.09
13:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 6 | 412 | 0 | 0 | 16.5 | 17 | 107 | 45 | 0 | 0 | 17 | 16 | 25 | 0 | 0 | 310 | 0 | 17 | 270 | 0 | 0 | 27 | 108 | 23 | 21 | 0 | 280 | 0 | 0 | 58 | 0 | 8 | 17 | 0 | 0 | 12 | 12 | 2.72 | 80 | 0 | 9 | 830 | 0 | 0 | 33 | 0 | 0 | 218 | 0 | 0 | 0 | 1170 | 12 | 0 | 0 | 230 | 290 | 0 | 51 | 0 | 204 | 0 | 115 | 91 | 0 | 0 | 19 | 0 | 168 | 0 | 40 | 0 | 315 | 0 | 382 | 42 | 0 | 156 | 9 | 22 | 0 | 41 | 0 | 70 | 0 | 97 | 0 | 45 | 35 | 10 | 2 | 32.39 | 3 | 6689.61 | 886 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 1176 | 0 | 0 | 0 | 967.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.03 | 93 | 0 | 0 | 52.45 | 0 | 0 | 189 | 0 | 0 | 0 | 414 | 0 | 4.95 | 0 | 56 | 0 | 29 | 0 | 0 | 0 | 0 | 3.8 | 188 | 0.14 | 0 | 278 | 120 | 220 | 0 | 0 | 972 | 0 | 5891.21 | 12580.82 | 89.07
14:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 6 | 412 | 0 | 0 | 16 | 17 | 75 | 15 | 0 | 0 | 17 | 50 | 32 | 0 | 0 | 310 | 0 | 17 | 270 | 0 | 0 | 24 | 108 | 10 | 21 | 0 | 280 | 0 | 0 | 58 | 0 | 9 | 16 | 0 | 0 | 12 | 12 | 2.61 | 80 | 0 | 0 | 830 | 0 | 0 | 33 | 0 | 0 | 219 | 0 | 0 | 0 | 1150 | 14 | 0 | 0 | 230 | 290 | 0 | 51 | 0 | 214 | 0 | 109 | 90 | 0 | 0 | 19 | 0 | 174 | 0 | 52 | 0 | 315 | 0 | 370 | 42 | 0 | 155 | 6 | 22 | 0 | 42 | 0 | 70 | 0 | 94 | 0 | 28 | 35 | 8 | 1 | 18.66 | 12 | 6604.27 | 886 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 1196 | 0 | 0 | 0 | 1080.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.64 | 80 | 0 | 0 | 46.45 | 0 | 0 | 193 | 0 | 0 | 0 | 414 | 0 | 4.47 | 0 | 54 | 0 | 27 | 0 | 0 | 0 | 0 | 4.6 | 136 | 0.32 | 0 | 276 | 120 | 220 | 0 | 0 | 1072 | 0 | 6073.13 | 12677.4 | 89.07
15:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 6 | 412 | 0 | 0 | 30.2 | 17 | 70 | 15 | 0 | 10 | 25 | 62 | 32 | 0 | 0 | 295 | 0 | 35 | 270 | 0 | 0 | 18 | 108 | 22 | 21 | 0 | 280 | 0 | 0 | 58 | 0 | 6 | 16 | 0 | 0 | 12 | 12 | 1.78 | 80 | 0 | 0 | 875 | 0 | 0 | 33 | 0 | 0 | 218 | 0 | 0 | 0 | 1160 | 11 | 0 | 0 | 230 | 290 | 0 | 51 | 0 | 200 | 0 | 73 | 90 | 24 | 0 | 19 | 0 | 184 | 0 | 36 | 0 | 310 | 0 | 362 | 42 | 0 | 155 | 5 | 22 | 0 | 42 | 0 | 69 | 0 | 94 | 0 | 46 | 74 | 7 | 1 | 12.26 | 12 | 6702.24 | 886 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1186 | 0 | 0 | 0 | 1229.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.02 | 61 | 0 | 0 | 33.05 | 0 | 0 | 194 | 0 | 0 | 0 | 409 | 0 | 3.12 | 0 | 54 | 0 | 19 | 0 | 0 | 0 | 0 | 3.4 | 99 | 0.14 | 0 | 275 | 120 | 220 | 0 | 0 | 1085.32 | 0 | 6086.17 | 12788.41 | 89.06
16:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 6 | 383 | 0 | 0 | 32.7 | 17 | 70 | 15 | 0 | 15 | 35 | 65 | 32 | 0 | 0 | 305 | 0 | 35 | 300 | 0 | 0 | 7 | 108 | 21 | 21 | 0 | 280 | 0 | 0 | 58 | 0 | 7 | 34 | 0 | 0 | 12 | 12 | 0.94 | 80 | 0 | 0 | 875 | 0 | 0 | 33 | 0 | 0 | 218 | 0 | 0 | 0 | 1168 | 7 | 0 | 0 | 260 | 315 | 0 | 51 | 0 | 208 | 0 | 34 | 90 | 34 | 0 | 19 | 0 | 178 | 0 | 18 | 0 | 315 | 0 | 402 | 42 | 0 | 153 | 1 | 22 | 0 | 41 | 0 | 71 | 0 | 94 | 0 | 46 | 76 | 7 | 0 | 15.33 | 12 | 6797.97 | 886 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1190 | 0 | 0 | 0 | 1334.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.83 | 31 | 0 | 0 | 19.72 | 0 | 0 | 194 | 0 | 0 | 0 | 410 | 0 | 1.83 | 0 | 54 | 0 | 11 | 0 | 0 | 0 | 0 | 1.4 | 66 | 0.07 | 0 | 307 | 120 | 220 | 0 | 0 | 1085.32 | 0 | 6115.25 | 12913.22 | 89.05
17:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 6 | 343 | 0 | 0 | 42 | 20 | 120 | 45 | 95 | 30 | 47 | 148 | 42 | 0 | 0 | 300 | 0 | 55 | 300 | 0 | 0 | 3 | 142 | 23 | 21 | 0 | 310 | 0 | 0 | 67 | 0 | 8 | 34 | 0 | 0 | 12 | 12 | 0.34 | 80 | 0 | 10 | 875 | 15 | 0 | 50 | 17 | 0 | 222 | 0 | 0 | 0 | 1224 | 2 | 30 | 0 | 230 | 295 | 0 | 51 | 0 | 196 | 0 | 34 | 90 | 44 | 0 | 19 | 17 | 182 | 9 | 3 | 0 | 310 | 0 | 370 | 42 | 0 | 154 | 1 | 22 | 0 | 41 | 0 | 70 | 0 | 94 | 9 | 57 | 78 | 7 | 0 | 3.8 | 12 | 7321.14 | 886 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 1122 | 0 | 0 | 0 | 1426.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.52 | 10 | 0 | 0 | 6.49 | 0 | 0 | 192 | 0 | 0 | 0 | 407 | 0 | 0.59 | 0 | 54 | 50 | 3 | 42 | 0 | 0 | 0 | 0.3 | 28 | 0.01 | 3 | 307 | 120 | 220 | 0 | 0 | 1085.32 | 6 | 6160.34 | 13481.48 | 89.04
18:00 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 6 | 297 | 0 | 0 | 47.4 | 35 | 149 | 45 | 290 | 55 | 55 | 150 | 52 | 0 | 0 | 310 | 0 | 55 | 240 | 0 | 0 | 0 | 142 | 15 | 21 | 0 | 310 | 0 | 0 | 78 | 0 | 15 | 51 | 20 | 0 | 12 | 12 | 0 | 80 | 0 | 15 | 875 | 15 | 0 | 50 | 25.5 | 0 | 187 | 0 | 0 | 0 | 1160 | 0 | 92 | 0 | 220 | 290 | 0 | 51 | 0 | 197 | 0 | 34 | 90 | 112 | 0 | 19 | 17 | 172 | 16 | 0 | 9 | 315 | 0 | 312 | 42 | 0 | 130 | 0 | 22 | 0 | 41 | 0 | 69 | 0 | 94 | 35 | 65 | 78 | 7 | 0 | 0 | 12 | 7498.9 | 886 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64 | 1090 | 0 | 0 | 0 | 1444.46 | 0 | 0 | 0 | 20 | 15 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 55 | 110 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 273 | 110 | 180 | 0 | 0 | 1085.32 | 90 | 6127.42 | 13626.32 | 89.03
19:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 6 | 339 | 0 | 0 | 47.1 | 35 | 149 | 15 | 292 | 55 | 55 | 149 | 66 | 0 | 0 | 300 | 0 | 55 | 240 | 0 | 0 | 0 | 142 | 22 | 22 | 0 | 310 | 0 | 0 | 84 | 0 | 6 | 51 | 24 | 0 | 12 | 12 | 0 | 80 | 0 | 16 | 875 | 0 | 0 | 50 | 25.5 | 0 | 186 | 0 | 0 | 0 | 1140 | 0 | 142 | 0 | 240 | 295 | 0 | 51 | 0 | 200 | 0 | 36 | 90 | 149 | 0 | 19 | 0 | 178 | 0 | 0 | 9 | 275 | 0 | 359 | 41 | 0 | 145 | 0 | 22 | 0 | 41 | 0 | 70 | 0 | 94 | 35 | 74 | 97 | 7 | 0 | 0 | 12 | 7636.6 | 886 | 159 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 0 | 0 | 0 | 1428.63 | 0 | 0 | 0 | 35 | 35 | 0 | 43 | 4 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 55 | 115 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 120 | 220 | 0 | 0 | 1085.32 | 15 | 6290.95 | 13927.55 | 89.02
19:30 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 6 | 315 | 0 | 0 | 47 | 17 | 149 | 15 | 245 | 55 | 55 | 148 | 66 | 0 | 0 | 250 | 0 | 55 | 240 | 0 | 0 | 0 | 125 | 22 | 21 | 0 | 310 | 0 | 0 | 84 | 0 | 8 | 51 | 24 | 0 | 12 | 12 | 0 | 80 | 0 | 19 | 875 | 0 | 0 | 50 | 25.5 | 0 | 186 | 0 | 0 | 0 | 1200 | 0 | 120 | 0 | 250 | 295 | 0 | 51 | 0 | 192 | 0 | 85 | 90 | 185 | 0 | 19 | 0 | 180 | 0 | 0 | 17 | 310 | 0 | 330 | 41 | 0 | 144 | 0 | 22 | 0 | 41 | 0 | 70 | 0 | 95 | 35 | 65 | 107 | 10 | 0 | 0 | 12 | 7628.5 | 886 | 159 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1182 | 0 | 0 | 0 | 1465.27 | 0 | 41 | 0 | 0 | 0 | 0 | 44 | 8 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 54 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 0 | 1085.32 | 0 | 6292.59 | 13921.09 | 89.02
20:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 6 | 312 | 0 | 0 | 45.3 | 19 | 149 | 15 | 195 | 55 | 55 | 145 | 50 | 0 | 0 | 290 | 0 | 55 | 280 | 0 | 0 | 0 | 108 | 24 | 21 | 0 | 310 | 0 | 0 | 84 | 0 | 8 | 51 | 24 | 0 | 12 | 12 | 0 | 80 | 0 | 22 | 875 | 0 | 0 | 50 | 25.5 | 0 | 186 | 0 | 0 | 0 | 1224 | 0 | 120 | 0 | 250 | 290 | 0 | 51 | 0 | 188 | 0 | 77 | 90 | 177 | 0 | 19 | 0 | 178 | 0 | 0 | 17 | 310 | 0 | 318 | 41 | 0 | 143 | 0 | 22 | 0 | 41 | 0 | 70 | 0 | 94 | 35 | 65 | 107 | 12 | 0 | 0 | 12 | 7597.8 | 886 | 164 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1222 | 0 | 0 | 0 | 1446.8 | 0 | 41 | 0 | 0 | 0 | 0 | 44 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 55 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 0 | 1085.32 | 0 | 6454.12 | 14051.92 | 89.01
21:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 6 | 338 | 0 | 0 | 47.4 | 17 | 149 | 0 | 145 | 55 | 55 | 147 | 30 | 0 | 0 | 350 | 0 | 55 | 270 | 0 | 0 | 0 | 108 | 24 | 21 | 0 | 340 | 0 | 0 | 84 | 0 | 5 | 51 | 24 | 0 | 12 | 12 | 0 | 80 | 0 | 22 | 875 | 0 | 0 | 50 | 25.5 | 0 | 186 | 0 | 0 | 0 | 1224 | 0 | 50 | 0 | 260 | 320 | 0 | 51 | 0 | 201 | 0 | 100 | 90 | 188 | 0 | 19 | 0 | 176 | 0 | 0 | 17 | 315 | 0 | 393 | 41 | 0 | 157 | 0 | 23 | 0 | 41 | 0 | 70 | 0 | 95 | 35 | 69 | 108 | 15 | 0 | 0 | 12 | 7720.9 | 886 | 169 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 1458.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 0 | 1085.32 | 0 | 6379.69 | 14100.59 | 89
22:00 | 0 | 37 | 33 | 0 | 0 | 0 | 0 | 6 | 354 | 0 | 0 | 51.7 | 17 | 149 | 0 | 145 | 55 | 55 | 162 | 16 | 0 | 0 | 395 | 0 | 55 | 270 | 0 | 0 | 0 | 108 | 23 | 21 | 0 | 310 | 0 | 0 | 84 | 0 | 7 | 51 | 24 | 0 | 12 | 12 | 0 | 80 | 0 | 16 | 875 | 0 | 0 | 50 | 25.5 | 0 | 225 | 0 | 0 | 0 | 1224 | 0 | 68 | 0 | 225 | 340 | 0 | 51 | 0 | 192 | 0 | 107 | 90 | 182 | 0 | 12 | 0 | 184 | 0 | 0 | 17 | 315 | 0 | 369 | 41 | 0 | 157 | 0 | 23 | 0 | 41 | 0 | 70 | 0 | 95 | 35 | 68 | 108 | 12 | 0 | 0 | 12 | 7762.2 | 886 | 164 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1215 | 0 | 0 | 0 | 1447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 0 | 1085.32 | 0 | 6344.32 | 14106.52 | 88.99
23:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 6 | 338 | 0 | 0 | 47.7 | 17 | 149 | 0 | 45 | 55 | 55 | 152 | 16 | 0 | 0 | 350 | 0 | 55 | 270 | 0 | 0 | 0 | 108 | 23 | 21 | 0 | 310 | 0 | 0 | 78 | 0 | 10 | 51 | 23 | 0 | 12 | 12 | 0 | 80 | 0 | 16 | 875 | 0 | 0 | 50 | 25.5 | 0 | 225 | 0 | 0 | 0 | 1224 | 0 | 50 | 0 | 225 | 320 | 0 | 51 | 0 | 202 | 0 | 72 | 90 | 186 | 0 | 17 | 0 | 182 | 0 | 0 | 17 | 310 | 0 | 362 | 41 | 0 | 158 | 0 | 23 | 0 | 42 | 0 | 70 | 0 | 95 | 35 | 59 | 48 | 10 | 0 | 0 | 8 | 7455.2 | 886 | 165 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1203 | 0 | 0 | 0 | 1465.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 90 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 0 | 1085.32 | 0 | 6324.64 | 13779.84 | 88.98
Total KWH | 0 | 845760 | 696000 | 0 | 0 | 0 | 0 | 166227.27 | 8262000 | 0 | 0 | 703080 | 407520 | 2792736 | 749760 | 2097600 | 674184 | 830504 | 1902240 | 492480 | 0 | 0 | 7784921 | 0 | 781825 | 6348839 | 0 | 0 | 149123 | 2794800 | 514200 | 501480 | 0 | 7734090.91 | 0 | 0 | 1865280 | 0 | 90720 | 920653 | 234768 | 0 | 288000 | 299520 | 19078 | 1922460 | 0 | 317760 | 20370909.09 | 23418 | 0 | 1517760 | 199747.8 | 0 | 4940090 | 0 | 0 | 0 | 26525452 | 102600 | 1124072 | 0 | 6291000 | 7465500 | 0 | 1245896 | 0 | 4789000 | 105336 | 1850880 | 2155646 | 1667040 | 0 | 471310 | 30780 | 3941760 | 32491 | 368627 | 158368 | 7466000 | 0 | 8967000 | 986000 | 0 | 3637554.55 | 45133 | 502296 | 0 | 993600 | 0 | 1649000 | 0 | 2288980 | 402120 | 1546800 | 1540800 | 204480 | 6200 | 126660 | 276720 | 169204635.62 | 20709090 | 4336416 | 0 | 83520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348480 | 25461810 | 0 | 0 | 0 | 29601091 | 0 | 200583 | 0 | 206112 | 240960 | 0 | 69984 | 82063 | 37637 | 207024 | 458702 | 92669 | 0 | 199488 | 0 | 0 | 4537518 | 0 | 0 | 0 | 9470981 | 0 | 16920 | 0 | 1254545 | 1083702 | 177478 | 1010275 | 0 | 0 | 0 | 29496.96 | 835200 | 2314 | 79488 | 6043000 | 2773000 | 5255090 | 0 | 0 | 24923636.36 | 284400 | 140112673.32 | 309317308.94

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 12-03-2026
Power Supply Scenario
| Day Peak Generation |  |  | 12258.15 | MW | 12:00 Hr. | Energy Generated |  |  | 309.3173 |  | MKWHr.
| Day Peak Demand |  |  | 12483.15 | MW | 12:00 Hr. | Energy Unserverd |  |  | 2.59 |  | MKWHr.
| Evening Peak Generation |  |  | 14100.59 | MW | 21:00 Hr. | Energy Demand |  |  | 311.9073 |  | MKWHr.
| Evening Peak Demand |  |  | 14136.59 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32 |  | °C
| Minimum Generation of the Day |  |  | 10836.59 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 822.3 |  | MMCFD
| Maximum Generation of the Day |  |  | 14106.52 | MW | 22:00 Hr. | Production Cost per KWHr |  |  | 6.4468 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 31.3118 | 0 | 15.7685 | 0 | 0 | 0.14912 | 0 | 0 | 47.2294 | Gas | 112.1612 | Gas | 383939096.2652
| Chattogram Zone |  |  | 5.2579 | 46.8964 | 5.3491 | 0 | 1.9225 | 0.12168 | 0 | 0.09072 | 59.6382 | Coal | 104.5794 | Coal | 683695056.4765
| Cumilla Zone |  |  | 22.5237 | 0 | 4.8636 | 0 | 0 | 0.36863 | 3.9418 | 0 | 31.6977 | HFO | 33.2191 | HFO | 563674419.88
| Mymensingh Zone |  |  | 0.20448 | 0 | 3.7664 | 0 | 0 | 0.13286 | 0 | 0 | 4.1038 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.4904 | 0 | 0 | 0 | 0 | 0.045133 | 0 | 0 | 26.5356 | Hydro | 1.9225 | Hydro | 192246
| Khulna Zone |  |  | 4.3364 | 25.4618 | 0.08352 | 0 | 0 | 0.34848 | 20.7091 | 0 | 50.9393 | Solar | 3.0925 | Solar | 49357319.412
| Barishal Zone |  |  | 8.0281 | 30.9666 | 0.36389 | 0 | 0 | 0.002314 | 0 | 0 | 39.3609 | Import | 54.2519 | Import | 311905157.79
| Rajshahi Zone |  |  | 14.0085 | 0 | 0.93001 | 0 | 0 | 0.88213 | 29.6011 | 0 | 45.4217 | Wind | 0.09072 | Wind | 1334491.2
| Rangpur Zone |  |  | 0 | 1.2545 | 2.094 | 0 | 0 | 1.0422 | 0 | 0 | 4.3907
| Total |  |  | 112.1612 | 104.5794 | 33.2191 | 0 | 1.9225 | 3.0925 | 54.2519 | 0.09072 | 309.3173
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 383939096.2652 |  | Hydro | 192246
|  |  |  | Coal | 683695056.4765 |  | Solar | 49357319.412
|  |  |  | HFO | 563674419.88 |  | Import | 311905157.79
|  |  |  | HSD | 0 |  | Wind | 1334491.2
[5 empty] | Total: | 199,40,97,787 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.7091 | Peak Hr Flow | 886.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 44724636.36 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 29.6011 | Peak Hr Flow | 1458.17 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2132 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.9418 | Peak Hr Flow | 176.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2394 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 54.2519 | Peak Hr Flow | 2520.17 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5269
|  |  |  | Chattogram |  | 34 |  | 1328
|  |  |  | Cumilla |  | 0 |  | 1366
|  |  |  | Mymensingh |  | 0 |  | 1097
|  |  |  | Sylhet |  | 0 |  | 560
|  |  |  | Khulna |  | 0 |  | 1586
|  |  |  | Barishal |  | 0 |  | 393
|  |  |  | Rajshahi |  | 0 |  | 1272
|  |  |  | Rangpur |  | 0 |  | 801
|  |  |  | Total |  | 34 |  | 13672
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:21 | 10:21 | Bogura(New)-Naogaon 132 kV Ckt-1 Tripped from Naogaon 132/33kV end showing Distance relay | [7 empty] | 22.0MW load
|  |  | relays Due to Naogaon ckt-1 is in trip from Bogura end. | [7 empty] | interrup. Naogaon
132/33kV end
| 08:22 | 09:10 | Bogura(New)-Naogaon 132 kV Ckt-2 Tripped from Bogura 230/132kV end showing Distance
Protection Relay Phase A, Zone 4 relays.
| 08:22 | 09:24 | Bogura 230/132kV S/S Confidance UN-2 Tripped showing Over Voltage relay relays.
| 08:35 | 10:55 | Fenchuganj -Sylhet 132kV Ckt-1 Scheduled S/D from Beanibazar 132/33kV end Due to | [7 empty] | 40.0MW load
|  |  | Schedule work | [7 empty] | interrup.
Beanibazar 132/33kV
end
| 08:36 | 10:55 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Scheduled S/D from Beanibazar 132/33kV
end Due to Schedule work and from Fenchuganj 230/132/33kV end Due to Sylhet(South) SS end
project work.
| 08:36 | 10:55 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Scheduled S/D from Beanibazar 132/33kV
end Due to Schedule work and from Fenchuganj 230/132/33kV end Due to Sylhet(South) SS end
project work.
| 08:42 |  | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-1 Project Work S/D Due to
Re-conductoring work.
| 08:48 | 15:49 | Baroirhat-Hathazari 132 kV Ckt-2 Scheduled S/D from Baroirhat 132/33kV end Due to Annual
deadline checking
|  | 08:58 | Mymensingh 132/33kV S/S Bus B is restored.
| 09:00 | 14:38 | Aminbazar-Keraniganj 230kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to
Disk cleaning and deadline checking at Aminbazar end. and from Aminbazar 400/230/132kV
end Due to Disc cleaning and deadline checking
|  | 09:01 | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) is restored.
| 09:03 |  | Baroirhat-Hathazari 132 kV Ckt-2 Scheduled S/D from Hathazari 230/132/33kV end.
| 09:11 | 17:08 | Chowmuhani 230/132/33kV S/S Korerhat-04 Scheduled S/D Due to Painting and Silicon work
|  | 09:16 | Ramganj 132/33kV S/S Transformer-01 HT is restored.
|  | 09:16 | Ramganj 132/33kV S/S Transformer-01 LT is restored.
|  | 09:17 | Ramganj 132/33kV S/S 132 Kv Bus-B is restored.
| 09:29 | 14:30 | Chowmuhani 230/132/33kV S/S ATR-03 LT Scheduled S/D Due to Shield wire and PI replacement
| 09:29 | 14:30 | Chowmuhani 230/132/33kV S/S ATR-03 HT Scheduled S/D Due to Shield wire and PI replacement
| 10:38 | 16:36 | Kachua 230/132/33kV S/S ATR-2 LT Project Work S/D Due to Project Work for DFDR test
| 10:39 | 16:35 | Kachua 230/132/33kV S/S ATR-2 HT Project Work S/D Due to project work for DFDR test
| 10:54 | 14:50 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) LT Scheduled S/D Due to 33 kv fakirhat 2
maintenance work
|  | 10:54 | Mymensingh-Netrokona 132kV Ckt-2 is restored.
| 10:55 | 16:29 | Kachua 230/132/33kV S/S Main Bus-2 (230 kV) Project Work S/D Due to project work for DFDR
test
| 10:55 | 14:47 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) HT Scheduled S/D Due to 33 kv fakirhat 2
maintenance work
| 11:26 | 12:37 | Khulna (C) S/S Tr-3 405T LT Scheduled S/D Due to Joragate-2 Red Hot maintenance.
| 11:27 | 12:36 | Khulna (C) S/S Tr-3 405T HT Scheduled S/D Due to Joragate to red hot maintenance.
| 11:28 | 11:38 | Benapole 132/33kV S/S Transformer-2(416T) LT Forced S/D Due to Bus Separation | [7 empty] | 20.0MW load
interrup.
| 11:29 | 11:37 | Benapole 132/33kV S/S Transformer-2(416T) HT Forced S/D Due to Bus Separation | [7 empty] | 20.0MW load
interrup.
|  | 11:35 | Kabirpur -Tongi 132kV Ckt-1 is restored.
| 11:47 | 14:46 | Bogura(New)-Naogaon 132 kV Ckt-1 Forced S/D from Naogaon 132/33kV end Due to Relay test
work by SPMD .
|  | 11:49 | Bogura 400/230kV S/S ATR-01 LT is restored.
|  | 11:49 | Bogura 400/230kV S/S ATR-01 HT is restored.
| 11:53 | 14:13 | Haripur 230/132kV S/S Auto TR-3 LT Scheduled S/D Due to High Tempareture Junction Point
Maintenance.
| 11:53 | 14:13 | Haripur 230/132kV S/S Auto TR-3 HT Scheduled S/D Due to High Tempareture Junction Point
Maintenance.
| 13:32 | 14:08 | Shahjadpur-Ullahpara 132kV Ckt-1 Forced S/D from Ullahpara 132/33kV end Due to 132 CT
terminal (R-Phase) Red-hot Maintenance.
| 13:38 |  | Day Peak Generation: 12255 MW.
| 13:48 | 19:41 | Dhamrai-Kaliakoir 132 kV Ckt-2 Project Work S/D from Dhamrai 132/33kV end Due to Project
work
|  | 14:54 | Ashuganj-Shahjibazar 132kV Ckt-1 is restored.
|  | 15:36 | Saidpur 132/33kV S/S TR-01 HT is restored.
| 15:47 | 17:36 | Bhandaria 132/33kV S/S Transformer-1 LT Scheduled S/D | [7 empty] | 10.0MW load
interrup.
| 15:47 | 17:36 | Bhandaria 132/33kV S/S Transformer-1 HT Scheduled S/D | [7 empty] | 10.0MW load
interrup.
| 16:03 |  | Saidpur 132/33kV S/S TR-01 HT Scheduled S/D Due to QF- GMD-39 and as the instruction of
ALDC Bogura (499264)
| 21:00 |  | Evening peak generation 14099 MW
| 23:40 |  | Shahjibazar-Sreemangal 132kV Ckt-1 Forced S/D from Sreemongol 132/33kV end Due to For
over load of Fen ckt-2
| 05:18 | 05:23 | Sreemongol 132/33kV S/S 132/33kv T-2 LT Tripped showing Over current relays Due to 33 kV | [7 empty] | 2.0MW load
|  |  | Bus fault. | [7 empty] | interrup.
| 05:18 |  | Sreemongol 132/33kV S/S 132/33kv T-1AB LT Tripped showing Over current relays Due to 33 | [7 empty] | 7.0MW load
|  |  | kV Bus fault | [7 empty] | interrup.
| 05:23 |  | Sreemongol 132/33kV S/S 132/33kv T-1AB LT Forced S/D Due to 33 kV Bus fault removing | [7 empty] | 5.0MW load
|  |  | work. | [7 empty] | interrup.
| 06:39 |  | Monakasha-Rahanpur 400kV Ckt-1 Scheduled S/D from Rahanpur 400/132kV end Due to
Maintenance work
| 07:00 |  | Minimum Generation: 10190 MW.
| 07:03 |  | Patuakhali 132/33kV S/S 425T (T-3) LT Scheduled S/D Due to 33 kV Bus Red hot maintenance | [7 empty] | 15.0MW load
|  |  | work | [7 empty] | interrup.
| 07:04 |  | Patuakhali 132/33kV S/S 425T (T-3) HT Scheduled S/D Due to 33 kV Bus Red hot maintenance | [7 empty] | 15.0MW load
|  |  | work | [7 empty] | interrup.
| 07:27 |  | Gopalganj 400/132kV S/S 400kV Rooppur Scheduled S/D
| 07:31 |  | Aminbazar 400/230/132kV S/S Gopalganj-2 Scheduled S/D Due to Disc cleaning
| 07:32 |  | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-2 Scheduled S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 12-03-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 6 | 166227.27 | Demand "05"MW due to gas restiction by Titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 338 | 8262000 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 674184 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 270 | 6348839 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 47.4 | 703080 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 749760 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 830504 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 781825 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 24 | 514200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 501480 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 33 | 696000 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 2097600 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2792736 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 845760 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 30 | 492480 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 147 | 1902240 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 149123 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 407520 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 340 | 7734090.91 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 350 | 7784921 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 108 | 2794800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2224.4 | 47229370.18
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Under Maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 199747.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 102600 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1517760 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1922460 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 186 | 4940090 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 24 | 234768 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 920653 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 288000 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 22 | 317760 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 84 | 1865280 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 19078 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 299520 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 23418 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 26525452 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 5 | 90720 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 875 | 20370909.09 | Plant availability less
Chattogram Area Total |  |  |  |  | 4898.863 | 2650.5 | 59638215.89
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 201 | 4789000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 320 | 7465500 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | FGMO ON
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 260 | 6291000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 105336 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1245896 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 50 | 1124072 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 17 | 158368 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2155646 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 188 | 1667040 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 176 | 3941760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 32491 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 471310 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 30780 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 100 | 1850880 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 368627 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1472 | 31697706
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 15 | 204480 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 6200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 108 | 1540800 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 69 | 1546800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 126660 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 276720 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 402120 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 239 | 4103780
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 45133 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 986000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 157 | 3637554.55 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 70 | 1649000 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 41 | 993600 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 95 | 2288980 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 23 | 502296 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7466000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 393 | 8967000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1135 | 26535563.55
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 886 | 20709090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 20 | 83520 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 169 | 4336416 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 348480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1234.2 | 25461810 | plant availability zero
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2309.2 | 50939316
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 79488 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2773000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1085.32 | 24923636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5255090 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 284400 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6043000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2314 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1732.32 | 39360928.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 207024 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 200583 | Under Maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 82063 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 190 | 4537518 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9470981 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 92669 | machine problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 37637 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 69984 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 240960 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 206112 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 16920 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1458.17 | 29601091 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 199488 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 458702 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2062.17 | 45421732
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 55 | 1254545 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 1010275 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 29496.96 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1083702 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 177478 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 835200 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 276 | 4390696.96
Eastern Grid Total |  |  |  |  | 17400.108 | 7720.9 | 169204635.62
Western Grid Total |  |  |  |  | 11852.195 | 6379.69 | 140112673.32
National Grid Total |  |  |  |  | 29252.303 | 14100.59 | 309317308.94
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 12-03-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9585.73 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4051.8 | MW
i) Dhaka area |  |  | 5268.73 |  | MW | i) Khulna area |  |  |  | 1586 | MW
ii) Chattogram area |  |  | 1294 |  | MW | ii) Barishal area |  |  |  | 393 | MW
iii) Cumilla area |  |  | 1366 |  | MW | iii) Rajshahi area |  |  |  | 1271.8 | MW
iv) Mymensingh area |  |  | 1097 |  | MW | iv) Rangpur area |  |  |  | 801 | MW
v) Sylhet area |  |  | 560 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13637.53 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 10 | 00:00 | 67 | Hasnabad | 88 | 19:30 | 133 | Nawabganj | 52 | 21:00
2 | AKSML | 7 | 21:00 | 68 | Hathazari | 71 | 13:00 | 134 | Netrakona | 137 | 17:00
3 | Aftabnagar | 34 | 19:00 | 69 | Hatirjheel | 42 | 12:00 | 135 | New | 72.6 | 14:00
4 | Agargaon | 104 | 14:00 | 70 | Ishurdi | 66 | 19:00 | 136 | Niamatpur | 84 | 00:00
5 | Agrabad | 62 | 19:00 | 71 | Jaldhaka | 71 | 18:00 | 137 | Noapara | 41 | 21:00
6 | Amnura | 33 | 00:00 | 72 | Jamalpur | 114 | 18:00 | 138 | PHP | 12 | 11:00
7 | Ashuganj | 88 | 23:00 | 73 | Jashore | 139 | 13:00 | 139 | Pabna | 84 | 18:00
8 | BSRM | 205 | 07:00 | 74 | Jhenaidah | 100 | 18:00 | 140 | Palashbari | 102 | 00:00
9 | Bagerhat | 79 | 21:00 | 75 | Joydebpur | 129 | 16:00 | 141 | Panchagarh | 53 | 17:00
10 | Bajitpur | 74 | 00:00 | 76 | Joypurhat | 63 | 00:00 | 142 | Patiya | 7.2 | 19:30
11 | Bakerganj | 12 | 21:00 | 77 | Juldah | 17.5 | 00:00 | 143 | Patuakhali | 47.5 | 00:00
12 | Bakulia | 70 | 19:00 | 78 | KSRM | 14 | 19:00 | 144 | Payra | 34 | 21:00
13 | Banani | 54 | 13:00 | 79 | Kabirpur | 253 | 19:00 | 145 | Postogola | 50 | 13:00
14 | Bangabhaban | 16 | 10:00 | 80 | Kachua | 87 | 22:00 | 146 | Pubail | 24 | 16:00
15 | Barapukuria | 65 | 04:00 | 81 | Kaliganj | 25.5 | 18:30 | 147 | Purbachal | 28 | 15:00
16 | Barguna | 18 | 21:00 | 82 | Kallyanpur | 108 | 20:00 | 148 | Purbasadipur | 120 | 19:00
17 | Barishal | 103 | 13:00 | 83 | Kalurghat | 54 | 12:00 | 149 | Rahanpur | 35 | 04:00
18 | Barishal-230 | 78 | 17:00 | 84 | Kamrangirchar | 79 | 17:00 | 150 | Rahim | 29 | 12:00
19 | Baroaulia | 68 | 11:00 | 85 | Kaptai | N/A | N/A | 151 | Rajbari | 70 | 21:00
20 | Baroirhat | 53 | 18:30 | 86 | Kasba | 35 | 18:30 | 152 | Rajendrapur | 133 | 13:00
21 | Bashundhara | 186 | 21:00 | 87 | Kazla | 113 | 13:00 | 153 | Rajshahi | 89 | 00:00
22 | BashundharaCement | 7 | 00:00 | 88 | Keranigonj | 80 | 20:00 | 154 | Rajshahi-230 | 78 | 18:00
23 | Beanibazar | 68 | 18:30 | 89 | Khagrachori | 34 | 18:30 | 155 | Ramganj | 98 | 19:00
24 | Benapole | 58 | 18:30 | 90 | Khulna | 50 | 20:00 | 156 | Rampur | 38 | 23:00
25 | Bhaluka | 140 | 12:00 | 91 | Khulshi | 180 | 12:00 | 157 | Rangamati | 16 | 18:30
26 | Bhandaria | 51 | 00:00 | 92 | Kishoreganj | 130 | 18:00 | 158 | Rangpur | 143 | 18:00
27 | Bhangura | 40 | 03:00 | 93 | Kodda | 299 | 17:00 | 159 | Ruppur | 4 | 15:00
28 | Bheramara(GK) | 54 | 21:00 | 94 | Kulaura | 42 | 18:30 | 160 | SSM | 14 | 06:00
29 | Bhulta | 228 | 12:00 | 95 | Kurigram | 61 | 18:00 | 161 | Saidpur | 92 | 18:00
30 | Bog-Sherpur | 72 | 01:00 | 96 | Kushtia | 128 | 20:00 | 162 | Satkhira | 124 | 21:00
31 | Bogura | 149 | 00:00 | 97 | Laksam | 18 | 00:00 | 163 | Satmasjid | 97 | 19:00
32 | Borhanuddin | 84 | 21:00 | 98 | Lakshmipur | 33 | 20:00 | 164 | Savar | 218 | 15:00
33 | Brahmanbaria | 124 | 18:30 | 99 | Lalbag | 74 | 17:00 | 165 | SevenRings | 20.47 | 03:00
34 | Cantonment | 96 | 17:00 | 100 | Lalmonirhat | 48 | 18:00 | 166 | ShahCement | 34 | 01:00
35 | Chandina | 20 | 22:00 | 101 | MI_Cement | 19 | 20:00 | 167 | Shahjadpur | 75 | 08:00
36 | Chandpur | 76 | 21:00 | 102 | Madanganj | 50 | 09:00 | 168 | Shahjibazar | 118 | 00:00
37 | Chandraghona | 32 | 19:00 | 103 | Madaripur | 89 | 18:30 | 169 | Shahmirpur | 61 | 00:00
38 | Chapai | 67.5 | 19:30 | 104 | Madartek | 72 | 21:00 | 170 | Shariatpur | 73 | 21:00
39 | Charsaidpur | 43 | 02:00 | 105 | Madunaghat | 46 | 22:00 | 171 | Sherpur | 148 | 04:00
40 | Chauddagram | 68 | 18:00 | 106 | Magura | 59 | 18:30 | 172 | Shikalbaha | 32 | 00:00
41 | Chhatak | 35 | 22:00 | 107 | Mahasthangarh | 82 | 03:00 | 173 | Shitalakhya | 79.9 | 15:00
42 | Chowmuhani | 123 | 21:00 | 108 | Maijdee | 43 | 21:00 | 174 | Sholosohor | 42 | 19:00
43 | Chuadanga | 111 | 22:00 | 109 | Manikganj | 124 | 20:00 | 175 | Shyampur | 188 | 12:00
44 | Coxsbazar | 133 | 20:00 | 110 | Maniknagar | 69 | 14:00 | 176 | Siddhirganj | 129 | 16:00
45 | Cumilla(N) | 121 | 01:00 | 111 | Matarbari | 49 | 03:00 | 177 | Sirajganj | 102 | 09:00
46 | Cumilla(S) | 183 | 22:00 | 112 | Matuail | 64 | 00:00 | 178 | Sonargaon | 148 | 23:00
47 | Daganbhuiyan | 30 | 22:00 | 113 | Metrorail_Motijheel | 30 | 17:00 | 179 | Sreemongol | 67 | 00:00
48 | Daudkandi | 145 | 17:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sreepur | 117 | 19:00
49 | DhakaUniversity | 72 | 13:00 | 115 | Millgate | 91 | 09:00 | 181 | Srinagar | 42.4 | 21:00
50 | Dhamrai | 128 | 09:00 | 116 | Mirpur | 149 | 20:00 | 182 | Sunamganj | 53 | 21:00
51 | Dhanmondi | 110 | 13:00 | 117 | Mirsorai | 38 | 02:00 | 183 | Sylhet | 50 | 00:00
52 | Dohazari | 102 | 18:30 | 118 | Mirzapur | 44 | 19:00 | 184 | Sylhet-132 | 105 | 21:00
53 | Faridpur | 150 | 19:00 | 119 | Mithapukur | 60 | 04:00 | 185 | TK | 24 | 22:00
54 | Fatullah | 101 | 15:00 | 120 | Modern | N/A | N/A | 186 | Tangail | 172 | 03:00
55 | Fenchuganj | 34 | 22:00 | 121 | Mogbazar | 75.4 | 14:00 | 187 | Taraganj | 21 | 18:00
56 | Feni | 94 | 22:00 | 122 | Mongla | 47 | 14:00 | 188 | Tasnim | 12 | 08:00
57 | GPH | 3 | 11:00 | 123 | Motijheel | 43 | 13:00 | 189 | Thakurgaon | 93 | 18:00
58 | Ghatail | 88 | 04:00 | 124 | Muktagacha | 40 | 17:00 | 190 | Tongi | 157 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 104 | 22:00 | 191 | Ullahpara | 41 | 02:00
60 | Ghorashal-230 | 107 | 01:00 | 126 | Muradnagar | 43 | 22:00 | 192 | Ullon | 52 | 18:30
61 | Goalpara | 36 | 00:00 | 127 | Mymensingh | 197 | 17:00 | 193 | Uttara | 73 | 15:00
62 | Gollamari | 94 | 19:00 | 128 | Naogaon | 129 | 00:00 | 194 | UttaraNew | 28 | 18:00
63 | Gopalganj | 82 | 23:00 | 129 | Narail | 52 | 19:00 | 195 | Zigatola | 76 | 20:00
64 | Gulshan | 108 | 12:00 | 130 | Narinda | 64 | 13:00
65 | Halishahar | 92 | 15:00 | 131 | Narshingdi | 169 | 19:30
66 | HaripurSBU | 130 | 07:00 | 132 | Natore | 144 | 04:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 12-03-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 13870.04 | 57 |  | 13929.61
1:00 | 13228.86 | 54 |  | 13285.29
2:00 | 12825.58 | 33 |  | 12860.07
3:00 | 12780.69 | 33 |  | 12814.69
4:00 | 13033.07 | 22 |  | 13056.07
5:00 | 11914.32 | 0 |  | 11914.32
6:00 | 10917.96 | 0 |  | 10917.96
7:00 | 10836.59 | 0 |  | 10836.59
8:00 | 11052.97 | 0 |  | 11052.97
9:00 | 11607.35 | 0 |  | 11607.35
10:00 | 11716.51 | 83 |  | 11803.51
11:00 | 11817.69 | 148 |  | 11972.69
12:00 | 12258.15 | 215 |  | 12483.15
13:00 | 12580.82 | 262 |  | 12854.82
14:00 | 12677.4 | 408 |  | 13103.4
15:00 | 12788.41 | 491 |  | 13301.41
16:00 | 12913.22 | 422 |  | 13354.22
17:00 | 13481.48 | 78 |  | 13563.48
18:00 | 13626.32 | 73 |  | 13702.32
19:00 | 13927.55 | 42 |  | 13971.55
19:30 | 13921.09 | 38 |  | 13961.09
20:00 | 14051.92 | 33 |  | 14085.92
21:00 | 14100.59 | 34 |  | 14136.59
22:00 | 14106.52 | 43 |  | 14151.52
23:00 | 13779.84 | 59 |  | 13841.84
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 12-03-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7406 | 6464.04 | 13870.04 | DAILY GENERATION CURVE
00:30 | 7354.3 | 6195.15 | 13549.45
01:00 | 7302.6 | 5926.26 | 13228.86 | 12-03-2026
01:30 | 7163.45 | 5863.77 | 13027.22
02:00 | 7024.3 | 5801.28 | 12825.58
02:30 | 7017.15 | 5785.985 | 12803.135
03:00 | 7010 | 5770.69 | 12780.69
03:30 | 7065.3 | 5841.58 | 12906.88
04:00 | 7120.6 | 5912.47 | 13033.07
04:30 | 6686.25 | 5787.445 | 12473.695
05:00 | 6251.9 | 5662.42 | 11914.32
05:30 | 6082.95 | 5333.19 | 11416.14
06:00 | 5914 | 5003.96 | 10917.96
06:30 | 5941.36 | 4935.915 | 10877.275
07:00 | 5968.72 | 4867.87 | 10836.59
07:30 | 6061.16 | 4883.62 | 10944.78
08:00 | 6153.6 | 4899.37 | 11052.97
08:30 | 6339.625 | 4990.535 | 11330.16
09:00 | 6525.65 | 5081.7 | 11607.35
09:30 | 6553.11 | 5108.82 | 11661.93
10:00 | 6580.57 | 5135.94 | 11716.51
10:30 | 6587.6 | 5179.5 | 11767.1
11:00 | 6594.63 | 5223.06 | 11817.69
11:30 | 6675.005 | 5362.915 | 12037.92
12:00 | 6755.38 | 5502.77 | 12258.15
12:30 | 6722.495 | 5696.99 | 12419.485
13:00 | 6689.61 | 5891.21 | 12580.82
13:30 | 6646.94 | 5982.17 | 12629.11
14:00 | 6604.27 | 6073.13 | 12677.4
14:30 | 6653.255 | 6079.65 | 12732.905
15:00 | 6702.24 | 6086.17 | 12788.41
15:30 | 6750.105 | 6100.71 | 12850.815
16:00 | 6797.97 | 6115.25 | 12913.22
16:30 | 7059.555 | 6137.795 | 13197.35
17:00 | 7321.14 | 6160.34 | 13481.48
17:30 | 7410.02 | 6143.88 | 13553.9
18:00 | 7498.9 | 6127.42 | 13626.32
18:30 | 7567.75 | 6209.185 | 13776.935
19:00 | 7636.6 | 6290.95 | 13927.55
19:30 | 7628.5 | 6292.59 | 13921.09
20:00 | 7597.8 | 6454.12 | 14051.92
20:30 | 7659.35 | 6416.905 | 14076.255 |  | Executive Engineer
21:00 | 7720.9 | 6379.69 | 14100.59 |  | Network Operation Division
21:30 | 7741.55 | 6362.005 | 14103.555
22:00 | 7762.2 | 6344.32 | 14106.52
22:30 | 7608.7 | 6334.48 | 13943.18
23:00 | 7455.2 | 6324.64 | 13779.84

## En-Curve
QF-LDC-12
Date | 12-03-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3088 | 1557 | 901 | 0 | 174 | 1455.04 | 80 | 4583 | 0 | 404 | 1628 | 0 | 0 | 0 | 57 | DAILY ENERGY CURVE
00:30 | 3041 | 1525 | 783.5 | 0 | 168 | 1413.15 | 80 | 4557 | 0 | 404 | 1577.8 | 0 | 0 | 0 | 55.5 | 12-03-2026
01:00 | 2994 | 1493 | 666 | 0 | 162 | 1371.26 | 80 | 4531 | 0 | 404 | 1527.6 | 0 | 0 | 0 | 54
01:30 | 2917 | 1469 | 705 | 0 | 156 | 1366.27 | 80 | 4398.5 | 0 | 403.5 | 1531.95 | 0 | 0 | 0 | 43.5 | Energy Generated | 309.3173 |  | MKWHr
02:00 | 2840 | 1445 | 744 | 0 | 150 | 1361.28 | 80 | 4266 | 0 | 403 | 1536.3 | 0 | 0 | 0 | 33 | Energy not Served | 2.59 |  | MKWHr
02:30 | 2839.5 | 1404 | 744.5 | 0 | 149 | 1354.485 | 80 | 4262.5 | 0 | 411.5 | 1557.65 | 0 | 0 | 0 | 33 | Total Energy Requirement | 311.9073 |  | MKWHr
03:00 | 2839 | 1363 | 745 | 0 | 148 | 1347.69 | 80 | 4259 | 0 | 420 | 1579 | 0 | 0 | 0 | 33
03:30 | 2970 | 1426 | 745 | 0 | 151 | 1359.08 | 80 | 4366.5 | 0 | 374.5 | 1434.8 | 0 | 0 | 0 | 27.5
04:00 | 3101 | 1489 | 745 | 0 | 154 | 1370.47 | 80 | 4474 | 0 | 329 | 1290.6 | 0 | 0 | 0 | 22
04:30 | 3111 | 1496 | 815.5 | 0 | 153 | 1366.445 | 80 | 4297.5 | 0 | 255 | 899.25 | 0 | 0 | 0 | 11
05:00 | 3121 | 1503 | 886 | 0 | 152 | 1362.42 | 80 | 4121 | 0 | 181 | 507.9 | 0 | 0 | 0 | 0
05:30 | 3049.5 | 1502 | 886 | 0 | 148 | 1268.19 | 80 | 3903 | 0 | 155 | 424.45 | 0 | 0 | 0 | 0
06:00 | 2978 | 1501 | 886 | 0 | 144 | 1173.96 | 80 | 3685 | 0 | 129 | 341 | 0 | 0 | 0 | 0
06:30 | 2977.5 | 1499 | 886 | 0 | 142 | 1093.22 | 80 | 3673 | 13.055 | 146.5 | 367 | 0 | 0 | 0 | 0
07:00 | 2977 | 1497 | 886 | 0 | 140 | 1012.48 | 80 | 3661 | 26.11 | 164 | 393 | 0 | 0 | 0 | 0
07:30 | 2989.5 | 1483 | 886.5 | 0 | 142 | 1021.425 | 80 | 3658.5 | 55.855 | 200.5 | 427.5 | 0 | 0 | 0 | 0
08:00 | 3002 | 1469 | 887 | 0 | 144 | 1030.37 | 80 | 3656 | 85.6 | 237 | 462 | 0 | 0 | 0 | 0
08:30 | 3098 | 1513.25 | 886.5 | 0 | 143 | 1022.705 | 80 | 3710 | 139.705 | 247 | 490 | 0 | 0 | 0 | 0
09:00 | 3194 | 1557.5 | 886 | 0 | 142 | 1015.04 | 80 | 3764 | 193.81 | 257 | 518 | 0 | 0 | 0 | 0
09:30 | 3193.5 | 1551.25 | 886 | 0 | 142 | 1020.82 | 80 | 3760 | 231.36 | 259 | 538 | 0 | 0 | 0 | 41.5
10:00 | 3193 | 1545 | 886 | 0 | 142 | 1026.6 | 80 | 3756 | 268.91 | 261 | 558 | 0 | 0 | 0 | 83
10:30 | 3171 | 1522.5 | 886.5 | 0 | 148 | 1024.525 | 80 | 3813 | 302.075 | 252.5 | 567 | 0 | 0 | 0 | 115.5
11:00 | 3149 | 1500 | 887 | 0 | 154 | 1022.45 | 80 | 3870 | 335.24 | 244 | 576 | 0 | 0 | 0 | 148
11:30 | 3204 | 1486 | 887 | 0 | 161 | 992.89 | 80 | 4009 | 404.03 | 245 | 567.5 | 0 | 0 | 1.5 | 181.5
12:00 | 3259 | 1472 | 887 | 0 | 168 | 963.33 | 80 | 4148 | 472.82 | 246 | 559 | 0 | 0 | 3 | 215
12:30 | 3239 | 1472.5 | 886.5 | 0 | 168 | 965.585 | 80 | 4315 | 515.15 | 228.5 | 543.75 | 0 | 0 | 5.5 | 238.5
13:00 | 3219 | 1473 | 886 | 0 | 168 | 967.84 | 80 | 4482 | 557.48 | 211 | 528.5 | 0 | 0 | 8 | 262
13:30 | 3215.5 | 1462 | 886 | 0 | 171 | 1024.245 | 80 | 4530 | 530.615 | 195.5 | 525.75 | 0 | 0 | 8.5 | 335
14:00 | 3212 | 1451 | 886 | 0 | 174 | 1080.65 | 80 | 4578 | 503.75 | 180 | 523 | 0 | 0 | 9 | 408
14:30 | 3194.5 | 1447 | 886 | 0 | 179 | 1154.885 | 80 | 4606.66 | 423.26 | 180 | 574.1 | 0 | 0 | 7.5 | 449.5
15:00 | 3177 | 1443 | 886 | 0 | 184 | 1229.12 | 80 | 4635.32 | 342.77 | 180 | 625.2 | 0 | 0 | 6 | 491
15:30 | 3230.5 | 1448.5 | 886 | 0 | 181 | 1281.6 | 80 | 4657.32 | 268.445 | 189 | 621.95 | 0 | 0 | 6.5 | 456.5
16:00 | 3284 | 1454 | 886 | 0 | 178 | 1334.08 | 80 | 4679.32 | 194.12 | 198 | 618.7 | 0 | 0 | 7 | 422
16:30 | 3214 | 1470.5 | 886 | 0 | 180 | 1380.095 | 80 | 4673.32 | 140.585 | 274.5 | 890.85 | 0 | 0 | 7.5 | 250
17:00 | 3144 | 1487 | 886 | 0 | 182 | 1426.11 | 80 | 4667.32 | 87.05 | 351 | 1163 | 0 | 0 | 8 | 78
17:30 | 2972 | 1461 | 886 | 0 | 177 | 1435.285 | 80 | 4602.82 | 43.845 | 353 | 1531.45 | 0 | 0 | 11.5 | 75.5
18:00 | 2800 | 1435 | 886 | 0 | 172 | 1444.46 | 80 | 4538.32 | 0.64 | 355 | 1899.9 | 0 | 0 | 15 | 73
18:30 | 2891.5 | 1442 | 886 | 0 | 175 | 1436.545 | 80 | 4560.32 | 0.32 | 378 | 1916.75 | 0 | 0 | 10.5 | 57.5
19:00 | 2983 | 1449 | 886 | 0 | 178 | 1428.63 | 80 | 4582.32 | 0 | 401 | 1933.6 | 0 | 0 | 6 | 42
19:30 | 2863 | 1435 | 886 | 0 | 180 | 1465.27 | 80 | 4703.32 | 0 | 450 | 1850.5 | 0 | 0 | 8 | 38
20:00 | 3007 | 1479 | 886 | 0 | 178 | 1446.8 | 80 | 4768.32 | 0 | 433 | 1765.8 | 0 | 0 | 8 | 33
20:30 | 3089.5 | 1534 | 886 | 0 | 177 | 1452.485 | 80 | 4774.42 | 0 | 360 | 1716.35 | 0 | 0 | 6.5 | 33.5
21:00 | 3172 | 1589 | 886 | 0 | 176 | 1458.17 | 80 | 4780.52 | 0 | 287 | 1666.9 | 0 | 0 | 5 | 34
21:30 | 3171.5 | 1589.5 | 886 | 0 | 180 | 1452.585 | 80 | 4770.92 | 0 | 288.5 | 1678.55 | 0 | 0 | 6 | 38.5
22:00 | 3171 | 1590 | 886 | 0 | 184 | 1447 | 80 | 4761.32 | 0 | 290 | 1690.2 | 0 | 0 | 7 | 43
22:30 | 3153 | 1568.5 | 886 | 0 | 183 | 1456.16 | 80 | 4755.32 | 0 | 296 | 1556.7 | 0 | 0 | 8.5 | 51
23:00 | 3135 | 1547 | 886 | 0 | 182 | 1465.32 | 80 | 4749.32 | 0 | 302 | 1423.2 | 0 | 0 | 10 | 59
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 12-03-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 392 | 03:00 | 374 | 16:00 | Madunaghat | 400 | 07:00 | 392 | 17:00
Amtali | 414 | 06:00 | 406 | 14:00 | Meghnaghat | 393 | 03:00 | 376 | 16:00
Ashuganj | 406 | 3:00 | 371 | 12:00 | Payra | 416 | 06:00 | 408 | 16:00
Bhulta | 401 | 02:00 | 365 | 12:00 | Rahanpur | 415 | 09:00 | 388 | 17:00
Bibiana | 407 | 18:00 | 394 | 14:00 | Rampal | 406 | 06:00 | 393 | 14:00
BIPTC | 402 | 04:00 | 388 | 15:00
Bogura | 404 | 08:00 | 373 | 16:00
Gopalganj | 403 | 06:00 | 387 | 16:00
Kaliakoir | 388 | 18:00 | 364 | 16:00
Korerhat | 400 | 03:00 | 389 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 233 | 03:00 | 218 | 16:00 | Jhenaidah | 231 | 06:00 | 217 | 19:00
AKSML | 233 | 06:00 | 226 | 12:00 | Kachua | 229 | 07:00 | 222 | 12:00
Aminbazar | 231 | 18:00 | 218 | 16:00 | Kaliakoir | 238 | 18:00 | 220 | 14:00
Ashuganj | 232 | 18:00 | 210 | 22:00 | Keranigonj | 231 | 18:30 | 216 | 13:00
Ashuganj-400 | 232 | 18:00 | 210 | 22:00 | Khulna(S) | 233 | 06:00 | 221 | 21:00
Baghabari | 233 | 01:00 | 223 | 18:30 | Korerhat | 230 | 03:00 | 221 | 12:00
Barapukuria | 227 | 07:00 | 206 | 16:00 | Madunaghat | 233 | 07:00 | 226 | 13:00
Barapukuria-230 | 227 | 07:00 | 206 | 16:00 | Madunaghat-400 | 233 | 07:00 | 228 | 12:00
Barishal | 230 | 06:00 | 223 | 16:00 | Maniknagar | 228 | 18:30 | 216 | 16:00
Bheramara | 234 | 01:00 | 221 | 19:00 | Meghnaghat | 236 | 21:00 | 225 | 14:00
Bhulta | 234 | 03:00 | 211 | 12:00 | Meghnaghat-400 | 233 | 18:30 | 220 | 14:00
Bibiana | 234 | 18:00 | 227 | 14:00 | Mirsorai | 235 | 02:00 | 228 | 13:00
BIPTC | 236 | 01:00 | 221 | 21:00 | Purbasadipur | 228 | 08:00 | 204 | 16:00
Bogura | 238 | 08:00 | 221 | 16:00 | Rajshahi | 233 | 02:00 | 220 | 21:00
Bogura-400 | 237 | 08:00 | 221 | 16:00 | Rampal | 232 | 06:00 | 221 | 22:00
Borhanuddin | 234 | 06:00 | 229 | 15:00 | Rampur | N/A | N/A | N/A | N/A
BSRM | 229 | 03:00 | 222 | 12:00 | Rampura | 235 | 19:00 | 210 | 12:00
Chowmuhani | 230 | 08:00 | 222 | 12:00 | Shikalbaha | 231 | 06:00 | 226 | 12:00
Cumilla(N) | 230 | 06:00 | 219 | 12:00 | Shyampur | 231 | 18:30 | 217 | 14:00
Faridpur | 227 | 06:00 | 217 | 15:00 | Siddhirganj | 227 | 05:00 | 223 | 21:00
Fenchuganj | 237 | 07:00 | 231 | 14:00 | Sirajgonj | 236 | 07:00 | 229 | 15:00
Feni | 230 | 06:00 | 221 | 12:00 | Sreepur | 226 | 03:00 | 212 | 16:00
Ghorashal | 235 | 06:00 | 218 | 14:00 | Tongi | 232 | 18:30 | 215 | 13:00
Ghorashal-230 | 230 | 03:00 | 211 | 16:00
Gopalganj | 226 | 06:00 | 217 | 15:00
GPH | 231 | 03:00 | 225 | 12:00
Haripur | 231 | 18:30 | 218 | 12:00
Hasnabad | 228 | 01:00 | 218 | 12:00
Hathazari | 228 | 18:30 | 222 | 12:00
Ishurdi | 237 | 01:00 | 223 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 03:00 | 123 | 12:00 | Madunaghat | 135 | 09:00 | 130 | 12:00
Agargaon | 137 | 02:00 | 128 | 14:00 | Magura | 133 | 06:00 | 120 | 13:00
Agrabad | 132 | 05:00 | 128 | 14:00 | Mahasthangarh | 141 | 08:00 | 128 | 16:00
AKS | 130 | 00:00 | 127 | 12:00 | Maijdee | 129 | 08:00 | 123 | 12:00
Aminbazar | 135 | 18:00 | 125 | 14:00 | Manikganj | 131 | 02:00 | 120 | 12:00
Amnura | 136 | 09:00 | 127 | 16:00 | Maniknagar | 134 | 18:30 | 126 | 12:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 119 | 10:00 | 109 | 21:00
Ashuganj-230 | 140 | 01:00 | 130 | 16:00 | Matuail | 136 | 18:30 | 122 | 16:00
Bagerhat | 131 | 05:00 | 121 | 16:00 | Metrorail_Motijheel | 134 | 18:30 | 120 | 13:00
Bajitpur | 131 | 06:00 | 124 | 12:00 | Metrorail_Uttara | 134 | 01:00 | 124 | 11:00
Bakerganj | 135 | 18:00 | 129 | 15:00 | Millgate | 139 | 18:00 | 126 | 14:00
Bakulia | 133 | 02:00 | 128 | 13:00 | Mirpur | 134 | 18:30 | 123 | 16:00
Banani | 138 | 02:00 | 122 | 12:00 | Mirzapur | 134 | 18:30 | 124 | 16:00
Bangabhaban | 134 | 06:00 | 126 | 12:00 | Mithapukur | 141 | 08:00 | 124 | 16:00
Barapukuria | 141 | 07:00 | 124 | 16:00 | MI_Cement | 134 | 02:00 | 124 | 14:00
Barguna | 135 | 06:00 | 129 | 21:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 134 | 06:00 | 128 | 13:00 | Mogbazar | 137 | 02:00 | 122 | 12:00
Barishal-230 | 134 | 03:00 | 129 | 13:00 | Mongla | 133 | 07:00 | 122 | 15:00
Baroaulia | 133 | 08:00 | 129 | 18:00 | Motijheel | 134 | 06:00 | 126 | 12:00
Baroirhat | 132 | 07:00 | 125 | 13:00 | Muktagacha | 136 | 11:00 | 118 | 00:00
Bashundhara | 137 | 00:00 | 123 | 12:00 | Munshiganj | 136 | 18:00 | 126 | 12:00
BashundharaCement | 138 | 18:30 | 127 | 12:00 | Muradnagar | 130 | 03:00 | 120 | 12:00
Beanibazar | 133 | 11:00 | 124 | 00:00 | Mymensingh | 134 | 11:00 | 116 | 00:00
Benapole | 131 | 06:00 | 117 | 13:00 | Naogaon | 141 | 08:00 | 125 | 17:00
Bhaluka | 134 | 01:00 | 127 | 12:00 | Narail | 133 | 06:00 | 121 | 19:00
Bhandaria | 130 | 05:00 | 124 | 14:00 | Narinda | 131 | 02:00 | 120 | 12:00
Bhangura | 133 | 02:00 | 125 | 13:00 | Narshingdi | 130 | 18:30 | 121 | 10:00
Bheramara | 134 | 01:00 | 130 | 19:00 | Natore | 135 | 09:00 | 127 | 21:00
Bheramara(GK) | 134 | 02:00 | 130 | 19:00 | Nawabganj | 134 | 03:00 | 125 | 12:00
Bhulta | 129 | 18:30 | 121 | 11:00 | Netrakona | 124 | 01:00 | 114 | 17:00
Bog-Sherpur | 140 | 08:00 | 128 | 16:00 | New | 140 | 18:30 | 127 | 14:00
Bogura | 143 | 08:00 | 131 | 16:00 | Niamatpur | 137 | 08:00 | 128 | 16:00
Bogura-230 | 143 | 08:00 | 131 | 16:00 | Noapara | 135 | 06:00 | 125 | 13:00
Brahmanbaria | 131 | 06:00 | 121 | 12:00 | Pabna | 134 | 01:00 | 127 | 21:00
Cantonment | 136 | 02:00 | 127 | 16:00 | Palashbari | 140 | 08:00 | 123 | 16:00
Chandina | 132 | 03:00 | 125 | 12:00 | Panchagarh | 138 | 01:00 | 124 | 12:00
Chandpur | 134 | 03:00 | 127 | 16:00 | Patiya | 130 | 11:00 | 127 | 20:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 134 | 07:00 | 130 | 15:00 | Patuakhali | 133 | 07:00 | 129 | 14:00
Chapai | 136 | 06:00 | 128 | 21:00 | Payra | 136 | 06:00 | 133 | 13:00
Charsaidpur | 138 | 18:30 | 128 | 10:00 | PHP | 131 | 07:00 | 124 | 13:00
Chauddagram | 130 | 06:00 | 124 | 12:00 | Postogola | 136 | 02:00 | 126 | 12:00
Chhatak | 127 | 06:00 | 120 | 17:00 | Pubail | 139 | 01:00 | 124 | 16:00
Chowmuhani | 127 | 00:00 | 123 | 15:00 | Purbachal | 138 | 02:00 | 121 | 12:00
Chuadanga | 131 | 06:00 | 118 | 21:00 | Purbasadipur | 135 | 02:00 | 121 | 16:00
Coxsbazar | 117 | 06:00 | 110 | 19:30 | Rahanpur | 138 | 07:00 | 130 | 16:00
Cumilla(N) | 133 | 06:00 | 120 | 14:00 | Rahanpur-400 | 139 | 08:00 | 130 | 16:00
Cumilla(S) | 132 | 07:00 | 116 | 14:00 | Rahim | 136 | 18:30 | 123 | 04:00
Daganbhuiyan | 129 | 06:00 | 123 | 13:00 | Rajbari | 130 | 06:00 | 123 | 16:00
Daudkandi | 131 | 18:00 | 116 | 14:00 | Rajendrapur | 134 | 03:00 | 125 | 13:00
DhakaUniversity | 138 | 00:00 | 123 | 12:00 | Rajshahi | 134 | 04:00 | 125 | 21:00
Dhamrai | 138 | 01:00 | 125 | 14:00 | Rajshahi-230 | 134 | 02:00 | 126 | 22:00
Dhanmondi | 137 | 01:00 | 128.9 | 12:00 | Ramganj | 129 | 03:00 | 123 | 15:00
Dohazari | 129 | 09:00 | 122 | 20:00 | Rampur | 133 | 07:00 | 128 | 14:00
Faridpur | 131 | 06:00 | 125 | 13:00 | Rampura | 138 | 03:00 | 122 | 12:00
Fatullah | 136 | 18:30 | 124 | 12:00 | Rangamati | 133 | 04:00 | 129 | 15:00
Fenchuganj | 134 | 08:00 | 130 | 00:00 | Rangpur | 140 | 07:00 | 126 | 15:00
Feni | 128 | 04:00 | 123 | 12:00 | Ruppur | 135 | 01:00 | 130 | 18:30
Feni-230 | 129 | 06:00 | 124 | 12:00 | Saidpur | 139 | 06:00 | 122 | 16:00
Ghatail | 133 | 11:00 | 118 | 16:00 | Satkhira | 134 | 06:00 | 121 | 21:00
Ghorashal | 141 | 03:00 | 127 | 16:00 | Satmasjid | 137 | 03:00 | 127 | 14:00
Goalpara | 138 | 06:00 | 127 | 21:00 | Savar | 136 | 02:00 | 122 | 12:00
Gollamari | 136 | 06:00 | 128 | 15:00 | SevenRings | 141 | 03:00 | 127 | 12:00
Gopalganj | 134 | 06:00 | 127 | 13:00 | ShahCement | 138 | 18:30 | 128 | 10:00
Gopalganj-400 | 134 | 06:00 | 128 | 16:00 | Shahjadpur | 135 | 00:00 | 130 | 21:00
Gulshan | 137 | 00:00 | 122 | 12:00 | Shahjibazar | 131 | 08:00 | 119 | 13:00
Halishahar | 133 | 08:00 | 129 | 14:00 | Shahmirpur | 133 | 18:00 | 129 | 00:00
Haripur | 137 | 18:30 | 128 | 12:00 | Shariatpur | 133 | 05:00 | 126 | 15:00
HaripurSBU | 137 | 19:30 | 128 | 12:00 | Sherpur | 138 | 11:00 | 110 | 00:00
Hasnabad | 136 | 02:00 | 126 | 11:00 | Shikalbaha | 121 | 07:00 | 118 | 12:00
Hathazari | 134 | 18:00 | 130 | 12:00 | Shikalbaha-230 | 134 | 08:00 | 130 | 00:00
Hatirjheel | 138 | 03:00 | 123 | 12:00 | Shitalakhya | 134 | 02:00 | 124 | 14:00
Ishurdi | 136 | 01:00 | 131 | 19:30 | Sholosohor | 133 | 06:00 | 130 | 00:00
Jaldhaka | 137 | 06:00 | 120 | 16:00 | Shyampur | 130 | 02:00 | 123 | 12:00
Jamalpur | 138 | 11:00 | 115 | 00:00 | Shyampur-230 | 133 | 18:30 | 124 | 16:00
Jashore | 133 | 06:00 | 117 | 13:00 | Siddhirganj | 138 | 18:00 | 128 | 12:00
Jhenaidah | 134 | 06:00 | 118 | 19:00 | Sirajganj | 136 | 11:00 | 124 | 17:00
Jhenaidah-230 | 134 | 06:00 | 124 | 13:00 | Sonargaon | 134 | 18:00 | 112 | 14:00
Joydebpur | 138 | 03:00 | 122 | 16:00 | Sreemongol | 130 | 08:00 | 123 | 00:00
Joypurhat | 140 | 08:00 | 122 | 14:00 | Sreepur | 138 | 02:00 | 130 | 12:00
Juldah | 132 | 07:00 | 129 | 00:00 | Srinagar | 135 | 03:00 | 125 | 16:00
Kabirpur | 139 | 18:00 | 123 | 14:00 | SSM | 140 | 22:00 | 132 | 18:30
Kachua | 131 | 06:00 | 126 | 15:00 | Sunamganj | 127 | 07:00 | 118 | 21:00
Kaliakoir | 143 | 18:00 | 131 | 12:00 | Sylhet | 131 | 08:00 | 122 | 21:00
Kaliganj | 133 | 06:00 | 122 | 13:00 | Sylhet-132 | 130 | 08:00 | 125 | 13:00
Kallyanpur | 134 | 18:30 | 125 | 12:00 | Tangail | 131 | 11:00 | 121 | 16:00
Kalurghat | 134 | 06:00 | 130 | 12:00 | Taraganj | 138 | 06:00 | 123 | 16:00
Kamrangirchar | 135 | 04:00 | 122 | 12:00 | Tasnim | 134 | 18:00 | 127 | 11:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 139 | 02:00 | 122 | 15:00
Kasba | 130 | 06:00 | 120 | 12:00 | TK | 134 | 18:00 | 130 | 12:00
Kazla | 134 | 19:00 | 125 | 13:00 | Tongi | 137 | 04:00 | 129 | 15:00
Keranigonj | 135 | 03:00 | 125 | 16:00 | Ullahpara | 132 | 06:00 | 126 | 16:00
Khagrachori | 133 | 06:00 | 128 | 15:00 | Ullon | 137 | 02:00 | 123 | 12:00
Khulna | 136 | 06:00 | 127 | 14:00 | Uttara | 135 | 03:00 | 124 | 12:00
Khulna(S) | 138 | 06:00 | 128 | 21:00 | UttaraNew | 134 | 01:00 | 124 | 12:00
Khulshi | 132 | 07:00 | 128 | 00:00 | Zigatola | 135 | 02:00 | 126 | 12:00
Kishoreganj | 130 | 07:00 | 120 | 11:00
Kodda | 138 | 01:00 | 120 | 16:00
Korerhat | 132 | 18:00 | 128 | 00:00
KSRM | 134 | 18:00 | 130 | 12:00
Kulaura | 133 | 10:00 | 128 | 14:00
Kurigram | 138 | 07:00 | 120 | 16:00
Kushtia | 131 | 06:00 | 123 | 13:00
Laksam | 132 | 03:00 | 125 | 16:00
Lakshmipur | 128 | 07:00 | 122 | 13:00
Lalbag | 133 | 03:00 | 124 | 16:00
Lalmonirhat | 138 | 07:00 | 118 | 17:00
Madanganj | 138 | 19:00 | 127 | 12:00
Madaripur | 133 | 06:00 | 127 | 16:00
Madartek | 136 | 06:00 | 121 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division