## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 14-03-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-03-2026 | during | 14-03-2026 | during | 14-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 6 | 6 | 97.7 | 97.7 | 7 | 7 | Demand "05"MW due to gas restiction by Titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 333 | 311 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 1 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 300 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 5 | 17.5 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 30 | 62 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 10 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 4 | 12 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 19 | 22 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 34 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 110 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 80 | 118 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 70 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 16 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 27 | 35 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 24 | 0 | 26 | 0 | 26 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 5 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 310 | 320 | 584 | 584 | 320 | 320 | FGMO
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 325 | 300 | 583 | 583 | 320 | 320 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 90 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1461 | 1893.5 | 5941.22 | 5915.22 | 2720.05 | 2695.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 1 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 16 | 0 | 16 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 46 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 80 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 218 | 206 | 220 | 225 | 220 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 1 | 38 | 40 | 56 | 56 | 64 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 50 | 50 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 13 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 65 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0 | 0 | 3.15 | 0 | 3.15 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 38 | 38 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1140 | 1120 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 28 | 11 | 25 | 0 | 25 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 670 | 670 | 670 | 670 | 670 | 670 | machine problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2180 | 2349.5 | 3566.01 | 3562.86 | 3100.65 | 3089.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 170 | 187 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 320 | 0 | 353.35 | 353.35 | 353.35 | 353.35 | Line trip
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 318.81 | 318.81 | 0 | 0 | Low gas pressure
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 250 | 0 | 393 | 393 | 0 | 0 | Line trip
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 42 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 21 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 153 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 41 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 1 | 100 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 9 | 32 | 32 | 32 | 32 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 36 | 80 | 163 | 163 | 100 | 100 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 7 | 151 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 156 | 148 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 12 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 1 | 50 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 45 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1057 | 994 | 2736.51 | 2670.51 | 1595.55 | 1535.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-03-2026 | during | 14-03-2026 | during | 14-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 12 | 21 | 157.5 | 157.5 | 10 | 10 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.8 | 0 | 1.8 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 66 | 76 | 60 | 80 | 60 | 80 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 56 | 98 | 70 | 115 | 70 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 15.5 | 0 | 45.12 | 0 | 45.12 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 35 | 54.5 | 54.5 | 17 | 35 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 156.5 | 236 | 410.92 | 429 | 209.92 | 246
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 41 | 0 | 0 | 41 | 41 | machine problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 152 | 152 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 70 | 70 | 70 | 70 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 41 | 41 | 86 | 86 | 42 | 42 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 96 | 97 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 17 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 295 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 215 | 382 | 385 | 385 | 385 | 385 | -
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 935 | 1095 | 1220 | 1220 | 1094 | 1094
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 865 | 662 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 22 | 44 | 44 | 44 | 44 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 189 | 180 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 73 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 851 | 1155 | 617.1 | 1234.2 | 1148.28 | 1148.28 | plant availability zero
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1978 | 2019 | 2972.1 | 3514.2 | 2532.38 | 2457.38
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 60 | 60 | 65 | 65 | 130 | 130 | GT-02 Offline Waterwash
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 820 | 1030 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 15 | 15 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 168 | 248 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.62 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1268.62 | 1558 | 1938.32 | 1937.32 | 1868.32 | 1867.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 28.93 | 0 | 48 | 0 | 48 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 150 | 197 | 220 | 220 | 200 | 200 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 405 | 402 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 21 | 21 | 21 | 21 | 21 | machine problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 43 | 50 | 50 | 34 | 34 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.47 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1069 | 1261 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 44.19 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 94 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1793.59 | 1994 | 3178.57 | 2963.87 | 2629.57 | 2414.87
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 54 | 54 | 55 | 55 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 90 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.9 | 0 | 6.2 | 0 | 6.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 11 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 102 | 0 | 150.83 | 0 | 150.83 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 170.9 | 214 | 504.03 | 317 | 415.03 | 228
System Total |  |  |  |  | 28823.2 | 29252.303 | 11000.61 | 12353 | 22467.68 | 22529.98 | 16165.47 | 15627.67
Forecast Scenario (14-03-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11660 |  | 0 |  | 11660
|  |  |  | 1:00 | 11080 |  | 0 |  | 11080
|  |  |  | 2:00 | 10740 |  | 0 |  | 10740
|  |  |  | 3:00 | 10770 |  | 0 |  | 10770
|  |  |  | 4:00 | 11550 |  | 0 |  | 11550
|  |  |  | 5:00 | 10500 |  | 0 |  | 10500
|  |  |  | 6:00 | 9590 |  | 0 |  | 9590
|  |  |  | 7:00 | 9750 |  | 0 |  | 9750
|  |  |  | 8:00 | 10430 |  | 0 |  | 10430
|  |  |  | 9:00 | 11080 |  | 0 |  | 11080
|  |  |  | 10:00 | 11150 |  | 0 |  | 11150
|  |  |  | 11:00 | 11460 |  | 0 |  | 11460
|  |  |  | 12:00 | 11900 |  | 0 |  | 11900
|  |  |  | 13:00 | 12350 |  | 0 |  | 12350
|  |  |  | 14:00 | 12570 |  | 0 |  | 12570
|  |  |  | 15:00 | 12550 |  | 0 |  | 12550
|  |  |  | 16:00 | 12620 |  | 0 |  | 12620
|  |  |  | 17:00 | 13260 |  | 0 |  | 13260
|  |  |  | 18:00 | 13270 |  | 0 |  | 13270
|  |  |  | 18:30 | 13300 |  | 0 |  | 13300
|  |  |  | 19:00 | 13380 |  | 0 |  | 13380
|  |  |  | 19:30 | 13580 |  | 0 |  | 13580
|  |  |  | 20:00 | 13600 |  | 0 |  | 13600
|  |  |  | 21:00 | 13740 |  | 0 |  | 13740
|  |  |  | 22:00 | 13430 |  | 0 |  | 13430
|  |  |  | 23:00 | 13090 |  | 0 |  | 13090
Probable Maximum Temperature: |  |  | 31.00°C
Probable Maximum Demand at Day Peak: |  |  | 11900.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13740.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12938.90 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 282.29031 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:40 hrs on 14-03-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 13-03-2026 | [28 empty] | Date: | 13-03-2026 | [28 empty] | Date: | 13-03-2026 | [28 empty] | Date: | 13-03-2026 | [28 empty] | Date: | 13-03-2026 | [17 empty] | Date: | 13-03-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [17 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 6 | 334 | 0 | 0 | 48.1 | 17 | 149 | 0 | 45 | 30 | 55 | 151 | 16 | 0 | 0 | 345 | 0 | 17 | 270 | 0 | 0 | 0 | 108 | 18 | 21 | 0 | 310 | 0 | 0 | 79 | 0 | 10 | 51 | 23 | 0 | 12 | 12 | 0 | 80 | 0 | 16 | 875 | 0 | 0 | 50 | 25.5 | 0 | 226 | 0 | 0 | 0 | 1217 | 0 | 45 | 0 | 225 | 320 | 0 | 51 | 0 | 202 | 0 | 0 | 86 | 100 | 0 | 20 | 0 | 178 | 0 | 0 | 17 | 305 | 0 | 356 | 41 | 0 | 157 | 0 | 23 | 0 | 42 | 0 | 71 | 0 | 95 | 35 | 59 | 48 | 10 | 0 | 0 | 12 | 7197.6 | 886 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1210 | 0 | 0 | 0 | 1449.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 120 | 220 | 0 | 0 | 1085 | 0 | 6184.72 | 13382.32 | 88.97
01:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 7 | 339 | 0 | 0 | 21.5 | 0 | 114 | 0 | 15 | 30 | 17 | 35 | 16 | 0 | 0 | 350 | 0 | 17 | 270 | 0 | 0 | 0 | 90 | 18 | 21 | 0 | 330 | 0 | 0 | 78 | 0 | 7 | 51 | 22 | 0 | 12 | 12 | 0 | 80 | 0 | 17 | 875 | 0 | 0 | 50 | 25.5 | 0 | 225 | 0 | 0 | 0 | 1163 | 0 | 12 | 0 | 225 | 320 | 0 | 51 | 0 | 203 | 0 | 0 | 0 | 51 | 0 | 20 | 0 | 168 | 0 | 0 | 17 | 305 | 0 | 370 | 41 | 0 | 159 | 0 | 23 | 0 | 41 | 0 | 69 | 0 | 95 | 35 | 58 | 48 | 10 | 0 | 0 | 12 | 6724 | 804 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1187 | 0 | 0 | 0 | 1446.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 56 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 120 | 220 | 0 | 0 | 1085.32 | 0 | 6019.31 | 12743.31 | 88.96
02:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 7 | 318 | 0 | 0 | 15.9 | 0 | 114 | 0 | 15 | 30 | 17 | 35 | 16 | 0 | 0 | 305 | 0 | 17 | 250 | 0 | 0 | 0 | 90 | 18 | 21 | 0 | 330 | 0 | 0 | 78 | 0 | 11 | 51 | 22 | 0 | 12 | 12 | 0 | 80 | 0 | 17 | 875 | 0 | 0 | 50 | 25.5 | 0 | 225 | 0 | 0 | 0 | 1030 | 0 | 12 | 0 | 225 | 320 | 0 | 51 | 0 | 208 | 0 | 0 | 0 | 49 | 0 | 20 | 0 | 158 | 0 | 0 | 17 | 310 | 0 | 342 | 41 | 0 | 158 | 0 | 23 | 0 | 41 | 0 | 70 | 0 | 96 | 35 | 58 | 47 | 10 | 0 | 0 | 12 | 6473.4 | 817 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 1454.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 56 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 120 | 180 | 0 | 0 | 1085.32 | 0 | 5792.63 | 12266.03 | 88.95
03:00 | 0 | 50 | 42 | 0 | 0 | 0 | 0 | 7 | 313 | 0 | 0 | 0 | 0 | 117 | 24 | 15 | 30 | 17 | 35 | 16 | 0 | 0 | 300 | 0 | 17 | 250 | 0 | 0 | 0 | 125 | 18 | 21 | 0 | 360 | 0 | 0 | 76 | 0 | 7 | 51 | 22 | 0 | 12 | 12 | 0 | 80 | 0 | 22 | 875 | 0 | 0 | 50 | 25.5 | 0 | 226 | 0 | 0 | 0 | 1006 | 0 | 12 | 0 | 225 | 320 | 0 | 51 | 0 | 212 | 0 | 0 | 0 | 51 | 0 | 20 | 0 | 162 | 0 | 0 | 17 | 305 | 0 | 377 | 41 | 0 | 159 | 0 | 23 | 0 | 41 | 0 | 71 | 0 | 96 | 35 | 59 | 95 | 12 | 0 | 0 | 12 | 6617.5 | 818 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 0 | 0 | 0 | 1455.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 56 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 120 | 220 | 0 | 0 | 1085.32 | 0 | 5846.49 | 12463.99 | 88.94
04:00 | 0 | 17 | 42 | 0 | 0 | 0 | 0 | 7 | 313 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 30 | 17 | 35 | 16 | 0 | 0 | 330 | 0 | 0 | 250 | 0 | 0 | 0 | 125 | 18 | 21 | 0 | 310 | 0 | 0 | 73 | 0 | 2 | 51 | 22 | 0 | 12 | 12 | 0 | 80 | 0 | 25 | 875 | 0 | 0 | 50 | 25.5 | 0 | 226 | 0 | 0 | 0 | 1115 | 0 | 6 | 0 | 225 | 320 | 0 | 51 | 0 | 211 | 0 | 0 | 0 | 48 | 0 | 17 | 0 | 162 | 0 | 0 | 0 | 305 | 0 | 357 | 41 | 0 | 156 | 0 | 23 | 0 | 41 | 0 | 70 | 0 | 96 | 35 | 58 | 97 | 12 | 0 | 0 | 12 | 6591.5 | 864 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1182 | 0 | 0 | 0 | 1430.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 57 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 0 | 1085.32 | 0 | 6033.59 | 12625.09 | 88.93
05:00 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 7 | 313 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 250 | 0 | 0 | 0 | 52 | 20 | 21 | 0 | 310 | 0 | 0 | 71 | 0 | 5 | 2 | 0 | 0 | 12 | 12 | 0 | 80 | 0 | 26 | 875 | 0 | 0 | 45 | 0 | 0 | 226 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 225 | 320 | 0 | 51 | 0 | 212 | 0 | 7 | 50 | 0 | 0 | 20 | 0 | 148 | 0 | 0 | 0 | 300 | 0 | 323 | 41 | 0 | 142 | 0 | 17 | 0 | 41 | 0 | 70 | 0 | 96 | 35 | 59 | 68 | 12 | 0 | 0 | 12 | 5998 | 865 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1094 | 0 | 0 | 0 | 1313.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 62 | 180 | 0 | 0 | 1040 | 0 | 5527.93 | 11525.93 | 88.92
06:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 7 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 250 | 0 | 0 | 0 | 52 | 17 | 21 | 0 | 310 | 0 | 0 | 64 | 0 | 5 | 0 | 0 | 0 | 12 | 12 | 0 | 80 | 0 | 0 | 875 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 887 | 0 | 0 | 0 | 225 | 320 | 0 | 51 | 0 | 170 | 0 | 0 | 50 | 0 | 0 | 17 | 0 | 148 | 0 | 0 | 0 | 310 | 0 | 327 | 41 | 0 | 136 | 0 | 17 | 0 | 41 | 0 | 70 | 0 | 96 | 0 | 59 | 35 | 18 | 0 | 0 | 0 | 5584 | 865 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 893 | 0 | 0 | 0 | 1079.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 62 | 180 | 0 | 0 | 850 | 0 | 4886.39 | 10470.39 | 88.91
07:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 7 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 250 | 0 | 0 | 1 | 35 | 18 | 21 | 0 | 310 | 0 | 0 | 42 | 0 | 15 | 0 | 0 | 0 | 12 | 12 | 0 | 80 | 0 | 0 | 875 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 900 | 1 | 0 | 0 | 250 | 320 | 0 | 51 | 0 | 170 | 0 | 0 | 50 | 0 | 0 | 17 | 0 | 142 | 0 | 3 | 0 | 305 | 0 | 337 | 41 | 0 | 139 | 0 | 17 | 0 | 41 | 0 | 70 | 0 | 96 | 0 | 45 | 8 | 18 | 0 | 0 | 0 | 5565 | 865 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 809 | 0 | 0 | 0 | 937.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.45 | 5 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 1 | 0.04 | 0 | 218 | 62 | 180 | 0 | 0 | 800 | 0 | 4626.38 | 10191.38 | 88.9
08:00 | 0 | 2 | 16 | 0 | 0 | 0 | 0 | 6 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 19 | 22 | 0 | 320 | 0 | 0 | 43 | 0 | 11 | 0 | 0 | 0 | 12 | 12 | 0 | 80 | 0 | 0 | 875 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 902 | 5 | 0 | 0 | 245 | 320 | 0 | 51 | 0 | 170 | 0 | 0 | 50 | 0 | 0 | 17 | 0 | 140 | 0 | 16 | 0 | 310 | 0 | 352 | 41 | 0 | 144 | 1 | 0 | 0 | 41 | 0 | 70 | 0 | 96 | 0 | 45 | 8 | 19 | 0 | 1.34 | 0 | 5586.34 | 772 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 810 | 0 | 0 | 0 | 830.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.03 | 24 | 0 | 0 | 0.58 | 0 | 0 | 168 | 0 | 0 | 0 | 376 | 0 | 0.26 | 0 | 57 | 0 | 5 | 0 | 0 | 0 | 0 | 0.1 | 26 | 0.13 | 0 | 221 | 62 | 180 | 0 | 0 | 800 | 0 | 4552.85 | 10139.19 | 88.89
09:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 6 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 20 | 22 | 0 | 330 | 0 | 0 | 19 | 0 | 4 | 0 | 0 | 0 | 12 | 12 | 0 | 80 | 0 | 6 | 875 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 902 | 11 | 0 | 0 | 280 | 320 | 0 | 51 | 0 | 170 | 0 | 0 | 50 | 0 | 0 | 17 | 0 | 138 | 0 | 21 | 0 | 325 | 0 | 339 | 41 | 0 | 148 | 3 | 0 | 0 | 41 | 0 | 70 | 0 | 96 | 0 | 56 | 24 | 19 | 0 | 7.83 | 0 | 5701.83 | 865 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 830 | 0 | 0 | 0 | 832.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.71 | 48 | 0 | 0 | 9.61 | 0 | 0 | 179 | 0 | 0 | 0 | 370 | 0 | 0.85 | 0 | 56 | 0 | 6 | 0 | 0 | 0 | 0 | 1.8 | 80 | 0.31 | 0 | 219 | 62 | 180 | 0 | 0 | 800 | 0 | 4774.93 | 10476.76 | 88.88
10:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 6 | 327 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 19 | 22 | 0 | 320 | 0 | 0 | 19 | 0 | 16 | 0 | 0 | 0 | 12 | 12 | 0 | 80 | 0 | 5 | 750 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1160 | 11 | 0 | 0 | 320 | 320 | 0 | 51 | 0 | 170 | 0 | 0 | 50 | 0 | 0 | 17 | 0 | 144 | 0 | 10 | 0 | 320 | 0 | 339 | 41 | 0 | 148 | 2 | 0 | 0 | 41 | 0 | 69 | 0 | 96 | 0 | 56 | 24 | 17 | 0 | 17.21 | 0 | 5879.21 | 865 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.65 | 832 | 0 | 0 | 0 | 833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.05 | 42 | 0 | 0 | 30.61 | 0 | 0 | 194 | 0 | 0 | 0 | 373 | 0 | 2.6 | 0 | 56 | 0 | 19 | 0 | 0 | 0 | 0 | 3.8 | 110 | 0.49 | 0 | 216 | 63 | 180 | 0 | 0 | 800 | 0 | 4887.2 | 10766.41 | 88.87
11:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 6 | 315 | 0 | 0 | 0 | 0 | 21 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 250 | 0 | 0 | 20 | 0 | 20 | 22 | 0 | 310 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 12 | 12 | 0 | 80 | 0 | 0 | 725 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1160 | 19 | 0 | 0 | 300 | 320 | 0 | 51 | 0 | 170 | 0 | 0 | 40 | 0 | 0 | 17 | 0 | 144 | 0 | 11 | 0 | 310 | 0 | 360 | 41 | 0 | 141 | 0 | 0 | 0 | 41 | 0 | 70 | 0 | 96 | 0 | 56 | 66 | 17 | 1 | 3.14 | 1 | 5844.14 | 865 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 806 | 0 | 0 | 0 | 835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.1 | 71 | 0 | 0 | 39.3 | 0 | 0 | 170 | 0 | 0 | 0 | 342 | 0 | 2.79 | 0 | 55 | 0 | 25 | 0 | 0 | 0 | 0 | 2.8 | 91 | 0.57 | 0 | 170 | 62 | 180 | 0 | 0 | 800 | 0 | 4806.56 | 10650.7 | 88.86
12:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 6 | 333 | 0 | 0 | 5 | 5 | 80 | 30 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 325 | 0 | 10 | 250 | 0 | 0 | 24 | 0 | 4 | 19 | 0 | 310 | 0 | 0 | 0 | 0 | 28 | 0 | 1 | 0 | 12 | 12 | 0 | 80 | 0 | 0 | 670 | 0 | 0 | 0 | 1 | 0 | 218 | 0 | 0 | 0 | 1140 | 18 | 1 | 0 | 250 | 320 | 0 | 51 | 0 | 170 | 0 | 1 | 36 | 7 | 0 | 20 | 0 | 156 | 0 | 45 | 0 | 320 | 0 | 215 | 41 | 0 | 152 | 0 | 0 | 0 | 41 | 0 | 70 | 0 | 96 | 0 | 56 | 66 | 12 | 1 | 15.5 | 6 | 5789.5 | 865 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 851 | 0 | 0 | 0 | 1069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.93 | 94 | 0 | 0 | 44.19 | 0 | 0 | 150 | 0 | 0 | 0 | 405 | 0 | 2.47 | 0 | 54 | 0 | 11 | 0 | 0 | 0 | 0 | 3.9 | 102 | 0.62 | 0 | 168 | 60 | 220 | 0 | 0 | 820 | 0 | 5211.11 | 11000.61 | 88.86
13:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 6 | 318 | 0 | 0 | 17 | 0 | 87 | 30 | 45 | 25 | 17 | 35 | 0 | 0 | 0 | 303 | 0 | 17 | 250 | 0 | 0 | 27 | 0 | 16 | 18 | 0 | 310 | 0 | 0 | 0 | 0 | 30 | 0 | 17 | 0 | 12 | 12 | 0 | 80 | 0 | 0 | 670 | 0 | 0 | 24 | 22 | 0 | 218 | 0 | 0 | 0 | 1092 | 16 | 50 | 0 | 230 | 320 | 0 | 51 | 0 | 180 | 0 | 30 | 27 | 51 | 0 | 20 | 0 | 164 | 0 | 25 | 0 | 310 | 0 | 215 | 41 | 0 | 140 | 0 | 0 | 0 | 41 | 0 | 69 | 0 | 96 | 0 | 66 | 60 | 10 | 1 | 23.5 | 6 | 5981.5 | 865 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.23 | 891 | 0 | 0 | 0 | 1118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.9 | 100 | 0 | 0 | 41.19 | 0 | 0 | 200 | 0 | 0 | 0 | 350 | 0 | 4.61 | 0 | 54 | 0 | 9 | 20 | 0 | 0 | 0 | 1.1 | 61 | 0.4 | 0 | 170 | 60 | 220 | 0 | 0 | 1030 | 0 | 5495.43 | 11476.93 | 88.85
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 328 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 280 | 0 | 0 | 13 | 0 | 17 | 18 | 0 | 335 | 0 | 0 | 36 | 0 | 35 | 0 | 8 | 0 | 12 | 12 | 0 | 80 | 0 | 0 | 670 | 0 | 0 | 44 | 8 | 0 | 218 | 0 | 0 | 0 | 990 | 8 | 0 | 0 | 230 | 360 | 0 | 51 | 0 | 212 | 0 | 0 | 28 | 0 | 0 | 12 | 0 | 162 | 0 | 41 | 0 | 315 | 0 | 215 | 41 | 0 | 145 | 0 | 0 | 0 | 41 | 0 | 70 | 0 | 96 | 0 | 66 | 24 | 10 | 1 | 27.55 | 6 | 5661.55 | 865 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.33 | 840 | 0 | 0 | 0 | 977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.89 | 72 | 0 | 0 | 38.55 | 0 | 0 | 200 | 0 | 0 | 0 | 414 | 0 | 3.47 | 0 | 54 | 0 | 11 | 34 | 0 | 0 | 0 | 1.9 | 23 | 0.23 | 0 | 199 | 60 | 220 | 0 | 0 | 920 | 0 | 5197.37 | 10858.92 | 88.85
15:00 | 0 | 9 | 11 | 0 | 0 | 0 | 0 | 6 | 354 | 0 | 0 | 12 | 0 | 72 | 30 | 0 | 0 | 4 | 30 | 0 | 0 | 0 | 345 | 0 | 0 | 280 | 0 | 0 | 16 | 0 | 21 | 0 | 0 | 410 | 0 | 0 | 30 | 0 | 32 | 0 | 8 | 0 | 12 | 12 | 0 | 80 | 0 | 0 | 670 | 0 | 0 | 44 | 8 | 0 | 220 | 0 | 0 | 0 | 1160 | 10 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 201 | 0 | 0 | 30 | 0 | 0 | 6 | 0 | 170 | 0 | 40 | 0 | 320 | 0 | 215 | 41 | 0 | 163 | 0 | 0 | 0 | 41 | 0 | 71 | 0 | 96 | 0 | 69 | 38 | 10 | 1 | 16.11 | 6 | 5471.11 | 864 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.05 | 955 | 0 | 0 | 0 | 970 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.12 | 68 | 0 | 0 | 31.69 | 0 | 0 | 200 | 0 | 0 | 0 | 407 | 0 | 3.17 | 0 | 54 | 0 | 14 | 36 | 0 | 0 | 0 | 1.3 | 15 | 0.18 | 0 | 247 | 60 | 220 | 0 | 0 | 920 | 0 | 5325.51 | 10796.62 | 88.84
16:00 | 0 | 41 | 40 | 0 | 0 | 0 | 0 | 6 | 336 | 0 | 0 | 17.5 | 0 | 107 | 30 | 110 | 0 | 17 | 35 | 8 | 0 | 0 | 395 | 0 | 17 | 280 | 0 | 0 | 8 | 35 | 21 | 18 | 0 | 400 | 0 | 0 | 30 | 0 | 36 | 0 | 8 | 0 | 12 | 12 | 0 | 80 | 0 | 0 | 670 | 0 | 0 | 44 | 8 | 0 | 219 | 0 | 0 | 0 | 1160 | 5 | 63 | 78 | 0 | 0 | 0 | 51 | 10 | 195 | 36 | 20 | 30 | 27 | 0 | 12 | 0 | 172 | 0 | 19 | 0 | 310 | 0 | 215 | 41 | 0 | 158 | 3 | 17 | 0 | 41 | 0 | 71 | 0 | 97 | 0 | 69 | 56 | 10 | 1 | 14.65 | 6 | 6028.15 | 864 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.33 | 945 | 0 | 0 | 0 | 1005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.05 | 42 | 0 | 0 | 11.22 | 0 | 0 | 201 | 0 | 0 | 0 | 403 | 0 | 0.96 | 0 | 54 | 20 | 2 | 34 | 0 | 0 | 0 | 0.7 | 9 | 0.07 | 0 | 246 | 60 | 220 | 0 | 0 | 930 | 0 | 5287.33 | 11315.48 | 88.83
17:00 | 0 | 98 | 51 | 0 | 0 | 0 | 0 | 6 | 336 | 0 | 0 | 17.5 | 10 | 130 | 96 | 110 | 0 | 17 | 35 | 15 | 0 | 0 | 380 | 0 | 17 | 280 | 0 | 0 | 4 | 108 | 16 | 18 | 0 | 310 | 0 | 0 | 51 | 0 | 20 | 0 | 8 | 0 | 12 | 12 | 0.47 | 80 | 0 | 14 | 670 | 0 | 0 | 46 | 15 | 0 | 220 | 0 | 0 | 0 | 1130 | 1 | 100 | 125 | 0 | 0 | 0 | 51 | 21 | 192 | 42 | 45 | 70 | 93 | 0 | 15 | 0 | 156 | 0 | 13 | 9 | 315 | 0 | 288 | 41 | 0 | 157 | 1 | 17 | 0 | 41 | 0 | 69 | 0 | 97 | 0 | 69 | 58 | 16 | 0 | 6.17 | 6 | 6447.14 | 865 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.64 | 1005 | 0 | 0 | 0 | 1105 | 0 | 0 | 0 | 15 | 2 | 0 | 0 | 0 | 0 | 5.49 | 17 | 0 | 0 | 6.59 | 0 | 0 | 200 | 0 | 0 | 0 | 401 | 0 | 0.58 | 0 | 54 | 60 | 1 | 68 | 0 | 0 | 0 | 0.2 | 9 | 0.07 | 0 | 271 | 60 | 220 | 0 | 0 | 1000 | 0 | 5560.57 | 12007.71 | 88.82
18:00 | 0 | 105 | 51 | 0 | 0 | 0 | 0 | 6 | 315 | 0 | 0 | 17.5 | 35 | 130 | 96 | 110 | 0 | 18 | 35 | 15 | 0 | 0 | 305 | 0 | 17 | 240 | 0 | 0 | 0 | 108 | 16 | 18 | 0 | 310 | 0 | 0 | 65 | 0 | 15 | 46 | 38 | 0 | 12 | 12 | 0 | 80 | 0 | 14 | 670 | 0 | 0 | 46 | 25.5 | 0 | 220 | 0 | 0 | 0 | 1084 | 0 | 100 | 140 | 0 | 0 | 0 | 51 | 22 | 199 | 42 | 51 | 80 | 132 | 0 | 19 | 0 | 148 | 0 | 3 | 9 | 320 | 0 | 340 | 41 | 0 | 160 | 0 | 0 | 0 | 41 | 0 | 70 | 0 | 97 | 29 | 97 | 77 | 18 | 0 | 0.1 | 6 | 6567.1 | 864 | 179 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86 | 1070 | 0 | 0 | 0 | 1126 | 0 | 0 | 0 | 35 | 35 | 0 | 43 | 0 | 0 | 0.14 | 0 | 15 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 54 | 70 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 60 | 180 | 0 | 0 | 1040 | 0 | 5674 | 12241.1 | 88.81
19:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 6 | 311 | 0 | 0 | 17.5 | 35 | 118 | 62 | 110 | 0 | 35 | 35 | 16 | 0 | 0 | 300 | 0 | 0 | 300 | 0 | 0 | 0 | 90 | 12 | 22 | 0 | 320 | 0 | 0 | 65 | 0 | 11 | 51 | 38 | 0 | 12 | 12 | 0 | 80 | 0 | 13 | 670 | 0 | 0 | 46 | 25.5 | 0 | 206 | 0 | 0 | 0 | 1120 | 0 | 100 | 153 | 0 | 0 | 0 | 41 | 21 | 187 | 42 | 50 | 80 | 151 | 0 | 12 | 0 | 148 | 0 | 0 | 9 | 295 | 0 | 382 | 41 | 0 | 152 | 0 | 17 | 0 | 41 | 0 | 70 | 0 | 97 | 35 | 98 | 76 | 21 | 0 | 0 | 6 | 6568 | 662 | 180 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1155 | 0 | 0 | 0 | 1261 | 0 | 0 | 0 | 35 | 35 | 0 | 43 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 54 | 70 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 60 | 220 | 0 | 0 | 1030 | 0 | 5785 | 12353 | 88.8
19:30 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 6 | 310 | 0 | 0 | 17.5 | 35 | 78 | 15 | 60 | 0 | 17 | 35 | 16 | 0 | 0 | 280 | 0 | 17 | 250 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 320 | 0 | 0 | 68 | 0 | 21 | 51 | 38 | 0 | 12 | 12 | 0 | 80 | 0 | 10 | 670 | 0 | 0 | 48 | 25.5 | 0 | 206 | 0 | 0 | 0 | 1125 | 0 | 70 | 163 | 0 | 0 | 0 | 51 | 21 | 187 | 42 | 51 | 80 | 171 | 0 | 12 | 0 | 144 | 0 | 0 | 0 | 300 | 0 | 389 | 41 | 0 | 151 | 0 | 17 | 0 | 41 | 0 | 70 | 0 | 97 | 0 | 75 | 45 | 21 | 0 | 0 | 6 | 6175 | 629 | 180 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1166 | 0 | 0 | 0 | 1265 | 0 | 0 | 0 | 0 | 35 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 54 | 50 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 60 | 220 | 0 | 0 | 1055 | 0 | 5695 | 11870
20:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 6 | 312 | 0 | 0 | 17.5 | 0 | 90 | 15 | 0 | 4 | 17 | 17 | 16 | 0 | 0 | 288 | 0 | 17 | 250 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 340 | 0 | 0 | 70 | 0 | 28 | 51 | 38 | 0 | 12 | 12 | 0 | 80 | 0 | 14 | 670 | 0 | 0 | 49 | 25.5 | 0 | 206 | 0 | 0 | 0 | 1115 | 0 | 50 | 140 | 0 | 3 | 0 | 51 | 18 | 202 | 42 | 16 | 80 | 51 | 0 | 12 | 0 | 156 | 0 | 0 | 0 | 305 | 0 | 334 | 41 | 0 | 144 | 0 | 17 | 0 | 41 | 0 | 70 | 0 | 97 | 0 | 65 | 45 | 23 | 0 | 0 | 6 | 5819 | 628 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1140 | 0 | 0 | 0 | 1189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 54 | 35 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 60 | 180 | 0 | 0 | 1030 | 0 | 5383 | 11202 | 88.79
21:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 6 | 315 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 290 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 350 | 0 | 0 | 72 | 0 | 25 | 51 | 38 | 0 | 12 | 12 | 0 | 80 | 0 | 25 | 670 | 0 | 0 | 50 | 25.5 | 0 | 222 | 0 | 0 | 0 | 1075 | 0 | 0 | 148 | 0 | 93 | 0 | 51 | 16 | 209 | 42 | 0 | 80 | 0 | 0 | 4 | 0 | 158 | 0 | 0 | 0 | 310 | 0 | 377 | 41 | 0 | 141 | 0 | 17 | 0 | 41 | 0 | 70 | 0 | 97 | 0 | 65 | 45 | 23 | 0 | 0 | 6 | 5754.5 | 627 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1045 | 0 | 0 | 0 | 1020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 54 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 60 | 220 | 0 | 0 | 960 | 0 | 5085 | 10839.5 | 88.78
22:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 6 | 357 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 330 | 0 | 0 | 0 | 17 | 18 | 0 | 0 | 350 | 0 | 0 | 73 | 0 | 33 | 50 | 38 | 0 | 12 | 12 | 0 | 80 | 0 | 25 | 670 | 0 | 0 | 50 | 25.5 | 0 | 223 | 0 | 0 | 0 | 1193 | 0 | 0 | 163 | 0 | 90 | 0 | 51 | 17 | 203 | 42 | 0 | 80 | 0 | 0 | 13 | 0 | 162 | 0 | 0 | 0 | 310 | 0 | 354 | 41 | 0 | 163 | 0 | 17 | 0 | 41 | 0 | 70 | 0 | 97 | 0 | 65 | 45 | 21 | 0 | 0 | 6 | 6038.5 | 769 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1013 | 0 | 0 | 0 | 1072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 54 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 60 | 220 | 0 | 0 | 1000 | 0 | 5351 | 11389.5 | 88.77
23:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 6 | 358 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 315 | 0 | 0 | 333 | 0 | 0 | 0 | 52 | 21.5 | 22 | 0 | 355 | 0 | 0 | 80 | 0 | 22 | 51 | 38 | 0 | 12 | 12 | 0 | 80 | 0 | 25 | 670 | 0 | 0 | 48 | 25.5 | 0 | 222 | 0 | 0 | 0 | 1224 | 0 | 0 | 163 | 0 | 90 | 0 | 51 | 17 | 207 | 42 | 0 | 0 | 3 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 305 | 0 | 395 | 41 | 0 | 163 | 0 | 17 | 0 | 41 | 0 | 71 | 0 | 98 | 0 | 59 | 48 | 20 | 0 | 0 | 0 | 6103 | 769 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 0 | 0 | 0 | 1186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 54 | 70 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299 | 60 | 220 | 0 | 0 | 1085 | 0 | 5760 | 11863 | 88.76
Total KWH | 0 | 804480 | 608640 | 0 | 0 | 0 | 0 | 167272.73 | 7930800 | 0 | 0 | 190800 | 133200 | 1811664 | 454080 | 564545 | 167677 | 198522 | 483840 | 155520 | 0 | 0 | 7812359 | 0 | 181680 | 6446485 | 0 | 0 | 120694 | 1089600 | 390600 | 433080 | 0 | 8109090.91 | 0 | 0 | 1223040 | 0 | 402720 | 557365 | 357840 | 0 | 283200 | 297600 | 1082 | 1924260 | 0 | 286560 | 18174545.46 | 0 | 0 | 816480 | 359375.4 | 0 | 5116265 | 0 | 0 | 0 | 25936362 | 103680 | 628945 | 1187636 | 3579500 | 5160800 | 0 | 1251760 | 159840 | 4772000 | 338760 | 307200 | 973628 | 911040 | 0 | 295880 | 0 | 3708480 | 0 | 297118 | 84736 | 7548000 | 0 | 7937000 | 978000 | 0 | 3641318.18 | 11812 | 283824 | 0 | 958080 | 0 | 1646000 | 0 | 2314870 | 264960 | 1534800 | 1262400 | 360960 | 5800 | 122690 | 139200 | 146762041.68 | 19809454 | 4468608 | 0 | 23040 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 509040 | 23796370 | 0 | 0 | 0 | 26846546 | 0 | 0 | 0 | 81504 | 126240 | 0 | 81808 | 0 | 0 | 238044 | 583462 | 31754 | 0 | 231008 | 0 | 0 | 4688373 | 0 | 0 | 0 | 9173236 | 0 | 20400 | 0 | 1294690 | 586431 | 106731 | 756355 | 0 | 0 | 0 | 16977.96 | 512640 | 3025 | 0 | 5760000 | 1727000 | 5178690 | 0 | 0 | 23826909.09 | 0 | 130478336.05 | 277240377.73

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 13-03-2026
Power Supply Scenario
| Day Peak Generation |  |  | 11000.61 | MW | 12:00 Hr. | Energy Generated |  |  | 277.2404 |  | MKWHr.
| Day Peak Demand |  |  | 11000.61 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.333 |  | MKWHr.
| Evening Peak Generation |  |  | 12353 | MW | 19:00 Hr. | Energy Demand |  |  | 277.5734 |  | MKWHr.
| Evening Peak Demand |  |  | 12353 | MW | 19:00 Hr. | Maximum Temperature |  |  | 32.9 |  | °C
| Minimum Generation of the Day |  |  | 10139.19 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 775.65 |  | MMCFD
| Maximum Generation of the Day |  |  | 13382.32 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.9564 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 31.2897 | 0 | 6.8442 | 0 | 0 | 0.12069 | 0 | 0 | 38.2546 | Gas | 105.3163 | Gas | 363765302.0058
| Chattogram Zone |  |  | 5.4028 | 44.1109 | 3.8949 | 0 | 1.9243 | 0.10476 | 0 | 0.40272 | 55.8404 | Coal | 98.7889 | Coal | 645208441.386
| Cumilla Zone |  |  | 17.7198 | 0 | 1.9319 | 0 | 0 | 0.29712 | 3.7085 | 0 | 23.6573 | HFO | 17.5596 | HFO | 303113440.61
| Mymensingh Zone |  |  | 0.36096 | 0 | 3.2014 | 0 | 0 | 0.12849 | 0 | 0 | 3.6908 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 25.3071 | 0 | 0 | 0 | 0 | 0.011812 | 0 | 0 | 25.3189 | Hydro | 1.9243 | Hydro | 192426
| Khulna Zone |  |  | 4.4686 | 23.7964 | 0.02304 | 0 | 0 | 0.50904 | 19.8095 | 0 | 48.6065 | Solar | 2.8842 | Solar | 45182859.862
| Barishal Zone |  |  | 6.9057 | 29.5869 | 0 | 0 | 0 | 0.003025 | 0 | 0 | 36.4956 | Import | 50.3645 | Import | 287957105.9
| Rajshahi Zone |  |  | 13.8616 | 0 | 0.32131 | 0 | 0 | 1.0729 | 26.8465 | 0 | 42.1024 | Wind | 0.40272 | Wind | 5924011.2
| Rangpur Zone |  |  | 0 | 1.2947 | 1.3428 | 0 | 0 | 0.63635 | 0 | 0 | 3.2738
| Total |  |  | 105.3163 | 98.7889 | 17.5596 | 0 | 1.9243 | 2.8842 | 50.3645 | 0.40272 | 277.2404
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 363765302.0058 |  | Hydro | 192426
|  |  |  | Coal | 645208441.386 |  | Solar | 45182859.862
|  |  |  | HFO | 303113440.61 |  | Import | 287957105.9
|  |  |  | HSD | 0 |  | Wind | 5924011.2
[5 empty] | Total: | 165,13,43,586 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 3345.45 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.8095 | Peak Hr Flow | 662.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 38265600 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.8465 | Peak Hr Flow | 1261.00 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1519 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.7085 | Peak Hr Flow | 148.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2402 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.3645 | Peak Hr Flow | 2071.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4321
|  |  |  | Chattogram |  | 0 |  | 1242
|  |  |  | Cumilla |  | 0 |  | 1087
|  |  |  | Mymensingh |  | 0 |  | 846
|  |  |  | Sylhet |  | 0 |  | 371
|  |  |  | Khulna |  | 0 |  | 1668
|  |  |  | Barishal |  | 0 |  | 404
|  |  |  | Rajshahi |  | 0 |  | 1258
|  |  |  | Rangpur |  | 0 |  | 733
|  |  |  | Total |  | 0 |  | 11930
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:25 |  | Tongi 230/132/33kV S/S 230 kV Bus-2 Scheduled S/D
| 08:40 |  | Barapukuria-Bogura 230 kV Ckt-1 Scheduled S/D from Bogura 400/230kV end Due to Project
work (LILO) at Barapukuria site
| 08:47 | 10:30 | Khulna (S)-Satkhira 132kV Ckt-2 Scheduled S/D from Khulna(S) 230/132kV end Due to Red Hot
Maintenance
|  | 09:10 | Sreemongol 132/33kV S/S 132/33kv T-1AB LT is restored.
|  | 09:15 | Patuakhali 132/33kV S/S 425T (T-3) HT is restored.
|  | 09:16 | Patuakhali 132/33kV S/S 425T (T-3) LT is restored.
| 09:34 | 16:30 | Chowmuhani 230/132/33kV S/S Korerhat-04 Scheduled S/D Due to For painting and Silicon
work.
| 09:34 | 10:34 | Purbasadipur 230/132/33kV S/S TR-1 (H01R22) LT Project Work S/D Due to 33kv bus coupler | [7 empty] | 35.0MW load
|  |  | maintenance | [7 empty] | interrup.
|  | 09:36 | Baghabari 230/132kV S/S T-1 LT is restored.
|  | 09:36 | Baghabari 230/132kV S/S T-1 HT is restored.
| 09:40 |  | Barapukuria-Bogura 230 kV Ckt-1 Project Work S/D from Barapukuria 230/132/33kV end Due to
Lilo work.
| 09:55 | 10:21 | Khulna(C )-Khulna (S) 132kV Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end Due to
Maintenance work at central s/s end. and from Khulna (C) end Due to Yarn Removal
| 10:30 | 20:26 | Kaliakoir 400/230/132kV S/S 400/132kV TR-3 LT Project Work S/D Due to CSD Commisioning
| 10:31 | 10:41 | Khulna (S)-Satkhira 132kV Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end Due to
Maintenance work at KSS end.
| 10:34 | 20:19 | Kaliakoir 400/230/132kV S/S 400/132kV TR-3 HT Project Work S/D Due to CSD Commmisioning
| 10:52 | 11:14 | Halishahar-Julda 132kV Ckt-1 Tripped from Juldah 132/33kV end showing Z4
Fault. IL3-5.20KA Distance-2.3Km relays Due to Transient Fault.
| 14:23 |  | Ashuganj 450 MW CCPP(North) Tripped with remarks:- unit
| 14:23 |  | Ashuganj-Bhulta 400 kV Ckt-2 Tripped from Bhulta 400/230kV end showing REL 670 relays.
| 14:23 | 18:58 | Ashuganj-Bhulta 400 kV Ckt-1 Tripped from Bhulta 400/230kV end showing REL 670 relays.
| 14:25 | 15:09 | Madartek-Rampura 132kV Ckt-1 Forced S/D from Rampura 230/132kV end Due to Force Shutdown
by NLDC
| 14:25 | 15:09 | Madartek-Rampura 132kV Ckt-2 Forced S/D from Rampura 230/132kV end Due to Force Shutdown
by NLDC
| 14:26 | 15:16 | Moghbazar-Rampura 132kV Ckt-2 Forced S/D from Rampura 230/132kV end Due to Force
Shutdown by NLDC
| 14:26 | 15:00 | Moghbazar-Rampura 132kV Ckt-1 Forced S/D from Rampura 230/132kV end Due to Force
Shutdown by NLDC
| 14:28 | 15:06 | Rampura-Ullon-2 132kV Ckt-1 Forced S/D from Rampura 230/132kV end Due to Force Shutdown
by NLDC
| 15:41 | 16:43 | Srinagar 132/33kV S/S Tr-02 LT Scheduled S/D Due to Red hot maintenance at F-5 by Pbs
| 15:43 | 16:42 | Srinagar 132/33kV S/S Tr-02 HT Scheduled S/D Due to Red hot maintenance at F-5 by Pbs
|  | 15:48 | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-2 is restored.
|  | 15:50 | Aminbazar 400/230/132kV S/S Gopalganj-2 is restored.
|  | 15:58 | Dhamrai 132/33kV S/S Main Bus-1 is restored.
|  | 16:25 | Gopalganj 400/132kV S/S 400kV Rooppur is restored.
|  | 17:36 | Monakasha-Rahanpur 400kV Ckt-1 is restored.
| 19:00 |  | Evening peak generation 12352 MW
| 19:12 | 19:21 | Kabirpur -Tongi 132kV Ckt-1 Tripped from Kabirpur 132/33kV end showing Distance relay
relays Due to Bad weather
| 19:25 | 21:40 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT Tripped showing FBCPU relays Due to Over | [7 empty] | 34.0MW load
|  |  | current | [7 empty] | interrup.
| 19:55 | 20:25 | Narshingdi 132/33kV S/S T-2 LT Tripped showing RET670 relays Due to Thundaring | [7 empty] | 30.0MW load
interrup.
| 19:55 | 20:25 | Narshingdi 132/33kV S/S T-2 HT Tripped showing RET670 relays Due to Thundaring | [7 empty] | 30.0MW load
interrup.
| 19:58 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- gt
| 20:10 | 22:20 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Tripped showing LBB initiation,Lock out relays
Due to N/A
| 20:11 | 21:34 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing MiCom: Ph-R, Zone-2 relays.
| 20:15 | 23:03 | Sonargaon 132/33kV S/S Tr-1 LT Tripped showing DIR O/C relays Due to Auxiliary | [7 empty] | 41.0MW load
|  |  | transformer flashing due to bad weather | [7 empty] | interrup.
| 20:21 | 21:58 | Sonargaon 132/33kV S/S Tr-2 LT Tripped showing O/C relays Due to Auxiliary transformer | [7 empty] | 16.0MW load
|  |  | flashing due to bad weather | [7 empty] | interrup.
| 20:25 |  | Sonargaon 132/33kV S/S Bashundhara Line Tripped showing O/C and Over Voltage Reday relays | [7 empty] | 4.0MW load
|  |  | Due to Due to flashing and overvoltage | [7 empty] | interrup.
| 20:30 | 22:00 | Haripur-Madanganj 132kV Ckt-1 Tripped from Madanganj 132/33kV end showing Main
protection trip relays.
| 20:30 | 00:44 | Madanganj-Munsiganj 132 kV Ckt-1 Tripped from Madanganj 132/33kV end showing U/V voltage | [7 empty] | 32.0MW load
|  |  | operated relays. | [7 empty] | interrup. Madanganj
132/33kV end
| 20:30 |  | Madanganj 132/33kV S/S Madanganj -Bashundhara 132 kv Ckt Tripped showing No relay
operated relays.
| 20:30 | 23:25 | Madanganj 132/33kV S/S GT-1 HT Tripped showing No relay operated relays. | [7 empty] | 10.0MW load
interrup.
| 20:30 |  | Madanganj 132/33kV S/S GT-2 HT Tripped showing Main protection trip, Overall differential | [7 empty] | 30.0MW load
|  |  | biased R and Y phase, CB fail timer 1 and 2, Backup protection, Buchhloz alarm. relays | [7 empty] | interrup.
Due to NoneB phase CT fail
| 20:34 | 20:56 | Kabirpur -Tongi 132kV Ckt-2 Tripped from Tongi 230/132/33kV end showing Y,B-phase,AR
BLOCKED OV/DTT relays.
| 20:45 | 21:24 | Hasnabad 132/33kV S/S 132/33kV 424 T-5 LT Tripped showing Over current and eart fault
relays Due to 33 kv feeder fault
| 20:45 | 21:24 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT Tripped showing Over current and eart fault
relays Due to 33kV feeder trip
| 20:45 | 21:24 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 LT Tripped showing Over current and eart fault
relays Due to 33kV feeder trip
| 22:12 | 23:02 | Bhangura 132/33kV S/S Tr-2(413T) LT Forced S/D Due to 33 Kv Tr-2 CT Red hot removing
| 22:16 | 22:59 | Bhangura 132/33kV S/S Tr-2(413T) HT Forced S/D Due to 33 Kv Tr-2 CT Red hot removing.
| 22:30 |  | Madanganj 132/33kV S/S Madanganj -Summit 55 MW 132 kv Ckt Tripped showing O/C and earth
fault relay relays.
|  | 23:29 | Madanganj 132/33kV S/S Madanganj -Haripur 132 kv Ckt-2 is restored.
| 02:26 | 02:41 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT Tripped showing Master Trip relay relays Due to | [7 empty] | 54.0MW load
|  |  | Pangoan Cb to mid d/s detached from the system. | [7 empty] | interrup.
| 02:26 | 02:41 | Hasnabad 132/33kV S/S 132/33kV 424 T-5 LT Tripped showing Trip relay relays Due to 33kv | [7 empty] | 54.0MW load
|  |  | pangoan CB to mid D/s loop detached from the system. | [7 empty] | interrup.
| 02:40 |  | Shahjibazar 330 MW CCPP was forced shutdown due to auxiliary system problem
| 05:22 |  | Rampal 1320 MW (BIFPCL) Tripped with remarks:- U2
| 05:22 |  | Rampal 1320 MW (BIFPCL) Tripped with remarks:- U2 (Unit 1 Running)
| 05:30 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- unit-2 ( False SMS )
| 05:48 |  | Ashuganj North 360 MW ST was synchronized
| 06:28 |  | Madunaghat-Sikalbaha 132kV Ckt-2 Scheduled S/D from Kalurghat 132/33kV end Due to Khulshi | [7 empty] | 7.0MW load
|  |  | - Madunaghat 230 KV underground cable line installation. | [7 empty] | interrup. Kalurghat
132/33kV end
| 07:00 |  | Minimum Generation: 10304 MW
| 07:00 |  | Minimum Generation: 10304 MW
| 07:13 |  | Fenchuganj -Sylhet 132kV Ckt-1 Scheduled S/D from Beanibazar 132/33kV end Due to Line | [7 empty] | 20.0MW load
|  |  | work | [7 empty] | interrup.
Beanibazar 132/33kV
end
| 07:14 |  | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Scheduled S/D from Beanibazar 132/33kV
end Due to Line work and from Fenchuganj 230/132/33kV end Due to For project work at the
Sylhet South SS end.
| 07:41 |  | Kabirpur 132/33kV S/S XFR, T-2 LT Scheduled S/D Due to 132 kV Main Bus DS Changing Work. | [7 empty] | 100.0MW load
interrup.
| 07:41 |  | Kabirpur 132/33kV S/S XFR, T-I LT Scheduled S/D Due to 132 kV Main Bus DS Changing Work.
| 07:42 |  | Kabirpur 132/33kV S/S XFR, T-I HT Scheduled S/D Due to 132 kV Main Bus DS Changing Work.
| 07:42 |  | Kabirpur 132/33kV S/S XFR, T-2 HT Scheduled S/D Due to 132 kV Main Bus DS Changing Work. | [7 empty] | 100.0MW load
interrup.
| 07:48 | 07:57 | Kabirpur-Kaliakoir 132kV Ckt-2 Tripped from Kabirpur 132/33kV end showing REL 316*4
relays.
| 07:54 |  | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT Scheduled S/D | [7 empty] | 10.0MW load
interrup.
| 07:54 |  | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT Scheduled S/D Due to 33 Kv BUS Cleaning | [7 empty] | 10.0MW load
|  |  | Switchgear maintenance work. | [7 empty] | interrup.
| 07:54 |  | Rajshahi 132/33kV S/S Transformer T-2(415T) HT Scheduled S/D
| 07:54 |  | Rajshahi 132/33kV S/S Transformer T-2(415T) LT Scheduled S/D Due to 33 Kv BUS Cleaning &
Maintenance Work.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 13-03-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 6 | 167272.73 | Demand "05"MW due to gas restiction by Titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 311 | 7930800 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 167677 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 6446485 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17.5 | 190800 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 62 | 454080 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 198522 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 181680 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 12 | 390600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 433080 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 34 | 608640 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 110 | 564545 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 118 | 1811664 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 804480 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 155520 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 483840 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 120694 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 133200 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 320 | 8109090.91 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 300 | 7812359 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 90 | 1089600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1893.5 | 38254629.64
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Under Maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 359375.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 103680 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 816480 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1924260 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 206 | 5116265 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 38 | 357840 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 557365 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 283200 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 13 | 286560 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 65 | 1223040 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 1082 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 297600 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1120 | 25936362 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 11 | 402720 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 670 | 18174545.46 | Plant availability less
Chattogram Area Total |  |  |  |  | 4898.863 | 2349.5 | 55840374.86
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 187 | 4772000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 5160800 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Low gas pressure
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 3579500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 42 | 338760 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 21 | 159840 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 153 | 1187636 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 41 | 1251760 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 100 | 628945 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 9 | 84736 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 973628 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 151 | 911040 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 148 | 3708480 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 12 | 295880 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 50 | 307200 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 297118 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 994 | 23657323
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 21 | 360960 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 5800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 76 | 1262400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 98 | 1534800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 122690 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 139200 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 264960 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 236 | 3690810
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 11812 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 978000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3641318.18 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 70 | 1646000 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 41 | 958080 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 97 | 2314870 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 283824 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7548000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 382 | 7937000 | Due to Air Filter DP High FGMO not available.
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1095 | 25318904.18
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 662 | 19809454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 22 | 23040 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 180 | 4468608 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 509040 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1155 | 23796370 | plant availability zero
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2019 | 48606512
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 60 | 1727000 | GT-02 Offline Waterwash
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1030 | 23826909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5178690 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 248 | 5760000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3025 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1558 | 36495624.09
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 238044 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 197 | 4688373 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 402 | 9173236 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 31754 | Machine problem and fuel shortage
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 43 | 81808 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 126240 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 81504 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 20400 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1261 | 26846546 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 231008 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 583462 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1994 | 42102375
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 54 | 1294690 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 90 | 756355 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 16977.96 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 586431 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 106731 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 512640 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 214 | 3273824.96
Eastern Grid Total |  |  |  |  | 17400.108 | 6568 | 146762041.68
Western Grid Total |  |  |  |  | 11852.195 | 5785 | 130478336.05
National Grid Total |  |  |  |  | 29252.303 | 12353 | 277240377.73
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 13-03-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7866.75 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4063.4 | MW
i) Dhaka area |  |  | 4320.75 |  | MW | i) Khulna area |  |  |  | 1668.5 | MW
ii) Chattogram area |  |  | 1242 |  | MW | ii) Barishal area |  |  |  | 403.7 | MW
iii) Cumilla area |  |  | 1087 |  | MW | iii) Rajshahi area |  |  |  | 1258.2 | MW
iv) Mymensingh area |  |  | 846 |  | MW | iv) Rangpur area |  |  |  | 733 | MW
v) Sylhet area |  |  | 371 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11930.15 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 12 | 23:00 | 67 | Hasnabad | 82 | 00:00 | 133 | Nawabganj | 56 | 21:00
2 | AKSML | 7 | 12:00 | 68 | Hathazari | 70 | 18:30 | 134 | Netrakona | 118 | 00:00
3 | Aftabnagar | 33 | 00:00 | 69 | Hatirjheel | 35 | 17:00 | 135 | New | 60 | 00:00
4 | Agargaon | 97 | 19:00 | 70 | Ishurdi | 70 | 19:00 | 136 | Niamatpur | 86 | 21:00
5 | Agrabad | 54 | 01:00 | 71 | Jaldhaka | 60 | 17:00 | 137 | Noapara | 40 | 22:00
6 | Amnura | 35 | 20:00 | 72 | Jamalpur | 102 | 03:00 | 138 | PHP | 9 | 07:00
7 | Ashuganj | 90 | 16:00 | 73 | Jashore | 123 | 22:00 | 139 | Pabna | 83 | 19:00
8 | BSRM | 198 | 03:00 | 74 | Jhenaidah | 102 | 19:00 | 140 | Palashbari | 82 | 00:00
9 | Bagerhat | 79 | 19:00 | 75 | Joydebpur | 115 | 00:00 | 141 | Panchagarh | 47 | 19:00
10 | Bajitpur | 67 | 04:00 | 76 | Joypurhat | 48 | 00:00 | 142 | Patiya | 9.5 | 19:00
11 | Bakerganj | 12.4 | 21:00 | 77 | Juldah | 17 | 00:00 | 143 | Patuakhali | 58.5 | 22:00
12 | Bakulia | 70 | 23:00 | 78 | KSRM | 18 | 14:00 | 144 | Payra | 32 | 00:00
13 | Banani | 40 | 15:00 | 79 | Kabirpur | 235 | 00:00 | 145 | Postogola | 48 | 00:00
14 | Bangabhaban | 4 | 00:00 | 80 | Kachua | 93 | 22:00 | 146 | Pubail | 22 | 16:00
15 | Barapukuria | 51 | 00:00 | 81 | Kaliganj | 29 | 19:00 | 147 | Purbachal | 26 | 15:00
16 | Barguna | 18 | 19:00 | 82 | Kallyanpur | 111 | 18:00 | 148 | Purbasadipur | 111 | 00:00
17 | Barishal | 91 | 14:00 | 83 | Kalurghat | 46 | 00:00 | 149 | Rahanpur | 34 | 21:00
18 | Barishal-230 | 84 | 18:30 | 84 | Kamrangirchar | 74 | 00:00 | 150 | Rahim | 22 | 06:00
19 | Baroaulia | 61 | 16:00 | 85 | Kaptai | N/A | N/A | 151 | Rajbari | 75 | 20:00
20 | Baroirhat | 51 | 21:00 | 86 | Kasba | 33 | 04:00 | 152 | Rajendrapur | 117 | 00:00
21 | Bashundhara | 171 | 12:00 | 87 | Kazla | 102 | 00:00 | 153 | Rajshahi | 92 | 19:30
22 | BashundharaCement | 7 | 05:00 | 88 | Keranigonj | 78 | 23:00 | 154 | Rajshahi-230 | 80 | 20:00
23 | Beanibazar | 50 | 03:00 | 89 | Khagrachori | 26 | 00:00 | 155 | Ramganj | 104 | 19:30
24 | Benapole | 84 | 18:30 | 90 | Khulna | 50 | 19:00 | 156 | Rampur | 36 | 00:00
25 | Bhaluka | 123 | 18:00 | 91 | Khulshi | 178 | 20:00 | 157 | Rangamati | 15 | 19:00
26 | Bhandaria | 49 | 21:00 | 92 | Kishoreganj | 114 | 00:00 | 158 | Rangpur | 120 | 18:00
27 | Bhangura | 44 | 13:00 | 93 | Kodda | 282 | 00:00 | 159 | Ruppur | 3.8 | 11:00
28 | Bheramara(GK) | 60 | 19:00 | 94 | Kulaura | 39 | 00:00 | 160 | SSM | 14 | 00:00
29 | Bhulta | 232 | 00:00 | 95 | Kurigram | 52 | 17:00 | 161 | Saidpur | 75 | 18:00
30 | Bog-Sherpur | 70 | 00:00 | 96 | Kushtia | 131 | 03:00 | 162 | Satkhira | 131 | 19:30
31 | Bogura | 132 | 04:00 | 97 | Laksam | 18 | 00:00 | 163 | Satmasjid | 93 | 19:30
32 | Borhanuddin | 80 | 19:00 | 98 | Lakshmipur | 34 | 17:00 | 164 | Savar | 184 | 00:00
33 | Brahmanbaria | 116 | 00:00 | 99 | Lalbag | 68 | 00:00 | 165 | SevenRings | 17.04 | 11:00
34 | Cantonment | 118 | 17:00 | 100 | Lalmonirhat | 48 | 17:00 | 166 | ShahCement | 22 | 12:00
35 | Chandina | 24 | 18:00 | 101 | MI_Cement | 19.1 | 00:00 | 167 | Shahjadpur | 68 | 07:00
36 | Chandpur | 72 | 19:00 | 102 | Madanganj | 40 | 00:00 | 168 | Shahjibazar | 115 | 00:00
37 | Chandraghona | 32 | 20:00 | 103 | Madaripur | 99 | 18:30 | 169 | Shahmirpur | 44 | 02:00
38 | Chapai | 72 | 21:00 | 104 | Madartek | 78 | 23:00 | 170 | Shariatpur | 76 | 18:30
39 | Charsaidpur | 48 | 03:00 | 105 | Madunaghat | 49 | 21:00 | 171 | Sherpur | 136 | 04:00
40 | Chauddagram | 67 | 19:00 | 106 | Magura | 64 | 19:30 | 172 | Shikalbaha | 31 | 21:00
41 | Chhatak | 33 | 00:00 | 107 | Mahasthangarh | 76 | 03:00 | 173 | Shitalakhya | 60.7 | 15:00
42 | Chowmuhani | 143 | 22:00 | 108 | Maijdee | 39 | 00:00 | 174 | Sholosohor | 39 | 22:00
43 | Chuadanga | 113 | 21:00 | 109 | Manikganj | 121 | 19:30 | 175 | Shyampur | 168 | 09:00
44 | Coxsbazar | 129 | 22:00 | 110 | Maniknagar | 62 | 00:00 | 176 | Siddhirganj | 109 | 00:00
45 | Cumilla(N) | 115 | 04:00 | 111 | Matarbari | 49 | 03:00 | 177 | Sirajganj | 96 | 04:00
46 | Cumilla(S) | 179 | 00:00 | 112 | Matuail | 64 | 00:00 | 178 | Sonargaon | 144 | 02:00
47 | Daganbhuiyan | 30 | 23:00 | 113 | Metrorail_Motijheel | 15 | 17:00 | 179 | Sreemongol | 64 | 00:00
48 | Daudkandi | 133 | 00:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sreepur | 102 | 04:00
49 | DhakaUniversity | 46 | 12:00 | 115 | Millgate | 71 | 01:00 | 181 | Srinagar | 45.2 | 19:00
50 | Dhamrai | 118 | 00:00 | 116 | Mirpur | 129 | 15:00 | 182 | Sunamganj | 49 | 00:00
51 | Dhanmondi | 90.8 | 15:00 | 117 | Mirsorai | 38 | 01:00 | 183 | Sylhet | 52 | 22:00
52 | Dohazari | 97 | 21:00 | 118 | Mirzapur | 49 | 20:00 | 184 | Sylhet-132 | 97 | 00:00
53 | Faridpur | 149 | 19:00 | 119 | Mithapukur | 67 | 03:00 | 185 | TK | 27 | 12:00
54 | Fatullah | 85 | 00:00 | 120 | Modern | N/A | N/A | 186 | Tangail | 176 | 03:00
55 | Fenchuganj | 31 | 00:00 | 121 | Mogbazar | 58.9 | 12:00 | 187 | Taraganj | 19 | 17:00
56 | Feni | 89 | 17:00 | 122 | Mongla | 37 | 15:00 | 188 | Tasnim | 20 | 23:00
57 | GPH | 1 | 00:00 | 123 | Motijheel | 35 | 13:00 | 189 | Thakurgaon | 82 | 19:00
58 | Ghatail | 84 | 04:00 | 124 | Muktagacha | 34 | 11:00 | 190 | Tongi | 133 | 00:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 104 | 00:00 | 191 | Ullahpara | 40 | 02:00
60 | Ghorashal-230 | 105 | 00:00 | 126 | Muradnagar | 37 | 00:00 | 192 | Ullon | 57 | 19:30
61 | Goalpara | 36 | 19:00 | 127 | Mymensingh | 179 | 00:00 | 193 | Uttara | 71 | 16:00
62 | Gollamari | 96 | 18:30 | 128 | Naogaon | 110 | 21:00 | 194 | UttaraNew | 26 | 12:00
63 | Gopalganj | 96 | 20:00 | 129 | Narail | 57.5 | 19:00 | 195 | Zigatola | 86 | 18:00
64 | Gulshan | 84 | 15:00 | 130 | Narinda | 51 | 13:00
65 | Halishahar | 63 | 18:30 | 131 | Narshingdi | 156 | 00:00
66 | HaripurSBU | 124 | 00:00 | 132 | Natore | 134 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 13-03-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 13382.32 | 28 |  | 13411.58
1:00 | 12743.31 | 0 |  | 12743.31
2:00 | 12266.03 | 0 |  | 12266.03
3:00 | 12463.99 | 0 |  | 12463.99
4:00 | 12625.09 | 0 |  | 12625.09
5:00 | 11525.93 | 0 |  | 11525.93
6:00 | 10470.39 | 0 |  | 10470.39
7:00 | 10191.38 | 0 |  | 10191.38
8:00 | 10139.19 | 0 |  | 10139.19
9:00 | 10476.76 | 0 |  | 10476.76
10:00 | 10766.41 | 0 |  | 10766.41
11:00 | 10650.7 | 0 |  | 10650.7
12:00 | 11000.61 | 0 |  | 11000.61
13:00 | 11476.93 | 0 |  | 11476.93
14:00 | 10858.92 | 0 |  | 10858.92
15:00 | 10796.62 | 196 |  | 11001.62
16:00 | 11315.48 | 65 |  | 11383.48
17:00 | 12007.71 | 44 |  | 12053.71
18:00 | 12241.1 | 0 |  | 12241.1
19:00 | 12353 | 0 |  | 12353
19:30 | 11870 | 0 |  | 11870
20:00 | 11202 | 0 |  | 11202
21:00 | 10839.5 | 0 |  | 10839.5
22:00 | 11389.5 | 0 |  | 11389.5
23:00 | 11863 | 0 |  | 11863
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 13-03-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7197.6 | 6184.72 | 13382.32 | DAILY GENERATION CURVE
00:30 | 6960.8 | 6102.015 | 13062.815
01:00 | 6724 | 6019.31 | 12743.31 | 13-03-2026
01:30 | 6598.7 | 5905.97 | 12504.67
02:00 | 6473.4 | 5792.63 | 12266.03
02:30 | 6545.45 | 5819.56 | 12365.01
03:00 | 6617.5 | 5846.49 | 12463.99
03:30 | 6604.5 | 5940.04 | 12544.54
04:00 | 6591.5 | 6033.59 | 12625.09
04:30 | 6294.75 | 5780.76 | 12075.51
05:00 | 5998 | 5527.93 | 11525.93
05:30 | 5791 | 5207.16 | 10998.16
06:00 | 5584 | 4886.39 | 10470.39
06:30 | 5574.5 | 4756.385 | 10330.885
07:00 | 5565 | 4626.38 | 10191.38
07:30 | 5575.67 | 4589.615 | 10165.285
08:00 | 5586.34 | 4552.85 | 10139.19
08:30 | 5644.085 | 4663.89 | 10307.975
09:00 | 5701.83 | 4774.93 | 10476.76
09:30 | 5790.52 | 4831.065 | 10621.585
10:00 | 5879.21 | 4887.2 | 10766.41
10:30 | 5861.675 | 4846.88 | 10708.555
11:00 | 5844.14 | 4806.56 | 10650.7
11:30 | 5816.82 | 5008.835 | 10825.655
12:00 | 5789.5 | 5211.11 | 11000.61
12:30 | 5885.5 | 5353.27 | 11238.77
13:00 | 5981.5 | 5495.43 | 11476.93
13:30 | 5821.525 | 5346.4 | 11167.925
14:00 | 5661.55 | 5197.37 | 10858.92
14:30 | 5566.33 | 5261.44 | 10827.77
15:00 | 5471.11 | 5325.51 | 10796.62
15:30 | 5749.63 | 5306.42 | 11056.05
16:00 | 6028.15 | 5287.33 | 11315.48
16:30 | 6237.645 | 5423.95 | 11661.595
17:00 | 6447.14 | 5560.57 | 12007.71
17:30 | 6507.12 | 5617.285 | 12124.405
18:00 | 6567.1 | 5674 | 12241.1
18:30 | 6567.55 | 5729.5 | 12297.05
19:00 | 6568 | 5785 | 12353
19:30 | 6175 | 5695 | 11870
20:00 | 5819 | 5383 | 11202
20:30 | 5786.75 | 5234 | 11020.75 |  | Executive Engineer
21:00 | 5754.5 | 5085 | 10839.5 |  | Network Operation Division
21:30 | 5896.5 | 5218 | 11114.5
22:00 | 6038.5 | 5351 | 11389.5
22:30 | 6070.75 | 5555.5 | 11626.25
23:00 | 6103 | 5760 | 11863

## En-Curve
QF-LDC-12
Date | 13-03-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3116 | 1534 | 886 | 0 | 178 | 1449.72 | 80 | 4742 | 0 | 282 | 1104.6 | 0 | 0 | 10 | 28 | DAILY ENERGY CURVE
00:30 | 3079 | 1548 | 845 | 0 | 173 | 1448.355 | 80 | 4692.16 | 0 | 272.5 | 916.3 | 0 | 0 | 8.5 | 14 | 13-03-2026
01:00 | 3042 | 1562 | 804 | 0 | 168 | 1446.99 | 80 | 4642.32 | 0 | 263 | 728 | 0 | 0 | 7 | 0
01:30 | 2979 | 1521.5 | 810.5 | 0 | 163 | 1450.65 | 80 | 4504.32 | 0 | 263 | 723.7 | 0 | 0 | 9 | 0 | Energy Generated | 277.2404 |  | MKWHr
02:00 | 2916 | 1481 | 817 | 0 | 158 | 1454.31 | 80 | 4366.32 | 0 | 263 | 719.4 | 0 | 0 | 11 | 0 | Energy not Served | 0.333 |  | MKWHr
02:30 | 2937 | 1514 | 817.5 | 0 | 160 | 1454.74 | 80 | 4358.32 | 0 | 297 | 737.45 | 0 | 0 | 9 | 0 | Total Energy Requirement | 277.5734 |  | MKWHr
03:00 | 2958 | 1547 | 818 | 0 | 162 | 1455.17 | 80 | 4350.32 | 0 | 331 | 755.5 | 0 | 0 | 7 | 0
03:30 | 2949 | 1535.5 | 841 | 0 | 162 | 1442.72 | 80 | 4485.82 | 0 | 294 | 750 | 0 | 0 | 4.5 | 0
04:00 | 2940 | 1524 | 864 | 0 | 162 | 1430.27 | 80 | 4621.32 | 0 | 257 | 744.5 | 0 | 0 | 2 | 0
04:30 | 2918.5 | 1489.5 | 864.5 | 0 | 155 | 1372.1 | 80 | 4453.16 | 0 | 167.5 | 571.75 | 0 | 0 | 3.5 | 0
05:00 | 2897 | 1455 | 865 | 0 | 148 | 1313.93 | 80 | 4285 | 0 | 78 | 399 | 0 | 0 | 5 | 0
05:30 | 2875 | 1433.5 | 865 | 0 | 148 | 1196.66 | 80 | 4031.5 | 0 | 73 | 290.5 | 0 | 0 | 5 | 0
06:00 | 2853 | 1412 | 865 | 0 | 148 | 1079.39 | 80 | 3778 | 0 | 68 | 182 | 0 | 0 | 5 | 0
06:30 | 2872 | 1414 | 865 | 0 | 145 | 1008.54 | 80 | 3718.5 | 7.845 | 59.5 | 150.5 | 0 | 0 | 10 | 0
07:00 | 2891 | 1416 | 865 | 0 | 142 | 937.69 | 80 | 3659 | 15.69 | 51 | 119 | 0 | 0 | 15 | 0
07:30 | 2918 | 1423 | 818.5 | 0 | 141 | 884.22 | 80 | 3662 | 63.065 | 43 | 119.5 | 0 | 0 | 13 | 0
08:00 | 2945 | 1430 | 772 | 0 | 140 | 830.75 | 80 | 3665 | 110.44 | 35 | 120 | 0 | 0 | 11 | 0
08:30 | 2965 | 1455.5 | 818.5 | 0 | 139 | 831.7 | 80 | 3673.5 | 173.275 | 42.5 | 121.5 | 0 | 0 | 7.5 | 0
09:00 | 2985 | 1481 | 865 | 0 | 138 | 832.65 | 80 | 3682 | 236.11 | 50 | 123 | 0 | 0 | 4 | 0
09:30 | 3010 | 1470 | 865 | 0 | 141 | 832.825 | 80 | 3748 | 281.76 | 60 | 123 | 0 | 0 | 10 | 0
10:00 | 3035 | 1459 | 865 | 0 | 144 | 833 | 80 | 3814 | 327.41 | 70 | 123 | 0 | 0 | 16 | 0
10:30 | 2997 | 1436 | 865 | 0 | 144 | 834 | 80 | 3765 | 357.555 | 66.5 | 145.5 | 0 | 0 | 18 | 0
11:00 | 2959 | 1413 | 865 | 0 | 144 | 835 | 80 | 3716 | 387.7 | 63 | 168 | 0 | 0 | 20 | 0
11:30 | 2887 | 1440.5 | 865 | 0 | 150 | 952 | 80 | 3709.5 | 425.655 | 63.5 | 228.5 | 0 | 0 | 24 | 0
12:00 | 2815 | 1468 | 865 | 0 | 156 | 1069 | 80 | 3703 | 463.61 | 64 | 289 | 0 | 0 | 28 | 0
12:30 | 2794 | 1451.5 | 865 | 0 | 160 | 1093.5 | 80 | 3805 | 442.27 | 76 | 442.5 | 0 | 0 | 29 | 0
13:00 | 2773 | 1435 | 865 | 0 | 164 | 1118 | 80 | 3907 | 420.93 | 88 | 596 | 0 | 0 | 30 | 0
13:30 | 2860.5 | 1452.5 | 865 | 0 | 163 | 1047.5 | 80 | 3790 | 369.925 | 48 | 459 | 0 | 0 | 32.5 | 0
14:00 | 2948 | 1470 | 865 | 0 | 162 | 977 | 80 | 3673 | 318.92 | 8 | 322 | 0 | 0 | 35 | 0
14:30 | 2659 | 1526.5 | 864.5 | 0 | 166 | 973.5 | 80 | 3839.5 | 304.77 | 33 | 347.5 | 0 | 0 | 33.5 | 98
15:00 | 2370 | 1583 | 864 | 0 | 170 | 970 | 80 | 4006 | 290.62 | 58 | 373 | 0 | 0 | 32 | 196
15:30 | 2372.5 | 1660 | 864 | 0 | 171 | 987.5 | 80 | 4005.5 | 232.8 | 106 | 542.75 | 0 | 0 | 34 | 130.5
16:00 | 2375 | 1737 | 864 | 0 | 172 | 1005 | 80 | 4005 | 174.98 | 154 | 712.5 | 0 | 0 | 36 | 65
16:30 | 2433.5 | 1721.5 | 864.5 | 0 | 164 | 1055 | 80 | 4067.5 | 127.595 | 262 | 858 | 0 | 0 | 28 | 54.5
17:00 | 2492 | 1706 | 865 | 0 | 156 | 1105 | 80 | 4130 | 80.21 | 370 | 1003.5 | 0 | 0 | 20 | 44
17:30 | 2470 | 1654 | 864.5 | 0 | 152 | 1115.5 | 80 | 4163 | 42.155 | 443 | 1122.75 | 0 | 0 | 17.5 | 22
18:00 | 2448 | 1602 | 864 | 0 | 148 | 1126 | 80 | 4196 | 4.1 | 516 | 1242 | 0 | 0 | 15 | 0
18:30 | 2512 | 1613.5 | 763 | 0 | 148 | 1193.5 | 80 | 4236.5 | 2.05 | 478 | 1257.5 | 0 | 0 | 13 | 0
19:00 | 2576 | 1625 | 662 | 0 | 148 | 1261 | 80 | 4277 | 0 | 440 | 1273 | 0 | 0 | 11 | 0
19:30 | 2468 | 1614 | 629 | 0 | 144 | 1265 | 80 | 4349 | 0 | 260 | 1040 | 0 | 0 | 21 | 0
20:00 | 2462 | 1556 | 628 | 0 | 156 | 1189 | 80 | 4254 | 0 | 154 | 695 | 0 | 0 | 28 | 0
20:30 | 2591.5 | 1592.5 | 627.5 | 0 | 157 | 1104.5 | 80 | 4143 | 0 | 146.5 | 551.75 | 0 | 0 | 26.5 | 0
21:00 | 2721 | 1629 | 627 | 0 | 158 | 1020 | 80 | 4032 | 0 | 139 | 408.5 | 0 | 0 | 25 | 0
21:30 | 2753.5 | 1681.5 | 698 | 0 | 160 | 1046 | 80 | 4119 | 0 | 138.5 | 409 | 0 | 0 | 29 | 0
22:00 | 2786 | 1734 | 769 | 0 | 162 | 1072 | 80 | 4206 | 0 | 138 | 409.5 | 0 | 0 | 33 | 0
22:30 | 2772.5 | 1727.75 | 769 | 0 | 157 | 1129 | 80 | 4344 | 0 | 164.5 | 455 | 0 | 0 | 27.5 | 0
23:00 | 2759 | 1721.5 | 769 | 0 | 152 | 1186 | 80 | 4482 | 0 | 191 | 500.5 | 0 | 0 | 22 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 13-03-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 396 | 20:00 | 376 | 14:00 | Madunaghat | 403 | 21:00 | 393 | 01:00
Amtali | 415 | 08:00 | 408 | 00:00 | Meghnaghat | 399 | 20:00 | 382 | 15:00
Ashuganj | 410 | 21:00 | 391 | 12:00 | Payra | 416 | 06:00 | 410 | 00:00
Bhulta | 399 | 20:00 | 377 | 15:00 | Rahanpur | 407 | 18:30 | 382 | 13:00
Bibiana | 408 | 18:00 | 399 | 00:00 | Rampal | 406 | 08:00 | 395 | 00:00
BIPTC | 403 | 20:00 | 391 | 12:00
Bogura | 396 | 18:30 | 372 | 13:00
Gopalganj | 404 | 08:00 | 393 | 00:00
Kaliakoir | 393 | 20:00 | 374 | 00:00
Korerhat | 406 | 21:00 | 393 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 233 | 20:00 | 222 | 15:00 | Jhenaidah | 233 | 06:00 | 218 | 00:00
AKSML | 232 | 18:30 | 226 | 00:00 | Kachua | 232 | 18:00 | 224 | 04:00
Aminbazar | 234 | 20:00 | 221 | 14:00 | Kaliakoir | 238 | 20:00 | 225 | 14:00
Ashuganj | 236 | 21:00 | 223 | 00:00 | Keranigonj | 235 | 21:00 | 221 | 15:00
Ashuganj-400 | 236 | 21:00 | 223 | 00:00 | Khulna(S) | 235 | 06:00 | 222 | 18:30
Baghabari | 234 | 06:00 | 225 | 00:00 | Korerhat | 231 | 21:00 | 224 | 00:00
Barapukuria | 224 | 06:00 | 206 | 13:00 | Madunaghat | 233 | 18:00 | 227 | 00:00
Barapukuria-230 | 224 | 06:00 | 206 | 13:00 | Madunaghat-400 | 234 | 21:00 | 229 | 00:00
Barishal | 230 | 06:00 | 225 | 00:00 | Maniknagar | 236 | 21:00 | 222 | 00:00
Bheramara | 235 | 07:00 | 225 | 00:00 | Meghnaghat | 244 | 21:00 | 229 | 02:00
Bhulta | 237 | 21:00 | 223 | 15:00 | Meghnaghat-400 | 238 | 20:00 | 225 | 15:00
Bibiana | 236 | 18:00 | 230 | 00:00 | Mirsorai | 239 | 21:00 | 231 | 00:00
BIPTC | 237 | 06:00 | 224 | 00:00 | Purbasadipur | 224 | 07:00 | 206 | 06:00
Bogura | 235 | 06:00 | 224 | 13:00 | Rajshahi | 234 | 07:00 | 222 | 00:00
Bogura-400 | 235 | 06:00 | 221 | 13:00 | Rampal | 233 | 06:00 | 223 | 00:00
Borhanuddin | 234 | 06:00 | 231 | 00:00 | Rampur | N/A | N/A | N/A | N/A
BSRM | 231 | 21:00 | 224 | 00:00 | Rampura | 235 | 21:00 | 221 | 12:00
Chowmuhani | 233 | 04:00 | 222 | 02:00 | Shikalbaha | 232 | 18:00 | 227 | 00:00
Cumilla(N) | 235 | 21:00 | 223 | 00:00 | Shyampur | 236 | 21:00 | 222 | 15:00
Faridpur | 226 | 06:00 | 220 | 00:00 | Siddhirganj | 239 | 21:00 | 224 | 00:00
Fenchuganj | 240 | 13:00 | 231 | 02:00 | Sirajgonj | 237 | 19:00 | 230 | 00:00
Feni | 233 | 21:00 | 224 | 00:00 | Sreepur | 229 | 21:00 | 216 | 00:00
Ghorashal | 235 | 21:00 | 225 | 00:00 | Tongi | 235 | 19:30 | 222 | 00:00
Ghorashal-230 | 234 | 21:00 | 219 | 15:00
Gopalganj | 226 | 06:00 | 220 | 00:00
GPH | 233 | 21:00 | 226 | 00:00
Haripur | 233 | 20:00 | 223 | 00:00
Hasnabad | 236 | 21:00 | 224 | 00:00
Hathazari | 231 | 19:00 | 226 | 00:00
Ishurdi | 237 | 07:00 | 226 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 20:00 | 128 | 14:00 | Madunaghat | 135 | 18:00 | 130 | 01:00
Agargaon | 137 | 20:00 | 131 | 15:00 | Magura | 134 | 06:00 | 125 | 00:00
Agrabad | 132 | 17:00 | 129 | 00:00 | Mahasthangarh | 140 | 06:00 | 131 | 03:00
AKS | 131 | 18:00 | 128 | 00:00 | Maijdee | 129 | 18:00 | 123 | 01:00
Aminbazar | 136 | 20:00 | 128 | 14:00 | Manikganj | 134 | 19:30 | 125 | 14:00
Amnura | 136 | 19:30 | 125 | 13:00 | Maniknagar | 142 | 21:00 | 130 | 00:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 119 | 15:00 | 111 | 00:00
Ashuganj-230 | 145 | 21:00 | 133 | 00:00 | Matuail | 143 | 21:00 | 130 | 01:00
Bagerhat | 133 | 06:00 | 121 | 18:30 | Metrorail_Motijheel | 142 | 21:00 | 130 | 00:00
Bajitpur | 135 | 12:00 | 128 | 00:00 | Metrorail_Uttara | 133 | 18:30 | 127 | 14:00
Bakerganj | 134 | 06:00 | 130 | 19:00 | Millgate | 140 | 21:00 | 131 | 15:00
Bakulia | 132 | 06:00 | 129 | 11:00 | Mirpur | 133 | 21:00 | 125 | 15:00
Banani | 139 | 19:30 | 130 | 12:00 | Mirzapur | 136 | 19:00 | 127 | 08:00
Bangabhaban | 141 | 21:00 | 130 | 00:00 | Mithapukur | 138 | 06:00 | 128 | 12:00
Barapukuria | 139 | 06:00 | 126 | 13:00 | MI_Cement | 139 | 21:00 | 129 | 15:00
Barguna | 134 | 06:00 | 130 | 13:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 134 | 07:00 | 129 | 23:00 | Mogbazar | 138 | 20:00 | 128 | 23:00
Barishal-230 | 134 | 06:00 | 130 | 00:00 | Mongla | 133 | 08:00 | 122 | 18:30
Baroaulia | 133 | 19:00 | 130 | 00:00 | Motijheel | 141 | 21:00 | 130 | 00:00
Baroirhat | 132 | 18:00 | 127 | 00:00 | Muktagacha | 136 | 19:00 | 122 | 00:00
Bashundhara | 139 | 20:00 | 128 | 00:00 | Munshiganj | 137 | 20:00 | 130 | 02:00
BashundharaCement | 137 | 20:00 | 131 | 03:00 | Muradnagar | 137 | 21:00 | 125 | 01:00
Beanibazar | 136 | 12:00 | 128 | 00:00 | Mymensingh | 135 | 18:30 | 118 | 20:00
Benapole | 132 | 06:00 | 117 | 18:30 | Naogaon | 140 | 06:00 | 127 | 16:00
Bhaluka | 138 | 20:00 | 129 | 15:00 | Narail | 134 | 06:00 | 124 | 13:00
Bhandaria | 131 | 10:00 | 125 | 00:00 | Narinda | 142 | 21:00 | 130 | 00:00
Bhangura | 133 | 19:00 | 127 | 00:00 | Narshingdi | 139 | 21:00 | 123 | 00:00
Bheramara | 136 | 07:00 | 131 | 00:00 | Natore | 136 | 06:00 | 129 | 00:00
Bheramara(GK) | 136 | 07:00 | 131 | 00:00 | Nawabganj | 136 | 21:00 | 129 | 15:00
Bhulta | 134 | 21:00 | 122 | 00:00 | Netrakona | 130 | 12:00 | 119 | 00:00
Bog-Sherpur | 140 | 06:00 | 132 | 00:00 | New | 141 | 19:30 | 132 | 00:00
Bogura | 142 | 06:00 | 134 | 00:00 | Niamatpur | 137 | 22:00 | 126 | 12:00
Bogura-230 | 142 | 06:00 | 134 | 00:00 | Noapara | 135 | 07:00 | 124 | 19:00
Brahmanbaria | 142 | 21:00 | 126 | 00:00 | Pabna | 134 | 06:00 | 129 | 00:00
Cantonment | 138 | 21:00 | 130 | 14:00 | Palashbari | 137 | 06:00 | 127 | 12:00
Chandina | 136 | 21:00 | 129 | 00:00 | Panchagarh | 137 | 18:30 | 123 | 11:00
Chandpur | 136 | 19:00 | 124 | 04:00 | Patiya | 130 | 07:00 | 127 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 135 | 19:30 | 131 | 00:00 | Patuakhali | 133 | 10:00 | 129 | 23:00
Chapai | 134 | 18:00 | 126 | 16:00 | Payra | 136 | 07:00 | 133 | 22:00
Charsaidpur | 138 | 20:00 | 130 | 10:00 | PHP | 132 | 20:00 | 127 | 00:00
Chauddagram | 132 | 20:00 | 126 | 00:00 | Postogola | 141 | 21:00 | 131 | 15:00
Chhatak | 133 | 11:00 | 121 | 00:00 | Pubail | 141 | 19:30 | 130 | 11:00
Chowmuhani | 128 | 18:30 | 125 | 00:00 | Purbachal | 139 | 20:00 | 130 | 12:00
Chuadanga | 131 | 06:00 | 120 | 00:00 | Purbasadipur | 133 | 08:00 | 121 | 13:00
Coxsbazar | 121 | 15:00 | 112 | 00:00 | Rahanpur | 138 | 18:30 | 128 | 12:00
Cumilla(N) | 136 | 21:00 | 129 | 00:00 | Rahanpur-400 | 136 | 06:00 | 128 | 12:00
Cumilla(S) | 135 | 21:00 | 124 | 16:00 | Rahim | 140 | 21:00 | 131 | 00:00
Daganbhuiyan | 131 | 20:00 | 125 | 00:00 | Rajbari | 130 | 06:00 | 125 | 00:00
Daudkandi | 137 | 21:00 | 124 | 00:00 | Rajendrapur | 141 | 20:00 | 128 | 00:00
DhakaUniversity | 140 | 20:00 | 128 | 23:00 | Rajshahi | 134 | 06:00 | 127 | 00:00
Dhamrai | 142 | 19:30 | 134 | 00:00 | Rajshahi-230 | 135 | 06:00 | 128 | 00:00
Dhanmondi | 140 | 22:00 | 132 | 03:00 | Ramganj | 130 | 18:00 | 122 | 14:00
Dohazari | 128 | 13:00 | 124 | 00:00 | Rampur | 133 | 19:30 | 129 | 00:00
Faridpur | 132 | 08:00 | 127 | 23:00 | Rampura | 137 | 20:00 | 128 | 23:00
Fatullah | 140 | 21:00 | 128 | 01:00 | Rangamati | 134 | 18:00 | 130 | 00:00
Fenchuganj | 137 | 13:00 | 131 | 00:00 | Rangpur | 137 | 06:00 | 126 | 12:00
Feni | 130 | 20:00 | 125 | 00:00 | Ruppur | 136 | 05:00 | 132 | 00:00
Feni-230 | 131 | 21:00 | 125 | 00:00 | Saidpur | 135 | 06:00 | 125 | 11:00
Ghatail | 133 | 19:00 | 118 | 08:00 | Satkhira | 134 | 06:00 | 123 | 19:30
Ghorashal | 142 | 21:00 | 132 | 00:00 | Satmasjid | 139 | 20:00 | 130 | 15:00
Goalpara | 139 | 06:00 | 128 | 23:00 | Savar | 134 | 20:00 | 126 | 11:00
Gollamari | 137 | 06:00 | 129 | 18:30 | SevenRings | 141 | 20:00 | 132 | 15:00
Gopalganj | 134 | 06:00 | 129 | 00:00 | ShahCement | 137 | 20:00 | 130 | 10:00
Gopalganj-400 | 134 | 06:00 | 130 | 00:00 | Shahjadpur | 136 | 18:30 | 132 | 00:00
Gulshan | 137 | 20:00 | 127 | 23:00 | Shahjibazar | 142 | 14:00 | 124 | 00:00
Halishahar | 133 | 17:00 | 130 | 00:00 | Shahmirpur | 133 | 13:00 | 130 | 00:00
Haripur | 139 | 22:00 | 131 | 00:00 | Shariatpur | 132 | 07:00 | 128 | 00:00
HaripurSBU | 138 | 20:00 | 131 | 01:00 | Sherpur | 137 | 18:30 | 118 | 00:00
Hasnabad | 138 | 20:00 | 132 | 00:00 | Shikalbaha | 123 | 19:30 | 118 | 00:00
Hathazari | 135 | 18:00 | 132 | 00:00 | Shikalbaha-230 | 135 | 19:30 | 130 | 00:00
Hatirjheel | 137 | 06:00 | 127 | 23:00 | Shitalakhya | 139 | 21:00 | 129 | 15:00
Ishurdi | 138 | 07:00 | 132 | 00:00 | Sholosohor | 134 | 18:00 | 131 | 00:00
Jaldhaka | 133 | 07:00 | 122 | 12:00 | Shyampur | 136 | 21:00 | 127 | 00:00
Jamalpur | 138 | 18:30 | 122 | 00:00 | Shyampur-230 | 137 | 21:00 | 128 | 15:00
Jashore | 132 | 07:00 | 121 | 18:30 | Siddhirganj | 143 | 21:00 | 131 | 15:00
Jhenaidah | 134 | 06:00 | 121 | 00:00 | Sirajganj | 136 | 07:00 | 128 | 04:00
Jhenaidah-230 | 135 | 06:00 | 125 | 00:00 | Sonargaon | 141 | 21:00 | 129 | 00:00
Joydebpur | 140 | 19:30 | 126 | 15:00 | Sreemongol | 135 | 13:00 | 124 | 00:00
Joypurhat | 137 | 07:00 | 128 | 00:00 | Sreepur | 140 | 19:30 | 132 | 00:00
Juldah | 134 | 18:00 | 130 | 00:00 | Srinagar | 138 | 20:00 | 129 | 15:00
Kabirpur | 141 | 18:30 | 128 | 00:00 | SSM | 140 | 00:00 | 132 | 01:00
Kachua | 133 | 19:00 | 127 | 01:00 | Sunamganj | 132 | 09:00 | 120 | 00:00
Kaliakoir | 144 | 20:00 | 133 | 14:00 | Sylhet | 132 | 09:00 | 123 | 00:00
Kaliganj | 133 | 05:00 | 124 | 18:30 | Sylhet-132 | 132 | 10:00 | 125 | 00:00
Kallyanpur | 135 | 21:00 | 128 | 15:00 | Tangail | 132 | 18:30 | 123 | 07:00
Kalurghat | 134 | 18:00 | 131 | 00:00 | Taraganj | 134 | 05:00 | 126 | 12:00
Kamrangirchar | 137 | 21:00 | 127 | 15:00 | Tasnim | 142 | 21:00 | 129 | 00:00
Kaptai | 136 | 7:00 | 134 | 1:00 | Thakurgaon | 136 | 18:30 | 123 | 11:00
Kasba | 137 | 21:00 | 125 | 00:00 | TK | 135 | 18:00 | 130 | 00:00
Kazla | 141 | 21:00 | 130 | 00:00 | Tongi | 142 | 19:30 | 132 | 00:00
Keranigonj | 138 | 21:00 | 129 | 15:00 | Ullahpara | 134 | 19:00 | 129 | 00:00
Khagrachori | 134 | 18:00 | 130 | 00:00 | Ullon | 136 | 01:00 | 127 | 00:00
Khulna | 137 | 06:00 | 120 | 19:00 | Uttara | 135 | 21:00 | 126 | 14:00
Khulna(S) | 138 | 06:00 | 129 | 18:30 | UttaraNew | 135 | 20:00 | 127 | 14:00
Khulshi | 132 | 18:30 | 128 | 00:00 | Zigatola | 139 | 21:00 | 129 | 15:00
Kishoreganj | 133 | 20:00 | 126 | 00:00
Kodda | 140 | 19:30 | 123 | 14:00
Korerhat | 134 | 21:00 | 128 | 08:00
KSRM | 135 | 15:00 | 130 | 12:00
Kulaura | 137 | 13:00 | 130 | 00:00
Kurigram | 136 | 06:00 | 123 | 12:00
Kushtia | 131 | 06:00 | 125 | 00:00
Laksam | 133 | 19:30 | 126 | 03:00
Lakshmipur | 129 | 18:30 | 123 | 01:00
Lalbag | 138 | 21:00 | 129 | 15:00
Lalmonirhat | 132 | 18:30 | 122 | 12:00
Madanganj | 137 | 20:00 | 131 | 10:00
Madaripur | 134 | 06:00 | 130 | 00:00
Madartek | 137 | 18:00 | 127 | 23:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division