## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 16-03-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-03-2026 | during | 16-03-2026 | during | 16-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 6 | 6 | 97.7 | 97.7 | 7 | 7 | Demand "05"MW due to gas restiction by Titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 327 | 295 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 40 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 280 | 335 | 335 | 335 | 335
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 45 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 62 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 22 | 22 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 34 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 60 | 300 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 70 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 54 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 15 | 0 | 26 | 0 | 26 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 6 | 17 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 345 | 340 | 584 | 584 | 320 | 320 | FGMO
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 310 | 300 | 583 | 583 | 320 | 320 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 90 | 160 | 160 | 160 | 160 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1522 | 2236 | 5941.22 | 5915.22 | 2921.02 | 2895.02
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 1 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 10 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 34 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 80 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 220 | 225 | 220 | 220 | 220 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 2 | 56 | 64 | 56 | 64 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 51 | 51 | 51 | 51 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 0 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 17 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 37 | 51 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.86 | 0 | 3.22 | 0 | 3.22 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 50 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1178 | 1151 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 31 | 0 | 34 | 0 | 34 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 580 | 580 | 580 | 580 | 580 | 580 | Coal shortage
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2184.86 | 2257 | 3503.08 | 3470.86 | 3503.08 | 3470.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 209 | 207 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 150 | 240 | 240 | 150 | 150 | Vibration
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 47 | 117 | 318.81 | 318.81 | 340 | 340 | FGMO ON
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 41 | 42 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 8 | 0 | 55 | 55 | 20 | 20 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 172 | 43 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 50 | 136 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 16 | 32 | 32 | 32 | 32 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 96 | 98 | 163 | 163 | 100 | 100 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 168 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 166 | 168 | 84 | 80 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 34 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 105 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 39 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2876.261 | 890 | 1371 | 2623.16 | 2559.16 | 2093.2 | 2033.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-03-2026 | during | 16-03-2026 | during | 16-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 10 | 8 | 157.5 | 157.5 | 10 | 10 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.8 | 0 | 1.8 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 78 | 60 | 80 | 60 | 80 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 69 | 98 | 70 | 115 | 70 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 46.75 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 22 | 22 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 184.75 | 231 | 407.8 | 429 | 260.3 | 281.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 41 | 41 | 41 | 41 | 41 | Gas shortage
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 162 | 152 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | BT Fan Under Maintanance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 0 | 0 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 82 | 85 | 85 | 42 | 42 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 98 | 98 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 21 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 305 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 388 | 389 | 385 | 385 | 385 | 385 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1116 | 1118 | 1190 | 1190 | 1094 | 1094
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 884 | 887 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 30 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 45 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 198 | 178 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 3 | 17 | 105 | 105 | 105 | 105 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 40.06 | 0 | 72 | 0 | 72 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1234.2 | 1216 | 1234.2 | 1234.2 | 1148.28 | 1148.28
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2359.26 | 2373 | 3584.2 | 3512.2 | 2722.28 | 2650.28
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 32 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 60 | 61 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1050 | 1215 | 1244 | 1244 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 76 | 150 | 150 | 150 | 150 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 278 | 307 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.61 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1608.61 | 1911 | 2162 | 2161 | 2003.32 | 2002.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 22.7 | 0 | 44 | 0 | 44 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 48 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 4 | 32 | 32 | 32 | 32 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 135 | 179 | 220 | 220 | 190 | 190 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 397 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 16 | 21 | 21 | 21 | 21 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 52 | 50 | 50 | 50 | 50 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.84 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1339.87 | 1457.14 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 13.21 | 0 | 59 | 0 | 59 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 56 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1982.62 | 2356.14 | 3172.57 | 2963.87 | 2708.57 | 2499.87
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 56 | 55 | 55 | 55 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 105 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.2 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 8 | 0 | 22 | 0 | 22 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 122 | 0 | 155.04 | 0 | 155.04 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 188.2 | 275 | 485.24 | 303 | 410.24 | 228
System Total |  |  |  |  | 28823.2 | 29275.503 | 12036.3 | 14128.14 | 23069.27 | 22504.31 | 17716.01 | 17155.05
Forecast Scenario (16-03-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12960 |  | 0 |  | 12960
|  |  |  | 1:00 | 12530 |  | 0 |  | 12530
|  |  |  | 2:00 | 12330 |  | 0 |  | 12330
|  |  |  | 3:00 | 12280 |  | 0 |  | 12280
|  |  |  | 4:00 | 12650 |  | 0 |  | 12650
|  |  |  | 5:00 | 11380 |  | 0 |  | 11380
|  |  |  | 6:00 | 10620 |  | 0 |  | 10620
|  |  |  | 7:00 | 10720 |  | 0 |  | 10720
|  |  |  | 8:00 | 11140 |  | 0 |  | 11140
|  |  |  | 9:00 | 11550 |  | 0 |  | 11550
|  |  |  | 10:00 | 11950 |  | 0 |  | 11950
|  |  |  | 11:00 | 12150 |  | 0 |  | 12150
|  |  |  | 12:00 | 12350 |  | 0 |  | 12350
|  |  |  | 13:00 | 12800 |  | 0 |  | 12800
|  |  |  | 14:00 | 12940 |  | 0 |  | 12940
|  |  |  | 15:00 | 13030 |  | 0 |  | 13030
|  |  |  | 16:00 | 13150 |  | 0 |  | 13150
|  |  |  | 17:00 | 13370 |  | 0 |  | 13370
|  |  |  | 18:00 | 13620 |  | 0 |  | 13620
|  |  |  | 18:30 | 13800 |  | 0 |  | 13800
|  |  |  | 19:00 | 14020 |  | 0 |  | 14020
|  |  |  | 19:30 | 14150 |  | 0 |  | 14150
|  |  |  | 20:00 | 14090 |  | 0 |  | 14090
|  |  |  | 21:00 | 13630 |  | 0 |  | 13630
|  |  |  | 22:00 | 13300 |  | 0 |  | 13300
|  |  |  | 23:00 | 13100 |  | 0 |  | 13100
Probable Maximum Temperature: |  |  | 30.00°C
Probable Maximum Demand at Day Peak: |  |  | 12350.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14150.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14150.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 301.31072 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:03 hrs on 16-03-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 15-03-2026 | [28 empty] | Date: | 15-03-2026 | [28 empty] | Date: | 15-03-2026 | [28 empty] | Date: | 15-03-2026 | [28 empty] | Date: | 15-03-2026 | [17 empty] | Date: | 15-03-2026
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [17 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 342.010 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 50 | 24 | 0 | 0 | 0 | 0 | 6 | 306 | 0 | 0 | 28 | 17 | 114 | 30 | 195 | 55 | 0 | 130 | 0 | 0 | 0 | 315 | 0 | 35 | 273 | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 320 | 0 | 0 | 85 | 0 | 7 | 51 | 32 | 0 | 12 | 0 | 0 | 80 | 0 | 2 | 520 | 0 | 0 | 50 | 25.5 | 0 | 224 | 0 | 0 | 0 | 1145 | 0 | 120 | 0 | 0 | 245 | 88 | 51 | 0 | 199 | 0 | 72 | 99 | 174 | 0 | 20 | 0 | 178 | 0 | 0 | 16 | 305 | 0 | 350 | 41 | 0 | 149 | 0 | 0 | 0 | 79 | 30 | 0 | 0 | 96 | 17 | 35 | 35 | 12 | 0 | 0 | 12 | 6598.5 | 734 | 196 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1165 | 0 | 0 | 0 | 1446.48 | 0 | 0 | 0 | 35 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 54 | 70 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 274 | 60 | 220 | 0 | 0 | 1085.32 | 52 | 6226.8 | 12825.3 | 88.51
01:00 | 0 | 50 | 24 | 0 | 0 | 0 | 0 | 6 | 291 | 0 | 0 | 31 | 17 | 108 | 30 | 145 | 40 | 17 | 138 | 0 | 0 | 0 | 305 | 0 | 17 | 270 | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 320 | 0 | 0 | 84 | 0 | 6 | 51 | 32 | 0 | 12 | 0 | 0 | 80 | 0 | 4 | 520 | 0 | 0 | 50 | 25.5 | 0 | 227 | 0 | 0 | 0 | 1145 | 0 | 100 | 0 | 0 | 248 | 92 | 51 | 0 | 210 | 0 | 50 | 100 | 146 | 0 | 20 | 0 | 172 | 0 | 0 | 16 | 300 | 0 | 357 | 41 | 0 | 152 | 0 | 0 | 0 | 79 | 30 | 0 | 0 | 96 | 17 | 35 | 35 | 12 | 0 | 0 | 12 | 6460.5 | 646 | 197 | 0 | 8 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1180 | 0 | 0 | 0 | 1448.75 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 54 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 272 | 60 | 220 | 0 | 0 | 1085.32 | 45 | 6028.07 | 12488.57 | 88.5
02:00 | 0 | 50 | 24 | 0 | 0 | 0 | 0 | 6 | 296 | 0 | 0 | 30.8 | 17 | 97 | 30 | 145 | 40 | 17 | 122 | 0 | 0 | 0 | 305 | 0 | 17 | 268 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 320 | 0 | 0 | 85 | 0 | 11 | 51 | 32 | 0 | 12 | 0 | 0 | 80 | 0 | 14 | 520 | 0 | 0 | 50 | 25.5 | 0 | 227 | 0 | 0 | 0 | 1140 | 0 | 70 | 0 | 0 | 249 | 99 | 51 | 0 | 216 | 0 | 37 | 99 | 139 | 0 | 20 | 0 | 164 | 0 | 0 | 16 | 300 | 0 | 350 | 41 | 0 | 154 | 0 | 8 | 0 | 79 | 30 | 0 | 0 | 96 | 17 | 35 | 35 | 12 | 0 | 0 | 12 | 6403.3 | 883 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1075 | 0 | 0 | 0 | 1308.73 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 12 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 54 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 227 | 60 | 220 | 0 | 0 | 1085.32 | 45 | 5884.05 | 12287.35 | 88.49
03:00 | 0 | 50 | 24 | 0 | 0 | 0 | 0 | 6 | 291 | 0 | 0 | 0 | 17 | 97 | 30 | 145 | 40 | 17 | 113 | 0 | 0 | 0 | 305 | 0 | 17 | 279 | 0 | 0 | 0 | 0 | 17.5 | 22 | 0 | 320 | 0 | 0 | 85 | 0 | 4 | 51 | 32 | 0 | 12 | 0 | 0 | 80 | 0 | 2 | 520 | 0 | 0 | 50 | 25.5 | 0 | 227 | 0 | 0 | 0 | 1160 | 0 | 70 | 0 | 0 | 251 | 103 | 51 | 0 | 209 | 0 | 33 | 99 | 136 | 0 | 20 | 0 | 158 | 0 | 0 | 16 | 305 | 0 | 371 | 41 | 0 | 152 | 0 | 8 | 0 | 79 | 30 | 0 | 0 | 96 | 17 | 35 | 35 | 12 | 0 | 0 | 12 | 6378 | 879 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1015 | 0 | 0 | 0 | 1335.04 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 13 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 54 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 228 | 60 | 220 | 0 | 0 | 1085.32 | 47 | 5856.36 | 12234.36 | 88.48
04:00 | 0 | 50 | 24 | 0 | 0 | 0 | 0 | 6 | 333 | 0 | 0 | 0 | 17 | 103 | 30 | 145 | 40 | 17 | 120 | 0 | 0 | 0 | 325 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 17.5 | 22 | 0 | 360 | 0 | 0 | 84 | 0 | 7 | 51 | 32 | 0 | 12 | 0 | 0 | 80 | 0 | 14 | 520 | 0 | 0 | 50 | 25.5 | 0 | 227 | 0 | 0 | 0 | 1160 | 0 | 70 | 0 | 0 | 251 | 103 | 51 | 0 | 198 | 0 | 34 | 100 | 149 | 0 | 20 | 0 | 162 | 0 | 0 | 16 | 305 | 0 | 362 | 41 | 0 | 161 | 0 | 0 | 0 | 79 | 30 | 0 | 0 | 96 | 17 | 53 | 47 | 17 | 0 | 0 | 0 | 6586 | 879 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1055 | 0 | 0 | 0 | 1363.07 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 13 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 55 | 35 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 275 | 60 | 220 | 0 | 0 | 1085.32 | 47 | 6021.39 | 12607.39 | 88.47
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 6 | 303 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 305 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 17.5 | 22 | 0 | 310 | 0 | 0 | 80 | 0 | 18 | 51 | 0 | 0 | 12 | 0 | 0 | 80 | 0 | 13 | 520 | 0 | 0 | 50 | 0 | 0 | 227 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 0 | 254 | 103 | 51 | 0 | 197 | 0 | 0 | 101 | 0 | 0 | 20 | 0 | 152 | 0 | 0 | 0 | 305 | 0 | 342 | 41 | 0 | 149 | 0 | 0 | 0 | 79 | 30 | 0 | 0 | 96 | 0 | 76 | 56 | 12 | 0 | 0 | 0 | 5695.5 | 879 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1025 | 0 | 0 | 0 | 1377.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 60 | 220 | 0 | 0 | 1050 | 0 | 5691.27 | 11386.77 | 88.46
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 6 | 312 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 17.5 | 22 | 0 | 310 | 0 | 0 | 37 | 0 | 22 | 0 | 0 | 0 | 12 | 0 | 0 | 80 | 0 | 11 | 520 | 0 | 0 | 50 | 0 | 0 | 227 | 0 | 0 | 0 | 1050 | 0 | 0 | 0 | 0 | 100 | 103 | 51 | 0 | 201 | 0 | 0 | 101 | 0 | 0 | 20 | 0 | 146 | 0 | 0 | 0 | 305 | 0 | 342 | 41 | 0 | 141 | 0 | 0 | 0 | 79 | 30 | 0 | 0 | 96 | 0 | 68 | 35 | 17 | 0 | 0 | 0 | 5232.5 | 883 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1010 | 0 | 0 | 0 | 1275.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 60 | 220 | 0 | 0 | 950 | 0 | 5394.47 | 10626.97 | 88.45
07:00 | 0 | 17 | 10 | 0 | 0 | 0 | 0 | 6 | 318 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 300 | 0 | 0 | 1 | 0 | 23 | 22 | 0 | 338 | 0 | 0 | 31 | 0 | 23 | 0 | 0 | 0 | 12 | 0 | 0.35 | 80 | 0 | 0 | 520 | 0 | 0 | 34 | 0 | 0 | 224 | 0 | 0 | 0 | 1060 | 2 | 0 | 0 | 0 | 100 | 99 | 51 | 0 | 207 | 0 | 0 | 100 | 0 | 0 | 19 | 0 | 152 | 0 | 8 | 0 | 310 | 0 | 357 | 41 | 0 | 143 | 0 | 17 | 0 | 79 | 30 | 0 | 0 | 96 | 0 | 69 | 54 | 17 | 0 | 2.79 | 0 | 5309.14 | 864 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1000 | 0 | 0 | 0 | 1278.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.43 | 0 | 0 | 0 | 1.28 | 0 | 0 | 179 | 0 | 0 | 0 | 376 | 0 | 0.11 | 0 | 56 | 0 | 1 | 0 | 0 | 0 | 0 | 0.2 | 6 | 0.05 | 0 | 201 | 60 | 220 | 0 | 0 | 950 | 0 | 5411.45 | 10720.59 | 88.44
08:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 6 | 316 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 300 | 0 | 0 | 2 | 0 | 22 | 22 | 0 | 310 | 0 | 0 | 30 | 0 | 9 | 0 | 0 | 0 | 12 | 0 | 1.31 | 80 | 0 | 0 | 520 | 0 | 0 | 33 | 0 | 0 | 223 | 0 | 0 | 0 | 1160 | 7 | 0 | 85 | 0 | 0 | 99 | 51 | 2 | 195 | 28 | 0 | 100 | 0 | 0 | 14 | 0 | 148 | 0 | 27 | 0 | 305 | 0 | 388 | 41 | 0 | 158 | 2 | 5 | 0 | 79 | 30 | 0 | 0 | 96 | 0 | 69 | 55 | 18 | 1 | 4.87 | 0 | 5409.18 | 884 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 1060 | 0 | 0 | 0 | 1264.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 10 | 0 | 0 | 9.65 | 0 | 0 | 182 | 0 | 0 | 0 | 400 | 0 | 0.92 | 0 | 56 | 0 | 7 | 0 | 0 | 0 | 0 | 0.4 | 21 | 0.16 | 0 | 275 | 60 | 220 | 0 | 0 | 1000 | 0 | 5691.02 | 11100.2 | 88.43
09:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 6 | 326 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 300 | 0 | 0 | 5 | 0 | 22 | 22 | 0 | 345 | 0 | 0 | 30 | 0 | 6 | 0 | 0 | 0 | 12 | 0 | 2.22 | 80 | 0 | 0 | 520 | 0 | 0 | 33 | 0 | 0 | 220 | 0 | 0 | 0 | 1187 | 12 | 0 | 108 | 0 | 0 | 40 | 51 | 5 | 213 | 42 | 0 | 98 | 0 | 0 | 14 | 0 | 150 | 0 | 8 | 0 | 305 | 0 | 390 | 41 | 0 | 161 | 5 | 17 | 0 | 79 | 30 | 0 | 0 | 96 | 0 | 69 | 57 | 16 | 1 | 26.13 | 0 | 5572.35 | 884 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 1113 | 0 | 0 | 0 | 1284.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.96 | 34 | 0 | 0 | 31.19 | 0 | 0 | 184 | 0 | 0 | 0 | 414 | 0 | 2.69 | 0 | 56 | 0 | 4 | 0 | 0 | 0 | 0 | 0.9 | 51 | 0.14 | 0 | 284 | 60 | 220 | 0 | 0 | 1050 | 0 | 5921.7 | 11494.05 | 88.42
10:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 6 | 342 | 0 | 0 | 0 | 0 | 34 | 0 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 300 | 0 | 0 | 11 | 0 | 22 | 22 | 0 | 320 | 0 | 0 | 30 | 0 | 24 | 0 | 0 | 0 | 12 | 0 | 1.66 | 80 | 0 | 0 | 580 | 0 | 0 | 32 | 0 | 0 | 221 | 0 | 0 | 0 | 1162 | 6 | 5 | 145 | 0 | 0 | 18 | 44 | 5 | 201 | 42 | 0 | 97 | 0 | 0 | 11 | 0 | 154 | 0 | 62 | 0 | 300 | 0 | 381 | 41 | 0 | 166 | 8 | 17 | 0 | 79 | 30 | 0 | 0 | 96 | 0 | 69 | 58 | 10 | 1 | 7.15 | 0 | 5685.81 | 884 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 1209 | 0 | 0 | 0 | 1327.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.59 | 56 | 0 | 0 | 19.62 | 0 | 0 | 186 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 56 | 0 | 6 | 0 | 0 | 0 | 0 | 0.9 | 96 | 0.37 | 0 | 277 | 60 | 220 | 0 | 0 | 1050 | 0 | 6127.52 | 11813.33 | 88.41
11:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 6 | 320 | 0 | 0 | 0 | 0 | 34 | 0 | 60 | 0 | 17 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 300 | 0 | 0 | 16 | 0 | 22 | 22 | 0 | 345 | 0 | 0 | 30 | 0 | 14 | 0 | 0 | 0 | 12 | 0 | 1.91 | 80 | 0 | 0 | 580 | 0 | 0 | 32 | 0 | 0 | 221 | 0 | 0 | 0 | 1171 | 19 | 50 | 172 | 0 | 0 | 29 | 44 | 5 | 207 | 42 | 0 | 96 | 0 | 0 | 11 | 0 | 168 | 0 | 57 | 0 | 285 | 0 | 390 | 41 | 0 | 160 | 6 | 17 | 0 | 79 | 30 | 0 | 0 | 97 | 0 | 69 | 58 | 10 | 2 | 25.46 | 0 | 5798.37 | 884 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.74 | 1233 | 0 | 0 | 0 | 1336.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.07 | 29 | 0 | 0 | 36.05 | 0 | 0 | 171 | 0 | 0 | 0 | 414 | 0 | 2.85 | 0 | 56 | 0 | 9 | 0 | 0 | 0 | 0 | 1 | 142 | 0.58 | 0 | 278 | 60 | 220 | 0 | 0 | 1050 | 0 | 6177.05 | 11975.42 | 88.4
12:00 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 6 | 327 | 0 | 0 | 0 | 6 | 34 | 0 | 60 | 0 | 17 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 300 | 0 | 0 | 15 | 0 | 22 | 22 | 0 | 345 | 0 | 0 | 37 | 0 | 31 | 0 | 0 | 0 | 12 | 0 | 2.86 | 80 | 0 | 0 | 580 | 0 | 0 | 34 | 0 | 0 | 220 | 0 | 0 | 0 | 1178 | 10 | 50 | 172 | 0 | 0 | 47 | 51 | 8 | 209 | 41 | 0 | 96 | 0 | 0 | 11 | 0 | 166 | 0 | 39 | 0 | 290 | 0 | 388 | 41 | 0 | 162 | 11 | 17 | 0 | 79 | 30 | 0 | 0 | 98 | 0 | 69 | 58 | 10 | 1 | 46.75 | 0 | 5897.61 | 884 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.06 | 1234.2 | 3 | 0 | 0 | 1339.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.7 | 56 | 0 | 0 | 13.21 | 0 | 0 | 135 | 0 | 0 | 0 | 414 | 0 | 1.84 | 0 | 56 | 0 | 8 | 0 | 0 | 0 | 0 | 2.2 | 122 | 0.61 | 0 | 278 | 60 | 220 | 0 | 0 | 1050 | 0 | 6138.69 | 12036.3 | 88.39
13:00 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 6 | 336 | 0 | 0 | 0 | 17 | 26 | 0 | 145 | 0 | 17 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 300 | 0 | 0 | 15 | 0 | 22 | 22 | 0 | 310 | 0 | 0 | 76 | 0 | 26 | 0 | 0 | 0 | 12 | 0 | 1.64 | 80 | 0 | 6 | 580 | 0 | 0 | 41 | 0 | 0 | 220 | 0 | 0 | 0 | 1162 | 18 | 82 | 187 | 0 | 0 | 47 | 51 | 24 | 204 | 42 | 0 | 95 | 0 | 0 | 11 | 0 | 160 | 0 | 30 | 0 | 300 | 0 | 388 | 41 | 0 | 162 | 11 | 17 | 0 | 79 | 30 | 0 | 0 | 96 | 0 | 69 | 58 | 10 | 2 | 42.93 | 1 | 6051.57 | 884 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 1234.2 | 17 | 0 | 0 | 1465.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.56 | 58 | 0 | 0 | 25.09 | 0 | 0 | 130 | 0 | 0 | 0 | 414 | 0 | 1.76 | 0 | 56 | 0 | 8 | 0 | 0 | 0 | 0 | 2.1 | 196 | 0.29 | 0 | 307 | 60 | 220 | 0 | 0 | 1050 | 0 | 6416.07 | 12467.64 | 88.38
14:00 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 6 | 338 | 0 | 0 | 17 | 17 | 17 | 0 | 145 | 4 | 17 | 49 | 0 | 0 | 0 | 315 | 0 | 0 | 300 | 0 | 0 | 20 | 0 | 0 | 22 | 0 | 335 | 0 | 0 | 91 | 0 | 30 | 0 | 0 | 0 | 12 | 0 | 2.96 | 80 | 0 | 0 | 580 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1183 | 16 | 140 | 180 | 0 | 0 | 58 | 51 | 25 | 208 | 42 | 13 | 94 | 0 | 0 | 11 | 0 | 176 | 0 | 22 | 0 | 305 | 0 | 356 | 41 | 0 | 161 | 9 | 17 | 0 | 79 | 30 | 0 | 0 | 98 | 0 | 65 | 58 | 10 | 1 | 36.34 | 12 | 6170.3 | 887 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.62 | 1234.2 | 17 | 0 | 0 | 1460.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.17 | 80 | 0 | 0 | 33.67 | 0 | 0 | 196 | 0 | 0 | 0 | 414 | 0 | 2.73 | 0 | 55 | 0 | 7 | 0 | 0 | 0 | 0 | 3.9 | 167 | 0.54 | 0 | 307 | 60 | 220 | 0 | 0 | 1072 | 0 | 6510.38 | 12680.68 | 88.37
15:00 | 0 | 34 | 26 | 0 | 0 | 0 | 0 | 6 | 313 | 0 | 0 | 17.5 | 17 | 50 | 45 | 145 | 15 | 17 | 54 | 0 | 0 | 0 | 295 | 0 | 0 | 300 | 0 | 0 | 16 | 17 | 17 | 21 | 0 | 310 | 0 | 0 | 91 | 0 | 33 | 0 | 0 | 0 | 12 | 0 | 1.82 | 80 | 0 | 2 | 580 | 0 | 0 | 28 | 0 | 0 | 219 | 0 | 0 | 0 | 1153 | 13 | 142 | 184 | 0 | 80 | 58 | 51 | 25 | 205 | 39 | 46 | 96 | 20 | 0 | 19 | 0 | 178 | 0 | 31 | 0 | 300 | 0 | 326 | 41 | 0 | 156 | 7 | 17 | 0 | 81 | 30 | 0 | 0 | 99 | 0 | 65 | 58 | 7 | 1 | 28.4 | 12 | 6330.72 | 886 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 1197 | 17 | 0 | 0 | 1455.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.62 | 51 | 0 | 0 | 25.65 | 0 | 0 | 192 | 0 | 0 | 0 | 399 | 0 | 1.53 | 0 | 55 | 0 | 12 | 34 | 0 | 0 | 0 | 3.9 | 110 | 0.29 | 0 | 307 | 60 | 180 | 0 | 0 | 1209 | 0 | 6451.63 | 12782.35 | 88.36
16:00 | 0 | 49 | 33 | 0 | 0 | 0 | 0 | 6 | 322 | 0 | 0 | 17.5 | 17 | 70 | 45 | 145 | 15 | 17 | 54 | 0 | 0 | 0 | 305 | 0 | 17 | 300 | 0 | 0 | 9 | 26 | 0 | 20 | 0 | 310 | 0 | 0 | 90 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 1.25 | 80 | 0 | 2 | 580 | 17 | 0 | 46 | 0 | 0 | 219 | 0 | 0 | 0 | 1160 | 8 | 145 | 173 | 0 | 150 | 73 | 51 | 25 | 191 | 42 | 47 | 94 | 40 | 0 | 20 | 0 | 172 | 1 | 18 | 0 | 315 | 0 | 347 | 41 | 0 | 157 | 4 | 17 | 0 | 80 | 30 | 0 | 0 | 99 | 10 | 67 | 58 | 7 | 0 | 16.35 | 12 | 6496.1 | 886 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 1208 | 17 | 0 | 0 | 1454.66 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 16.42 | 19 | 0 | 0 | 13.41 | 0 | 0 | 191 | 0 | 0 | 0 | 405 | 0 | 0.97 | 0 | 54 | 0 | 5 | 38 | 0 | 0 | 0 | 1.3 | 71 | 0.18 | 0 | 307 | 61 | 220 | 0 | 0 | 1242 | 4 | 6429.94 | 12926.04 | 88.35
17:00 | 0 | 61 | 40 | 0 | 0 | 0 | 0 | 6 | 318 | 0 | 0 | 35 | 17 | 93 | 62 | 185 | 27 | 35 | 54 | 0 | 0 | 0 | 300 | 0 | 17 | 300 | 0 | 0 | 3 | 90 | 17 | 20 | 0 | 310 | 0 | 0 | 54 | 0 | 9 | 51 | 0 | 0 | 0 | 0 | 0.39 | 80 | 0 | 7 | 580 | 50 | 0 | 46 | 0 | 0 | 222 | 0 | 0 | 0 | 1159 | 2 | 145 | 110 | 0 | 150 | 88 | 51 | 7 | 184 | 42 | 61 | 96 | 96 | 0 | 20 | 30 | 170 | 8 | 9 | 8 | 310 | 0 | 360 | 41 | 0 | 156 | 1 | 17 | 0 | 80 | 30 | 0 | 0 | 99 | 17 | 77 | 58 | 6 | 0 | 5.75 | 12 | 6795.14 | 886 | 190 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.72 | 1234.2 | 17 | 0 | 0 | 1441.54 | 0 | 0 | 0 | 15 | 35 | 4 | 52 | 12 | 0 | 5.14 | 12 | 14 | 0 | 4.86 | 0 | 0 | 190 | 0 | 0 | 0 | 409 | 0 | 0.52 | 0 | 54 | 35 | 3 | 70 | 0 | 0 | 0 | 0.7 | 15 | 0.77 | 15 | 307 | 61 | 220 | 0 | 0 | 1205 | 17 | 6548.45 | 13343.59 | 88.34
18:00 | 0 | 70 | 50 | 0 | 0 | 0 | 0 | 6 | 342 | 0 | 0 | 37.5 | 17 | 122 | 95 | 195 | 30 | 35 | 54 | 0 | 0 | 0 | 310 | 0 | 17 | 300 | 0 | 0 | 0 | 108 | 21.5 | 20 | 0 | 340 | 0 | 0 | 51 | 0 | 2 | 50 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 7 | 580 | 50 | 0 | 46 | 0 | 0 | 221 | 0 | 0 | 0 | 1123 | 0 | 150 | 80 | 0 | 150 | 95 | 20 | 0 | 162 | 42 | 84 | 97 | 128 | 0 | 20 | 34 | 174 | 25 | 0 | 16 | 305 | 0 | 360 | 41 | 0 | 158 | 0 | 21 | 0 | 53 | 30 | 0 | 0 | 97 | 17 | 98 | 78 | 5 | 0 | 0 | 12 | 6932 | 887 | 177 | 0 | 30 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 0 | 0 | 1456.06 | 0 | 41 | 0 | 70 | 42 | 4 | 52 | 20 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 53 | 70 | 0 | 75 | 0 | 0 | 0 | 0.1 | 0 | 0 | 17 | 287 | 61 | 220 | 0 | 0 | 1205 | 52 | 6697.36 | 13629.36 | 88.33
19:00 | 0 | 70 | 50 | 0 | 0 | 0 | 0 | 6 | 299 | 0 | 0 | 49.5 | 17 | 149 | 95 | 280 | 30 | 55 | 54 | 0 | 0 | 0 | 303 | 0 | 45 | 280 | 0 | 0 | 0 | 108 | 23 | 22 | 0 | 340 | 0 | 0 | 51 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 14 | 580 | 100 | 0 | 50 | 0 | 0 | 225 | 0 | 0 | 0 | 1151 | 0 | 145 | 43 | 0 | 150 | 110 | 30 | 0 | 194 | 42 | 87 | 98 | 141 | 0 | 20 | 38 | 170 | 30 | 0 | 16 | 300 | 0 | 356 | 41 | 0 | 148 | 0 | 21 | 0 | 82 | 30 | 0 | 0 | 98 | 17 | 98 | 78 | 8 | 0 | 0 | 12 | 7179.5 | 886 | 178 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1192 | 17 | 0 | 0 | 1449.95 | 0 | 48 | 0 | 100 | 80 | 4 | 52 | 20 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 53 | 110 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 280 | 61 | 220 | 0 | 0 | 1215 | 79 | 6848.95 | 14028.45 | 88.32
19:30 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 6 | 295 | 0 | 0 | 45 | 17 | 149 | 62 | 300 | 40 | 55 | 54 | 0 | 0 | 0 | 300 | 0 | 55 | 280 | 0 | 0 | 0 | 90 | 22 | 22 | 0 | 340 | 0 | 0 | 51 | 0 | 0 | 50 | 2 | 0 | 0 | 0 | 0 | 80 | 0 | 17 | 580 | 50 | 0 | 50 | 1 | 0 | 225 | 0 | 0 | 0 | 1151 | 0 | 136 | 43 | 0 | 150 | 117 | 51 | 0 | 207 | 42 | 105 | 98 | 168 | 0 | 20 | 34 | 168 | 16 | 0 | 16 | 305 | 0 | 389 | 41 | 0 | 152 | 0 | 21 | 0 | 82 | 30 | 0 | 0 | 98 | 35 | 98 | 78 | 8 | 0 | 0 | 12 | 7213 | 887 | 178 | 0 | 30 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1216 | 17 | 0 | 0 | 1457.14 | 0 | 48 | 0 | 70 | 113 | 4 | 52 | 20 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 55 | 115 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 61 | 220 | 0 | 0 | 1215 | 76 | 6915.14 | 14128.14 | 88.31
20:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 6 | 298 | 0 | 0 | 44.9 | 17 | 149 | 62 | 245 | 55 | 55 | 54 | 0 | 0 | 0 | 290 | 0 | 55 | 280 | 0 | 0 | 0 | 90 | 21.5 | 22 | 0 | 340 | 0 | 0 | 51 | 0 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 80 | 0 | 19 | 580 | 50 | 0 | 50 | 4 | 0 | 225 | 0 | 0 | 0 | 1160 | 0 | 100 | 45 | 0 | 150 | 136 | 51 | 0 | 213 | 42 | 99 | 98 | 168 | 0 | 20 | 34 | 170 | 16 | 0 | 16 | 305 | 0 | 390 | 41 | 0 | 150 | 0 | 21 | 0 | 82 | 30 | 0 | 0 | 98 | 34 | 98 | 78 | 8 | 0 | 0 | 12 | 7170.4 | 886 | 179 | 0 | 30 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1228 | 17 | 0 | 0 | 1460.34 | 0 | 48 | 0 | 70 | 70 | 4 | 52 | 20 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 53 | 115 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 61 | 220 | 0 | 0 | 1215 | 81 | 6898.34 | 14068.74 | 88.3
21:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 6 | 311 | 0 | 0 | 46.7 | 17 | 149 | 45 | 195 | 55 | 17 | 54 | 0 | 0 | 0 | 295 | 0 | 55 | 280 | 0 | 0 | 0 | 70 | 21.5 | 22 | 0 | 340 | 0 | 0 | 40 | 0 | 9 | 50 | 8 | 0 | 0 | 0 | 0 | 80 | 0 | 14 | 580 | 17 | 0 | 50 | 8 | 0 | 225 | 0 | 0 | 0 | 1165 | 0 | 100 | 45 | 0 | 150 | 147 | 51 | 0 | 212 | 42 | 71 | 100 | 155 | 0 | 20 | 12 | 172 | 16 | 0 | 16 | 305 | 0 | 354 | 41 | 0 | 153 | 0 | 21 | 0 | 82 | 30 | 0 | 0 | 98 | 35 | 98 | 78 | 9 | 0 | 0 | 12 | 6934.2 | 886 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 0 | 0 | 1459.75 | 0 | 48 | 0 | 35 | 35 | 4 | 50 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 54 | 70 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 61 | 220 | 0 | 0 | 1220 | 81 | 6678.95 | 13613.15 | 88.3
22:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 6 | 306 | 0 | 0 | 45.2 | 17 | 130 | 45 | 95 | 55 | 17 | 54 | 0 | 0 | 0 | 290 | 0 | 17 | 280 | 0 | 0 | 0 | 70 | 21.5 | 22 | 0 | 340 | 0 | 0 | 38 | 0 | 13 | 50 | 16 | 0 | 0 | 0 | 0 | 80 | 0 | 15 | 580 | 0 | 0 | 50 | 8 | 0 | 225 | 0 | 0 | 0 | 1165 | 0 | 50 | 45 | 0 | 150 | 180 | 51 | 0 | 210 | 42 | 51 | 99 | 100 | 0 | 20 | 0 | 172 | 0 | 0 | 16 | 310 | 0 | 370 | 41 | 0 | 151 | 0 | 21 | 0 | 82 | 30 | 0 | 0 | 99 | 23 | 98 | 78 | 8 | 0 | 0 | 12 | 6643.7 | 886 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1174 | 17 | 0 | 0 | 1258.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 54 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247 | 61 | 180 | 0 | 0 | 1190 | 0 | 5729.81 | 12373.51 | 88.29
23:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 6 | 305 | 0 | 0 | 16.5 | 17 | 80 | 15 | 45 | 55 | 0 | 54 | 0 | 0 | 0 | 290 | 0 | 0 | 280 | 0 | 0 | 0 | 70 | 21.5 | 22 | 0 | 340 | 0 | 0 | 38 | 0 | 12 | 51 | 16 | 0 | 0 | 0 | 0 | 80 | 0 | 17 | 580 | 0 | 0 | 50 | 8 | 0 | 225 | 0 | 0 | 0 | 1160 | 0 | 10 | 45 | 0 | 150 | 285 | 51 | 0 | 159 | 42 | 50 | 100 | 54 | 0 | 20 | 0 | 176 | 0 | 0 | 0 | 310 | 0 | 327 | 41 | 0 | 137 | 0 | 4 | 0 | 82 | 30 | 0 | 0 | 98 | 17 | 8 | 8 | 8 | 0 | 0 | 0 | 6150 | 885 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 980 | 17 | 0 | 0 | 930.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 61 | 180 | 0 | 0 | 960 | 0 | 4810.9 | 10960.9 | 88.28
Total KWH | 0 | 1045440 | 677760 | 0 | 0 | 0 | 0 | 159954.55 | 7750800 | 0 | 0 | 388800 | 288720 | 1911744 | 637440 | 2620244 | 558723 | 397438 | 1166400 | 0 | 0 | 0 | 7359860 | 0 | 306177 | 7074385 | 0 | 0 | 109707 | 640800 | 433800 | 517680 | 0 | 7908636.36 | 0 | 0 | 1367040 | 0 | 329280 | 639867 | 206109 | 0 | 181440 | 0 | 21262 | 1918860 | 0 | 177120 | 13418181.82 | 252581 | 0 | 1055040 | 166273.2 | 0 | 5490592 | 0 | 0 | 0 | 27676361 | 118530 | 1818254 | 1773091 | 0 | 3064600 | 2420000 | 1205904 | 138720 | 4929000 | 646560 | 826560 | 2344393 | 1601280 | 0 | 415890 | 148200 | 3961920 | 112646 | 376155 | 151216 | 7342000 | 0 | 9028000 | 972000 | 0 | 3697773 | 58291 | 261072 | 0 | 1907520 | 717696 | 0 | 0 | 2337400 | 266760 | 1603200 | 1298400 | 244800 | 8850 | 236440 | 163440 | 151051076.93 | 21132363 | 4757472 | 0 | 136320 | 143872 | 0 | 0 | 0 | 0 | 0 | 0 | 461520 | 27236360 | 181872 | 0 | 0 | 32269029 | 0 | 201030 | 0 | 480809 | 552864 | 30768 | 256848 | 135996 | 0 | 169192 | 376320 | 158421 | 0 | 204000 | 0 | 0 | 4367264 | 0 | 0 | 0 | 9136436 | 0 | 17580 | 0 | 1264581 | 629446 | 86228 | 893616 | 0 | 0 | 0 | 21127.08 | 982080 | 3066 | 204480 | 6502000 | 1483000 | 5373640 | 0 | 0 | 26727272.73 | 507600 | 147084472.81 | 298135549.74

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 15-03-2026
Power Supply Scenario
| Day Peak Generation |  |  | 12036.3 | MW | 12:00 Hr. | Energy Generated |  |  | 298.1355 |  | MKWHr.
| Day Peak Demand |  |  | 12355.3 | MW | 12:00 Hr. | Energy Unserverd |  |  | 2.223 |  | MKWHr.
| Evening Peak Generation |  |  | 14128.14 | MW | 19:30 Hr. | Energy Demand |  |  | 300.3585 |  | MKWHr.
| Evening Peak Demand |  |  | 14150.14 | MW | 19:30 Hr. | Maximum Temperature |  |  | 31.7 |  | °C
| Minimum Generation of the Day |  |  | 10626.97 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 739.76 |  | MMCFD
| Maximum Generation of the Day |  |  | 14128.14 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.3418 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 31.2051 | 0 | 10.6397 | 0 | 0 | 0.10971 | 0 | 0 | 41.9545 | Gas | 105.4371 | Gas | 368070597.0137
| Chattogram Zone |  |  | 5.6677 | 41.0945 | 3.8684 | 0 | 1.9189 | 0.13979 | 0 | 0.32928 | 53.0185 | Coal | 102.8248 | Coal | 672693919.768
| Cumilla Zone |  |  | 16.9382 | 0 | 4.6582 | 0 | 0 | 0.37616 | 3.9619 | 0 | 25.9344 | HFO | 27.0119 | HFO | 460732331.76
| Mymensingh Zone |  |  | 0.2448 | 0 | 3.3318 | 0 | 0 | 0.24529 | 0 | 0 | 3.8219 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.2635 | 0 | 0 | 0 | 0 | 0.058291 | 0 | 0 | 26.3218 | Hydro | 1.9189 | Hydro | 191886
| Khulna Zone |  |  | 4.7575 | 27.2364 | 0.46206 | 0 | 0 | 0.46152 | 21.1324 | 0 | 54.0498 | Solar | 3.2503 | Solar | 52670793.446
| Barishal Zone |  |  | 6.8566 | 33.2293 | 0.71208 | 0 | 0 | 0.003066 | 0 | 0 | 40.8011 | Import | 57.3633 | Import | 331522982.43
| Rajshahi Zone |  |  | 13.5037 | 0 | 1.8167 | 0 | 0 | 0.76709 | 32.269 | 0 | 48.3566 | Wind | 0.32928 | Wind | 4843708.8
| Rangpur Zone |  |  | 0 | 1.2646 | 1.5231 | 0 | 0 | 1.0894 | 0 | 0 | 3.8771
| Total |  |  | 105.4371 | 102.8248 | 27.0119 | 0 | 1.9189 | 3.2503 | 57.3633 | 0.32928 | 298.1355
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 368070597.0137 |  | Hydro | 191886
|  |  |  | Coal | 672693919.768 |  | Solar | 52670793.446
|  |  |  | HFO | 460732331.76 |  | Import | 331522982.43
|  |  |  | HSD | 0 |  | Wind | 4843708.8
[5 empty] | Total: | 189,07,26,219 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.1324 | Peak Hr Flow | 887.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 43490327.27 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 32.269 | Peak Hr Flow | 1457.14 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2474 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.9619 | Peak Hr Flow | 168.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2869 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 57.3633 | Peak Hr Flow | 2512.14 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5269
|  |  |  | Chattogram |  | 21 |  | 1346
|  |  |  | Cumilla |  | 0 |  | 1327
|  |  |  | Mymensingh |  | 0 |  | 1088
|  |  |  | Sylhet |  | 0 |  | 393
|  |  |  | Khulna |  | 0 |  | 1620
|  |  |  | Barishal |  | 0 |  | 392
|  |  |  | Rajshahi |  | 0 |  | 1416
|  |  |  | Rangpur |  | 0 |  | 770
|  |  |  | Total |  | 21 |  | 13621
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 400
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:04 | 16:52 | Baroirhat-Hathazari 132 kV Ckt-2 Scheduled S/D from Hathazari 230/132/33kV end Due to
none
| 09:08 | 13:30 | Savar 132/33kV S/S Main Bus-I Scheduled S/D Due to Red hot maintenance
| 09:10 | 15:54 | Ashuganj-Shahjibazar 132kV Ckt-1 Scheduled S/D from Shahjibazar 132/33kV end Due to
Annaul Maintenance.
| 09:18 | 10:47 | Savar 132/33kV S/S T-1 LT Scheduled S/D Due to Red hot maintenance
| 09:20 | 10:46 | Savar 132/33kV S/S T-1 HT Scheduled S/D Due to Red hot maintenance
| 10:08 | 13:45 | Maniknagar-Matuail 132kV Ckt-1 Tripped from Matuail 132/33kV end showing distance relay
operate. Zone-1, Distance-4.1Km Phase A relays Due to trip
|  | 10:40 | Rampur 230/132/33 S/S TR 02 (417T) LT is restored.
| 10:48 | 13:34 | Savar 132/33kV S/S T-2 LT Scheduled S/D Due to Red hot maintenance
| 10:50 | 13:31 | Savar 132/33kV S/S T-2 HT Scheduled S/D Due to Red hot maintenance
| 11:42 | 12:54 | Matuail-Siddhirganj 132kV Ckt-1 Tripped from Siddhirganj 132/33kV end showing Distance | [7 empty] | 70.0MW load
|  |  | Relay- 1. Zone-01 2. Phase0 R & B 3. Distance- 2 KM 4. Fault Current-21563A relays. | [7 empty] | interrup.
Siddhirganj
132/33kV end
|  | 11:51 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT is restored.
| 12:00 |  | Day Peak Generation: 12031 MW.
| 14:17 | 14:55 | Bheramara P/S-Kustia 132 kV Ckt-1 Tripped from Bheramara 230/132kV end showing DIST.PROTN | [7 empty] | 180.0MW load
|  |  | RLY 21 relays. | [7 empty] | interrup. Bheramara
230/132kV end
| 14:18 | 15:13 | Jhenaidah-Kushtia 132kV Ckt-1 Tripped from Kushtia 132/33kV end showing Distance relay | [7 empty] | 126.0MW load
|  |  | F-21 relays. | [7 empty] | interrup. Kushtia
132/33kV end
| 14:18 | 15:13 | Jhenaidah-Kushtia 132kV Ckt-1 Tripped from Kushtia 132/33kV end showing Distance relay | [7 empty] | 126.0MW load
|  |  | F-21 relays. | [7 empty] | interrup. Kushtia
132/33kV end
| 14:28 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- GT
| 14:49 | 15:02 | Kushtia 132/33kV S/S T2 LT Forced S/D Due to The power at the grid substation dropped to | [7 empty] | 50.0MW load
|  |  | zero due to transmission line trip. | [7 empty] | interrup.
| 14:49 | 15:01 | Kushtia 132/33kV S/S T2 HT Forced S/D Due to Power at the Kushtia Grid Substation dropped | [7 empty] | 50.0MW load
|  |  | to zero following a trip on the Bheramara-Kushtia Circuit-1 (Bheramara end) and the | [7 empty] | interrup.
Kushtia-Jhenaidah Circuit-1 (Kushtia end).
| 14:50 | 15:04 | Kushtia 132/33kV S/S T-1 LT Forced S/D Due to Power at the Kushtia Grid Substation | [7 empty] | 15.0MW load
|  |  | dropped to zero following a trip on the Bheramara-Kushtia Circuit-1 (Bheramara end) and | [7 empty] | interrup.
the Kushtia-Jhenaidah Circuit-1 (Kushtia end).
| 14:50 | 15:03 | Kushtia 132/33kV S/S T-1 HT Forced S/D Due to Power at the Kushtia Grid Substation | [7 empty] | 15.0MW load
|  |  | dropped to zero following a trip on the Bheramara-Kushtia Circuit-1 (Bheramara end) and | [7 empty] | interrup.
the Kushtia-Jhenaidah Circuit-1 (Kushtia end).
| 14:51 | 15:04 | Kushtia 132/33kV S/S T-3 LT Forced S/D Due to Power at the Kushtia Grid Substation | [7 empty] | 61.0MW load
|  |  | dropped to zero following a trip on the Bheramara-Kushtia Circuit-1 (Bheramara end) and | [7 empty] | interrup.
the Kushtia-Jhenaidah Circuit-1 (Kushtia end).
| 14:51 | 15:03 | Kushtia 132/33kV S/S T-3 HT Forced S/D Due to Power at the Kushtia Grid Substation | [7 empty] | 61.0MW load
|  |  | dropped to zero following a trip on the Bheramara-Kushtia Circuit-1 (Bheramara end) and | [7 empty] | interrup.
the Kushtia-Jhenaidah Circuit-1 (Kushtia end).
| 15:49 | 17:23 | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) LT Forced S/D Due to 33kV Feeder Redhot | [7 empty] | 40.0MW load
|  |  | Maintenance work by PBS. | [7 empty] | interrup.
| 15:49 | 16:50 | Bhandaria 132/33kV S/S Transformer-1 LT Forced S/D Due to Bus D/S maintenances for Pbs | [7 empty] | 10.0MW load
|  |  | bamna feeder. | [7 empty] | interrup.
| 15:50 | 17:21 | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) HT Forced S/D Due to 33kV Feeder Redhot | [7 empty] | 40.0MW load
|  |  | Maintenance work by PBS. | [7 empty] | interrup.
| 15:50 | 16:47 | Bhandaria 132/33kV S/S Transformer-1 HT Forced S/D Due to Bus D/S maintenances for Pbs | [7 empty] | 10.0MW load
|  |  | bamna feeder. | [7 empty] | interrup.
|  | 17:08 | Chowmuhani-Feni 132 kV Ckt-2 is restored.
|  | 17:15 | Rampur 230/132/33 S/S Khulshi-1 is restored.
|  | 17:28 | Bhulta-Haripur 230 kV Ckt-1 is restored.
| 19:12 | 22:58 | Khulna(C )-Noapara 132kV Ckt-1 Forced S/D from Khulna (C) end Due to Spark in lighting
arrester and from Noapara 132/33kVend.
| 20:15 |  | Ruppur 400/230 AT20 was charged and switched on at 20:34 PM
| 20:54 |  | BIPTC S/S 10CF25 Tripped showing 87 (differential relay). relays Due to Tripped by
capacitor bank-1 T1 60C current unbalance 1 ph (B-Phase).
| 20:54 |  | BIPTC S/S 10CF16 Tripped showing differential protection. relays.
| 22:29 | 05:06 | Bogura 230/132kV S/S Confidance UN-1 Tripped showing no relay relays Due to Stromy
weather
| 22:30 | 02:33 | Rajshahi 132/33kV S/S Transformer T-2(415T) LT Tripped showing O/C relays Due to টি-২ ৩৩ | [7 empty] | 8.0MW load
|  |  | কেভি বাস-কাপলারের ইনসুলেটর Cracked | [7 empty] | interrup.
| 23:11 | 23:39 | Khulna(C )-Noapara 132kV Ckt-2 Scheduled S/D from Noapara 132/33kV end Due to By ALDC.
and from Khulna (C) end Due to Emergency maintenance
| 23:49 | 00:10 | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) LT Tripped showing Over current protection | [7 empty] | 10.0MW load
|  |  | (P142) relays Due to Over current | [7 empty] | interrup.
| 23:49 | 00:10 | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) HT Tripped showing Over current protection | [7 empty] | 10.0MW load
|  |  | (P132) Differential Protection (F1-P632) Differential Protection (F4-P632) relays Due | [7 empty] | interrup.
to Over current
| 00:42 |  | Shahjibazar-Sreemangal 132kV Ckt-1 Tripped from Sreemongol 132/33kV end showing DISTANCE
RELAY relays Due to BY FAULT and from Shahjibazar 132/33kV end showing Distance relay
relays Due to Heavy rain
| 00:46 | 02:31 | Rajshahi 132/33kV S/S Transformer T-2(415T) HT Forced S/D Due to Crack Insulator changed
by nesco
| 01:48 |  | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) LT Forced S/D Due to 33 kV bus conductor | [7 empty] | 10.0MW load
|  |  | snapped. | [7 empty] | interrup.
| 01:49 |  | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT Forced S/D Due to 33 kV bus conductor | [7 empty] | 10.0MW load
|  |  | snapped | [7 empty] | interrup.
| 02:05 |  | Shahjibazar-Sreemangal 132kV Ckt-1 Forced S/D from Sreemongol 132/33kV end Due to FOR
FAULT REMOVING WORK
| 02:25 | 02:37 | Cox'sbazar-Dohazari 132 kV Ckt-1 Tripped from Dohazari 132/33kV end showing Distance | [7 empty] | 39.0MW load
|  |  | Relay. relays. | [7 empty] | interrup. Dohazari
132/33kV end
| 02:39 | 03:07 | GPH 230/33kV S/S BSRM CKT-1 Tripped showing 86.1,86.2,21.1,21.2 relays Due to line
tripped for bad weather
| 07:05 | 07:57 | Noapara 132/33kV S/S T-1 HT Scheduled S/D
| 07:05 | 07:57 | Noapara 132/33kV S/S T-1 LT Scheduled S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 15-03-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 6 | 159954.55 | Demand "05"MW due to gas restiction by Titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 295 | 7750800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 40 | 558723 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 7074385 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 45 | 388800 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 62 | 637440 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 397438 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 306177 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22 | 433800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 517680 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 34 | 677760 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 300 | 2620244 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1911744 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1045440 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 1166400 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 109707 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 288720 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 340 | 7908636.36 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 300 | 7359860 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 90 | 640800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2236 | 41954508.91
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 1 | 166273.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 118530 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1055040 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1918860 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 225 | 5490592 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 2 | 206109 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 639867 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 181440 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 17 | 177120 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 51 | 1367040 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21262 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 50 | 252581 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1151 | 27676361 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 329280 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 580 | 13418181.82 | Coal shortage
Chattogram Area Total |  |  |  |  | 4898.863 | 2257 | 53018537.02
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 207 | 4929000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 150 | 3064600 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 117 | 2420000 | STG Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Line trip
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 42 | 646560 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 138720 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 43 | 1773091 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1205904 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 136 | 1818254 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 16 | 151216 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 98 | 2344393 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 168 | 1601280 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 168 | 3961920 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 16 | 112646 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 415890 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 148200 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 105 | 826560 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 376155 | -
Cumilla Area Total |  |  |  |  | 2876.261 | 1371 | 25934389
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 8 | 244800 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8850 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 78 | 1298400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 98 | 1603200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 236440 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 163440 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 266760 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 231 | 3821890
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 58291 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 972000 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3697773 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | O.4 kv aux transformer tripped
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 717696 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1907520 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 98 | 2337400 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 261072 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7342000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 389 | 9028000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1118 | 26321752
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 887 | 21132363 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 30 | 136320 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 45 | 143872 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 178 | 4757472 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 181872 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 461520 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1216 | 27236360 | plant availability zero
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2373 | 54049779
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 32 | 204480 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 61 | 1483000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1215 | 26727272.73 | DCT
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5373640 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 76 | 507600 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6502000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3066 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1911 | 40801058.73
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 169192 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 48 | 201030 | Under Maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 4 | 30768 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 135996 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 179 | 4367264 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 397 | 9136436 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 16 | 158421 | machine problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 52 | 256848 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 552864 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 70 | 480809 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 17580 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1457.14 | 32269029 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 204000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 376320 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2356.14 | 48356557
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 55 | 1264581 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 105 | 893616 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 21127.08 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 629446 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 86228 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 982080 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 275 | 3877078.08
Eastern Grid Total |  |  |  |  | 17423.308 | 7213 | 151051076.93
Western Grid Total |  |  |  |  | 11852.195 | 6915.14 | 147084472.81
National Grid Total |  |  |  |  | 29275.503 | 14128.14 | 298135549.74
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 15-03-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9401.42 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4198.7 | MW
i) Dhaka area |  |  | 5268.62 |  | MW | i) Khulna area |  |  |  | 1620 | MW
ii) Chattogram area |  |  | 1324.8 |  | MW | ii) Barishal area |  |  |  | 392.5 | MW
iii) Cumilla area |  |  | 1327 |  | MW | iii) Rajshahi area |  |  |  | 1416.2 | MW
iv) Mymensingh area |  |  | 1088 |  | MW | iv) Rangpur area |  |  |  | 770 | MW
v) Sylhet area |  |  | 393 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13600.12 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 8 | 19:00 | 67 | Hasnabad | 89 | 19:30 | 133 | Nawabganj | 52 | 16:00
2 | AKSML | 7 | 16:00 | 68 | Hathazari | 75 | 21:00 | 134 | Netrakona | 112 | 18:00
3 | Aftabnagar | 32 | 18:00 | 69 | Hatirjheel | 41 | 15:00 | 135 | New | 74 | 11:00
4 | Agargaon | 106 | 13:00 | 70 | Ishurdi | 72 | 19:00 | 136 | Niamatpur | 99 | 13:00
5 | Agrabad | 58 | 18:30 | 71 | Jaldhaka | 64 | 17:00 | 137 | Noapara | 51 | 14:00
6 | Amnura | 39 | 20:00 | 72 | Jamalpur | 118 | 18:30 | 138 | PHP | 11 | 16:00
7 | Ashuganj | 89 | 22:00 | 73 | Jashore | 124 | 18:00 | 139 | Pabna | 90 | 21:00
8 | BSRM | 197 | 16:00 | 74 | Jhenaidah | 101 | 19:00 | 140 | Palashbari | 104 | 00:00
9 | Bagerhat | 79 | 21:00 | 75 | Joydebpur | 130 | 19:00 | 141 | Panchagarh | 47 | 17:00
10 | Bajitpur | 72 | 19:00 | 76 | Joypurhat | 54 | 00:00 | 142 | Patiya | 9 | 18:30
11 | Bakerganj | 12 | 19:00 | 77 | Juldah | 17.5 | 14:00 | 143 | Patuakhali | 56 | 19:00
12 | Bakulia | 72 | 20:00 | 78 | KSRM | 10 | 12:00 | 144 | Payra | 28 | 23:00
13 | Banani | 30.2 | 13:00 | 79 | Kabirpur | 264 | 16:00 | 145 | Postogola | 48 | 00:00
14 | Bangabhaban | 17 | 10:00 | 80 | Kachua | 90 | 18:30 | 146 | Pubail | 27 | 16:00
15 | Barapukuria | 60 | 19:00 | 81 | Kaliganj | 27 | 18:30 | 147 | Purbachal | 27 | 13:00
16 | Barguna | 18 | 19:00 | 82 | Kallyanpur | 102 | 00:00 | 148 | Purbasadipur | 113 | 17:00
17 | Barishal | 90 | 21:00 | 83 | Kalurghat | 52 | 14:00 | 149 | Rahanpur | 35 | 21:00
18 | Barishal-230 | 86 | 19:00 | 84 | Kamrangirchar | 77 | 15:00 | 150 | Rahim | 37 | 09:00
19 | Baroaulia | 60 | 11:00 | 85 | Kaptai | N/A | N/A | 151 | Rajbari | 73 | 03:00
20 | Baroirhat | 56 | 19:00 | 86 | Kasba | 36 | 22:00 | 152 | Rajendrapur | 131 | 16:00
21 | Bashundhara | 163 | 19:00 | 87 | Kazla | 109 | 19:30 | 153 | Rajshahi | 100 | 00:00
22 | BashundharaCement | 13 | 23:00 | 88 | Keranigonj | 83 | 19:00 | 154 | Rajshahi-230 | 86 | 19:00
23 | Beanibazar | 40 | 16:00 | 89 | Khagrachori | 28 | 18:30 | 155 | Ramganj | 94 | 04:00
24 | Benapole | 78 | 13:00 | 90 | Khulna | 50 | 19:30 | 156 | Rampur | 38 | 19:00
25 | Bhaluka | 133 | 18:00 | 91 | Khulshi | 174 | 00:00 | 157 | Rangamati | 16 | 19:00
26 | Bhandaria | 49 | 22:00 | 92 | Kishoreganj | 120 | 18:00 | 158 | Rangpur | 140 | 18:00
27 | Bhangura | 41 | 14:00 | 93 | Kodda | 311 | 17:00 | 159 | Ruppur | 3.6 | 10:00
28 | Bheramara(GK) | 60 | 19:00 | 94 | Kulaura | 33 | 18:00 | 160 | SSM | 12 | 02:00
29 | Bhulta | 213 | 17:00 | 95 | Kurigram | 56 | 17:00 | 161 | Saidpur | 101 | 17:00
30 | Bog-Sherpur | 72 | 21:00 | 96 | Kushtia | 145 | 02:00 | 162 | Satkhira | 126 | 19:30
31 | Bogura | 150 | 01:00 | 97 | Laksam | 111 | 10:00 | 163 | Satmasjid | 94 | 19:00
32 | Borhanuddin | 90 | 21:00 | 98 | Lakshmipur | 44 | 22:00 | 164 | Savar | 214 | 09:00
33 | Brahmanbaria | 118 | 22:00 | 99 | Lalbag | 72 | 13:00 | 165 | SevenRings | 17.39 | 17:00
34 | Cantonment | 142 | 14:00 | 100 | Lalmonirhat | 46 | 17:00 | 166 | ShahCement | 31 | 01:00
35 | Chandina | 16 | 13:00 | 101 | MI_Cement | 19.3 | 00:00 | 167 | Shahjadpur | 88 | 07:00
36 | Chandpur | 76 | 19:00 | 102 | Madanganj | 30 | 19:00 | 168 | Shahjibazar | 105 | 22:00
37 | Chandraghona | 34 | 19:30 | 103 | Madaripur | 101 | 22:00 | 169 | Shahmirpur | 60 | 00:00
38 | Chapai | 77 | 03:00 | 104 | Madartek | 68 | 19:00 | 170 | Shariatpur | 79 | 22:00
39 | Charsaidpur | 45 | 04:00 | 105 | Madunaghat | 51 | 19:00 | 171 | Sherpur | 118 | 17:00
40 | Chauddagram | 70 | 18:30 | 106 | Magura | 61 | 19:00 | 172 | Shikalbaha | 33 | 19:30
41 | Chhatak | 23 | 18:00 | 107 | Mahasthangarh | 70 | 03:00 | 173 | Shitalakhya | 82.4 | 15:00
42 | Chowmuhani | 132 | 20:00 | 108 | Maijdee | 42 | 19:30 | 174 | Sholosohor | 44 | 14:00
43 | Chuadanga | 112 | 03:00 | 109 | Manikganj | 126 | 19:00 | 175 | Shyampur | 192 | 12:00
44 | Coxsbazar | 130 | 18:00 | 110 | Maniknagar | 67 | 11:00 | 176 | Siddhirganj | 122 | 15:00
45 | Cumilla(N) | 120 | 21:00 | 111 | Matarbari | 50 | 03:00 | 177 | Sirajganj | 116 | 19:30
46 | Cumilla(S) | 181 | 18:30 | 112 | Matuail | 68 | 14:00 | 178 | Sonargaon | 162 | 00:00
47 | Daganbhuiyan | 32 | 22:00 | 113 | Metrorail_Motijheel | 30 | 15:00 | 179 | Sreemongol | 55 | 22:00
48 | Daudkandi | 142 | 21:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sreepur | 116 | 17:00
49 | DhakaUniversity | 72 | 13:00 | 115 | Millgate | 92 | 10:00 | 181 | Srinagar | 43.68 | 22:00
50 | Dhamrai | 126 | 19:00 | 116 | Mirpur | 125 | 14:00 | 182 | Sunamganj | 40 | 20:00
51 | Dhanmondi | 109 | 13:00 | 117 | Mirsorai | 38 | 05:00 | 183 | Sylhet | 56 | 17:00
52 | Dohazari | 85 | 01:00 | 118 | Mirzapur | 52 | 20:00 | 184 | Sylhet-132 | 67 | 12:00
53 | Faridpur | 152 | 21:00 | 119 | Mithapukur | 50 | 18:00 | 185 | TK | 21 | 20:00
54 | Fatullah | 100 | 15:00 | 120 | Modern | N/A | N/A | 186 | Tangail | 196 | 03:00
55 | Fenchuganj | 26 | 16:00 | 121 | Mogbazar | 56.4 | 12:00 | 187 | Taraganj | 21 | 17:00
56 | Feni | 96 | 18:30 | 122 | Mongla | 45 | 01:00 | 188 | Tasnim | 20 | 01:00
57 | GPH | 20 | 19:30 | 123 | Motijheel | 43 | 13:00 | 189 | Thakurgaon | 84 | 18:00
58 | Ghatail | 92 | 18:00 | 124 | Muktagacha | 39 | 17:00 | 190 | Tongi | 142 | 17:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 108 | 22:00 | 191 | Ullahpara | 45 | 03:00
60 | Ghorashal-230 | 106 | 19:00 | 126 | Muradnagar | 40 | 14:00 | 192 | Ullon | 48 | 18:30
61 | Goalpara | 36 | 19:00 | 127 | Mymensingh | 211 | 18:00 | 193 | Uttara | 76 | 14:00
62 | Gollamari | 98 | 19:00 | 128 | Naogaon | 122 | 00:00 | 194 | UttaraNew | 27 | 18:00
63 | Gopalganj | 94 | 21:00 | 129 | Narail | 57 | 19:30 | 195 | Zigatola | 87 | 15:00
64 | Gulshan | 112 | 13:00 | 130 | Narinda | 66 | 13:00
65 | Halishahar | 92 | 15:00 | 131 | Narshingdi | 177 | 19:30
66 | HaripurSBU | 139 | 09:00 | 132 | Natore | 155 | 04:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 15-03-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 12825.3 | 43 |  | 12870.24
1:00 | 12488.57 | 46 |  | 12536.57
2:00 | 12287.35 | 43 |  | 12332.35
3:00 | 12234.36 | 45 |  | 12281.36
4:00 | 12607.39 | 42 |  | 12651.39
5:00 | 11386.77 | 0 |  | 11386.77
6:00 | 10626.97 | 0 |  | 10626.97
7:00 | 10720.59 | 0 |  | 10720.59
8:00 | 11100.2 | 42 |  | 11144.2
9:00 | 11494.05 | 57 |  | 11554.05
10:00 | 11813.33 | 134 |  | 11953.33
11:00 | 11975.42 | 171 |  | 12154.42
12:00 | 12036.3 | 305 |  | 12355.3
13:00 | 12467.64 | 321 |  | 12802.64
14:00 | 12680.68 | 253 |  | 12944.68
15:00 | 12782.35 | 237 |  | 13030.35
16:00 | 12926.04 | 218 |  | 13154.04
17:00 | 13343.59 | 31 |  | 13375.59
18:00 | 13629.36 | 0 |  | 13629.36
19:00 | 14028.45 | 0 |  | 14028.45
19:30 | 14128.14 | 21 |  | 14150.14
20:00 | 14068.74 | 22 |  | 14091.74
21:00 | 13613.15 | 23 |  | 13637.15
22:00 | 12373.51 | 94 |  | 12471.51
23:00 | 10960.9 | 96 |  | 11060.9
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 15-03-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6598.5 | 6226.8 | 12825.3 | DAILY GENERATION CURVE
00:30 | 6529.5 | 6127.435 | 12656.935
01:00 | 6460.5 | 6028.07 | 12488.57 | 15-03-2026
01:30 | 6431.9 | 5956.06 | 12387.96
02:00 | 6403.3 | 5884.05 | 12287.35
02:30 | 6390.65 | 5870.205 | 12260.855
03:00 | 6378 | 5856.36 | 12234.36
03:30 | 6482 | 5938.875 | 12420.875
04:00 | 6586 | 6021.39 | 12607.39
04:30 | 6140.75 | 5856.33 | 11997.08
05:00 | 5695.5 | 5691.27 | 11386.77
05:30 | 5464 | 5542.87 | 11006.87
06:00 | 5232.5 | 5394.47 | 10626.97
06:30 | 5270.82 | 5402.96 | 10673.78
07:00 | 5309.14 | 5411.45 | 10720.59
07:30 | 5359.16 | 5551.235 | 10910.395
08:00 | 5409.18 | 5691.02 | 11100.2
08:30 | 5490.765 | 5806.36 | 11297.125
09:00 | 5572.35 | 5921.7 | 11494.05
09:30 | 5629.08 | 6024.61 | 11653.69
10:00 | 5685.81 | 6127.52 | 11813.33
10:30 | 5742.09 | 6152.285 | 11894.375
11:00 | 5798.37 | 6177.05 | 11975.42
11:30 | 5847.99 | 6157.87 | 12005.86
12:00 | 5897.61 | 6138.69 | 12036.3
12:30 | 5974.59 | 6277.38 | 12251.97
13:00 | 6051.57 | 6416.07 | 12467.64
13:30 | 6110.935 | 6463.225 | 12574.16
14:00 | 6170.3 | 6510.38 | 12680.68
14:30 | 6250.51 | 6481.005 | 12731.515
15:00 | 6330.72 | 6451.63 | 12782.35
15:30 | 6413.41 | 6440.785 | 12854.195
16:00 | 6496.1 | 6429.94 | 12926.04
16:30 | 6645.62 | 6489.195 | 13134.815
17:00 | 6795.14 | 6548.45 | 13343.59
17:30 | 6863.57 | 6622.905 | 13486.475
18:00 | 6932 | 6697.36 | 13629.36
18:30 | 7055.75 | 6773.155 | 13828.905
19:00 | 7179.5 | 6848.95 | 14028.45
19:30 | 7213 | 6915.14 | 14128.14
20:00 | 7170.4 | 6898.34 | 14068.74
20:30 | 7052.3 | 6788.645 | 13840.945 |  | Executive Engineer
21:00 | 6934.2 | 6678.95 | 13613.15 |  | Network Operation Division
21:30 | 6788.95 | 6204.38 | 12993.33
22:00 | 6643.7 | 5729.81 | 12373.51
22:30 | 6396.85 | 5270.355 | 11667.205
23:00 | 6150 | 4810.9 | 10960.9

## En-Curve
QF-LDC-12
Date | 15-03-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2817 | 1511 | 734 | 0 | 178 | 1446.48 | 80 | 4243.32 | 0 | 251 | 1557.5 | 0 | 0 | 7 | 43 | DAILY ENERGY CURVE
00:30 | 2788 | 1506 | 690 | 0 | 175 | 1447.615 | 80 | 4249.82 | 0 | 279 | 1435 | 0 | 0 | 6.5 | 44.5 | 15-03-2026
01:00 | 2759 | 1501 | 646 | 0 | 172 | 1448.75 | 80 | 4256.32 | 0 | 307 | 1312.5 | 0 | 0 | 6 | 46
01:30 | 2763.5 | 1510 | 764.5 | 0 | 168 | 1378.74 | 80 | 4178.82 | 0 | 271.5 | 1264.4 | 0 | 0 | 8.5 | 44.5 | Energy Generated | 298.1355 |  | MKWHr
02:00 | 2768 | 1519 | 883 | 0 | 164 | 1308.73 | 80 | 4101.32 | 0 | 236 | 1216.3 | 0 | 0 | 11 | 43 | Energy not Served | 2.223 |  | MKWHr
02:30 | 2784.5 | 1513.25 | 881 | 0 | 161 | 1321.885 | 80 | 4081.82 | 0 | 236.5 | 1193.4 | 0 | 0 | 7.5 | 44 | Total Energy Requirement | 300.3585 |  | MKWHr
03:00 | 2801 | 1507.5 | 879 | 0 | 158 | 1335.04 | 80 | 4062.32 | 0 | 237 | 1170.5 | 0 | 0 | 4 | 45
03:30 | 2846 | 1544 | 879 | 0 | 160 | 1349.055 | 80 | 4106.32 | 0 | 237 | 1214 | 0 | 0 | 5.5 | 43.5
04:00 | 2891 | 1580.5 | 879 | 0 | 162 | 1363.07 | 80 | 4150.32 | 0 | 237 | 1257.5 | 0 | 0 | 7 | 42
04:30 | 2852.5 | 1539 | 879 | 0 | 157 | 1370.17 | 80 | 4118.66 | 0 | 156.5 | 831.75 | 0 | 0 | 12.5 | 21
05:00 | 2814 | 1497.5 | 879 | 0 | 152 | 1377.27 | 80 | 4087 | 0 | 76 | 406 | 0 | 0 | 18 | 0
05:30 | 2742.5 | 1487.5 | 881 | 0 | 149 | 1326.37 | 80 | 3936 | 0 | 50.5 | 334 | 0 | 0 | 20 | 0
06:00 | 2671 | 1477.5 | 883 | 0 | 146 | 1275.47 | 80 | 3785 | 0 | 25 | 262 | 0 | 0 | 22 | 0
06:30 | 2692.5 | 1502.75 | 873.5 | 0 | 149 | 1276.925 | 80 | 3786 | 15.605 | 26 | 249 | 0 | 0 | 22.5 | 0
07:00 | 2714 | 1528 | 864 | 0 | 152 | 1278.38 | 80 | 3787 | 31.21 | 27 | 236 | 0 | 0 | 23 | 0
07:30 | 2699.5 | 1543.5 | 874 | 0 | 150 | 1271.585 | 80 | 3929 | 78.31 | 34 | 234.5 | 0 | 0 | 16 | 21
08:00 | 2685 | 1559 | 884 | 0 | 148 | 1264.79 | 80 | 4071 | 125.41 | 41 | 233 | 0 | 0 | 9 | 42
08:30 | 2681.5 | 1622 | 884 | 0 | 149 | 1274.805 | 80 | 4140.5 | 174.32 | 41 | 242.5 | 0 | 0 | 7.5 | 49.5
09:00 | 2678 | 1685 | 884 | 0 | 150 | 1284.82 | 80 | 4210 | 223.23 | 41 | 252 | 0 | 0 | 6 | 57
09:30 | 2660.5 | 1681 | 884 | 0 | 152 | 1305.93 | 80 | 4272 | 280.26 | 41 | 282 | 0 | 0 | 15 | 95.5
10:00 | 2643 | 1677 | 884 | 0 | 154 | 1327.04 | 80 | 4334 | 337.29 | 41 | 312 | 0 | 0 | 24 | 134
10:30 | 2634.5 | 1684.5 | 884 | 0 | 161 | 1331.9 | 80 | 4351 | 370.475 | 41 | 337 | 0 | 0 | 19 | 152.5
11:00 | 2626 | 1692 | 884 | 0 | 168 | 1336.76 | 80 | 4368 | 403.66 | 41 | 362 | 0 | 0 | 14 | 171
11:30 | 2620 | 1703.5 | 884 | 0 | 167 | 1338.315 | 80 | 4372.1 | 397.945 | 49.5 | 371 | 0 | 0 | 22.5 | 238
12:00 | 2614 | 1715 | 884 | 0 | 166 | 1339.87 | 80 | 4376.2 | 392.23 | 58 | 380 | 0 | 0 | 31 | 305
12:30 | 2610.5 | 1723.5 | 884 | 0 | 163 | 1402.47 | 80 | 4382.7 | 448.8 | 58 | 470.5 | 0 | 0 | 28.5 | 313
13:00 | 2607 | 1732 | 884 | 0 | 160 | 1465.07 | 80 | 4389.2 | 505.37 | 58 | 561 | 0 | 0 | 26 | 321
13:30 | 2632 | 1729.5 | 885.5 | 0 | 168 | 1462.81 | 80 | 4410.2 | 502.65 | 58 | 617.5 | 0 | 0 | 28 | 287
14:00 | 2657 | 1727 | 887 | 0 | 176 | 1460.55 | 80 | 4431.2 | 499.93 | 58 | 674 | 0 | 0 | 30 | 253
14:30 | 2658 | 1695.5 | 886.5 | 0 | 177 | 1458.095 | 80 | 4466.1 | 431.57 | 90 | 757.25 | 0 | 0 | 31.5 | 245
15:00 | 2659 | 1664 | 886 | 0 | 178 | 1455.64 | 80 | 4501 | 363.21 | 122 | 840.5 | 0 | 0 | 33 | 237
15:30 | 2713 | 1682.5 | 886 | 0 | 175 | 1455.15 | 80 | 4526 | 282.545 | 137.5 | 893.5 | 0 | 0 | 23 | 227.5
16:00 | 2767 | 1701 | 886 | 0 | 172 | 1454.66 | 80 | 4551 | 201.88 | 153 | 946.5 | 0 | 0 | 13 | 218
16:30 | 2776.5 | 1666 | 886 | 0 | 171 | 1448.1 | 80 | 4545.1 | 135.865 | 281.5 | 1133.75 | 0 | 0 | 11 | 124.5
17:00 | 2786 | 1631 | 886 | 0 | 170 | 1441.54 | 80 | 4539.2 | 69.85 | 410 | 1321 | 0 | 0 | 9 | 31
17:30 | 2774 | 1606.25 | 886.5 | 0 | 172 | 1448.8 | 80 | 4510.7 | 34.975 | 495.5 | 1472.25 | 0 | 0 | 5.5 | 15.5
18:00 | 2762 | 1581.5 | 887 | 0 | 174 | 1456.06 | 80 | 4482.2 | 0.1 | 581 | 1623.5 | 0 | 0 | 2 | 0
18:30 | 2757 | 1576.75 | 886.5 | 0 | 172 | 1453.005 | 80 | 4476.6 | 0.05 | 590 | 1836 | 0 | 0 | 1 | 0
19:00 | 2752 | 1572 | 886 | 0 | 170 | 1449.95 | 80 | 4471 | 0 | 599 | 2048.5 | 0 | 0 | 0 | 0
19:30 | 2795 | 1601 | 887 | 0 | 168 | 1457.14 | 80 | 4524 | 0 | 539 | 2077 | 0 | 0 | 0 | 21
20:00 | 2836 | 1592.5 | 886 | 0 | 170 | 1460.34 | 80 | 4543 | 0 | 542 | 1958.9 | 0 | 0 | 0 | 22
20:30 | 2830.5 | 1594 | 886 | 0 | 171 | 1460.045 | 80 | 4551.6 | 0 | 466 | 1797.3 | 0 | 0 | 4.5 | 22.5
21:00 | 2825 | 1595.5 | 886 | 0 | 172 | 1459.75 | 80 | 4560.2 | 0 | 390 | 1635.7 | 0 | 0 | 9 | 23
21:30 | 2777 | 1575 | 886 | 0 | 172 | 1359.28 | 80 | 4485.1 | 0 | 335.5 | 1312.45 | 0 | 0 | 11 | 58.5
22:00 | 2729 | 1554.5 | 886 | 0 | 172 | 1258.81 | 80 | 4410 | 0 | 281 | 989.2 | 0 | 0 | 13 | 94
22:30 | 2709.5 | 1540 | 885.5 | 0 | 174 | 1094.855 | 80 | 4154 | 0 | 258.5 | 758.35 | 0 | 0 | 12.5 | 95
23:00 | 2690 | 1525.5 | 885 | 0 | 176 | 930.9 | 80 | 3898 | 0 | 236 | 527.5 | 0 | 0 | 12 | 96
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 15-03-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 391 | 01:00 | 373 | 10:00 | Madunaghat | 404 | 03:00 | 393 | 10:00
Amtali | 413 | 03:00 | 406 | 14:00 | Meghnaghat | 396 | 04:00 | 374 | 11:00
Ashuganj | 407 | 2:00 | 380 | 15:00 | Payra | 415 | 02:00 | 408 | 11:00
Bhulta | 399 | 02:00 | 368 | 10:00 | Rahanpur | 417 | 23:00 | 394 | 14:00
Bibiana | 409 | 02:00 | 396 | 10:00 | Rampal | 405 | 06:00 | 390 | 14:00
BIPTC | 405 | 01:00 | 393 | 13:00
Bogura | 403 | 23:00 | 378 | 13:00
Gopalganj | 402 | 06:00 | 359 | 10:00
Kaliakoir | 389 | 02:00 | 366 | 14:00
Korerhat | 404 | 02:00 | 388 | 14:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 239 | 00:00 | 216 | 11:00 | Jhenaidah | 234 | 22:00 | 219 | 14:00
AKSML | 234.2 | 04:00 | 224.6 | 14:00 | Kachua | 232 | 02:00 | 220 | 10:00
Aminbazar | 233 | 03:00 | 218 | 10:00 | Kaliakoir | 236 | 02:00 | 221 | 10:00
Ashuganj | 230 | 00:00 | 221 | 09:00 | Keranigonj | 231 | 04:00 | 216 | 10:00
Ashuganj-400 | 230 | 00:00 | 221 | 09:00 | Khulna(S) | 231 | 06:00 | 221 | 14:00
Baghabari | 236 | 23:00 | 223 | 14:00 | Korerhat | 230 | 01:00 | 222 | 10:00
Barapukuria | 225 | 23:00 | 208 | 09:00 | Madunaghat | 233 | 03:00 | 226 | 09:00
Barapukuria-230 | 225 | 23:00 | 208 | 09:00 | Madunaghat-400 | 234 | 02:00 | 227 | 12:00
Barishal | 229 | 02:00 | 223 | 14:00 | Maniknagar | 230 | 02:00 | 216 | 11:00
Bheramara | 235 | 01:00 | 222 | 13:00 | Meghnaghat | 239 | 04:00 | 224 | 16:00
Bhulta | 232 | 01:00 | 216 | 10:00 | Meghnaghat-400 | 234 | 04:00 | 220 | 10:00
Bibiana | 237 | 02:00 | 228 | 12:00 | Mirsorai | 237 | 02:00 | 228 | 14:00
BIPTC | 237 | 22:00 | 222 | 14:00 | Purbasadipur | 224 | 19:00 | 205 | 10:00
Bogura | 241 | 23:00 | 225 | 14:00 | Rajshahi | 236 | 22:00 | 220 | 14:00
Bogura-400 | 240 | 23:00 | 225 | 10:00 | Rampal | 231 | 06:00 | 221 | 14:00
Borhanuddin | 233 | 04:00 | 229 | 14:00 | Rampur | N/A | N/A | N/A | N/A
BSRM | 230 | 02:00 | 222 | 10:00 | Rampura | 232 | 04:00 | 215 | 10:00
Chowmuhani | N/A | N/A | N/A | N/A | Shikalbaha | 231 | 00:00 | 226 | 11:00
Cumilla(N) | 231 | 02:00 | 219 | 11:00 | Shyampur | 232 | 02:00 | 217 | 10:00
Faridpur | 225 | 06:00 | 217 | 14:00 | Siddhirganj | 231 | 04:00 | 220 | 14:00
Fenchuganj | 241 | 01:00 | 234 | 14:00 | Sirajgonj | 239 | 23:00 | 229 | 14:00
Feni | 231 | 02:00 | 221 | 10:00 | Sreepur | 226 | 01:00 | 215 | 16:00
Ghorashal | 230 | 00:00 | 220 | 12:00 | Tongi | 233 | 01:00 | 214 | 10:00
Ghorashal-230 | 229 | 01:00 | 214 | 11:00
Gopalganj | 225 | 06:00 | 216 | 15:00
GPH | 232 | 02:00 | 220 | 05:00
Haripur | 232 | 04:00 | 217 | 11:00
Hasnabad | 232 | 03:00 | 216 | 10:00
Hathazari | 230 | 00:00 | 221 | 11:00
Ishurdi | 237 | 22:00 | 224 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 132 | 02:00 | 121 | 10:00 | Madunaghat | 134 | 03:00 | 130 | 09:00
Agargaon | 137 | 02:00 | 126 | 11:00 | Magura | 135 | 19:30 | 122 | 14:00
Agrabad | 132 | 02:00 | 127 | 14:00 | Mahasthangarh | 140 | 23:00 | 127 | 10:00
AKS | 131 | 02:00 | 126 | 09:00 | Maijdee | 128 | 02:00 | 122 | 13:00
Aminbazar | 136 | 01:00 | 122 | 11:00 | Manikganj | 134 | 04:00 | 122 | 11:00
Amnura | 139 | 23:00 | 126 | 14:00 | Maniknagar | 136 | 04:00 | 126 | 10:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 119 | 08:00 | 111 | 18:00
Ashuganj-230 | 140 | 01:00 | 133 | 14:00 | Matuail | 136 | 02:00 | 127 | 13:00
Bagerhat | 132 | 06:00 | 124 | 00:00 | Metrorail_Motijheel | 139 | 08:00 | 126 | 10:00
Bajitpur | 132 | 00:00 | 126 | 15:00 | Metrorail_Uttara | 134 | 01:00 | 122 | 10:00
Bakerganj | 133 | 00:00 | 129 | 15:00 | Millgate | 140 | 02:00 | 127 | 10:00
Bakulia | 133 | 04:00 | 127 | 14:00 | Mirpur | 133 | 00:00 | 122 | 11:00
Banani | 140 | 04:00 | 126 | 10:00 | Mirzapur | 139 | 23:00 | 125 | 11:00
Bangabhaban | 136 | 03:00 | 126 | 11:00 | Mithapukur | 137 | 23:00 | 124 | 12:00
Barapukuria | 139 | 23:00 | 126 | 09:00 | MI_Cement | 136 | 04:00 | 123 | 11:00
Barguna | 133 | 05:00 | 129 | 14:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 133 | 03:00 | 128 | 14:00 | Mogbazar | 133 | 04:00 | 121 | 11:00
Barishal-230 | 133 | 01:00 | 128 | 13:00 | Mongla | 131 | 06:00 | 124 | 14:00
Baroaulia | 135 | 00:00 | 130 | 09:00 | Motijheel | 136 | 03:00 | 126 | 11:00
Baroirhat | 132 | 01:00 | 125 | 10:00 | Muktagacha | 143 | 23:00 | 123 | 17:00
Bashundhara | 139 | 01:00 | 121 | 10:00 | Munshiganj | 135 | 00:00 | 126 | 08:00
BashundharaCement | 135 | 00:00 | 129 | 13:00 | Muradnagar | 130 | 02:00 | 124 | 10:00
Beanibazar | 135 | 00:00 | 127 | 17:00 | Mymensingh | 142 | 23:00 | 119 | 18:00
Benapole | 139 | 21:00 | 117 | 14:00 | Naogaon | 142 | 23:00 | 123 | 13:00
Bhaluka | 135 | 23:00 | 127 | 10:00 | Narail | 135 | 20:00 | 122 | 14:00
Bhandaria | 130 | 04:00 | 121 | 21:00 | Narinda | 136 | 04:00 | 126 | 10:00
Bhangura | 137 | 23:00 | 125 | 13:00 | Narshingdi | 131 | 18:30 | 119 | 22:00
Bheramara | 136 | 22:00 | 130 | 14:00 | Natore | 137 | 22:00 | 126 | 14:00
Bheramara(GK) | 136 | 22:00 | 131 | 12:00 | Nawabganj | 135 | 04:00 | 125 | 10:00
Bhulta | 130 | 18:00 | 122 | 11:00 | Netrakona | 130 | 00:00 | 119 | 18:00
Bog-Sherpur | 141 | 23:00 | 127 | 10:00 | New | 140 | 03:00 | 128 | 10:00
Bogura | 142 | 23:00 | 130 | 09:00 | Niamatpur | 140 | 23:00 | 129 | 13:00
Bogura-230 | 141 | 23:00 | 130 | 10:00 | Noapara | 133 | 22:00 | 124 | 14:00
Brahmanbaria | 135 | 03:00 | 124 | 14:00 | Pabna | 137 | 23:00 | 128 | 12:00
Cantonment | 137 | 02:00 | 126 | 11:00 | Palashbari | 138 | 23:00 | 123 | 10:00
Chandina | 133 | 01:00 | 126 | 14:00 | Panchagarh | 140 | 19:00 | 126 | 09:00
Chandpur | 135 | 18:30 | 124 | 10:00 | Patiya | 131 | 02:00 | 126 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 134 | 00:00 | 130 | 14:00 | Patuakhali | 134 | 00:00 | 129 | 13:00
Chapai | 140 | 23:00 | 129 | 14:00 | Payra | 136 | 01:00 | 132 | 14:00
Charsaidpur | 136 | 00:00 | 127 | 10:00 | PHP | 131 | 07:00 | 125 | 10:00
Chauddagram | 131 | 04:00 | 124 | 11:00 | Postogola | 138 | 04:00 | 126 | 11:00
Chhatak | 136 | 00:00 | 125 | 17:00 | Pubail | 137 | 18:00 | 126 | 09:00
Chowmuhani | 128 | 19:00 | 122 | 10:00 | Purbachal | 139 | 02:00 | 126 | 11:00
Chuadanga | 136 | 21:00 | 120 | 14:00 | Purbasadipur | 134 | 18:30 | 122 | 09:00
Coxsbazar | 118 | 03:00 | 114 | 00:00 | Rahanpur | 140 | 23:00 | 132 | 10:00
Cumilla(N) | 133 | 02:00 | 126 | 14:00 | Rahanpur-400 | 141 | 23:00 | 131 | 14:00
Cumilla(S) | 132 | 00:00 | 122 | 12:00 | Rahim | 135 | 01:00 | 128 | 10:00
Daganbhuiyan | 129 | 01:00 | 124 | 10:00 | Rajbari | 129 | 06:00 | 123 | 13:00
Daudkandi | 130 | 03:00 | 122 | 09:00 | Rajendrapur | 140 | 23:00 | 126 | 09:00
DhakaUniversity | 131 | 01:00 | 121 | 11:00 | Rajshahi | 136 | 22:00 | 124 | 14:00
Dhamrai | 138 | 00:00 | 127 | 09:00 | Rajshahi-230 | 137 | 22:00 | 126 | 14:00
Dhanmondi | 137.5 | 04:00 | 129 | 10:00 | Ramganj | 130 | 20:00 | 122 | 12"00
Dohazari | 127 | 05:00 | 123 | 14:00 | Rampur | 133 | 04:00 | 127 | 14:00
Faridpur | 130 | 01:00 | 126 | 10:00 | Rampura | 132 | 02:00 | 121 | 11:00
Fatullah | 136 | 02:00 | 123 | 11:00 | Rangamati | 134 | 05:00 | 128 | 14:00
Fenchuganj | 137 | 01:00 | 132 | 14:00 | Rangpur | 136 | 23:00 | 125 | 13:00
Feni | 128 | 06:00 | 124 | 11:00 | Ruppur | 137 | 22:00 | 131 | 10:00
Feni-230 | 129 | 00:00 | 124 | 10:00 | Saidpur | 135 | 19:30 | 124 | 10:00
Ghatail | 143 | 23:00 | 122 | 14:00 | Satkhira | 134 | 21:00 | 123 | 14:00
Ghorashal | 138 | 04:00 | 129 | 14:00 | Satmasjid | 137 | 02:00 | 126 | 11:00
Goalpara | 135 | 06:00 | 128 | 14:00 | Savar | 137 | 03:00 | 120 | 11:00
Gollamari | 135 | 06:00 | 128 | 13:00 | SevenRings | 138 | 01:00 | 127 | 10:00
Gopalganj | 133 | 06:00 | 125 | 12:00 | ShahCement | 136 | 00:00 | 127 | 10:00
Gopalganj-400 | 134 | 06:00 | 128 | 14:00 | Shahjadpur | 140 | 23:00 | 130 | 10:00
Gulshan | 132 | 03:00 | 121 | 11:00 | Shahjibazar | 137 | 01:00 | 127 | 21:00
Halishahar | 133 | 02:00 | 127 | 14:00 | Shahmirpur | 133 | 04:00 | 128 | 14:00
Haripur | 136 | 01:00 | 128 | 10:00 | Shariatpur | 132 | 06:00 | 126 | 13:00
HaripurSBU | 139 | 16:00 | 129 | 14:00 | Sherpur | 140 | 23:00 | 123 | 13:00
Hasnabad | 138 | 04:00 | 126 | 10:00 | Shikalbaha | 122 | 00:00 | 117 | 14:00
Hathazari | 134 | 20:00 | 129 | 14:00 | Shikalbaha-230 | 133 | 03:00 | 129 | 10:00
Hatirjheel | 132 | 02:00 | 122 | 10:00 | Shitalakhya | 136 | 04:00 | 123 | 11:00
Ishurdi | 139 | 22:00 | 132 | 10:00 | Sholosohor | 134 | 04:00 | 129 | 14:00
Jaldhaka | 133 | 19:00 | 121 | 09:00 | Shyampur | 130 | 02:00 | 122 | 11:00
Jamalpur | 144 | 23:00 | 123 | 13:00 | Shyampur-230 | 134 | 04:00 | 124 | 10:00
Jashore | 139 | 21:00 | 122 | 13:00 | Siddhirganj | 136 | 01:00 | 128 | 10:00
Jhenaidah | 137 | 22:00 | 118 | 14:00 | Sirajganj | 138 | 23:00 | 125 | 10:00
Jhenaidah-230 | 136 | 22:00 | 124 | 14:00 | Sonargaon | 132 | 00:00 | 125 | 08:00
Joydebpur | 135 | 18:30 | 123 | 10:00 | Sreemongol | 136 | 01:00 | 128 | 17:00
Joypurhat | 140 | 23:00 | 123 | 14:00 | Sreepur | 138 | 23:00 | 130 | 16:00
Juldah | 132 | 01:00 | 127 | 14:00 | Srinagar | 135 | 03:00 | 125 | 11:00
Kabirpur | 138 | 23:00 | 127 | 10:00 | SSM | 140 | 03:00 | 132 | 10:00
Kachua | 132 | 01:00 | 125 | 11:00 | Sunamganj | 135 | 00:00 | 125 | 17:00
Kaliakoir | 142 | 02:00 | 131 | 11:00 | Sylhet | 135 | 00:00 | 128 | 16:00
Kaliganj | 137 | 21:00 | 124 | 13:00 | Sylhet-132 | 134 | 00:00 | 128 | 16:00
Kallyanpur | 136 | 04:00 | 122 | 11:00 | Tangail | 141 | 23:00 | 122 | 11:00
Kalurghat | 135 | 02:00 | 129 | 14:00 | Taraganj | 135 | 19:30 | 123 | 09:00
Kamrangirchar | 135 | 01:00 | 121 | 11:00 | Tasnim | 134 | 02:00 | 126 | 10:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 139 | 19:00 | 123 | 09:00
Kasba | 130 | 03:00 | 123 | 10:00 | TK | 134 | 04:00 | 130 | 11:00
Kazla | 136 | 03:00 | 125 | 13:00 | Tongi | 140 | 01:00 | 128 | 10:00
Keranigonj | 136 | 04:00 | 125 | 10:00 | Ullahpara | 138 | 23:00 | 126 | 10:00
Khagrachori | 133 | 03:00 | 128 | 14:00 | Ullon | 133 | 16:00 | 121 | 14:00
Khulna | 135 | 06:00 | 128 | 13:00 | Uttara | 136 | 02:00 | 122 | 10:00
Khulna(S) | 136 | 06:00 | 128 | 14:00 | UttaraNew | 136 | 02:00 | 121 | 11:00
Khulshi | 131 | 02:00 | 126 | 14:00 | Zigatola | 135 | 01:00 | 126 | 10:00
Kishoreganj | 132 | 06:00 | 125 | 14:00
Kodda | 140 | 22:00 | 122 | 09:00
Korerhat | 134 | 02:00 | 125 | 15:00
KSRM | 133 | 01:00 | 129 | 10:00
Kulaura | 137 | 00:00 | 131 | 16:00
Kurigram | 132 | 00:00 | 121 | 09:00
Kushtia | 136 | 22:00 | 122 | 02:00
Laksam | 132 | 01:00 | 124 | 11:00
Lakshmipur | 128 | 01:00 | 122 | 11:00
Lalbag | 135 | 02:00 | 125 | 10:00
Lalmonirhat | 133 | 23:00 | 123 | 17:00
Madanganj | 135 | 00:00 | 127 | 08:00
Madaripur | 132 | 06:00 | 128 | 13:00
Madartek | 132 | 04:00 | 120 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division