## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 17-03-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-03-2026 | during | 17-03-2026 | during | 17-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 6 | 6 | 97.7 | 97.7 | 7 | 7 | Demand "05"MW due to gas restiction by Titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 331 | 284 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 250 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 51.4 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 30 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 10 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 22 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 42 | 49 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 20 | 195 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 47 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 58 | 140 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 12 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 330 | 340 | 584 | 584 | 320 | 320 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 345 | 330 | 583 | 583 | 320 | 320 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 70 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1642 | 2224.4 | 5945.22 | 5915.22 | 2724.05 | 2694.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 80 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 222 | 220 | 220 | 220 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 | 56 | 64 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 4 | 18 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 15 | 61 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.56 | 0 | 3.25 | 0 | 3.25 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1140 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 25 | 7 | 3 | 1 | 3 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 580 | 580 | 680 | 680 | 580 | 580 | Coal shortage
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2154.56 | 2209 | 3516.11 | 3507.86 | 2886.75 | 2886.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 206 | 197 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 150 | 150 | 150 | 150 | 150 | 150 | Vibration
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 342 | 270 | 342.01 | 342.01 | 340 | 340 | FGMO ON
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 20 | 20 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 1 | 140 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 14 | 32 | 32 | 32 | 32 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 96 | 100 | 163 | 163 | 100 | 100 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 1 | 136 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 158 | 172 | 84 | 80 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 95 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 37 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2876.261 | 1056 | 1345 | 2556.36 | 2492.36 | 1947.2 | 1887.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-03-2026 | during | 17-03-2026 | during | 17-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 10 | 9 | 157.5 | 157.5 | 10 | 10 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 0 | 0 | 0 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 16 | 78 | 60 | 80 | 60 | 80 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 98 | 70 | 115 | 70 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 43.34 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | From12:00 hrs to24:00 hrs will be dispatching12MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 35 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 115.34 | 197 | 409 | 429 | 214 | 252
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 41 | 41 | 41 | 41 | 41 | plant availability zero
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 159 | 155 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 100 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 0 | 0 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 5 | 85 | 85 | 42 | 42 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 98 | 98 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 21 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 305 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 392 | 387 | 385 | 385 | 385 | 385 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1138 | 1142 | 1190 | 1190 | 1094 | 1094
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 898 | 897 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 216 | 175 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 94 | 0 | 84 | 0 | 84 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 793 | 1202 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2001 | 2291 | 3590.2 | 3506.2 | 2625.1 | 2541.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 127 | 125 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 660 | 1190 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 58 | 150 | 150 | 75 | 75 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 169 | 257 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.63 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1176.63 | 1850 | 2162 | 2161 | 1993 | 1992
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 53.88 | 0 | 55 | 0 | 55 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 7 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 184 | 182 | 220 | 220 | 190 | 190 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 357 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 18 | 21 | 21 | 21 | 21 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 42 | 50 | 50 | 50 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 80 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.73 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1189 | 1447 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 47.76 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 110 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2003.37 | 2286 | 3185.57 | 2963.87 | 2689.57 | 2467.87
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 54 | 55 | 55 | 55 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 90 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.1 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 21 | 0 | 21 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 197 | 0 | 168.69 | 0 | 168.69 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 291.1 | 260 | 497.89 | 303 | 422.89 | 228
System Total |  |  |  |  | 28823.2 | 29275.503 | 11578 | 13804.4 | 23052.35 | 22468.51 | 16596.56 | 16042.72
Forecast Scenario (17-03-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12800 |  | 0 |  | 12800
|  |  |  | 1:00 | 11900 |  | 0 |  | 11900
|  |  |  | 2:00 | 11650 |  | 0 |  | 11650
|  |  |  | 3:00 | 11600 |  | 0 |  | 11600
|  |  |  | 4:00 | 11660 |  | 0 |  | 11660
|  |  |  | 5:00 | 10370 |  | 0 |  | 10370
|  |  |  | 6:00 | 9640 |  | 0 |  | 9640
|  |  |  | 7:00 | 9390 |  | 0 |  | 9390
|  |  |  | 8:00 | 9760 |  | 0 |  | 9760
|  |  |  | 9:00 | 10230 |  | 0 |  | 10230
|  |  |  | 10:00 | 10430 |  | 0 |  | 10430
|  |  |  | 11:00 | 10720 |  | 0 |  | 10720
|  |  |  | 12:00 | 10900 |  | 0 |  | 10900
|  |  |  | 13:00 | 11350 |  | 0 |  | 11350
|  |  |  | 14:00 | 11660 |  | 0 |  | 11660
|  |  |  | 15:00 | 12020 |  | 0 |  | 12020
|  |  |  | 16:00 | 11880 |  | 0 |  | 11880
|  |  |  | 17:00 | 11900 |  | 0 |  | 11900
|  |  |  | 18:00 | 12200 |  | 0 |  | 12200
|  |  |  | 18:30 | 12350 |  | 0 |  | 12350
|  |  |  | 19:00 | 12510 |  | 0 |  | 12510
|  |  |  | 19:30 | 12900 |  | 0 |  | 12900
|  |  |  | 20:00 | 12830 |  | 0 |  | 12830
|  |  |  | 21:00 | 12650 |  | 0 |  | 12650
|  |  |  | 22:00 | 12570 |  | 0 |  | 12570
|  |  |  | 23:00 | 11920 |  | 0 |  | 11920
Probable Maximum Temperature: |  |  | 29.50°C
Probable Maximum Demand at Day Peak: |  |  | 10900.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12900.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12900.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 274.54 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:15 hrs on 17-03-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 16-03-2026 | [28 empty] | Date: | 16-03-2026 | [28 empty] | Date: | 16-03-2026 | [28 empty] | Date: | 16-03-2026 | [28 empty] | Date: | 16-03-2026 | [17 empty] | Date: | 16-03-2026
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [17 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 342.010 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 6 | 312 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 21.5 | 22 | 0 | 340 | 0 | 0 | 40 | 0 | 9 | 51 | 15 | 0 | 0 | 0 | 0 | 80 | 0 | 18 | 580 | 0 | 0 | 50 | 8 | 0 | 226 | 0 | 0 | 0 | 1170 | 0 | 0 | 0 | 0 | 150 | 305 | 51 | 0 | 187 | 10 | 0 | 100 | 0 | 0 | 20 | 0 | 174 | 0 | 0 | 0 | 310 | 0 | 338 | 41 | 0 | 137 | 0 | 0 | 0 | 82 | 30 | 0 | 0 | 96 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 5632.5 | 884 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 850 | 3 | 0 | 0 | 825.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 110 | 180 | 0 | 0 | 850 | 0 | 4516.81 | 10149.31 | 88.27
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 6 | 317 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 340 | 0 | 0 | 38 | 0 | 0 | 51 | 15 | 0 | 0 | 0 | 0 | 80 | 0 | 15 | 580 | 0 | 0 | 50 | 0 | 0 | 226 | 0 | 0 | 0 | 965 | 0 | 0 | 0 | 0 | 150 | 335 | 51 | 0 | 178 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 174 | 0 | 0 | 0 | 310 | 0 | 341 | 41 | 0 | 138 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 98 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 5331 | 882 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 0 | 0 | 0 | 828.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 127 | 180 | 0 | 0 | 846 | 0 | 4493.65 | 9824.65 | 88.26
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 6 | 326 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 365 | 0 | 0 | 39 | 0 | 0 | 51 | 15 | 0 | 0 | 0 | 0 | 80 | 0 | 24 | 580 | 0 | 0 | 50 | 0 | 0 | 225 | 0 | 0 | 0 | 965 | 0 | 0 | 0 | 0 | 150 | 345 | 51 | 0 | 173 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 152 | 0 | 0 | 0 | 310 | 0 | 346 | 41 | 0 | 143 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 98 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 5379 | 882 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 0 | 0 | 0 | 832.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 130 | 180 | 0 | 0 | 850 | 0 | 4474.55 | 9853.55 | 88.25
03:00 | 0 | 34 | 13 | 0 | 0 | 0 | 0 | 6 | 323 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 310 | 0 | 0 | 39 | 0 | 4 | 51 | 15 | 0 | 0 | 0 | 0 | 80 | 0 | 27 | 580 | 0 | 0 | 50 | 0 | 0 | 226 | 0 | 0 | 0 | 1045 | 0 | 0 | 0 | 0 | 150 | 345 | 51 | 0 | 165 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 160 | 0 | 0 | 0 | 315 | 0 | 346 | 41 | 0 | 141 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 98 | 0 | 8 | 8 | 18 | 0 | 0 | 0 | 5443 | 883 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 830 | 0 | 0 | 0 | 828.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244 | 130 | 180 | 0 | 0 | 878 | 0 | 4637.06 | 10080.06 | 88.24
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 6 | 326 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 310 | 0 | 0 | 39 | 0 | 16 | 51 | 15 | 0 | 0 | 0 | 0 | 80 | 0 | 20 | 580 | 0 | 0 | 50 | 0 | 0 | 226 | 0 | 0 | 0 | 1060 | 0 | 0 | 0 | 0 | 150 | 300 | 51 | 0 | 160 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 156 | 0 | 0 | 0 | 305 | 0 | 342 | 41 | 0 | 137 | 0 | 8 | 0 | 0 | 30 | 0 | 0 | 98 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 5370 | 882 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 890 | 0 | 0 | 0 | 904.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 130 | 220 | 0 | 0 | 944 | 0 | 5044.07 | 10414.07 | 88.23
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 21.5 | 22 | 0 | 330 | 0 | 0 | 39 | 0 | 5 | 51 | 15 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 580 | 0 | 0 | 50 | 0 | 0 | 226 | 0 | 0 | 0 | 850 | 0 | 0 | 0 | 0 | 150 | 300 | 0 | 0 | 196 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 148 | 0 | 0 | 0 | 305 | 0 | 390 | 41 | 0 | 138 | 0 | 17 | 0 | 0 | 30 | 0 | 0 | 98 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 5132.5 | 883 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 815 | 0 | 0 | 0 | 835.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 130 | 180 | 0 | 0 | 600 | 0 | 4370.21 | 9502.71 | 88.22
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 21.5 | 22 | 0 | 310 | 0 | 0 | 30 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 580 | 0 | 0 | 50 | 0 | 0 | 175 | 0 | 0 | 0 | 830 | 0 | 0 | 0 | 0 | 150 | 260 | 0 | 0 | 170 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 138 | 0 | 0 | 0 | 310 | 0 | 317 | 41 | 0 | 137 | 0 | 17 | 0 | 0 | 30 | 0 | 0 | 98 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 4820.5 | 882 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 0 | 0 | 0 | 829.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 130 | 180 | 0 | 0 | 600 | 0 | 4221.48 | 9041.98 | 88.21
07:00 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 6 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 250 | 0 | 0 | 2 | 0 | 21.5 | 22 | 0 | 330 | 0 | 0 | 18 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0.44 | 80 | 0 | 17 | 580 | 0 | 0 | 50 | 0 | 0 | 173 | 0 | 0 | 0 | 850 | 2 | 0 | 0 | 0 | 150 | 260 | 0 | 0 | 140 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 136 | 0 | 7 | 0 | 310 | 0 | 345 | 41 | 0 | 137 | 0 | 17 | 0 | 0 | 30 | 0 | 0 | 98 | 0 | 0 | 0 | 19 | 0 | 6.96 | 0 | 4850.9 | 882 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 762 | 0 | 0 | 0 | 833.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.08 | 6 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 270 | 0 | 0.44 | 0 | 55 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 18 | 0.58 | 0 | 140 | 100 | 180 | 0 | 0 | 600 | 0 | 4221.67 | 9072.57 | 88.2
08:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 6 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 250 | 0 | 0 | 12 | 0 | 21 | 22 | 0 | 335 | 0 | 0 | 18 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 1.28 | 80 | 0 | 4 | 580 | 0 | 0 | 50 | 0 | 0 | 173 | 0 | 0 | 0 | 864 | 7 | 0 | 0 | 0 | 150 | 300 | 0 | 0 | 201 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 146 | 0 | 18 | 0 | 310 | 0 | 357 | 41 | 0 | 163 | 0 | 0 | 0 | 55 | 30 | 0 | 0 | 98 | 0 | 0 | 0 | 18 | 0 | 10.42 | 0 | 5150.7 | 881 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 780 | 0 | 0 | 0 | 843.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.93 | 35 | 0 | 0 | 14.89 | 0 | 0 | 140 | 0 | 0 | 0 | 386 | 0 | 1.34 | 0 | 55 | 0 | 9 | 0 | 0 | 0 | 0 | 1.6 | 64 | 0.16 | 0 | 201 | 100 | 220 | 0 | 0 | 600 | 0 | 4571.89 | 9722.59 | 88.19
09:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 6 | 334 | 0 | 0 | 0 | 5 | 12 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 250 | 0 | 0 | 19 | 0 | 21 | 21 | 0 | 310 | 0 | 0 | 18 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 1.47 | 80 | 0 | 5 | 580 | 0 | 0 | 50 | 0 | 0 | 173 | 0 | 0 | 0 | 947 | 9 | 0 | 0 | 0 | 150 | 345 | 51 | 0 | 202 | 0 | 0 | 99 | 0 | 0 | 20 | 0 | 150 | 0 | 31 | 0 | 305 | 0 | 362 | 41 | 0 | 163 | 0 | 17 | 0 | 77 | 30 | 0 | 0 | 99 | 0 | 0 | 0 | 16 | 0 | 28.72 | 0 | 5441.19 | 885 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 818 | 0 | 0 | 0 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.45 | 69 | 0 | 0 | 36.04 | 0 | 0 | 180 | 0 | 0 | 0 | 366 | 0 | 3.22 | 0 | 54 | 0 | 21 | 0 | 0 | 0 | 0 | 1.7 | 115 | 0.11 | 0 | 230 | 127 | 220 | 0 | 0 | 690 | 0 | 5019.52 | 10460.71 | 88.18
10:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 6 | 312 | 0 | 0 | 17 | 17 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 250 | 0 | 0 | 23 | 0 | 21 | 21 | 0 | 310 | 0 | 0 | 14 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 3.08 | 80 | 0 | 5 | 580 | 0 | 0 | 50 | 0 | 0 | 173 | 0 | 0 | 0 | 950 | 15 | 0 | 0 | 0 | 150 | 345 | 51 | 0 | 195 | 0 | 0 | 98 | 0 | 0 | 9 | 0 | 158 | 0 | 60 | 0 | 305 | 0 | 391 | 41 | 0 | 156 | 10 | 17 | 0 | 80 | 30 | 0 | 0 | 98 | 0 | 0 | 0 | 16 | 0 | 37.8 | 0 | 5522.88 | 886 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 888 | 0 | 0 | 0 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.88 | 77 | 0 | 0 | 47.74 | 0 | 0 | 183 | 0 | 0 | 0 | 346 | 0 | 4.3 | 0 | 55 | 0 | 28 | 0 | 0 | 0 | 0 | 4.5 | 162 | 0.5 | 0 | 248 | 127 | 220 | 0 | 0 | 845 | 0 | 5383.92 | 10906.8 | 88.17
11:00 | 0 | 45 | 42 | 0 | 0 | 0 | 0 | 6 | 330 | 0 | 0 | 17 | 17 | 26 | 0 | 0 | 0 | 17 | 31 | 0 | 0 | 0 | 330 | 0 | 0 | 280 | 0 | 0 | 26 | 0 | 21 | 21 | 0 | 310 | 0 | 0 | 12 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 2.91 | 80 | 0 | 3 | 580 | 0 | 0 | 50 | 0 | 0 | 222 | 0 | 0 | 0 | 1160 | 8 | 0 | 0 | 0 | 150 | 345 | 44 | 0 | 200 | 0 | 0 | 96 | 0 | 0 | 14 | 0 | 162 | 0 | 56 | 0 | 310 | 0 | 390 | 41 | 0 | 139 | 11 | 17 | 0 | 79 | 30 | 0 | 0 | 99 | 0 | 5 | 2 | 10 | 2 | 44.9 | 0 | 5906.81 | 886 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 849 | 0 | 0 | 0 | 949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.98 | 102 | 0 | 0 | 55.78 | 0 | 0 | 184 | 0 | 0 | 0 | 414 | 0 | 4.91 | 0 | 55 | 0 | 33 | 0 | 0 | 0 | 0 | 4.7 | 189 | 0.41 | 0 | 177 | 127 | 220 | 0 | 0 | 720 | 0 | 5321.78 | 11228.59 | 88.16
12:00 | 0 | 50 | 42 | 0 | 0 | 0 | 0 | 6 | 331 | 0 | 0 | 17 | 17 | 47 | 0 | 20 | 0 | 35 | 58 | 0 | 0 | 0 | 345 | 0 | 10 | 280 | 0 | 0 | 12 | 0 | 21 | 21 | 0 | 330 | 0 | 0 | 15 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 2.56 | 80 | 0 | 4 | 580 | 0 | 0 | 50 | 0 | 0 | 219 | 0 | 0 | 0 | 1160 | 19 | 1 | 0 | 0 | 150 | 342 | 51 | 0 | 206 | 0 | 0 | 96 | 1 | 0 | 14 | 0 | 158 | 0 | 37 | 0 | 310 | 0 | 392 | 41 | 0 | 159 | 12 | 17 | 0 | 79 | 30 | 0 | 0 | 98 | 0 | 45 | 16 | 10 | 1 | 43.34 | 0 | 6105.9 | 898 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 793 | 0 | 0 | 0 | 1189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.88 | 110 | 0 | 0 | 47.76 | 0 | 0 | 184 | 0 | 0 | 0 | 414 | 0 | 4.73 | 0 | 54 | 0 | 35 | 0 | 0 | 0 | 0 | 5.1 | 197 | 0.63 | 0 | 169 | 127 | 220 | 0 | 0 | 660 | 0 | 5472.1 | 11578 | 88.15
13:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 6 | 328 | 0 | 0 | 17 | 17 | 51 | 0 | 90 | 10 | 35 | 100 | 0 | 0 | 0 | 355 | 0 | 17 | 280 | 0 | 0 | 29 | 0 | 20 | 14 | 0 | 310 | 0 | 0 | 18 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 3.68 | 80 | 0 | 8 | 580 | 0 | 0 | 50 | 0 | 0 | 220 | 0 | 0 | 0 | 1160 | 14 | 24 | 0 | 0 | 150 | 345 | 51 | 0 | 194 | 0 | 11 | 96 | 16 | 0 | 14 | 0 | 172 | 0 | 63 | 0 | 305 | 0 | 350 | 42 | 0 | 158 | 12 | 17 | 0 | 81 | 30 | 0 | 0 | 98 | 0 | 45 | 16 | 10 | 2 | 17.82 | 4 | 6258.5 | 897 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 887 | 0 | 0 | 0 | 1359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.16 | 86 | 0 | 0 | 59.84 | 0 | 0 | 184 | 0 | 0 | 0 | 403 | 0 | 5.48 | 0 | 55 | 0 | 35 | 0 | 0 | 0 | 0 | 6.2 | 195 | 0.22 | 0 | 247 | 127 | 220 | 0 | 0 | 650 | 0 | 5742.9 | 12001.4 | 88.14
14:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 6 | 327 | 0 | 0 | 17 | 17 | 51 | 0 | 125 | 15 | 35 | 108 | 0 | 0 | 0 | 375 | 0 | 17 | 280 | 0 | 0 | 23 | 17 | 0 | 21 | 0 | 330 | 0 | 0 | 18 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 2.96 | 80 | 0 | 3 | 580 | 0 | 0 | 50 | 0 | 0 | 219 | 0 | 0 | 0 | 1173 | 15 | 24 | 0 | 0 | 150 | 338 | 51 | 0 | 211 | 0 | 17 | 94 | 16 | 0 | 19 | 0 | 190 | 0 | 55 | 0 | 310 | 0 | 402 | 42 | 0 | 156 | 8 | 17 | 0 | 81 | 30 | 0 | 0 | 98 | 0 | 55 | 19 | 10 | 2 | 23.51 | 12 | 6441.47 | 898 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 1013 | 0 | 0 | 0 | 1370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.01 | 80 | 0 | 0 | 44.39 | 0 | 0 | 183 | 0 | 0 | 0 | 414 | 0 | 4.48 | 0 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 5.8 | 181 | 0.52 | 0 | 282 | 127 | 220 | 0 | 0 | 690 | 0 | 5856.2 | 12297.67 | 88.13
15:00 | 0 | 50 | 42 | 0 | 0 | 0 | 0 | 6 | 328 | 0 | 0 | 17 | 17 | 62 | 0 | 125 | 15 | 35 | 107 | 6 | 0 | 0 | 405 | 0 | 17 | 280 | 0 | 0 | 11 | 17 | 0 | 21 | 0 | 310 | 0 | 0 | 19 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0.81 | 80 | 0 | 2 | 580 | 0 | 0 | 50 | 0 | 0 | 220 | 0 | 0 | 0 | 1227 | 11 | 24 | 0 | 0 | 150 | 340 | 51 | 0 | 196 | 0 | 15 | 95 | 16 | 0 | 13 | 0 | 186 | 0 | 52 | 0 | 300 | 0 | 377 | 42 | 0 | 157 | 3 | 17 | 0 | 80 | 30 | 0 | 0 | 98 | 0 | 55 | 45 | 10 | 2 | 24.03 | 12 | 6489.84 | 897 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 1156 | 0 | 0 | 0 | 1424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.57 | 57 | 0 | 0 | 40 | 0 | 0 | 184 | 0 | 0 | 0 | 403 | 0 | 3.76 | 0 | 55 | 0 | 23 | 0 | 0 | 0 | 0 | 3.9 | 143 | 0.19 | 0 | 277 | 60 | 220 | 0 | 0 | 885 | 0 | 6089.42 | 12579.26 | 88.12
16:00 | 0 | 50 | 49 | 0 | 0 | 0 | 0 | 6 | 313 | 0 | 0 | 17 | 17 | 70 | 0 | 125 | 15 | 35 | 99 | 12 | 0 | 0 | 395 | 0 | 17 | 280 | 0 | 0 | 9 | 17 | 20.5 | 21 | 0 | 330 | 0 | 0 | 18 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 1.03 | 80 | 0 | 2 | 580 | 0 | 0 | 50 | 0 | 0 | 220 | 0 | 0 | 0 | 1226 | 5 | 24 | 0 | 0 | 150 | 340 | 51 | 0 | 200 | 0 | 14 | 96 | 15 | 0 | 13 | 0 | 178 | 0 | 29 | 0 | 305 | 0 | 390 | 42 | 0 | 157 | 3 | 17 | 0 | 81 | 30 | 0 | 0 | 98 | 0 | 55 | 45 | 9 | 1 | 17.77 | 12 | 6476.3 | 897 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 1198 | 0 | 0 | 0 | 1419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.48 | 43 | 0 | 0 | 26.05 | 0 | 0 | 185 | 0 | 0 | 0 | 407 | 0 | 2.33 | 0 | 55 | 0 | 15 | 0 | 0 | 0 | 0 | 2.9 | 89 | 0.34 | 0 | 277 | 60 | 220 | 0 | 0 | 945 | 0 | 6096.1 | 12572.4 | 88.11
17:00 | 0 | 54 | 49 | 0 | 0 | 0 | 0 | 6 | 325 | 0 | 0 | 17 | 17 | 70 | 30 | 125 | 15 | 35 | 106 | 15 | 0 | 0 | 400 | 0 | 17 | 280 | 0 | 0 | 3 | 70 | 20.5 | 21 | 0 | 340 | 0 | 0 | 19 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0.6 | 80 | 0 | 8 | 580 | 0 | 0 | 50 | 0 | 0 | 221 | 0 | 0 | 0 | 1225 | 2 | 24 | 0 | 0 | 150 | 350 | 51 | 0 | 184 | 0 | 20 | 95 | 23 | 0 | 20 | 0 | 166 | 0 | 6 | 0 | 305 | 0 | 358 | 42 | 0 | 159 | 1 | 17 | 0 | 82 | 30 | 0 | 0 | 98 | 0 | 60 | 56 | 7 | 0 | 5.54 | 12 | 6535.64 | 897 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 1230 | 12 | 0 | 0 | 1446 | 0 | 0 | 0 | 15 | 10 | 0 | 0 | 0 | 0 | 8.14 | 18 | 0 | 0 | 8.8 | 0 | 0 | 185 | 0 | 0 | 0 | 399 | 0 | 0.79 | 0 | 53 | 35 | 6 | 34 | 0 | 0 | 0 | 1.2 | 31 | 0 | 0 | 275 | 90 | 220 | 0 | 0 | 1060 | 6 | 6241.93 | 12777.57 | 88.1
18:00 | 0 | 102 | 49 | 0 | 0 | 0 | 0 | 6 | 340 | 0 | 0 | 22.5 | 17 | 129 | 30 | 125 | 21 | 35 | 115 | 16 | 0 | 0 | 400 | 0 | 17 | 250 | 0 | 0 | 0 | 70 | 20.5 | 21 | 0 | 360 | 0 | 0 | 38 | 0 | 11 | 34 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 13 | 580 | 0 | 0 | 50 | 0 | 0 | 221 | 0 | 0 | 0 | 1097 | 0 | 46 | 0 | 0 | 150 | 350 | 51 | 0 | 165 | 0 | 48 | 97 | 65 | 0 | 20 | 0 | 164 | 0 | 0 | 0 | 310 | 0 | 384 | 41 | 0 | 159 | 0 | 17 | 0 | 43 | 30 | 0 | 0 | 98 | 0 | 98 | 76 | 6 | 0 | 0 | 12 | 6700 | 898 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1225 | 17 | 0 | 0 | 1454 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 409 | 0 | 0 | 0 | 55 | 70 | 1 | 85 | 0 | 0 | 0 | 0.1 | 1 | 0 | 0 | 258 | 120 | 220 | 0 | 0 | 1100 | 35 | 6389.25 | 13089.25 | 88.09
19:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 6 | 328 | 0 | 0 | 51.4 | 17 | 149 | 30 | 130 | 55 | 55 | 142 | 16 | 0 | 0 | 390 | 0 | 40 | 250 | 0 | 0 | 0 | 70 | 22 | 21 | 0 | 360 | 0 | 0 | 53 | 0 | 7 | 51 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 15 | 580 | 0 | 0 | 50 | 0 | 0 | 222 | 0 | 0 | 0 | 1173 | 0 | 88 | 0 | 0 | 150 | 270 | 51 | 0 | 192 | 0 | 52 | 100 | 78 | 0 | 20 | 0 | 172 | 0 | 0 | 0 | 310 | 0 | 321 | 41 | 0 | 156 | 0 | 17 | 0 | 5 | 30 | 90 | 0 | 98 | 0 | 98 | 78 | 8 | 0 | 0 | 12 | 6954.4 | 830 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1172 | 17 | 0 | 0 | 1458 | 0 | 0 | 0 | 70 | 43 | 0 | 42 | 4 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 113 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 120 | 220 | 0 | 0 | 1115 | 66 | 6463 | 13417.4 | 88.08
19:30 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 6 | 284 | 0 | 0 | 51.4 | 17 | 149 | 30 | 195 | 55 | 55 | 140 | 0 | 0 | 0 | 330 | 0 | 55 | 250 | 0 | 0 | 0 | 70 | 22 | 21 | 0 | 340 | 0 | 0 | 61 | 0 | 7 | 51 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 18 | 580 | 0 | 0 | 50 | 0 | 0 | 222 | 0 | 0 | 0 | 1140 | 0 | 140 | 0 | 0 | 150 | 270 | 51 | 0 | 197 | 0 | 95 | 100 | 136 | 0 | 20 | 0 | 172 | 0 | 0 | 14 | 305 | 0 | 387 | 41 | 0 | 155 | 0 | 21 | 0 | 5 | 30 | 100 | 0 | 98 | 0 | 98 | 78 | 9 | 0 | 0 | 12 | 7117.4 | 897 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1202 | 17 | 0 | 0 | 1447 | 0 | 40 | 0 | 113 | 80 | 0 | 42 | 7 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 55 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257 | 125 | 220 | 0 | 0 | 1190 | 58 | 6687 | 13804.4
20:00 | 0 | 105 | 33 | 0 | 0 | 0 | 0 | 6 | 300 | 0 | 0 | 45.5 | 17 | 140 | 15 | 195 | 55 | 55 | 145 | 0 | 0 | 0 | 360 | 0 | 55 | 250 | 0 | 0 | 0 | 70 | 17 | 22 | 0 | 340 | 0 | 0 | 62 | 0 | 10 | 51 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 21 | 680 | 0 | 0 | 50 | 0 | 0 | 223 | 0 | 0 | 0 | 1152 | 0 | 133 | 0 | 0 | 150 | 270 | 51 | 0 | 200 | 0 | 103 | 100 | 119 | 0 | 20 | 0 | 174 | 0 | 0 | 16 | 305 | 0 | 388 | 41 | 0 | 150 | 0 | 17 | 0 | 5 | 30 | 100 | 0 | 96 | 0 | 98 | 78 | 9 | 0 | 0 | 12 | 7219.5 | 757 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1206 | 17 | 0 | 0 | 1446 | 0 | 40 | 0 | 50 | 50 | 0 | 42 | 7 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 55 | 115 | 0 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 125 | 220 | 0 | 0 | 1218 | 30 | 6516 | 13735.5 | 88.07
21:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 6 | 305 | 0 | 0 | 45.3 | 17 | 123 | 15 | 15 | 55 | 21 | 118 | 0 | 0 | 0 | 365 | 0 | 55 | 250 | 0 | 0 | 0 | 70 | 17.5 | 22 | 0 | 340 | 0 | 0 | 76 | 0 | 8 | 51 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 17 | 680 | 0 | 0 | 50 | 0 | 0 | 224 | 0 | 0 | 0 | 1160 | 0 | 70 | 0 | 0 | 150 | 270 | 51 | 0 | 190 | 0 | 101 | 100 | 120 | 0 | 20 | 0 | 172 | 0 | 0 | 16 | 310 | 0 | 387 | 41 | 0 | 150 | 0 | 17 | 0 | 5 | 30 | 101 | 0 | 96 | 0 | 98 | 78 | 9 | 0 | 0 | 12 | 6882.8 | 897 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1219 | 17 | 0 | 0 | 1452 | 0 | 40 | 0 | 35 | 50 | 0 | 42 | 7 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 55 | 95 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 129 | 220 | 0 | 0 | 1240 | 31 | 6677 | 13559.8 | 88.06
22:00 | 0 | 52 | 33 | 0 | 0 | 0 | 0 | 6 | 321 | 0 | 0 | 48.5 | 17 | 123 | 15 | 15 | 55 | 17 | 72 | 0 | 0 | 0 | 380 | 0 | 55 | 250 | 0 | 0 | 0 | 70 | 17.5 | 22 | 0 | 340 | 0 | 0 | 84 | 0 | 11 | 51 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 20 | 680 | 0 | 0 | 50 | 0 | 0 | 225 | 0 | 0 | 0 | 1150 | 0 | 20 | 0 | 0 | 150 | 300 | 51 | 0 | 190 | 0 | 100 | 100 | 130 | 0 | 20 | 0 | 172 | 0 | 0 | 7 | 310 | 0 | 375 | 41 | 0 | 155 | 0 | 17 | 0 | 5 | 30 | 100 | 0 | 96 | 0 | 98 | 78 | 9 | 0 | 0 | 0 | 6814 | 898 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1228 | 17 | 0 | 0 | 1451 | 0 | 40 | 0 | 35 | 50 | 0 | 42 | 30 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 50 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 129 | 220 | 0 | 0 | 1241 | 15 | 6661 | 13475 | 88.05
23:00 | 0 | 52 | 33 | 0 | 0 | 0 | 0 | 6 | 303 | 0 | 0 | 28 | 17 | 123 | 15 | 15 | 30 | 0 | 35 | 0 | 0 | 0 | 365 | 0 | 17 | 250 | 0 | 0 | 0 | 70 | 0 | 22 | 0 | 340 | 0 | 0 | 84 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 23 | 680 | 0 | 0 | 50 | 0 | 0 | 225 | 0 | 0 | 0 | 1148 | 0 | 20 | 0 | 0 | 150 | 300 | 51 | 0 | 191 | 0 | 98 | 100 | 120 | 0 | 20 | 0 | 174 | 0 | 0 | 7 | 310 | 0 | 361 | 41 | 0 | 150 | 0 | 21 | 0 | 5 | 30 | 100 | 0 | 96 | 0 | 59 | 48 | 8 | 0 | 0 | 0 | 6522 | 897 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1119 | 17 | 0 | 0 | 1449 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 49 | 50 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 129 | 220 | 0 | 0 | 1240 | 0 | 6314 | 12836 | 88.04
Total KWH | 0 | 1104000 | 673440 | 0 | 0 | 0 | 0 | 171454.55 | 7786800 | 0 | 0 | 389520 | 277560 | 1422144 | 140160 | 1170742 | 412793 | 406273 | 1176480 | 73920 | 0 | 0 | 8398859 | 0 | 343600 | 6369330 | 0 | 0 | 178003 | 588000 | 472800 | 514080 | 0 | 7955000 | 0 | 0 | 901440 | 0 | 370560 | 587941 | 0 | 0 | 3840 | 3840 | 21242 | 1907040 | 0 | 338400 | 14392727.27 | 0 | 0 | 1215840 | 991.8 | 0 | 4781313 | 0 | 0 | 0 | 25614543 | 105435 | 635636 | 0 | 0 | 3827800 | 7696000 | 1045370 | 0 | 4659000 | 49608 | 663360 | 2352305 | 775680 | 0 | 415890 | 0 | 3917760 | 0 | 356709 | 50112 | 7430000 | 0 | 9072000 | 978000 | 0 | 3618736 | 54294 | 338232 | 0 | 933120 | 718176 | 554000 | 0 | 2341500 | 0 | 948000 | 700800 | 281280 | 8000 | 288410 | 111120 | 145091009.62 | 21371636 | 4874400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 509040 | 23425450 | 118560 | 0 | 0 | 27543220 | 0 | 126675 | 0 | 278743 | 353184 | 0 | 188512 | 36727 | 0 | 325192 | 704940 | 69883 | 0 | 381008 | 0 | 0 | 4302345 | 0 | 0 | 0 | 8947418 | 0 | 33600 | 0 | 1304727 | 503941 | 227624 | 542563 | 0 | 0 | 0 | 35597.52 | 1365120 | 2758 | 0 | 5520000 | 2791000 | 5278490 | 0 | 0 | 22337454.55 | 194400 | 133694208.07 | 278785217.69

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 16-03-2026
Power Supply Scenario
| Day Peak Generation |  |  | 11578 | MW | 12:00 Hr. | Energy Generated |  |  | 278.7852 |  | MKWHr.
| Day Peak Demand |  |  | 11964 | MW | 12:00 Hr. | Energy Unserverd |  |  | 3.306 |  | MKWHr.
| Evening Peak Generation |  |  | 13804.4 | MW | 19:30 Hr. | Energy Demand |  |  | 282.0912 |  | MKWHr.
| Evening Peak Demand |  |  | 13880.4 | MW | 19:30 Hr. | Maximum Temperature |  |  | 30.1 |  | °C
| Minimum Generation of the Day |  |  | 9041.98 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 805.39 |  | MMCFD
| Maximum Generation of the Day |  |  | 13804.4 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.0247 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 31.6683 | 0 | 8.1786 | 0 | 0 | 0.178 | 0 | 0 | 40.025 | Gas | 109.2927 | Gas | 376578590.0925
| Chattogram Zone |  |  | 5.1197 | 40.0073 | 2.7139 | 0 | 1.907 | 0.12668 | 0 | 0.37056 | 50.2452 | Coal | 92.5949 | Coal | 627309068.0846
| Cumilla Zone |  |  | 20.046 | 0 | 2.1248 | 0 | 0 | 0.35671 | 3.9178 | 0 | 26.4452 | HFO | 17.1904 | HFO | 292722606.46
| Mymensingh Zone |  |  | 0.28128 | 0 | 1.7599 | 0 | 0 | 0.29641 | 0 | 0 | 2.3376 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 25.9838 | 0 | 0 | 0 | 0 | 0.054294 | 0 | 0 | 26.0381 | Hydro | 1.907 | Hydro | 190704
| Khulna Zone |  |  | 4.8744 | 23.4255 | 0.11856 | 0 | 0 | 0.50904 | 21.3716 | 0 | 50.2991 | Solar | 4.597 | Solar | 74600243.924
| Barishal Zone |  |  | 8.0695 | 27.8575 | 0.1944 | 0 | 0 | 0.002758 | 0 | 0 | 36.1241 | Import | 52.8326 | Import | 302745042.8
| Rajshahi Zone |  |  | 13.2498 | 0 | 1.0537 | 0 | 0 | 1.4447 | 27.5432 | 0 | 43.2914 | Wind | 0.37056 | Wind | 5450937.6
| Rangpur Zone |  |  | 0 | 1.3047 | 1.0465 | 0 | 0 | 1.6283 | 0 | 0 | 3.9796
| Total |  |  | 109.2927 | 92.5949 | 17.1904 | 0 | 1.907 | 4.597 | 52.8326 | 0.37056 | 278.7852
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 376578590.0925 |  | Hydro | 190704
|  |  |  | Coal | 627309068.0846 |  | Solar | 74600243.924
|  |  |  | HFO | 292722606.46 |  | Import | 302745042.8
|  |  |  | HSD | 0 |  | Wind | 5450937.6
[5 empty] | Total: | 167,95,97,192 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.3716 | Peak Hr Flow | 897.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 45877672.73 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.5432 | Peak Hr Flow | 1447.00 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2379 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.9178 | Peak Hr Flow | 172.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2671 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 52.8326 | Peak Hr Flow | 2516.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5040
|  |  |  | Chattogram |  | 73 |  | 1443
|  |  |  | Cumilla |  | 0 |  | 1325
|  |  |  | Mymensingh |  | 0 |  | 1019
|  |  |  | Sylhet |  | 0 |  | 451
|  |  |  | Khulna |  | 0 |  | 1620
|  |  |  | Barishal |  | 0 |  | 378
|  |  |  | Rajshahi |  | 0 |  | 1276
|  |  |  | Rangpur |  | 0 |  | 816
|  |  |  | Total |  | 73 |  | 13368
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
[5 empty] | Total | 300 |  |  |  | Total | 454
|  |  |  | Total Unavailable Capacity |  |  |  | 754
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:27 | 10:16 | Benapole-Jashore 132 kV Ckt-2 Forced S/D from Benapole 132/33kV end Due to Tree trimming
| 09:04 |  | Baroirhat-Hathazari 132 kV Ckt-2 Scheduled S/D from Hathazari 230/132/33kV end.
| 09:48 | 10:44 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Scheduled S/D Due to Red
hot Maintanence
|  | 10:07 | Shahjibazar-Sreemangal 132kV Ckt-1 is restored.
| 10:18 | 10:57 | BIPTC S/S 10CF25 Forced S/D
|  | 10:44 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT is restored.
| 10:45 | 11:24 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT Scheduled S/D Due to Red
hot Maintanence work
| 10:45 | 11:24 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) HT Scheduled S/D Due to Red
hot Maintanence
| 10:49 | 11:59 | BIPTC S/S 10CF16 Forced S/D
| 10:53 | 13:48 | Cox'sbazar-Dohazari 132 kV Ckt-1 Scheduled S/D from Coxsbazar 132/33kV end Due to Disc | [7 empty] | and 39.0MW load
|  |  | Cleaning and from Dohazari 132/33kV end Due to Disk Ceaning | [7 empty] | interrup. Dohazari
132/33kV end
| 11:00 | 12:45 | Ishurdi 230/132kV S/S 230/132 kV T-01 HT Forced S/D Due to 230/132kv transformer T01 red
hot maintenance.
| 11:02 | 12:46 | Ishurdi 230/132kV S/S 230/132 kV T-01 LT Forced S/D Due to 230/132kv transformer T01 red
hot maintenance
|  | 11:45 | Dhamrai 132/33kV S/S Main Bus-2 is restored.
|  | 11:50 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT is restored.
|  | 11:51 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) LT is restored.
| 12:00 |  | Day peak generation 11574 MW
| 12:22 | 13:03 | Maijdee 132/33kV S/S TR-01 HT Forced S/D Due to Transformer-01 emergency shutdown
beacause 33KV bus load side DS Finger Flashing .
|  | 12:36 | Bheramara P/S-Kustia 132 kV Ckt-2 is restored.
|  | 12:38 | Jhenaidah-Kushtia 132kV Ckt-2 is restored.
| 12:42 |  | Dhamrai-Nabinagar 132 kV ckt-1 was charged from Dhamrai end for the first time
| 12:50 | 17:26 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-2 Project Work S/D Due to Project Work
| 12:52 | 14:54 | Ishurdi 230/132kV S/S 230/132 kV T-02 HT Forced S/D Due to red hot maintenance work
| 12:52 | 14:55 | Ishurdi 230/132kV S/S 230/132 kV T-02 LT Forced S/D Due to red hot maintenance work
| 13:00 |  | Dhamrai-Nabinagar 132 kV ckt-2 was charged from Dhamrai end for the first time
|  | 13:30 | Naogaon-Niyamatpur 132kV Ckt-1 is restored.
|  | 13:31 | Niamatpur 132/33kV S/S 132 kV Naogaon ckt-2 is restored.
|  | 14:24 | Mirpur 132/33kV S/S T3 HT is restored.
| 14:29 |  | Bhola CCPP GT-2 Shutdown.
| 14:34 | 14:54 | Sirajganj 132/33kV S/S T2-(425) LT Tripped showing Schneider MICOM P142 (Over Current | [7 empty] | 20.0MW load
|  |  | Protection ) relays Due to 33 KV Sialkole Feeder BUS DS (R PH) Insulator Failure | [7 empty] | interrup.
| 14:34 | 14:54 | Sirajganj 132/33kV S/S T1-(415) LT Tripped showing Schneider MICOM P142 (Over Current | [7 empty] | 20.0MW load
|  |  | Protection ) relays Due to 33 KV Sialkole Feeder BUS DS (R PH) Insulator Failure | [7 empty] | interrup.
|  | 14:50 | Kalurghat 132/33kV S/S TRFO-01(506T) HT is restored.
|  | 15:15 | Sreemongol 132/33kV S/S 132/33kv T-3 HT is restored.
| 16:10 | 17:03 | Kasba 132/33kV S/S Muradnagar-Kasba Ckt-2 Tripped showing line distance relay relays Due
to bad weather
|  | 17:25 | Siddhirganj 230/132kV S/S MTR 2 HT is restored.
|  | 17:27 | Siddhirganj 132/33kV S/S 132kV MTR 2 is restored.
| 19:30 |  | Evening Peak Generation: 13804 MW.
| 23:10 | 00:34 | Madanganj 132/33kV S/S Madanganj -Haripur 132 kv Ckt-2 Forced S/D Due to Y-ph CT clamp
redhot
| 23:10 |  | Haripur 230/132kV S/S Madanganj-2 Forced S/D Due to ordered by NLDC.
| 23:22 | 00:42 | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat Tripped showing 59 Overvolt relays Due to
Bad Weather & Stormy wind.
| 23:25 | 00:41 | Lalmonirhat-Rangpur 132 kV Ckt-2 Tripped from Kurigram 132/33kV end showing Distance
Protection P443 relays.
| 23:47 | 01:06 | Mongla 132/33kV S/S T-2 LT Tripped showing Over current pro. Fault relays Due to | [7 empty] | 27.0MW load
|  |  | Auxiliary Tx-2 trip | [7 empty] | interrup.
| 23:48 | 01:05 | Mongla 132/33kV S/S T-1 LT Tripped showing Overcurrent pro.Trip &Earth fault pro. Trip | [7 empty] | 8.0MW load
|  |  | relays Due to Mongla cement trip | [7 empty] | interrup.
| 00:29 | 07:44 | Khulna(C )-Noapara 132kV Ckt-2 Tripped from Noapara 132/33kV end showing Siemens
SIPROTEC 7SA87 relays Due to Distance Relay Trip and from Khulna (C) end showing Distance
relay. R Phase.(6ka)9km relays Due to E/F TRIP R Phase
| 00:43 | 05:11 | Bagerhat-Bhandaria 132 kV Ckt-1 Tripped from Bagerhat 132/33kV end showing Over voltage
(59) relays Due to System over voltage 145kv increase by Thunderstorm Rain
| 02:35 |  | Bagerhat-Labanchura 132 kV Ckt-2 Tripped from Bagerhat 132/33kV end showing Distance
relay A,B,C phase Zone-1 relays Due to Thunder storm
| 02:50 | 03:09 | Shahjibazar 132/33kV S/S TR-02 HT Tripped showing Lock out Relay. relays Due to | [7 empty] | 55.0MW load
|  |  | Shaistaganj Feeder OC/EF Fault. | [7 empty] | interrup.
| 02:50 | 03:30 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing Lock out relays Due to Shaistagang | [7 empty] | 55.0MW load
|  |  | Feeder OC/EF Fault. | [7 empty] | interrup.
| 03:37 | 04:28 | Fenchuganj-Fenchuganj 132 kV Ckt-2 Tripped from Fenchuganj 230/132/33kV end showing REC
650 REL 670 relays Due to Bad Weather
| 05:00 | 06:28 | Bakulia 132/33kV S/S T-3 (422T) LT Tripped showing Micom relays. | [7 empty] | 12.0MW load
interrup.
|  | 05:42 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT is restored.
| 05:42 |  | Sirajgonj 400 MW CCPP Unit-4 Tripped
| 05:42 | 07:48 | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-1 Tripped showing Distance Relay Zone1 (Phase
A) and Auto reclose unsuccessful relays.
| 05:42 | 06:06 | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-2 Tripped showing OC and E/F relays.
| 05:42 | 06:51 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-1 Tripped showing Main-1, Main-2 relays Due | [7 empty] | 48.0MW load
|  |  | to DTT | [7 empty] | interrup.
| 05:42 | 06:40 | Sreepur 230/132/33kV S/S Sreepur-Valuka Ckt-2 Tripped showing Main1,2 relays Due to DTT
| 05:42 |  | Barisal 307 MW Tripped
| 05:43 |  | Bagerhat-Bhandaria 132 kV Ckt-1 Tripped from Bagerhat 132/33kV end showing Line
protection Relay: OV(59) Definite - T2: pickup Phase A
Phase B relays Due to System over voltage.
| 05:43 | 07:20 | Savar 132/33kV S/S T-3 LT Tripped showing LV Backup protection Relay relays Due to
Frequency Protection Trip
| 05:43 | 07:24 | Savar 132/33kV S/S T-4 LT Tripped showing LV Backup Protection Relay relays Due to Under
Frequency Tripping
| 05:44 |  | Bhaluka-Mymensingh 132 kV Ckt-2 Tripped from Bhaluka 132/33kV end showing Micon relays | [7 empty] | 17.0MW load
|  |  | Due to Distance Trip 3-Phase | [7 empty] | interrup. Bhaluka
132/33kV end
| 05:44 |  | Bhaluka-Mymensingh 132 kV Ckt-1 Tripped from Bhaluka 132/33kV end showing Micom relays | [7 empty] | 17.0MW load
|  |  | Due to Distance Trip 3-PHASE | [7 empty] | interrup. Bhaluka
132/33kV end
| 05:44 | 06:52 | Kabirpur -Tongi 132kV Ckt-2 Tripped from Tongi 230/132/33kV end showing
B,Y-PHASE OV/DTT AR BLOCKED SYNCH NOT WORK relays.
| 05:44 |  | Bogura 230/132kV S/S Confidance UN-2 Tripped showing Signal=Close Block operated,Main
protection gen. trip relays.
| 05:44 |  | Bhaluka 132/33kV S/S BR Powergen Ckt- 02 Tripped showing MiCOM relays Due to OV RED
broken CoND (GR)
| 05:44 |  | Bhaluka 132/33kV S/S BR Powergen Ckt- 01 Tripped showing MiCOM relays Due to Trip (OV RED
Broken Cond (GR)
| 05:45 | 07:17 | Sonargaon 132/33kV S/S Tr-1 LT Tripped showing Under frequency relays Due to Under | [7 empty] | 60.0MW load
|  |  | frequency Trip | [7 empty] | interrup.
| 05:45 | 07:17 | Sonargaon 132/33kV S/S Tr-2 LT Tripped showing Under frequency relays Due to Under | [7 empty] | 57.0MW load
|  |  | frequency | [7 empty] | interrup.
| 06:06 | 06:24 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT Tripped showing Main1 relays. | [7 empty] | 32.0MW load
interrup.
| 06:06 | 06:24 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Tripped showing Main1 relays. | [7 empty] | 44.0MW load
interrup.
| 06:07 | 06:29 | Jaldhaka 132/33kV S/S 406T-1 LT Tripped showing Micom P142 relays Due to Frequency | [7 empty] | 11.0MW load
|  |  | unbalance. | [7 empty] | interrup.
| 06:07 | 06:30 | Jaldhaka 132/33kV S/S 416T-2 LT Tripped showing Micom P142 relays Due to Frequency | [7 empty] | 11.0MW load
|  |  | unbalance | [7 empty] | interrup.
| 06:35 |  | Mongla 132/33kV S/S T-1 LT Tripped showing Lockout Reay relays Due to Auxiliary Tx-1 | [7 empty] | 8.0MW load
|  |  | blast and oil leakage | [7 empty] | interrup.
| 07:02 | 07:37 | Niamatpur 132/33kV S/S Transformer-2 (417T) LT Tripped showing Siprotec 7SJ1 relays Due | [7 empty] | 15.0MW load
|  |  | to Birds are causing flashover on the PBS 33 kV feeder (Niamatpur-2). | [7 empty] | interrup.
| 07:02 | 07:37 | Niamatpur 132/33kV S/S Transformer-2 (417T) HT Tripped showing Main Protection Relay-2 | [7 empty] | 15.0MW load
|  |  | relays Due to Birds are causing flashover on the PBS 33 kV feeder(Niamatpur-2). | [7 empty] | interrup.
| 07:15 |  | Munshiganj 132/33kV S/S Transformer-2 LT Scheduled S/D Due to PBS maintenance work | [7 empty] | 20.0MW load
interrup.
| 07:29 | 07:42 | Naogaon 132/33kV S/S T-1 HT Forced S/D Due to T-1 CB SF6 GASS LOW
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 16-03-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 6 | 171454.55 | Demand "05"MW due to gas restiction by Titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 284 | 7786800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 412793 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 250 | 6369330 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 51.4 | 389520 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 30 | 140160 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 406273 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 343600 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22 | 472800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 514080 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 49 | 673440 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 1170742 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1422144 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1104000 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 73920 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 140 | 1176480 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 178003 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 277560 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 340 | 7955000 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 330 | 8398859 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 70 | 588000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2224.4 | 40024958.55
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 991.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 105435 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1215840 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1907040 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 222 | 4781313 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 587941 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 3840 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 18 | 338400 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 61 | 901440 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21242 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 3840 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1140 | 25614543 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 7 | 370560 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 580 | 14392727.27 | Coal shortage
Chattogram Area Total |  |  |  |  | 4898.863 | 2209 | 50245153.07
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 197 | 4659000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 150 | 3827800 | Vibration
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 270 | 7696000 | FGMO ON
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 49608 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1045370 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 140 | 635636 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 14 | 50112 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2352305 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 136 | 775680 | -
| Import (Tripura) |  | Import | 0 | 160 | 172 | 3917760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 415890 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 95 | 663360 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 356709 | -
Cumilla Area Total |  |  |  |  | 2876.261 | 1345 | 26445230
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 9 | 281280 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 78 | 700800 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 98 | 948000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 288410 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 111120 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 197 | 2337610
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 54294 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 978000 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3618736 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 100 | 554000 | BT Fan Under Maintanance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 718176 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 5 | 933120 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 98 | 2341500 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 338232 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7430000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 387 | 9072000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1142 | 26038058
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 897 | 21371636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 175 | 4874400 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 118560 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 509040 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1202 | 23425450 | plant availability zero
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2291 | 50299086
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 125 | 2791000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1190 | 22337454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5278490 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 58 | 194400 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 257 | 5520000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2758 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1850 | 36124102.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 325192 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 126675 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 7 | 36727 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 182 | 4302345 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 357 | 8947418 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 18 | 69883 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 42 | 188512 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 80 | 353184 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 278743 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 33600 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1447 | 27543220 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 381008 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 704940 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2286 | 43291447
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 55 | 1304727 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 90 | 542563 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 35597.52 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 503941 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 227624 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1365120 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 260 | 3979572.52
Eastern Grid Total |  |  |  |  | 17423.308 | 7117.4 | 145091009.62
Western Grid Total |  |  |  |  | 11852.195 | 6687 | 133694208.07
National Grid Total |  |  |  |  | 29275.503 | 13804.4 | 278785217.69
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 16-03-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9204.3 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4090.1 | MW
i) Dhaka area |  |  | 5039.8 |  | MW | i) Khulna area |  |  |  | 1620.4 | MW
ii) Chattogram area |  |  | 1369.5 |  | MW | ii) Barishal area |  |  |  | 377.5 | MW
iii) Cumilla area |  |  | 1325 |  | MW | iii) Rajshahi area |  |  |  | 1276.2 | MW
iv) Mymensingh area |  |  | 1019 |  | MW | iv) Rangpur area |  |  |  | 816 | MW
v) Sylhet area |  |  | 451 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13294.4 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 10 | 15:00 | 67 | Hasnabad | 90 | 20:00 | 133 | Nawabganj | 45.6 | 19:00
2 | AKSML | 8.1 | 18:00 | 68 | Hathazari | 77 | 19:00 | 134 | Netrakona | 116 | 18:00
3 | Aftabnagar | 32 | 18:00 | 69 | Hatirjheel | 38 | 12:00 | 135 | New | 72 | 12:00
4 | Agargaon | 104 | 13:00 | 70 | Ishurdi | 67 | 19:00 | 136 | Niamatpur | 60 | 18:30
5 | Agrabad | 60 | 12:00 | 71 | Jaldhaka | 69 | 18:00 | 137 | Noapara | 46 | 17:00
6 | Amnura | 27 | 21:00 | 72 | Jamalpur | 94 | 18:00 | 138 | PHP | 9 | 13:00
7 | Ashuganj | 79 | 00:00 | 73 | Jashore | 143 | 22:00 | 139 | Pabna | 84 | 21:00
8 | BSRM | 206 | 17:00 | 74 | Jhenaidah | 103 | 20:00 | 140 | Palashbari | 98 | 18:00
9 | Bagerhat | 78 | 23:00 | 75 | Joydebpur | 124 | 10:00 | 141 | Panchagarh | 52 | 18:00
10 | Bajitpur | 87 | 21:00 | 76 | Joypurhat | 57 | 22:00 | 142 | Patiya | 8 | 14:00
11 | Bakerganj | 11.6 | 00:00 | 77 | Juldah | 14.5 | 10:00 | 143 | Patuakhali | 61 | 21:00
12 | Bakulia | 69 | 19:00 | 78 | KSRM | 11 | 10:00 | 144 | Payra | 28 | 22:00
13 | Banani | 30.4 | 13:00 | 79 | Kabirpur | 247 | 17:00 | 145 | Postogola | 47 | 00:00
14 | Bangabhaban | 17 | 10:00 | 80 | Kachua | 91 | 18:30 | 146 | Pubail | 29 | 15:00
15 | Barapukuria | 55 | 19:00 | 81 | Kaliganj | 28 | 20:00 | 147 | Purbachal | 24 | 00:00
16 | Barguna | 18 | 00:00 | 82 | Kallyanpur | 102 | 18:30 | 148 | Purbasadipur | 105 | 18:00
17 | Barishal | 94 | 21:00 | 83 | Kalurghat | 50 | 14:00 | 149 | Rahanpur | 29 | 19:00
18 | Barishal-230 | 78 | 21:00 | 84 | Kamrangirchar | 76 | 17:00 | 150 | Rahim | 33 | 11:00
19 | Baroaulia | 68 | 19:00 | 85 | Kaptai | N/A | N/A | 151 | Rajbari | 73 | 21:00
20 | Baroirhat | 55 | 20:00 | 86 | Kasba | 35 | 22:00 | 152 | Rajendrapur | 120 | 18:30
21 | Bashundhara | 160 | 19:30 | 87 | Kazla | 111 | 16:00 | 153 | Rajshahi | 100 | 04:00
22 | BashundharaCement | 13 | 00:00 | 88 | Keranigonj | 83 | 19:00 | 154 | Rajshahi-230 | 80 | 22:00
23 | Beanibazar | 58 | 18:00 | 89 | Khagrachori | 28 | 18:00 | 155 | Ramganj | 94 | 18:00
24 | Benapole | 80 | 19:00 | 90 | Khulna | 53 | 18:30 | 156 | Rampur | 38 | 18:30
25 | Bhaluka | 157 | 17:00 | 91 | Khulshi | 170 | 14:00 | 157 | Rangamati | 16 | 18:30
26 | Bhandaria | 49 | 21:00 | 92 | Kishoreganj | 116 | 23:00 | 158 | Rangpur | 131 | 18:00
27 | Bhangura | 42 | 14:00 | 93 | Kodda | 297 | 16:00 | 159 | Ruppur | 3.6 | 15:00
28 | Bheramara(GK) | 59 | 22:00 | 94 | Kulaura | 36 | 19:00 | 160 | SSM | 3 | 23:00
29 | Bhulta | 222 | 17:00 | 95 | Kurigram | 64 | 18:00 | 161 | Saidpur | 104 | 18:30
30 | Bog-Sherpur | 60 | 23:00 | 96 | Kushtia | 130 | 19:00 | 162 | Satkhira | 131 | 19:00
31 | Bogura | 139 | 19:00 | 97 | Laksam | 18 | 00:00 | 163 | Satmasjid | 94 | 20:00
32 | Borhanuddin | 90 | 21:00 | 98 | Lakshmipur | 46 | 20:00 | 164 | Savar | 222 | 14:00
33 | Brahmanbaria | 120 | 21:00 | 99 | Lalbag | 71 | 13:00 | 165 | SevenRings | 17.48 | 17:00
34 | Cantonment | 138 | 13:00 | 100 | Lalmonirhat | 53 | 18:00 | 166 | ShahCement | 26 | 00:00
35 | Chandina | 18 | 15:00 | 101 | MI_Cement | 18.8 | 00:00 | 167 | Shahjadpur | 83 | 21:00
36 | Chandpur | 74 | 21:00 | 102 | Madanganj | 28 | 00:00 | 168 | Shahjibazar | 114 | 22:00
37 | Chandraghona | 33 | 18:30 | 103 | Madaripur | 97 | 22:00 | 169 | Shahmirpur | 56 | 03:00
38 | Chapai | 70 | 23:00 | 104 | Madartek | 67 | 19:00 | 170 | Shariatpur | 73 | 22:00
39 | Charsaidpur | 43 | 09:00 | 105 | Madunaghat | 49 | 14:00 | 171 | Sherpur | 132 | 18:00
40 | Chauddagram | 69 | 23:00 | 106 | Magura | 64 | 19:00 | 172 | Shikalbaha | 32 | 02:00
41 | Chhatak | 31 | 19:30 | 107 | Mahasthangarh | 58 | 23:00 | 173 | Shitalakhya | 80.9 | 15:00
42 | Chowmuhani | 136 | 18:00 | 108 | Maijdee | 37 | 18:00 | 174 | Sholosohor | 42 | 19:00
43 | Chuadanga | 114 | 23:00 | 109 | Manikganj | 123 | 19:30 | 175 | Shyampur | 156 | 15:00
44 | Coxsbazar | 126 | 23:00 | 110 | Maniknagar | 63 | 13:00 | 176 | Siddhirganj | 123 | 12:00
45 | Cumilla(N) | 113 | 21:00 | 111 | Matarbari | 50 | 19:30 | 177 | Sirajganj | 110 | 20:00
46 | Cumilla(S) | 188 | 14:00 | 112 | Matuail | 66 | 15:00 | 178 | Sonargaon | 147 | 00:00
47 | Daganbhuiyan | 32 | 21:00 | 113 | Metrorail_Motijheel | 41 | 16:00 | 179 | Sreemongol | 59 | 23:00
48 | Daudkandi | 146 | 20:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sreepur | 111 | 19:30
49 | DhakaUniversity | 66 | 14:00 | 115 | Millgate | 90 | 12:00 | 181 | Srinagar | 45.2 | 19:00
50 | Dhamrai | 120 | 18:00 | 116 | Mirpur | 124 | 15:00 | 182 | Sunamganj | 43 | 20:00
51 | Dhanmondi | 107 | 13:00 | 117 | Mirsorai | 11 | 00:00 | 183 | Sylhet | 56 | 14:00
52 | Dohazari | 92 | 18:30 | 118 | Mirzapur | 54 | 18:00 | 184 | Sylhet-132 | 81 | 17:00
53 | Faridpur | 155 | 23:00 | 119 | Mithapukur | 52 | 18:00 | 185 | TK | 23 | 18:30
54 | Fatullah | 99 | 15:00 | 120 | Modern | N/A | N/A | 186 | Tangail | 192 | 18:00
55 | Fenchuganj | 33 | 21:00 | 121 | Mogbazar | 54.2 | 11:00 | 187 | Taraganj | 19 | 18:00
56 | Feni | 93 | 22:00 | 122 | Mongla | 40 | 12:00 | 188 | Tasnim | 14 | 02:00
57 | GPH | 24 | 03:00 | 123 | Motijheel | 41 | 13:00 | 189 | Thakurgaon | 91 | 19:00
58 | Ghatail | 84 | 19:00 | 124 | Muktagacha | 29 | 23:00 | 190 | Tongi | 133 | 15:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 110 | 19:30 | 191 | Ullahpara | 45 | 20:00
60 | Ghorashal-230 | 106 | 19:00 | 126 | Muradnagar | 49 | 13:00 | 192 | Ullon | 48 | 19:00
61 | Goalpara | 36 | 18:30 | 127 | Mymensingh | 166 | 18:00 | 193 | Uttara | 77 | 13:00
62 | Gollamari | 98 | 19:00 | 128 | Naogaon | 101 | 21:00 | 194 | UttaraNew | 27 | 18:00
63 | Gopalganj | 94 | 22:00 | 129 | Narail | 58 | 19:30 | 195 | Zigatola | 86 | 14:00
64 | Gulshan | 110 | 12:00 | 130 | Narinda | 62 | 13:00
65 | Halishahar | 81 | 16:00 | 131 | Narshingdi | 164 | 19:30
66 | HaripurSBU | 128 | 17:00 | 132 | Natore | 142 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 16-03-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 10149.31 | 107 |  | 10261.13
1:00 | 9824.65 | 101 |  | 9930.65
2:00 | 9853.55 | 102 |  | 9960.55
3:00 | 10080.06 | 96 |  | 10180.06
4:00 | 10414.07 | 101 |  | 10520.07
5:00 | 9502.71 | 0 |  | 9502.71
6:00 | 9041.98 | 0 |  | 9041.98
7:00 | 9072.57 | 0 |  | 9072.57
8:00 | 9722.59 | 0 |  | 9722.59
9:00 | 10460.71 | 0 |  | 10460.71
10:00 | 10906.8 | 35 |  | 10943.8
11:00 | 11228.59 | 265 |  | 11505.59
12:00 | 11578 | 369 |  | 11964
13:00 | 12001.4 | 384 |  | 12402.4
14:00 | 12297.67 | 388 |  | 12702.67
15:00 | 12579.26 | 453 |  | 13052.26
16:00 | 12572.4 | 316 |  | 12902.4
17:00 | 12777.57 | 129 |  | 12912.57
18:00 | 13089.25 | 107 |  | 13201.25
19:00 | 13417.4 | 79 |  | 13500.4
19:30 | 13804.4 | 73 |  | 13880.4
20:00 | 13735.5 | 72 |  | 13810.5
21:00 | 13559.8 | 68 |  | 13630.8
22:00 | 13475 | 73 |  | 13551
23:00 | 12836 | 61 |  | 12900
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 16-03-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5632.5 | 4516.81 | 10149.31 | DAILY GENERATION CURVE
00:30 | 5481.75 | 4505.23 | 9986.98
01:00 | 5331 | 4493.65 | 9824.65 | 16-03-2026
01:30 | 5355 | 4484.1 | 9839.1
02:00 | 5379 | 4474.55 | 9853.55
02:30 | 5411 | 4555.805 | 9966.805
03:00 | 5443 | 4637.06 | 10080.06
03:30 | 5406.5 | 4840.565 | 10247.065
04:00 | 5370 | 5044.07 | 10414.07
04:30 | 5251.25 | 4707.14 | 9958.39
05:00 | 5132.5 | 4370.21 | 9502.71
05:30 | 4976.5 | 4295.845 | 9272.345
06:00 | 4820.5 | 4221.48 | 9041.98
06:30 | 4835.7 | 4221.575 | 9057.275
07:00 | 4850.9 | 4221.67 | 9072.57
07:30 | 5000.8 | 4396.78 | 9397.58
08:00 | 5150.7 | 4571.89 | 9722.59
08:30 | 5295.945 | 4795.705 | 10091.65
09:00 | 5441.19 | 5019.52 | 10460.71
09:30 | 5482.035 | 5201.72 | 10683.755
10:00 | 5522.88 | 5383.92 | 10906.8
10:30 | 5714.845 | 5352.85 | 11067.695
11:00 | 5906.81 | 5321.78 | 11228.59
11:30 | 6006.355 | 5396.94 | 11403.295
12:00 | 6105.9 | 5472.1 | 11578
12:30 | 6182.2 | 5607.5 | 11789.7
13:00 | 6258.5 | 5742.9 | 12001.4
13:30 | 6349.985 | 5799.55 | 12149.535
14:00 | 6441.47 | 5856.2 | 12297.67
14:30 | 6465.655 | 5972.81 | 12438.465
15:00 | 6489.84 | 6089.42 | 12579.26
15:30 | 6483.07 | 6092.76 | 12575.83
16:00 | 6476.3 | 6096.1 | 12572.4
16:30 | 6505.97 | 6169.015 | 12674.985
17:00 | 6535.64 | 6241.93 | 12777.57
17:30 | 6617.82 | 6315.59 | 12933.41
18:00 | 6700 | 6389.25 | 13089.25
18:30 | 6827.2 | 6426.125 | 13253.325
19:00 | 6954.4 | 6463 | 13417.4
19:30 | 7117.4 | 6687 | 13804.4
20:00 | 7219.5 | 6516 | 13735.5
20:30 | 7051.15 | 6596.5 | 13647.65 |  | Executive Engineer
21:00 | 6882.8 | 6677 | 13559.8 |  | Network Operation Division
21:30 | 6848.4 | 6669 | 13517.4
22:00 | 6814 | 6661 | 13475
22:30 | 6668 | 6487.5 | 13155.5
23:00 | 6522 | 6314 | 12836

## En-Curve
QF-LDC-12
Date | 16-03-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2790 | 1482.5 | 884 | 0 | 174 | 825.81 | 80 | 3671 | 0 | 99 | 134 | 0 | 0 | 9 | 107 | DAILY ENERGY CURVE
00:30 | 2814 | 1443.25 | 883 | 0 | 174 | 827.23 | 80 | 3546.5 | 0 | 95 | 119.5 | 0 | 0 | 4.5 | 104 | 16-03-2026
01:00 | 2838 | 1404 | 882 | 0 | 174 | 828.65 | 80 | 3422 | 0 | 91 | 105 | 0 | 0 | 0 | 101
01:30 | 2854 | 1428.5 | 882 | 0 | 163 | 830.6 | 80 | 3404.5 | 0 | 91 | 105.5 | 0 | 0 | 0 | 101.5 | Energy Generated | 278.7852 |  | MKWHr
02:00 | 2870 | 1453 | 882 | 0 | 152 | 832.55 | 80 | 3387 | 0 | 91 | 106 | 0 | 0 | 0 | 102 | Energy not Served | 3.306 |  | MKWHr
02:30 | 2867 | 1425 | 882.5 | 0 | 156 | 830.305 | 80 | 3508 | 0 | 102 | 114 | 0 | 0 | 2 | 99 | Total Energy Requirement | 282.0912 |  | MKWHr
03:00 | 2864 | 1397 | 883 | 0 | 160 | 828.06 | 80 | 3629 | 0 | 113 | 122 | 0 | 0 | 4 | 96
03:30 | 2906.5 | 1405.5 | 882.5 | 0 | 158 | 866.065 | 80 | 3714.5 | 0 | 102 | 122 | 0 | 0 | 10 | 98.5
04:00 | 2949 | 1414 | 882 | 0 | 156 | 904.07 | 80 | 3800 | 0 | 91 | 122 | 0 | 0 | 16 | 101
04:30 | 2955.5 | 1389.75 | 882.5 | 0 | 152 | 869.64 | 80 | 3434.5 | 0 | 78.5 | 105.5 | 0 | 0 | 10.5 | 50.5
05:00 | 2962 | 1365.5 | 883 | 0 | 148 | 835.21 | 80 | 3069 | 0 | 66 | 89 | 0 | 0 | 5 | 0
05:30 | 2821.5 | 1355.5 | 882.5 | 0 | 143 | 832.345 | 80 | 3026 | 0 | 33 | 84.5 | 0 | 0 | 14 | 0
06:00 | 2681 | 1345.5 | 882 | 0 | 138 | 829.48 | 80 | 2983 | 0 | 0 | 80 | 0 | 0 | 23 | 0
06:30 | 2662 | 1350.5 | 882 | 0 | 137 | 831.475 | 80 | 2985 | 27.8 | 2 | 74 | 0 | 0 | 25.5 | 0
07:00 | 2643 | 1355.5 | 882 | 0 | 136 | 833.47 | 80 | 2987 | 55.6 | 4 | 68 | 0 | 0 | 28 | 0
07:30 | 2771 | 1420.75 | 881.5 | 0 | 141 | 838.72 | 80 | 3033.5 | 123.61 | 18.5 | 68 | 0 | 0 | 21 | 0
08:00 | 2899 | 1486 | 881 | 0 | 146 | 843.97 | 80 | 3080 | 191.62 | 33 | 68 | 0 | 0 | 14 | 0
08:30 | 2947.5 | 1518.5 | 883 | 0 | 148 | 883.985 | 80 | 3199.5 | 292.165 | 50 | 78.5 | 0 | 0 | 10.5 | 0
09:00 | 2996 | 1551 | 885 | 0 | 150 | 924 | 80 | 3319 | 392.71 | 67 | 89 | 0 | 0 | 7 | 0
09:30 | 2986 | 1533.5 | 885.5 | 0 | 154 | 921 | 80 | 3442.5 | 494.255 | 67 | 110.5 | 0 | 0 | 9.5 | 17.5
10:00 | 2976 | 1516 | 886 | 0 | 158 | 918 | 80 | 3566 | 595.8 | 67 | 132 | 0 | 0 | 12 | 35
10:30 | 3055 | 1515 | 886 | 0 | 160 | 933.5 | 80 | 3553.5 | 635.695 | 77 | 154.5 | 0 | 0 | 17.5 | 150
11:00 | 3134 | 1514 | 886 | 0 | 162 | 949 | 80 | 3541 | 675.59 | 87 | 177 | 0 | 0 | 23 | 265
11:30 | 3135 | 1545.5 | 892 | 0 | 160 | 1069 | 80 | 3478.5 | 675.295 | 89.5 | 254.5 | 0 | 0 | 24 | 317
12:00 | 3136 | 1577 | 898 | 0 | 158 | 1189 | 80 | 3416 | 675 | 92 | 332 | 0 | 0 | 25 | 369
12:30 | 3097.5 | 1568 | 897.5 | 0 | 165 | 1274 | 80 | 3497.5 | 664.2 | 83.5 | 426.5 | 0 | 0 | 36 | 376.5
13:00 | 3059 | 1559 | 897 | 0 | 172 | 1359 | 80 | 3579 | 653.4 | 75 | 521 | 0 | 0 | 47 | 384
13:30 | 3092 | 1574 | 897.5 | 0 | 181 | 1364.5 | 80 | 3686 | 593.535 | 84 | 558.5 | 0 | 0 | 38.5 | 386
14:00 | 3125 | 1589 | 898 | 0 | 190 | 1370 | 80 | 3793 | 533.67 | 93 | 596 | 0 | 0 | 30 | 388
14:30 | 3069 | 1585.5 | 897.5 | 0 | 188 | 1397 | 80 | 3986.5 | 482.965 | 101 | 616.5 | 0 | 0 | 34.5 | 420.5
15:00 | 3013 | 1582 | 897 | 0 | 186 | 1424 | 80 | 4180 | 432.26 | 109 | 637 | 0 | 0 | 39 | 453
15:30 | 3014 | 1600.25 | 897 | 0 | 182 | 1421.5 | 80 | 4230.5 | 368.08 | 112.5 | 638.5 | 0 | 0 | 31.5 | 384.5
16:00 | 3015 | 1618.5 | 897 | 0 | 178 | 1419 | 80 | 4281 | 303.9 | 116 | 640 | 0 | 0 | 24 | 316
16:30 | 3010 | 1634 | 897 | 0 | 172 | 1432.5 | 80 | 4352 | 202.985 | 159.5 | 716.5 | 0 | 0 | 18.5 | 222.5
17:00 | 3005 | 1649.5 | 897 | 0 | 166 | 1446 | 80 | 4423 | 102.07 | 203 | 793 | 0 | 0 | 13 | 129
17:30 | 3018 | 1645 | 897.5 | 0 | 165 | 1450 | 80 | 4369 | 52.66 | 244 | 1000.25 | 0 | 0 | 12 | 118
18:00 | 3031 | 1640.5 | 898 | 0 | 164 | 1454 | 80 | 4315 | 3.25 | 285 | 1207.5 | 0 | 0 | 11 | 107
18:30 | 3006 | 1616.75 | 864 | 0 | 168 | 1456 | 80 | 4343.5 | 1.625 | 323 | 1385.45 | 0 | 0 | 9 | 93
19:00 | 2981 | 1593 | 830 | 0 | 172 | 1458 | 80 | 4372 | 0 | 361 | 1563.4 | 0 | 0 | 7 | 79
19:30 | 2977 | 1514 | 897 | 0 | 172 | 1447 | 80 | 4424 | 0 | 426 | 1860.4 | 0 | 0 | 7 | 73
20:00 | 3037 | 1534 | 757 | 0 | 174 | 1446 | 80 | 4584 | 0 | 400 | 1713.5 | 0 | 0 | 10 | 72
20:30 | 3041.5 | 1537.25 | 827 | 0 | 173 | 1449 | 80 | 4607.5 | 0 | 379.5 | 1543.9 | 0 | 0 | 9 | 70
21:00 | 3046 | 1540.5 | 897 | 0 | 172 | 1452 | 80 | 4631 | 0 | 359 | 1374.3 | 0 | 0 | 8 | 68
21:30 | 3062.5 | 1552 | 897.5 | 0 | 172 | 1451.5 | 80 | 4630 | 0 | 357 | 1305.4 | 0 | 0 | 9.5 | 70.5
22:00 | 3079 | 1563.5 | 898 | 0 | 172 | 1451 | 80 | 4629 | 0 | 355 | 1236.5 | 0 | 0 | 11 | 73
22:30 | 3062.5 | 1548.25 | 897.5 | 0 | 173 | 1450 | 80 | 4569.5 | 0 | 320 | 1049.25 | 0 | 0 | 5.5 | 67
23:00 | 3046 | 1533 | 897 | 0 | 174 | 1449 | 80 | 4510 | 0 | 285 | 862 | 0 | 0 | 0 | 61
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 16-03-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 396 | 06:00 | 380 | 16:00 | Madunaghat | 403 | 07:00 | 395 | 15:00
Amtali | 416 | 06:00 | 411 | 00:00 | Meghnaghat | 396 | 06:00 | 382 | 16:00
Ashuganj | 404 | 6:00 | 390 | 14:00 | Payra | 418 | 06:00 | 408 | 16:00
Bhulta | 398 | 06:00 | 380 | 15:00 | Rahanpur | 419 | 00:00 | 396 | 16:00
Bibiana | 406 | 02:00 | 392 | 10:00 | Rampal | 408 | 06:00 | 393 | 16:00
BIPTC | 399 | 02:00 | 389 | 12:00
Bogura | 406 | 00:00 | 381 | 16:00
Gopalganj | 407 | 06:00 | 391 | 16:00
Kaliakoir | 389 | 06:00 | 358 | 10:00
Korerhat | 403 | 06:00 | 394 | 16:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 234 | 06:00 | 223 | 10:00 | Jhenaidah | 232 | 06:00 | 217 | 12:00
AKSML | 235 | 06:00 | 226 | 15:00 | Kachua | 231 | 06:00 | 222 | 00:00
Aminbazar | 233 | 06:00 | 224 | 11:00 | Kaliakoir | 236 | 06:00 | 221 | 10:00
Ashuganj | 231 | 03:00 | 223 | 15:00 | Keranigonj | 233 | 06:00 | 221 | 10:00
Ashuganj-400 | 232 | 6:00 | 218 | 14:00 | Khulna(S) | 235 | 06:00 | 221 | 21:00
Baghabari | 236 | 00:00 | 223 | 16:00 | Korerhat | 231 | 07:00 | 224 | 14:00
Barapukuria | 226 | 00:00 | 208 | 17:00 | Madunaghat | 232 | 08:00 | 228 | 00:00
Barapukuria-230 | 226 | 0:00 | 210 | 16:00 | Madunaghat-400 | 234 | 06:00 | 229 | 00:00
Barishal | 232 | 06:00 | 223 | 16:00 | Maniknagar | 229 | 05:00 | 220 | 15:00
Bheramara | 233 | 06:00 | 222 | 12:00 | Meghnaghat | 238 | 06:00 | 230 | 12:00
Bhulta | 232 | 06:00 | 221 | 15:00 | Meghnaghat-400 | 234 | 06:00 | 225 | 10:00
Bibiana | 236 | 06:00 | 229 | 10:00 | Mirsorai | 238 | 06:00 | 231 | 17:00
BIPTC | 235 | 06:00 | 221 | 14:00 | Purbasadipur | 226 | 00:00 | 209 | 16:00
Bogura | 242 | 00:00 | 226 | 16:00 | Rajshahi | 232 | 00:00 | 219 | 16:00
Bogura-400 | 241 | 00:00 | 226 | 16:00 | Rampal | 234 | 06:00 | 222 | 21:00
Borhanuddin | 235 | 06:00 | 229 | 21:00 | Rampur | N/A | N/A | N/A | N/A
BSRM | 230 | 06:00 | 223 | 15:00 | Rampura | 232 | 06:00 | 220 | 14:00
Chowmuhani | 0 | 00:00 | N/A | N/A | Shikalbaha | 233 | 06:00 | 227 | 00:00
Cumilla(N) | 232 | 06:00 | 223 | 15:00 | Shyampur | 233 | 06:00 | 222 | 16:00
Faridpur | 227 | 06:00 | 218 | 16:00 | Siddhirganj | 231 | 18:30 | 223 | 10:00
Fenchuganj | 242 | 06:00 | 234 | 14:00 | Sirajgonj | 241 | 06:00 | 230 | 16:00
Feni | 231 | 06:00 | 223 | 17:00 | Sreepur | 230 | 00:00 | 216 | 15:00
Ghorashal | 232 | 18:30 | 220 | 09:00 | Tongi | 230 | 04:00 | 218 | 09:00
Ghorashal-230 | 230 | 06:00 | 217 | 11:00
Gopalganj | 228 | 06:00 | 218 | 21:00
GPH | 233 | 08:00 | 226 | 00:00
Haripur | 232 | 06:00 | 222 | 15:00
Hasnabad | 232 | 18:00 | 222 | 10:00
Hathazari | 230 | 19:00 | 225 | 07:00
Ishurdi | 236 | 06:00 | 224 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 133 | 06:00 | 125 | 10:00 | Madunaghat | 134 | 05:00 | 130 | 23:00
Agargaon | 138 | 06:00 | 130 | 10:00 | Magura | 132 | 06:00 | 119 | 12:00
Agrabad | 133 | 05:00 | 129 | 00:00 | Mahasthangarh | 141 | 00:00 | 127 | 16:00
AKS | 131 | 05:00 | 126 | 15:00 | Maijdee | 128 | 06:00 | 123 | 00:00
Aminbazar | 134 | 05:00 | 128 | 11:00 | Manikganj | 134 | 05:00 | 124 | 10:00
Amnura | 139 | 00:00 | 126 | 14:00 | Maniknagar | 137 | 06:00 | 128 | 15:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 120 | 07:00 | 111 | 21:00
Ashuganj-230 | 140 | 06:00 | 133 | 21:00 | Matuail | 136 | 18:30 | 131 | 01:00
Bagerhat | 135 | 06:00 | 123 | 14:00 | Metrorail_Motijheel | 137 | 06:00 | 128 | 15:00
Bajitpur | 136 | 00:00 | 127 | 16:00 | Metrorail_Uttara | 134 | 18:30 | 126 | 10:00
Bakerganj | 134 | 06:00 | 130 | 15:00 | Millgate | 139 | 05:00 | 129 | 10:00
Bakulia | 133 | 04:00 | 129 | 00:00 | Mirpur | 133 | 05:00 | 126 | 10:00
Banani | 140 | 06:00 | 129 | 10:00 | Mirzapur | 138 | 00:00 | 125 | 10:00
Bangabhaban | 136 | 05:00 | 128 | 15:00 | Mithapukur | 138 | 00:00 | 125 | 16:00
Barapukuria | 140 | 00:00 | 125 | 17:00 | MI_Cement | 136.6 | 06:00 | 127 | 15:00
Barguna | 135 | 06:00 | 130 | 14:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 133 | 07:00 | 128 | 21:00 | Mogbazar | 131 | 06:00 | 125 | 10:00
Barishal-230 | 135 | 06:00 | 129 | 14:00 | Mongla | 133 | 04:00 | 124 | 14:00
Baroaulia | 133 | 04:00 | 129 | 14:00 | Motijheel | 136 | 05:00 | 128 | 15:00
Baroirhat | 133 | 06:00 | 127 | 00:00 | Muktagacha | 141 | 00:00 | 128 | 16:00
Bashundhara | 139 | 06:00 | 124 | 14:00 | Munshiganj | 136 | 18:30 | 129 | 10:00
BashundharaCement | 134 | 02:00 | 130 | 17:00 | Muradnagar | 131 | 06:00 | 126 | 00:00
Beanibazar | 135 | 01:00 | 127 | 14:00 | Mymensingh | 142 | 00:00 | 120 | 18:00
Benapole | 135 | 06:00 | 112 | 21:00 | Naogaon | 142 | 00:00 | 127 | 16:00
Bhaluka | 141 | 00:00 | 126 | 16:00 | Narail | 132 | 00:00 | 119 | 12:00
Bhandaria | 132 | 07:00 | 122 | 00:00 | Narinda | 137 | 6:00 | 128 | 15:00
Bhangura | 137 | 00:00 | 126 | 16:00 | Narshingdi | 130 | 18:30 | 123 | 17:00
Bheramara | 136 | 00:00 | 130 | 14:00 | Natore | 137 | 00:00 | 127 | 14:00
Bheramara(GK) | 136 | 00:00 | 131 | 12:00 | Nawabganj | 136 | 06:00 | 128 | 17:00
Bhulta | 129 | 05:00 | 123 | 15:00 | Netrakona | 141 | 00:00 | 120 | 18:00
Bog-Sherpur | 139 | 00:00 | 128 | 16:00 | New | 138 | 01:00 | 130 | 10:00
Bogura | 142 | 00:00 | 129 | 16:00 | Niamatpur | 140 | 00:00 | 131 | 16:00
Bogura-230 | 142 | 00:00 | 130 | 16:00 | Noapara | 136 | 06:00 | 124 | 14:00
Brahmanbaria | 135 | 01:00 | 126 | 22:00 | Pabna | 137 | 00:00 | 128 | 14:00
Cantonment | 137 | 06:00 | 129 | 10:00 | Palashbari | 138 | 00:00 | 123 | 16:00
Chandina | 134 | 06:00 | 128 | 15:00 | Panchagarh | 139 | 19:00 | 128 | 10:00
Chandpur | 132 | 19:30 | 125 | 00:00 | Patiya | 130 | 18:30 | 127 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 136 | 06:00 | 130 | 00:00 | Patuakhali | 134 | 07:00 | 129 | 23:00
Chapai | 139 | 02:00 | 129 | 18:00 | Payra | 136 | 05:00 | 133 | 14:00
Charsaidpur | 139 | 19:00 | 130 | 00:00 | PHP | 131 | 06:00 | 127 | 00:00
Chauddagram | 131 | 06:00 | 125 | 16:00 | Postogola | 136 | 05:00 | 129 | 10:00
Chhatak | 135 | 01:00 | 125 | 14:00 | Pubail | 136 | 04:00 | 128 | 10:00
Chowmuhani | 127 | 09:00 | 125 | 00:00 | Purbachal | 140 | 05:00 | 129 | 10:00
Chuadanga | 131 | 06:00 | 118 | 21:00 | Purbasadipur | 135 | 06:00 | 124 | 16:00
Coxsbazar | 122 | 06:00 | 112 | 21:00 | Rahanpur | 141 | 00:00 | 133 | 16:00
Cumilla(N) | 134 | 06:00 | 127 | 11:00 | Rahanpur-400 | 141 | 00:00 | 133 | 16:00
Cumilla(S) | 132 | 05:00 | 120 | 14:00 | Rahim | 135 | 07:00 | 130 | 10:00
Daganbhuiyan | 129 | 06:00 | 125 | 00:00 | Rajbari | 131 | 06:00 | 123 | 22:00
Daudkandi | 129 | 06:00 | 124 | 17:00 | Rajendrapur | 142 | 00:00 | 126 | 16:00
DhakaUniversity | 133 | 06:00 | 125 | 10:00 | Rajshahi | 134 | 00:00 | 125 | 14:00
Dhamrai | 139 | 05:00 | 129 | 10:00 | Rajshahi-230 | 135 | 00:00 | 126 | 16:00
Dhanmondi | 136 | 04:00 | 132 | 15:00 | Ramganj | 128 | 19:00 | 122 | 00:00
Dohazari | 128 | 02:00 | 123 | 23:00 | Rampur | 132 | 04:00 | 129 | 00:00
Faridpur | 132 | 06:00 | 124 | 23:00 | Rampura | 132 | 06:00 | 124 | 14:00
Fatullah | 135 | 05:00 | 127 | 16:00 | Rangamati | 134 | 05:00 | 130 | 00:00
Fenchuganj | 138 | 06:00 | 129 | 07:00 | Rangpur | 138 | 00:00 | 123 | 16:00
Feni | 129 | 05:00 | 124 | 16:00 | Ruppur | 137 | 00:00 | 130 | 14:00
Feni-230 | 130 | 06:00 | 125 | 15:00 | Saidpur | 137 | 06:00 | 123 | 16:00
Ghatail | 140 | 00:00 | 123 | 10:00 | Satkhira | 136 | 06:00 | 122 | 14:00
Ghorashal | 138 | 18:30 | 131 | 10:00 | Satmasjid | 137 | 08:00 | 130 | 10:00
Goalpara | 139 | 06:00 | 128 | 14:00 | Savar | 135 | 18:00 | 124 | 10:00
Gollamari | 139 | 06:00 | 128 | 14:00 | SevenRings | 137 | 06:00 | 131 | 10:00
Gopalganj | 136 | 06:00 | 127 | 21:00 | ShahCement | 139 | 19:00 | 130 | 00:00
Gopalganj-400 | 135 | 07:00 | 125 | 06:00 | Shahjadpur | 140 | 00:00 | 130 | 15:00
Gulshan | 132 | 06:00 | 124 | 15:00 | Shahjibazar | 137 | 08:00 | 125 | 21:00
Halishahar | 134 | 06:00 | 130 | 00:00 | Shahmirpur | 132 | 07:00 | 128 | 15:00
Haripur | 137 | 06:00 | 131 | 10:00 | Shariatpur | 134 | 06:00 | 126 | 16:00
HaripurSBU | 137 | 07:00 | 131 | 10:00 | Sherpur | 140 | 00:00 | 119 | 14:00
Hasnabad | 136 | 04:00 | 130 | 10:00 | Shikalbaha | 123 | 05:00 | 118 | 00:00
Hathazari | 134 | 05:00 | 131 | 01:00 | Shikalbaha-230 | 134 | 04:00 | 130 | 00:00
Hatirjheel | 133 | 06:00 | 124 | 15:00 | Shitalakhya | 137 | 06:00 | 127 | 15:00
Ishurdi | 139 | 06:00 | 131 | 14:00 | Sholosohor | 134 | 05:00 | 130 | 15:00
Jaldhaka | 136 | 23:00 | 121 | 16:00 | Shyampur | 133 | 19:00 | 120 | 12:00
Jamalpur | 142 | 00:00 | 127 | 09:00 | Shyampur-230 | 134 | 06:00 | 127 | 16:00
Jashore | 135 | 06:00 | 116 | 12:00 | Siddhirganj | 136 | 05:00 | 131 | 10:00
Jhenaidah | 132 | 03:00 | 121 | 12:00 | Sirajganj | 138 | 00:00 | 125 | 16:00
Jhenaidah-230 | 133 | 06:00 | 123 | 12:00 | Sonargaon | 132 | 04:00 | 128 | 10:00
Joydebpur | 136 | 19:00 | 125 | 10:00 | Sreemongol | 136 | 08:00 | 126 | 22:00
Joypurhat | 140 | 00:00 | 125 | 16:00 | Sreepur | 143 | 00:00 | 128 | 16:00
Juldah | 133 | 05:00 | 128 | 15:00 | Srinagar | 136 | 06:00 | 128 | 17:00
Kabirpur | 138 | 00:00 | 123 | 10:00 | SSM | 134 | 11:00 | 129 | 16:00
Kachua | 130 | 06:00 | 126 | 00:00 | Sunamganj | 133 | 02:00 | 124 | 21:00
Kaliakoir | 142 | 06:00 | 129 | 10:00 | Sylhet | 135 | 06:00 | 128 | 14:00
Kaliganj | 133 | 01:00 | 120 | 21:00 | Sylhet-132 | 134 | 07:00 | 128 | 15:00
Kallyanpur | 135 | 06:00 | 126 | 10:00 | Tangail | 136 | 01:00 | 121 | 13:00
Kalurghat | 135 | 06:00 | 130 | 16:00 | Taraganj | 137 | 00:00 | 125 | 16:00
Kamrangirchar | 135 | 05:00 | 125 | 10:00 | Tasnim | 134 | 05:00 | 128 | 09:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 139 | 20:00 | 125 | 16:00
Kasba | 132 | 06:00 | 124 | 17:00 | TK | 134 | 18:00 | 131 | 14:00
Kazla | 136 | 06:00 | 128 | 15:00 | Tongi | 140 | 04:00 | 133 | 09:00
Keranigonj | 137 | 06:00 | 129 | 10:00 | Ullahpara | 138 | 00:00 | 126 | 16:00
Khagrachori | 134 | 05:00 | 130 | 00:00 | Ullon | 132 | 06:00 | 124 | 15:00
Khulna | 136 | 05:00 | 127 | 14:00 | Uttara | 135 | 06:00 | 127 | 10:00
Khulna(S) | 139 | 06:00 | 129 | 14:00 | UttaraNew | 134 | 18:30 | 126 | 10:00
Khulshi | 132 | 05:00 | 128 | 00:00 | Zigatola | 136 | 06:00 | 128 | 17:00
Kishoreganj | 137 | 00:00 | 125 | 18:00
Kodda | 137 | 18:30 | 121 | 10:00
Korerhat | 132 | 06:00 | 129 | 00:00
KSRM | 134 | 06:00 | 130 | 00:00
Kulaura | 136 | 01:00 | 131 | 19:00
Kurigram | 135 | 00:00 | 120 | 16:00
Kushtia | 133 | 00:00 | 125 | 12:00
Laksam | 139 | 06:00 | 125 | 00:00
Lakshmipur | 128 | 06:00 | 123 | 00:00
Lalbag | 136 | 06:00 | 128 | 17:00
Lalmonirhat | 134 | 00:00 | 121 | 16:00
Madanganj | 134 | 02:00 | 130 | 17:00
Madaripur | 133 | 05:00 | 128 | 21:00
Madartek | 132 | 06:00 | 124 | 10:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division