## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 17-03-2026 | [28 empty] | Date: | 17-03-2026 | [28 empty] | Date: | 17-03-2026 | [28 empty] | Date: | 17-03-2026 | [28 empty] | Date: | 17-03-2026 | [17 empty] | Date: | 17-03-2026
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [17 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 342.010 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 6 | 301 | 0 | 0 | 17.5 | 17 | 123 | 15 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 250 | 0 | 0 | 0 | 70 | 18.5 | 22 | 0 | 340 | 0 | 0 | 84 | 0 | 2 | 68 | 0 | 0 | 10 | 12 | 0 | 80 | 0 | 25 | 680 | 0 | 0 | 50 | 0 | 0 | 226 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 0 | 150 | 300 | 51 | 0 | 193 | 0 | 0 | 100 | 17 | 0 | 20 | 0 | 166 | 0 | 0 | 0 | 305 | 0 | 349 | 41 | 0 | 149 | 0 | 17 | 0 | 5 | 30 | 100 | 0 | 96 | 0 | 59 | 48 | 9 | 0 | 0 | 0 | 6246 | 897 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 909 | 0 | 0 | 0 | 1219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 129 | 220 | 0 | 0 | 1160 | 0 | 5621 | 11867 | 88.03
01:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 6 | 308 | 0 | 0 | 17.5 | 0 | 89 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 280 | 0 | 0 | 0 | 52 | 18.5 | 22 | 0 | 340 | 0 | 0 | 55 | 0 | 12 | 68 | 0 | 0 | 12 | 12 | 0 | 80 | 0 | 25 | 680 | 0 | 0 | 50 | 0 | 0 | 226 | 0 | 0 | 0 | 1130 | 0 | 0 | 0 | 0 | 150 | 300 | 51 | 0 | 188 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 164 | 0 | 0 | 0 | 300 | 0 | 332 | 41 | 0 | 140 | 0 | 17 | 0 | 5 | 30 | 99 | 0 | 96 | 0 | 24 | 8 | 12 | 0 | 0 | 0 | 5963 | 897 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 901 | 0 | 0 | 0 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213 | 100 | 180 | 0 | 0 | 1100 | 0 | 5259 | 11222 | 88.02
02:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 6 | 297 | 0 | 0 | 17.5 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 250 | 0 | 0 | 0 | 35 | 18.5 | 22 | 0 | 340 | 0 | 0 | 43 | 0 | 1 | 68 | 0 | 0 | 12 | 12 | 0 | 80 | 0 | 30 | 680 | 0 | 0 | 50 | 0 | 0 | 225 | 0 | 0 | 0 | 990 | 0 | 0 | 0 | 0 | 150 | 300 | 5 | 0 | 191 | 0 | 0 | 100 | 0 | 0 | 17 | 0 | 162 | 0 | 0 | 0 | 300 | 0 | 336 | 41 | 0 | 135 | 0 | 17 | 0 | 5 | 30 | 99 | 0 | 96 | 0 | 35 | 25 | 15 | 0 | 0 | 0 | 5626 | 897 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 816 | 0 | 0 | 0 | 973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 100 | 180 | 0 | 0 | 1000 | 0 | 4773 | 10399 | 88.01
03:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 6 | 300 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 18.5 | 22 | 0 | 340 | 0 | 0 | 30 | 0 | 0 | 68 | 0 | 0 | 12 | 12 | 0 | 80 | 0 | 16 | 680 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 905 | 0 | 0 | 0 | 0 | 150 | 300 | 5 | 0 | 201 | 0 | 0 | 100 | 0 | 0 | 17 | 0 | 152 | 0 | 0 | 0 | 305 | 0 | 362 | 41 | 0 | 136 | 0 | 0 | 0 | 5 | 30 | 101 | 0 | 96 | 0 | 25 | 8 | 18 | 0 | 0 | 0 | 5425.5 | 897 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 812 | 0 | 0 | 0 | 929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 100 | 180 | 0 | 0 | 950 | 0 | 4658 | 10083.5 | 88
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 6 | 330 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 18.5 | 22 | 0 | 340 | 0 | 0 | 30 | 0 | 13 | 68 | 0 | 0 | 12 | 12 | 0 | 80 | 0 | 22 | 680 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 911 | 0 | 0 | 0 | 0 | 150 | 300 | 30 | 0 | 190 | 0 | 0 | 100 | 0 | 0 | 17 | 0 | 156 | 0 | 0 | 0 | 300 | 0 | 362 | 41 | 0 | 149 | 0 | 0 | 0 | 5 | 30 | 100 | 0 | 96 | 0 | 25 | 8 | 17 | 0 | 0 | 0 | 5536.5 | 898 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 761 | 0 | 0 | 0 | 833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 129 | 220 | 0 | 0 | 930 | 0 | 4730 | 10266.5 | 87.99
05:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 6 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 18.5 | 22 | 0 | 330 | 0 | 0 | 12 | 0 | 1 | 17 | 0 | 0 | 12 | 12 | 0 | 80 | 0 | 22 | 590 | 0 | 0 | 18 | 0 | 0 | 180 | 0 | 0 | 0 | 776 | 0 | 0 | 0 | 0 | 150 | 260 | 10 | 0 | 203 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 148 | 0 | 0 | 0 | 300 | 0 | 338 | 41 | 0 | 135 | 0 | 0 | 0 | 5 | 30 | 99 | 0 | 98 | 7 | 8 | 8 | 18 | 0 | 0 | 0 | 4947.5 | 897 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773 | 0 | 0 | 0 | 838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 100 | 180 | 0 | 0 | 700 | 0 | 4337 | 9284.5 | 87.98
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 340 | 0 | 0 | 0 | 0 | 10 | 17 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 27 | 580 | 0 | 0 | 19 | 0 | 0 | 180 | 0 | 0 | 0 | 690 | 0 | 0 | 0 | 0 | 150 | 290 | 0 | 0 | 170 | 0 | 0 | 100 | 0 | 0 | 8 | 0 | 130 | 0 | 0 | 0 | 295 | 0 | 384 | 41 | 0 | 124 | 0 | 17 | 0 | 0 | 7 | 101 | 0 | 98 | 17 | 8 | 8 | 20 | 0 | 0 | 0 | 4838 | 898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 824 | 0 | 0 | 0 | 446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 300 | 0 | 2557 | 7395 | 87.97
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 280 | 0 | 0 | 3 | 0 | 0 | 22 | 0 | 370 | 0 | 0 | 0 | 0 | 63 | 17 | 0 | 0 | 0 | 0 | 0.24 | 80 | 0 | 21 | 680 | 0 | 0 | 18 | 0 | 0 | 223 | 0 | 0 | 0 | 879 | 2 | 0 | 0 | 0 | 150 | 345 | 27 | 0 | 209 | 15 | 0 | 100 | 0 | 0 | 14 | 0 | 122 | 0 | 10 | 0 | 305 | 0 | 408 | 41 | 0 | 101 | 1 | 17 | 0 | 5 | 30 | 100 | 0 | 98 | 17 | 9 | 8 | 21 | 0 | 6.05 | 0 | 5498.29 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.63 | 971 | 0 | 0 | 0 | 608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.42 | 10 | 0 | 0 | 10.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46 | 0 | 52 | 0 | 3 | 0 | 0 | 0 | 0 | 0.6 | 18 | 0.34 | 0 | 0 | 70 | 35 | 0 | 0 | 220 | 0 | 2913.98 | 8412.27 | 87.96
08:00 | 0 | 8 | 5 | 0 | 0 | 0 | 0 | 6 | 355 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 360 | 0 | 0 | 280 | 0 | 0 | 12 | 0 | 26 | 22 | 0 | 368 | 0 | 0 | 2 | 0 | 44 | 17 | 0 | 0 | 0 | 0 | 0.81 | 80 | 0 | 15 | 680 | 0 | 0 | 27 | 0 | 0 | 223 | 0 | 0 | 0 | 1100 | 7 | 0 | 25 | 0 | 150 | 345 | 51 | 0 | 204 | 20 | 0 | 100 | 0 | 0 | 14 | 0 | 134 | 0 | 38 | 0 | 300 | 0 | 385 | 41 | 0 | 30 | 2 | 17 | 0 | 5 | 30 | 100 | 0 | 98 | 17 | 45 | 35 | 21 | 0 | 23.24 | 0 | 5900.05 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.3 | 1026 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.77 | 26 | 0 | 0 | 18.37 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 1.49 | 0 | 53 | 0 | 8 | 0 | 0 | 0 | 0 | 2.1 | 50 | 0.26 | 0 | 0 | 110 | 31 | 0 | 0 | 290 | 0 | 3334.29 | 9234.34 | 87.95
09:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 5 | 342 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 12 | 0 | 34 | 0 | 0 | 0 | 305 | 0 | 0 | 280 | 0 | 0 | 14 | 0 | 24 | 22 | 0 | 370 | 0 | 0 | 12 | 0 | 6 | 17 | 0 | 0 | 0 | 0 | 2.65 | 80 | 0 | 15 | 680 | 0 | 0 | 32 | 0 | 0 | 221 | 0 | 0 | 0 | 1160 | 13 | 12 | 26 | 0 | 150 | 350 | 51 | 0 | 200 | 20 | 4 | 100 | 0 | 0 | 14 | 0 | 136 | 0 | 54 | 0 | 305 | 0 | 398 | 41 | 0 | 20 | 7 | 17 | 0 | 5 | 30 | 101 | 0 | 99 | 17 | 45 | 35 | 19 | 1.4 | 30.12 | 0 | 6018.17 | 898 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.44 | 1036 | 0 | 0 | 0 | 752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.11 | 75 | 0 | 0 | 22.6 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3.29 | 0 | 52 | 0 | 20 | 0 | 0 | 0 | 0 | 4.3 | 124 | 0.38 | 0 | 0 | 129 | 45 | 0 | 0 | 550 | 0 | 3910.12 | 9928.29 | 87.94
10:00 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 5 | 338 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 15 | 0 | 33 | 0 | 0 | 0 | 300 | 0 | 0 | 280 | 0 | 0 | 21 | 0 | 23.5 | 22 | 0 | 350 | 0 | 0 | 12 | 0 | 13 | 17 | 0 | 0 | 0 | 0 | 3.2 | 80 | 0 | 15 | 580 | 0 | 0 | 33 | 0 | 0 | 219 | 0 | 0 | 0 | 1160 | 17 | 0 | 26 | 0 | 150 | 330 | 43 | 0 | 179 | 20 | 16 | 99 | 0 | 0 | 17 | 0 | 138 | 0 | 66 | 0 | 305 | 0 | 377 | 41 | 0 | 30 | 12 | 8 | 0 | 5 | 30 | 40 | 0 | 99 | 0 | 45 | 35 | 18 | 1.6 | 44.66 | 0 | 5803.96 | 898 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.21 | 1152 | 0 | 0 | 0 | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.82 | 60 | 0 | 0 | 27.21 | 0 | 0 | 72 | 0 | 0 | 0 | 108 | 0 | 4.15 | 0 | 51 | 0 | 27 | 0 | 0 | 0 | 0 | 5.7 | 169 | 0.36 | 0 | 0 | 129 | 110 | 0 | 0 | 690 | 0 | 4541.45 | 10345.41 | 87.93
11:00 | 0 | 34 | 29 | 0 | 0 | 0 | 0 | 6 | 322 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 15 | 0 | 16 | 0 | 0 | 0 | 285 | 0 | 0 | 280 | 0 | 0 | 15 | 0 | 23.5 | 22 | 0 | 350 | 0 | 0 | 12 | 0 | 3 | 17 | 0 | 0 | 12 | 12 | 3.71 | 80 | 0 | 13 | 580 | 0 | 0 | 34 | 0 | 0 | 218 | 0 | 0 | 0 | 1047 | 14 | 0 | 10 | 0 | 150 | 330 | 43 | 0 | 141 | 5 | 0 | 97 | 0 | 0 | 17 | 0 | 146 | 0 | 66 | 0 | 310 | 0 | 383 | 41 | 0 | 97 | 12 | 8 | 0 | 5 | 30 | 102 | 0 | 99 | 0 | 35 | 16 | 18 | 1.8 | 49.09 | 0 | 5689.1 | 897 | 268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 1098 | 0 | 0 | 0 | 845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.33 | 106 | 0 | 0 | 54.55 | 0 | 0 | 177 | 0 | 0 | 0 | 180 | 0 | 4.86 | 0 | 52 | 0 | 32 | 0 | 0 | 0 | 0 | 6.8 | 189 | 0.35 | 0 | 0 | 129 | 110 | 0 | 0 | 780 | 0 | 5045.89 | 10734.99 | 87.92
12:00 | 0 | 34 | 36 | 0 | 0 | 0 | 0 | 6 | 335 | 0 | 0 | 0 | 12 | 41 | 0 | 0 | 15 | 0 | 14 | 0 | 0 | 0 | 295 | 0 | 0 | 280 | 0 | 0 | 31 | 0 | 24 | 22 | 0 | 350 | 0 | 0 | 40 | 0 | 14 | 34 | 0 | 0 | 25 | 12 | 3.78 | 80 | 0 | 12 | 580 | 0 | 0 | 44 | 1 | 0 | 219 | 0 | 0 | 0 | 1073 | 18 | 0 | 0 | 0 | 150 | 300 | 43 | 0 | 190 | 0 | 0 | 97 | 0 | 1 | 17 | 0 | 154 | 0 | 76 | 0 | 315 | 0 | 388 | 41 | 0 | 155 | 10 | 17 | 0 | 5 | 30 | 100 | 0 | 98 | 0 | 55 | 16 | 16 | 2.2 | 44.46 | 0 | 5971.44 | 898 | 273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 1094 | 0 | 0 | 0 | 864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.26 | 113 | 0 | 0 | 63.51 | 0 | 0 | 196 | 0 | 0 | 0 | 349 | 0 | 5.66 | 0 | 52 | 0 | 34 | 0 | 0 | 0 | 0 | 7.1 | 204 | 0.5 | 0 | 0 | 129 | 110 | 0 | 0 | 790 | 0 | 5313.03 | 11284.47 | 87.91
13:00 | 0 | 34 | 41 | 0 | 0 | 0 | 0 | 6 | 349 | 0 | 0 | 0 | 17 | 51 | 0 | 0 | 15 | 0 | 15 | 0 | 0 | 0 | 310 | 0 | 0 | 280 | 0 | 0 | 29 | 0 | 24 | 22 | 0 | 380 | 0 | 0 | 80 | 0 | 16 | 34 | 0 | 0 | 25 | 25 | 3.28 | 80 | 0 | 20 | 580 | 0 | 0 | 46 | 16 | 0 | 218 | 0 | 0 | 0 | 1104 | 19 | 0 | 0 | 0 | 150 | 310 | 43 | 0 | 193 | 0 | 0 | 95 | 0 | 9 | 17 | 0 | 164 | 0 | 71 | 0 | 310 | 0 | 407 | 42 | 0 | 158 | 10 | 17 | 0 | 5 | 30 | 101 | 0 | 98 | 0 | 55 | 16 | 16 | 0 | 48.72 | 8 | 6213 | 897 | 268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 1116 | 0 | 0 | 0 | 1022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.59 | 94 | 0 | 0 | 62.07 | 0 | 0 | 208 | 0 | 0 | 0 | 409 | 0 | 5.56 | 0 | 52 | 0 | 33 | 0 | 0 | 0 | 0 | 6.4 | 187 | 0.61 | 0 | 0 | 125 | 110 | 0 | 0 | 820 | 0 | 5542.23 | 11755.23 | 87.9
14:00 | 0 | 34 | 41 | 0 | 0 | 0 | 0 | 6 | 353 | 0 | 0 | 0 | 17 | 51 | 0 | 0 | 16 | 0 | 17 | 0 | 0 | 0 | 355 | 0 | 0 | 280 | 0 | 0 | 26 | 17 | 24 | 22 | 0 | 380 | 0 | 0 | 70 | 0 | 21 | 34 | 0 | 0 | 25 | 25 | 3.1 | 80 | 0 | 15 | 580 | 0 | 0 | 50 | 16 | 0 | 219 | 0 | 0 | 0 | 1162 | 17 | 2 | 0 | 0 | 150 | 310 | 43 | 0 | 197 | 0 | 4 | 96 | 3 | 9 | 20 | 0 | 164 | 0 | 59 | 0 | 310 | 0 | 390 | 42 | 0 | 159 | 10 | 17 | 0 | 5 | 30 | 100 | 0 | 98 | 0 | 69 | 47 | 16 | 1.8 | 22.19 | 11 | 6341.09 | 897 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 1195 | 0 | 0 | 0 | 1225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.93 | 83 | 0 | 0 | 52.44 | 0 | 0 | 206 | 0 | 0 | 0 | 408 | 0 | 4.72 | 0 | 52 | 0 | 28 | 0 | 0 | 0 | 0 | 6 | 174 | 0.55 | 0 | 0 | 125 | 110 | 0 | 0 | 984 | 0 | 5924.64 | 12265.73 | 87.89
15:00 | 0 | 34 | 41 | 0 | 0 | 0 | 0 | 6 | 314 | 0 | 0 | 0 | 17 | 67 | 0 | 30 | 55 | 0 | 17 | 0 | 0 | 0 | 350 | 0 | 17 | 280 | 0 | 0 | 19 | 17 | 25.2 | 22 | 0 | 350 | 0 | 0 | 70 | 0 | 21 | 34 | 0 | 0 | 25 | 25 | 2.36 | 80 | 0 | 11 | 580 | 0 | 0 | 50 | 17 | 0 | 219 | 0 | 0 | 0 | 1165 | 13 | 45 | 0 | 0 | 150 | 315 | 43 | 0 | 202 | 0 | 30 | 95 | 47 | 9 | 20 | 0 | 178 | 0 | 51 | 0 | 315 | 0 | 342 | 42 | 0 | 148 | 8 | 17 | 0 | 33 | 30 | 75 | 0 | 97 | 0 | 69 | 45 | 16 | 0 | 31.87 | 12 | 6439.43 | 897 | 251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 1184 | 0 | 0 | 0 | 1306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.55 | 68 | 0 | 0 | 38.45 | 0 | 0 | 204 | 0 | 0 | 0 | 367 | 0 | 3.25 | 0 | 52 | 0 | 17 | 0 | 0 | 0 | 0 | 4.4 | 136 | 0.44 | 0 | 0 | 125 | 110 | 0 | 0 | 1040 | 0 | 5909.09 | 12348.52 | 87.88
16:00 | 0 | 34 | 41 | 0 | 0 | 0 | 0 | 6 | 330 | 0 | 0 | 17 | 17 | 71 | 0 | 30 | 55 | 0 | 17 | 0 | 0 | 0 | 360 | 0 | 17 | 280 | 0 | 0 | 9 | 35 | 25.2 | 22 | 0 | 370 | 0 | 0 | 70 | 0 | 18 | 34 | 0 | 0 | 25 | 25 | 1.43 | 80 | 0 | 22 | 580 | 0 | 0 | 50 | 17 | 0 | 219 | 0 | 0 | 0 | 1167 | 8 | 56 | 0 | 0 | 150 | 310 | 43 | 0 | 198 | 0 | 34 | 94 | 60 | 9 | 17 | 0 | 162 | 0 | 31 | 0 | 315 | 0 | 342 | 42 | 0 | 148 | 5 | 17 | 0 | 33 | 30 | 76 | 0 | 97 | 0 | 68 | 55 | 16 | 0.8 | 17.99 | 12 | 6491.42 | 897 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 1195 | 0 | 0 | 0 | 1359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.44 | 45 | 0 | 0 | 23.91 | 0 | 0 | 200 | 0 | 0 | 0 | 386 | 0 | 2.03 | 0 | 52 | 0 | 14 | 0 | 0 | 0 | 0 | 2.2 | 88 | 0.26 | 0 | 0 | 125 | 110 | 0 | 0 | 1050 | 0 | 5845.84 | 12337.26 | 87.87
17:00 | 0 | 34 | 41 | 0 | 0 | 0 | 0 | 6 | 315 | 0 | 0 | 17 | 17 | 103 | 4 | 30 | 55 | 18 | 28 | 0 | 0 | 0 | 350 | 0 | 17 | 280 | 0 | 0 | 5 | 46 | 24.2 | 22 | 0 | 320 | 0 | 0 | 70 | 0 | 21 | 34 | 0 | 0 | 25 | 25 | 0.52 | 80 | 0 | 30 | 580 | 0 | 0 | 50 | 23 | 0 | 220 | 0 | 0 | 0 | 1164 | 3 | 100 | 0 | 0 | 200 | 275 | 51 | 0 | 171 | 0 | 34 | 96 | 96 | 0 | 20 | 0 | 164 | 0 | 11 | 0 | 320 | 0 | 342 | 42 | 0 | 144 | 1 | 17 | 0 | 33 | 30 | 75 | 0 | 97 | 0 | 78 | 57 | 16 | 0 | 7.67 | 12 | 6547.39 | 897 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 1194 | 0 | 0 | 0 | 1452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.79 | 24 | 0 | 0 | 6.4 | 0 | 0 | 200 | 0 | 0 | 0 | 378 | 0 | 0.56 | 0 | 52 | 35 | 6 | 34 | 0 | 0 | 0 | 0.9 | 34 | 0.08 | 0 | 41 | 125 | 110 | 0 | 0 | 1150 | 0 | 6008.73 | 12556.12 | 87.86
18:00 | 0 | 40 | 50 | 0 | 0 | 0 | 0 | 6 | 299 | 0 | 0 | 17 | 17 | 133 | 15 | 65 | 55 | 55 | 35 | 0 | 0 | 0 | 350 | 0 | 17 | 280 | 0 | 0 | 0 | 108 | 24.2 | 22 | 0 | 310 | 0 | 0 | 71 | 0 | 21 | 40 | 0 | 0 | 50 | 50 | 0 | 80 | 0 | 30 | 580 | 17 | 0 | 50 | 25.5 | 0 | 220 | 0 | 0 | 0 | 1160 | 0 | 125 | 0 | 0 | 150 | 270 | 51 | 0 | 182 | 0 | 35 | 97 | 148 | 0 | 20 | 0 | 166 | 7 | 0 | 0 | 310 | 0 | 347 | 42 | 0 | 152 | 0 | 17 | 0 | 33 | 30 | 75 | 0 | 97 | 0 | 97 | 76 | 12 | 0 | 0.06 | 12 | 6843.76 | 897 | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1169 | 0 | 0 | 0 | 1438 | 0 | 0 | 0 | 20 | 7 | 0 | 0 | 0 | 0 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 348 | 0 | 0.02 | 0 | 54 | 110 | 0 | 100 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 102 | 125 | 110 | 0 | 0 | 1200 | 22 | 6138.34 | 12982.1 | 87.85
19:00 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 6 | 346 | 0 | 0 | 17 | 17 | 146 | 15 | 95 | 55 | 55 | 35 | 0 | 0 | 0 | 300 | 0 | 17 | 250 | 0 | 0 | 0 | 108 | 24.2 | 22 | 0 | 370 | 0 | 0 | 74 | 0 | 11 | 51 | 0 | 0 | 50 | 50 | 0 | 80 | 0 | 30 | 580 | 17 | 0 | 50 | 25.5 | 0 | 222 | 0 | 0 | 0 | 1181 | 0 | 144 | 0 | 0 | 150 | 320 | 51 | 0 | 198 | 0 | 35 | 98 | 176 | 0 | 20 | 0 | 172 | 16 | 0 | 1 | 280 | 0 | 407 | 42 | 0 | 149 | 0 | 17 | 0 | 33 | 30 | 75 | 0 | 97 | 0 | 97 | 76 | 16 | 0 | 0 | 12 | 7111.7 | 897 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1199 | 0 | 0 | 0 | 1464 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 54 | 115 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 156 | 125 | 120 | 0 | 0 | 1175 | 34 | 6333 | 13444.7 | 87.84
19:30 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 6 | 333 | 0 | 0 | 17 | 17 | 146 | 15 | 95 | 55 | 17 | 35 | 0 | 0 | 0 | 298 | 0 | 17 | 250 | 0 | 0 | 0 | 108 | 20.5 | 21 | 0 | 350 | 0 | 0 | 78 | 0 | 11 | 51 | 15 | 0 | 50 | 50 | 0 | 80 | 0 | 30 | 580 | 17 | 0 | 50 | 25.5 | 0 | 222 | 0 | 0 | 0 | 1224 | 0 | 143 | 0 | 0 | 150 | 290 | 51 | 0 | 187 | 0 | 17 | 98 | 172 | 0 | 20 | 0 | 166 | 16 | 0 | 1 | 310 | 0 | 385 | 42 | 0 | 158 | 0 | 17 | 0 | 33 | 30 | 75 | 0 | 97 | 0 | 98 | 76 | 18 | 0 | 0 | 12 | 7046 | 897 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1187 | 0 | 0 | 0 | 1450 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 54 | 115 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 157 | 125 | 130 | 0 | 0 | 1194 | 31 | 6353 | 13399
20:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 6 | 325 | 0 | 0 | 17 | 20 | 143 | 0 | 145 | 55 | 17 | 35 | 0 | 0 | 0 | 295 | 0 | 17 | 250 | 0 | 0 | 0 | 70 | 20.5 | 21 | 0 | 350 | 0 | 0 | 73 | 0 | 11 | 51 | 21 | 0 | 50 | 50 | 0 | 80 | 3 | 30 | 580 | 0 | 0 | 50 | 8 | 4 | 222 | 0 | 0 | 0 | 1226 | 0 | 142 | 0 | 0 | 150 | 295 | 51 | 0 | 185 | 0 | 20 | 98 | 175 | 0 | 20 | 0 | 170 | 0 | 0 | 7 | 305 | 0 | 385 | 41 | 0 | 155 | 0 | 17 | 0 | 33 | 30 | 75 | 0 | 98 | 0 | 98 | 76 | 17 | 0 | 0 | 12 | 6967.5 | 897 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1185 | 10 | 0 | 0 | 1451 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 54 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 125 | 65 | 0 | 0 | 1220 | 31 | 6309 | 13276.5 | 87.83
21:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 6 | 341 | 0 | 0 | 17 | 35 | 134 | 0 | 145 | 55 | 17 | 17 | 0 | 0 | 0 | 305 | 0 | 17 | 250 | 0 | 0 | 0 | 70 | 20.5 | 21 | 0 | 375 | 0 | 0 | 72 | 0 | 10 | 51 | 0 | 0 | 50 | 50 | 0 | 80 | 16 | 24 | 580 | 0 | 0 | 50 | 8 | 17 | 224 | 0 | 0 | 0 | 1223 | 0 | 143 | 0 | 0 | 150 | 320 | 51 | 0 | 200 | 0 | 17 | 99 | 185 | 0 | 20 | 0 | 168 | 0 | 0 | 7 | 305 | 0 | 410 | 41 | 0 | 160 | 0 | 17 | 0 | 33 | 30 | 75 | 0 | 98 | 0 | 98 | 78 | 18 | 0 | 0 | 12 | 7082.5 | 897 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 0 | 0 | 1456 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 54 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 125 | 60 | 0 | 0 | 1220 | 34 | 6374.2 | 13456.7 | 87.82
22:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 6 | 349 | 0 | 0 | 0 | 35 | 134 | 0 | 145 | 55 | 0 | 17 | 0 | 0 | 0 | 305 | 0 | 17 | 250 | 0 | 0 | 0 | 70 | 20 | 21 | 0 | 350 | 0 | 0 | 70 | 0 | 0 | 51 | 0 | 0 | 50 | 50 | 0 | 80 | 17 | 26 | 580 | 0 | 0 | 50 | 8 | 16 | 224 | 0 | 0 | 0 | 1224 | 0 | 142 | 0 | 0 | 160 | 295 | 51 | 0 | 193 | 0 | 17 | 100 | 186 | 0 | 20 | 0 | 170 | 0 | 0 | 7 | 310 | 0 | 390 | 41 | 0 | 159 | 0 | 17 | 0 | 33 | 30 | 75 | 0 | 98 | 0 | 98 | 78 | 18 | 0 | 0 | 12 | 6987 | 898 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 0 | 0 | 1457 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 54 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 125 | 60 | 0 | 0 | 1225 | 31 | 6507.2 | 13494.2 | 87.81
23:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 6 | 325 | 0 | 0 | 0 | 35 | 134 | 0 | 95 | 55 | 0 | 17 | 0 | 0 | 0 | 285 | 0 | 0 | 250 | 0 | 0 | 0 | 52 | 20 | 22 | 0 | 350 | 0 | 0 | 57 | 0 | 0 | 51 | 0 | 0 | 50 | 25 | 0 | 80 | 14 | 26 | 580 | 0 | 0 | 50 | 8 | 17 | 225 | 0 | 0 | 0 | 1222 | 0 | 145 | 0 | 0 | 210 | 300 | 51 | 0 | 192 | 0 | 0 | 100 | 85 | 0 | 20 | 0 | 168 | 0 | 0 | 7 | 300 | 0 | 368 | 41 | 0 | 151 | 0 | 17 | 0 | 5 | 30 | 75 | 0 | 97 | 0 | 58 | 48 | 18 | 0 | 0 | 12 | 6608 | 897 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 0 | 0 | 1438 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 55 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 125 | 170 | 0 | 0 | 1230 | 31 | 6483.2 | 13091.2 | 87.8
Total KWH | 0 | 723840 | 644640 | 0 | 0 | 0 | 0 | 162045.46 | 7959600 | 0 | 0 | 132480 | 301680 | 1727856 | 47040 | 812444 | 680606 | 133104 | 410400 | 0 | 0 | 0 | 7746364 | 0 | 140700 | 6514439 | 0 | 0 | 186756 | 771600 | 480600 | 520200 | 0 | 8373636.36 | 0 | 0 | 1090560 | 0 | 331200 | 923785 | 22176 | 0 | 524160 | 500160 | 23387 | 1926000 | 68580 | 273600 | 14843636.36 | 23418 | 0 | 983040 | 198826.2 | 75272 | 5345338 | 0 | 0 | 0 | 25881816 | 128115 | 1170909 | 117091 | 0 | 4022900 | 7448000 | 996274 | 0 | 4680000 | 82800 | 279360 | 2335840 | 1239840 | 37800 | 427230 | 0 | 3744000 | 34315 | 521891 | 32400 | 7376000 | 0 | 9136000 | 980000 | 0 | 3097473 | 81854 | 304896 | 0 | 335040 | 687264 | 2063000 | 0 | 2345060 | 81720 | 1320000 | 931200 | 384000 | 12050 | 324340 | 140640 | 148404287.38 | 21714909 | 4609440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581040 | 25294540 | 65760 | 0 | 0 | 26140119 | 0 | 0 | 0 | 205824 | 220032 | 0 | 0 | 0 | 0 | 344040 | 697320 | 0 | 0 | 392240 | 0 | 0 | 3898164 | 0 | 0 | 0 | 7000363 | 0 | 34380 | 0 | 1224436 | 702808 | 222344 | 647923 | 0 | 0 | 0 | 45538.08 | 1361520 | 4095 | 26304 | 2487000 | 2739000 | 3004170 | 0 | 0 | 23010909.09 | 206400 | 126880618.17 | 275284905.55

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 18-03-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-03-2026 | during | 18-03-2026 | during | 18-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 6 | 6 | 97.7 | 97.7 | 7 | 7 | Demand "05"MW due to gas restiction by Titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 335 | 341 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 1 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 250 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 24 | 20.5 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 21 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 36 | 33 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 145 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 41 | 134 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 34 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 14 | 17 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 12 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 350 | 375 | 584 | 584 | 320 | 320 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 295 | 305 | 583 | 583 | 320 | 320 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 70 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1495 | 1892.5 | 5946.22 | 5915.22 | 2725.05 | 2695.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 1 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 44 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 80 | 0 | 0 | 0 | 0 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 224 | 220 | 225 | 220 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 56 | 64 | 56 | 64 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 34 | 51 | 68 | 68 | 68 | 68 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 50 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 12 | 24 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 40 | 72 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.78 | 0 | 3.27 | 0 | 3.27 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 16 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 50 | 100 | 100 | 25 | 25 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1073 | 1223 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 14 | 10 | 1 | 1 | 1 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 580 | 580 | 580 | 580 | 580 | 580 | Coal shortage
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2155.78 | 2455 | 3407.13 | 3418.86 | 2834.77 | 2846.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 190 | 200 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 150 | 150 | 150 | 150 | 150 | 150 | Vibration
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 300 | 320 | 342.01 | 342.01 | 340 | 340 | FGMO ON
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0.01 | 0.01 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0.01 | 0.01 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 20 | 20 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 143 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 7 | 32 | 32 | 32 | 32 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 97 | 99 | 163 | 163 | 100 | 100 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 185 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 154 | 168 | 0 | 0 | 0 | 0 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 1 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 17 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 76 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2876.261 | 1028 | 1360 | 2472.36 | 2412.36 | 1787.22 | 1727.22
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-03-2026 | during | 18-03-2026 | during | 18-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 16 | 18 | 157.5 | 157.5 | 10 | 10 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 16 | 78 | 60 | 80 | 60 | 80 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 55 | 98 | 70 | 115 | 70 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 44.46 | 0 | 45.12 | 0 | 45.12 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | From12:00 hrs to24:00 hrs will be dispatching12MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 35 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 133.66 | 206 | 411.12 | 429 | 216.12 | 252
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 41 | 41 | 41 | 41 | 41 | plant availability zero
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 160 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 100 | 75 | 100 | 100 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 0 | 0 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 33 | 82 | 82 | 42 | 42 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 98 | 98 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 305 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 388 | 410 | 385 | 385 | 385 | 385 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | plant will be shutdown due to 3rd Minor Inspection
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1159 | 1169 | 1287 | 1287 | 1094 | 1094
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 898 | 897 | 0 | 0 | 0 | 0 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 273 | 222 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 73 | 0 | 93 | 0 | 93 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1094 | 1234.2 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2338 | 2370.2 | 2599.2 | 2506.2 | 1634.1 | 1541.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 129 | 125 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 790 | 1220 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 110 | 60 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 34 | 150 | 150 | 75 | 75 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 154 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.5 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1029.5 | 1593 | 2162 | 2161 | 1993 | 1992
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 57.26 | 0 | 57 | 0 | 57 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 196 | 196 | 220 | 220 | 190 | 190 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 349 | 414 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 21 | 21 | 21 | 21 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 50 | 50 | 50 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.66 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 864 | 1456 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 63.51 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 113 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1648.43 | 2136 | 3187.57 | 2963.87 | 2691.57 | 2467.87
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 52 | 54 | 53 | 53 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 106 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.1 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 21 | 0 | 21 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 204 | 0 | 179.97 | 0 | 179.97 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 297.1 | 275 | 487.17 | 281 | 434.17 | 228
System Total |  |  |  |  | 28823.2 | 29275.503 | 11284.47 | 13456.7 | 21959.77 | 21374.51 | 15410 | 14843.74
Forecast Scenario (18-03-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11760 |  | 0 |  | 11760
|  |  |  | 1:00 | 11120 |  | 0 |  | 11120
|  |  |  | 2:00 | 10290 |  | 0 |  | 10290
|  |  |  | 3:00 | 9980 |  | 0 |  | 9980
|  |  |  | 4:00 | 10160 |  | 0 |  | 10160
|  |  |  | 5:00 | 9180 |  | 0 |  | 9180
|  |  |  | 6:00 | 8600 |  | 0 |  | 8600
|  |  |  | 7:00 | 8600 |  | 0 |  | 8600
|  |  |  | 8:00 | 9300 |  | 0 |  | 9300
|  |  |  | 9:00 | 10000 |  | 0 |  | 10000
|  |  |  | 10:00 | 10300 |  | 0 |  | 10300
|  |  |  | 11:00 | 10630 |  | 0 |  | 10630
|  |  |  | 12:00 | 11180 |  | 0 |  | 11180
|  |  |  | 13:00 | 11750 |  | 0 |  | 11750
|  |  |  | 14:00 | 12160 |  | 0 |  | 12160
|  |  |  | 15:00 | 12240 |  | 0 |  | 12240
|  |  |  | 16:00 | 12230 |  | 0 |  | 12230
|  |  |  | 17:00 | 12450 |  | 0 |  | 12450
|  |  |  | 18:00 | 12880 |  | 0 |  | 12880
|  |  |  | 18:30 | 13050 |  | 0 |  | 13050
|  |  |  | 19:00 | 13328.03 |  | 0 |  | 13328.03
|  |  |  | 19:30 | 13290 |  | 0 |  | 13290
|  |  |  | 20:00 | 13170 |  | 0 |  | 13170
|  |  |  | 21:00 | 13350 |  | 0 |  | 13350
|  |  |  | 22:00 | 13390 |  | 0 |  | 13390
|  |  |  | 23:00 | 12800 |  | 0 |  | 12800
Probable Maximum Temperature: |  |  | 30.60°C
Probable Maximum Demand at Day Peak: |  |  | 11180.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13350.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13350.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 270.84803 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:32 hrs on 18-03-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 17-03-2026
Power Supply Scenario
| Day Peak Generation |  |  | 11284.47 | MW | 12:00 Hr. | Energy Generated |  |  | 275.2849 |  | MKWHr.
| Day Peak Demand |  |  | 11284.47 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 13456.7 | MW | 21:00 Hr. | Energy Demand |  |  | 275.2849 |  | MKWHr.
| Evening Peak Demand |  |  | 13456.7 | MW | 21:00 Hr. | Maximum Temperature |  |  | 29.7 |  | °C
| Minimum Generation of the Day |  |  | 7395 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 815.99 |  | MMCFD
| Maximum Generation of the Day |  |  | 13494.2 | MW | 22:00 Hr. | Production Cost per KWHr |  |  | 6.1127 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 31.7569 | 0 | 6.5264 | 0 | 0 | 0.18676 | 0 | 0 | 38.47 | Gas | 105.4458 | Gas | 361592614.8622
| Chattogram Zone |  |  | 5.6189 | 40.7255 | 4.41 | 0 | 1.926 | 0.1515 | 0 | 0.3312 | 53.1631 | Coal | 92.7423 | Coal | 629147063.8505
| Cumilla Zone |  |  | 20.1101 | 0 | 2.7946 | 0 | 0 | 0.52189 | 3.744 | 0 | 27.1706 | HFO | 18.2796 | HFO | 314214951.91
| Mymensingh Zone |  |  | 0.384 | 0 | 2.4736 | 0 | 0 | 0.33639 | 0 | 0 | 3.194 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.3247 | 0 | 0 | 0 | 0 | 0.081854 | 0 | 0 | 26.4066 | Hydro | 1.926 | Hydro | 192600
| Khulna Zone |  |  | 4.6094 | 25.2945 | 0.06576 | 0 | 0 | 0.58104 | 21.7149 | 0 | 52.2657 | Solar | 4.9609 | Solar | 79648749.916
| Barishal Zone |  |  | 5.7432 | 25.4979 | 0.2327 | 0 | 0 | 0.004095 | 0 | 0 | 31.4779 | Import | 51.599 | Import | 293074355.76
| Rajshahi Zone |  |  | 10.8985 | 0 | 0.42586 | 0 | 0 | 1.468 | 26.1401 | 0 | 38.9325 | Wind | 0.3312 | Wind | 4871952
| Rangpur Zone |  |  | 0 | 1.2244 | 1.3507 | 0 | 0 | 1.6294 | 0 | 0 | 4.2046
| Total |  |  | 105.4458 | 92.7423 | 18.2796 | 0 | 1.926 | 4.9609 | 51.599 | 0.3312 | 275.2849
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 361592614.8622 |  | Hydro | 192600
|  |  |  | Coal | 629147063.8505 |  | Solar | 79648749.916
|  |  |  | HFO | 314214951.91 |  | Import | 293074355.76
|  |  |  | HSD | 0 |  | Wind | 4871952
[5 empty] | Total: | 168,27,42,288 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7149 | Peak Hr Flow | 897.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 39729272.73 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.1401 | Peak Hr Flow | 1456.00 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2010 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.744 | Peak Hr Flow | 168.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2584 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 51.599 | Peak Hr Flow | 2521.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4818
|  |  |  | Chattogram |  | 0 |  | 1334
|  |  |  | Cumilla |  | 0 |  | 1341
|  |  |  | Mymensingh |  | 0 |  | 1025
|  |  |  | Sylhet |  | 0 |  | 436
|  |  |  | Khulna |  | 0 |  | 1680
|  |  |  | Barishal |  | 0 |  | 382
|  |  |  | Rajshahi |  | 0 |  | 1342
|  |  |  | Rangpur |  | 0 |  | 750
|  |  |  | Total |  | 0 |  | 13108
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:22 | Munshiganj 132/33kV S/S Transformer-2 LT is restored.
| 08:24 | 10:37 | Gopalganj 132/33kV S/S T2 LT Scheduled S/D Due to 33kV incoming DS maintenance | [7 empty] | 15.0MW load
interrup.
| 08:25 | 10:36 | Gopalganj 132/33kV S/S T2 HT Scheduled S/D Due to 33kV incoming DS maintenance | [7 empty] | 15.0MW load
interrup.
| 08:44 |  | Bhola Nutan Biddut BD LTD ST Synchronized with remarks:- STG was started and synchronized
to grid at 08:44 hrs.
| 08:52 | 12:28 | Cox'sbazar-Dohazari 132 kV Ckt-2 Scheduled S/D from Coxsbazar 132/33kV end Due to Disc
Cleaning and from Dohazari 132/33kV end Due to Disk Cleaning
|  | 09:02 | Bogura 230/132kV S/S Confidance UN-2 is restored.
| 09:29 | 11:46 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-1 Forced S/D from Bog-Sherpur 132/33kV end Due to
Red hot Maintenance and from Sirajganj 132/33kV end Due to Red Hot at Sherpur End
| 09:32 |  | Sirajgonj 400 MW CCPP Unit-4 Synchronized with remarks:- GT
|  | 09:42 | Bagerhat-Bhandaria 132 kV Ckt-1 is restored.
|  | 09:45 | Mongla 132/33kV S/S T-1 LT is restored.
| 09:56 | 11:06 | Amnura 132/33kV S/S T-1 (406T) LT Scheduled S/D Due to 33kV Bus Section-1 Shutdown.
| 09:56 | 11:05 | Amnura 132/33kV S/S T-1 (406T) HT Scheduled S/D Due to 33kV Bus Section-1 Shutdown.
|  | 10:08 | Bagerhat-Labanchura 132 kV Ckt-2 is restored.
| 10:35 |  | Sirajgonj 400 MW CCPP Unit-4 Synchronized with remarks:- ST
| 11:04 | 11:19 | Halishahar-Khulshi 132kV Ckt-2 Tripped from Halishahar 132/33kV end showing Distance
relay relays Due to Zone -1,general trip, B-phase trip
| 11:15 | 12:39 | Ghorashal 230kV S/S TARFO-2 HT Scheduled S/D Due to Transformer Body Grounding, LA | [7 empty] | 80.0MW load
|  |  | grounding Maintenance Work | [7 empty] | interrup.
| 12:00 |  | Day Peak Generation: 11281 MW.
| 12:11 | 12:36 | Bhandaria 132/33kV S/S Transformer-2 LT Forced S/D Due to Remove polybag from 33kv
bushing of T2
| 12:12 | 12:35 | Bhandaria 132/33kV S/S Transformer-2 HT Forced S/D Due to Remove polybag from 33kv
bushing of T2
|  | 12:53 | Saidpur 132/33kV S/S TR-01 HT is restored.
| 16:44 |  | Barisal 307 MW Synchronized
| 18:23 |  | Nutan Biddut CCPP GT-11 was synchronized
|  | 19:23 | Ashuganj-Bhulta 400 kV Ckt-2 is restored.
| 19:51 |  | Nutan Biddut CCPP ST tripped
| 21:00 |  | Evening peak generation 13456 MW
| 07:40 |  | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to Nut Bolt tighting | [7 empty] | 30.0MW load
interrup.
| 07:41 |  | Barishal 230/132kV S/S T-5 HT Scheduled S/D | [7 empty] | 30.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 17-03-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 6 | 162045.46 | Demand "05"MW due to gas restiction by Titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 341 | 7959600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 680606 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 250 | 6514439 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 132480 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 47040 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 133104 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 140700 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20.5 | 480600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 520200 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 33 | 644640 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 812444 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 134 | 1727856 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 723840 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 410400 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 186756 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 301680 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 375 | 8373636.36 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 305 | 7746364 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 70 | 771600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1892.5 | 38470030.82
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 198826.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 128115 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 983040 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1926000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 224 | 5345338 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 75272 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 22176 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 923785 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 524160 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 24 | 273600 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 72 | 1090560 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 23387 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 16 | 68580 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 500160 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 23418 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1223 | 25881816 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 10 | 331200 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 580 | 14843636.36 | Coal shortage
Chattogram Area Total |  |  |  |  | 4898.863 | 2455 | 53163069.56
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 200 | 4680000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 150 | 4022900 | Vibration
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 320 | 7448000 | FGMO ON
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 82800 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 117091 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 996274 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 143 | 1170909 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 7 | 32400 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 99 | 2335840 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 185 | 1239840 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 168 | 3744000 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 34315 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 427230 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 37800 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 17 | 279360 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 521891 | -
Cumilla Area Total |  |  |  |  | 2876.261 | 1360 | 27170650
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 18 | 384000 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 78 | 931200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 98 | 1320000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 324340 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 140640 | From12:00 hrs to24:00 hrs will be dispatching12MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 81720 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 206 | 3193950
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 81854 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 980000 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 160 | 3097473 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 75 | 2063000 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 687264 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 33 | 335040 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 98 | 2345060 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 304896 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7376000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 410 | 9136000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1169 | 26406587
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 897 | 21714909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 222 | 4609440 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 65760 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 581040 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1234.2 | 25294540 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2370.2 | 52265689
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 26304 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 125 | 2739000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1220 | 23010909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 60 | 3004170 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 34 | 206400 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 154 | 2487000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4095 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1593 | 31477878.09
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 344040 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 196 | 3898164 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 7000363 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 220032 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 205824 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 34380 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1456 | 26140119 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 392240 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 697320 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2136 | 38932482
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 54 | 1224436 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 647923 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 45538.08 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 702808 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 222344 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1361520 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 275 | 4204569.08
Eastern Grid Total |  |  |  |  | 17423.308 | 7082.5 | 148404287.38
Western Grid Total |  |  |  |  | 11852.195 | 6374.2 | 126880618.17
National Grid Total |  |  |  |  | 29275.503 | 13456.7 | 275284905.55
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 17-03-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8953.65 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4153.6 | MW
i) Dhaka area |  |  | 4818.05 |  | MW | i) Khulna area |  |  |  | 1679.5 | MW
ii) Chattogram area |  |  | 1333.6 |  | MW | ii) Barishal area |  |  |  | 382.3 | MW
iii) Cumilla area |  |  | 1341 |  | MW | iii) Rajshahi area |  |  |  | 1341.8 | MW
iv) Mymensingh area |  |  | 1025 |  | MW | iv) Rangpur area |  |  |  | 750 | MW
v) Sylhet area |  |  | 436 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13107.25 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 18 | 06:00 | 67 | Hasnabad | 80 | 22:00 | 133 | Nawabganj | 44.8 | 21:00
2 | AKSML | 8.3 | 11:00 | 68 | Hathazari | 80 | 21:00 | 134 | Netrakona | 125 | 18:00
3 | Aftabnagar | 30 | 00:00 | 69 | Hatirjheel | 32 | 20:00 | 135 | New | 64 | 11:00
4 | Agargaon | 87 | 19:00 | 70 | Ishurdi | 63 | 00:00 | 136 | Niamatpur | 82 | 21:00
5 | Agrabad | 60 | 19:00 | 71 | Jaldhaka | 76 | 18:00 | 137 | Noapara | 48 | 19:00
6 | Amnura | 32 | 21:00 | 72 | Jamalpur | 106 | 18:30 | 138 | PHP | 8 | 00:00
7 | Ashuganj | 80 | 15:00 | 73 | Jashore | 142 | 19:00 | 139 | Pabna | 85 | 03:00
8 | BSRM | 203 | 03:00 | 74 | Jhenaidah | 99 | 18:00 | 140 | Palashbari | 94 | 18:30
9 | Bagerhat | 75 | 20:00 | 75 | Joydebpur | 118 | 12:00 | 141 | Panchagarh | 53 | 18:00
10 | Bajitpur | 81 | 18:30 | 76 | Joypurhat | 53 | 19:00 | 142 | Patiya | 10 | 00:00
11 | Bakerganj | 9.3 | 21:00 | 77 | Juldah | 16 | 23:00 | 143 | Patuakhali | 58.7 | 22:00
12 | Bakulia | 70 | 19:30 | 78 | KSRM | 10 | 08:00 | 144 | Payra | 26 | 00:00
13 | Banani | 24 | 19:00 | 79 | Kabirpur | 229 | 15:00 | 145 | Postogola | 43 | 00:00
14 | Bangabhaban | 4 | 05:00 | 80 | Kachua | 90 | 18:00 | 146 | Pubail | 25 | 00:00
15 | Barapukuria | 55 | 21:00 | 81 | Kaliganj | 28 | 18:30 | 147 | Purbachal | 22 | 00:00
16 | Barguna | 18 | 00:00 | 82 | Kallyanpur | 96 | 19:30 | 148 | Purbasadipur | 99 | 19:30
17 | Barishal | 90 | 20:00 | 83 | Kalurghat | 46 | 12:00 | 149 | Rahanpur | 35 | 03:00
18 | Barishal-230 | 86 | 18:30 | 84 | Kamrangirchar | 68 | 00:00 | 150 | Rahim | 29 | 01:00
19 | Baroaulia | 73 | 15:00 | 85 | Kaptai | N/A | N/A | 151 | Rajbari | 71 | 00:00
20 | Baroirhat | 60 | 19:00 | 86 | Kasba | 35 | 21:00 | 152 | Rajendrapur | 116 | 18:00
21 | Bashundhara | 147 | 19:00 | 87 | Kazla | 97 | 00:00 | 153 | Rajshahi | 91 | 00:00
22 | BashundharaCement | 12 | 01:00 | 88 | Keranigonj | 75 | 00:00 | 154 | Rajshahi-230 | 78 | 00:00
23 | Beanibazar | 56 | 18:30 | 89 | Khagrachori | 30 | 18:30 | 155 | Ramganj | 100 | 22:00
24 | Benapole | 75 | 13:00 | 90 | Khulna | 48 | 13:00 | 156 | Rampur | 38 | 18:30
25 | Bhaluka | 154 | 18:00 | 91 | Khulshi | 155 | 19:00 | 157 | Rangamati | 16 | 18:30
26 | Bhandaria | 48 | 00:00 | 92 | Kishoreganj | 116 | 18:30 | 158 | Rangpur | 134 | 18:00
27 | Bhangura | 40 | 14:00 | 93 | Kodda | 287 | 11:00 | 159 | Ruppur | 3.4 | 09:00
28 | Bheramara(GK) | 56 | 00:00 | 94 | Kulaura | 32 | 18:00 | 160 | SSM | 2 | 00:00
29 | Bhulta | 214 | 11:00 | 95 | Kurigram | 56 | 18:00 | 161 | Saidpur | 95 | 17:00
30 | Bog-Sherpur | 72 | 22:00 | 96 | Kushtia | 126 | 00:00 | 162 | Satkhira | 124 | 19:30
31 | Bogura | 134 | 03:00 | 97 | Laksam | 19 | 22:00 | 163 | Satmasjid | 84 | 19:30
32 | Borhanuddin | 83 | 00:00 | 98 | Lakshmipur | 42 | 23:00 | 164 | Savar | 188 | 12:00
33 | Brahmanbaria | 117 | 21:00 | 99 | Lalbag | 62 | 11:00 | 165 | SevenRings | 17.26 | 10:00
34 | Cantonment | 124 | 19:30 | 100 | Lalmonirhat | 50 | 22:00 | 166 | ShahCement | 32 | 12:00
35 | Chandina | 22 | 09:00 | 101 | MI_Cement | 18.5 | 05:00 | 167 | Shahjadpur | 77 | 19:00
36 | Chandpur | 74 | 22:00 | 102 | Madanganj | 28 | 01:00 | 168 | Shahjibazar | 104 | 22:00
37 | Chandraghona | 34 | 19:00 | 103 | Madaripur | 98 | 21:00 | 169 | Shahmirpur | 57 | 19:00
38 | Chapai | 69 | 21:00 | 104 | Madartek | 64 | 00:00 | 170 | Shariatpur | 80 | 22:00
39 | Charsaidpur | 40 | 02:00 | 105 | Madunaghat | 46 | 20:00 | 171 | Sherpur | 130 | 18:00
40 | Chauddagram | 70 | 18:00 | 106 | Magura | 62 | 19:00 | 172 | Shikalbaha | 29 | 00:00
41 | Chhatak | 28 | 00:00 | 107 | Mahasthangarh | 66 | 21:00 | 173 | Shitalakhya | 71.9 | 12:00
42 | Chowmuhani | 127 | 19:00 | 108 | Maijdee | 34 | 00:00 | 174 | Sholosohor | 39 | 12:00
43 | Chuadanga | 109 | 00:00 | 109 | Manikganj | 116 | 21:00 | 175 | Shyampur | 166 | 13:00
44 | Coxsbazar | 131 | 21:00 | 110 | Maniknagar | 57 | 19:00 | 176 | Siddhirganj | 107 | 15:00
45 | Cumilla(N) | 114 | 19:30 | 111 | Matarbari | 49 | 03:00 | 177 | Sirajganj | 110 | 21:00
46 | Cumilla(S) | 176 | 15:00 | 112 | Matuail | 61 | 12:00 | 178 | Sonargaon | 151 | 21:00
47 | Daganbhuiyan | 32 | 00:00 | 113 | Metrorail_Motijheel | 26 | 15:00 | 179 | Sreemongol | 62 | 18:30
48 | Daudkandi | 136 | 21:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sreepur | 105 | 19:30
49 | DhakaUniversity | 48 | 13:00 | 115 | Millgate | 77 | 14:00 | 181 | Srinagar | 43.68 | 22:00
50 | Dhamrai | 124 | 08:00 | 116 | Mirpur | 114 | 20:00 | 182 | Sunamganj | 42 | 23:00
51 | Dhanmondi | 86.5 | 20:00 | 117 | Mirsorai | 9 | 00:00 | 183 | Sylhet | 47 | 18:00
52 | Dohazari | 102 | 18:00 | 118 | Mirzapur | 49 | 18:00 | 184 | Sylhet-132 | 77 | 22:00
53 | Faridpur | 150 | 19:00 | 119 | Mithapukur | 54 | 18:00 | 185 | TK | 22 | 18:30
54 | Fatullah | 88 | 09:00 | 120 | Modern | N/A | N/A | 186 | Tangail | 185 | 18:00
55 | Fenchuganj | 31 | 00:00 | 121 | Mogbazar | 43.4 | 14:00 | 187 | Taraganj | 20 | 18:00
56 | Feni | 93 | 18:30 | 122 | Mongla | 49 | 19:00 | 188 | Tasnim | 10 | 07:00
57 | GPH | 17 | 01:00 | 123 | Motijheel | 32 | 20:00 | 189 | Thakurgaon | 89 | 19:00
58 | Ghatail | 92 | 18:00 | 124 | Muktagacha | 36 | 18:30 | 190 | Tongi | 118 | 15:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 117 | 21:00 | 191 | Ullahpara | 41 | 15:00
60 | Ghorashal-230 | 105 | 23:00 | 126 | Muradnagar | 37 | 21:00 | 192 | Ullon | 46 | 19:00
61 | Goalpara | 36 | 19:00 | 127 | Mymensingh | 155 | 00:00 | 193 | Uttara | 70 | 19:30
62 | Gollamari | 98 | 19:00 | 128 | Naogaon | 113 | 22:00 | 194 | UttaraNew | 27 | 20:00
63 | Gopalganj | 97.7 | 19:30 | 129 | Narail | 59 | 18:30 | 195 | Zigatola | 78 | 19:00
64 | Gulshan | 80 | 19:30 | 130 | Narinda | 52 | 13:00
65 | Halishahar | 74 | 15:00 | 131 | Narshingdi | 167 | 20:00
66 | HaripurSBU | 125 | 03:00 | 132 | Natore | 138 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 17-03-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 11867 | 0 |  | 11867
1:00 | 11222 | 0 |  | 11222
2:00 | 10399 | 0 |  | 10399
3:00 | 10083.5 | 0 |  | 10083.5
4:00 | 10266.5 | 0 |  | 10266.5
5:00 | 9284.5 | 0 |  | 9284.5
6:00 | 7395 | 0 |  | 7395
7:00 | 8412.27 | 0 |  | 8412.27
8:00 | 9234.34 | 0 |  | 9234.34
9:00 | 9928.29 | 0 |  | 9928.29
10:00 | 10345.41 | 0 |  | 10345.41
11:00 | 10734.99 | 0 |  | 10734.99
12:00 | 11284.47 | 0 |  | 11284.47
13:00 | 11755.23 | 0 |  | 11755.23
14:00 | 12265.73 | 0 |  | 12265.73
15:00 | 12348.52 | 0 |  | 12348.52
16:00 | 12337.26 | 0 |  | 12337.26
17:00 | 12556.12 | 0 |  | 12556.12
18:00 | 12982.1 | 0 |  | 12982.1
19:00 | 13444.7 | 0 |  | 13444.7
19:30 | 13399 | 0 |  | 13399
20:00 | 13276.5 | 0 |  | 13276.5
21:00 | 13456.7 | 0 |  | 13456.7
22:00 | 13494.2 | 0 |  | 13494.2
23:00 | 13091.2 | 0 |  | 13091.2
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 17-03-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6246 | 5621 | 11867 | DAILY GENERATION CURVE
00:30 | 6104.5 | 5440 | 11544.5
01:00 | 5963 | 5259 | 11222 | 17-03-2026
01:30 | 5794.5 | 5016 | 10810.5
02:00 | 5626 | 4773 | 10399
02:30 | 5525.75 | 4715.5 | 10241.25
03:00 | 5425.5 | 4658 | 10083.5
03:30 | 5481 | 4694 | 10175
04:00 | 5536.5 | 4730 | 10266.5
04:30 | 5242 | 4533.5 | 9775.5
05:00 | 4947.5 | 4337 | 9284.5
05:30 | 4892.75 | 3447 | 8339.75
06:00 | 4838 | 2557 | 7395
06:30 | 5168.145 | 2735.49 | 7903.635
07:00 | 5498.29 | 2913.98 | 8412.27
07:30 | 5699.17 | 3124.135 | 8823.305
08:00 | 5900.05 | 3334.29 | 9234.34
08:30 | 5959.11 | 3622.205 | 9581.315
09:00 | 6018.17 | 3910.12 | 9928.29
09:30 | 5911.065 | 4225.785 | 10136.85
10:00 | 5803.96 | 4541.45 | 10345.41
10:30 | 5746.53 | 4793.67 | 10540.2
11:00 | 5689.1 | 5045.89 | 10734.99
11:30 | 5830.27 | 5179.46 | 11009.73
12:00 | 5971.44 | 5313.03 | 11284.47
12:30 | 6092.22 | 5427.63 | 11519.85
13:00 | 6213 | 5542.23 | 11755.23
13:30 | 6277.045 | 5733.435 | 12010.48
14:00 | 6341.09 | 5924.64 | 12265.73
14:30 | 6390.26 | 5916.865 | 12307.125
15:00 | 6439.43 | 5909.09 | 12348.52
15:30 | 6465.425 | 5877.465 | 12342.89
16:00 | 6491.42 | 5845.84 | 12337.26
16:30 | 6519.405 | 5927.285 | 12446.69
17:00 | 6547.39 | 6008.73 | 12556.12
17:30 | 6695.575 | 6073.535 | 12769.11
18:00 | 6843.76 | 6138.34 | 12982.1
18:30 | 6977.73 | 6235.67 | 13213.4
19:00 | 7111.7 | 6333 | 13444.7
19:30 | 7046 | 6353 | 13399
20:00 | 6967.5 | 6309 | 13276.5
20:30 | 7025 | 6341.6 | 13366.6 |  | Executive Engineer
21:00 | 7082.5 | 6374.2 | 13456.7 |  | Network Operation Division
21:30 | 7034.75 | 6440.7 | 13475.45
22:00 | 6987 | 6507.2 | 13494.2
22:30 | 6797.5 | 6495.2 | 13292.7
23:00 | 6608 | 6483.2 | 13091.2

## En-Curve
QF-LDC-12
Date | 17-03-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3032 | 1543.5 | 897 | 0 | 166 | 1219 | 80 | 4238 | 0 | 203 | 486.5 | 0 | 0 | 2 | 0 | DAILY ENERGY CURVE
00:30 | 2994 | 1511.5 | 897 | 0 | 165 | 1169.5 | 80 | 4158 | 0 | 178 | 384.5 | 0 | 0 | 7 | 0 | 17-03-2026
01:00 | 2956 | 1479.5 | 897 | 0 | 164 | 1120 | 80 | 4078 | 0 | 153 | 282.5 | 0 | 0 | 12 | 0
01:30 | 2871 | 1430 | 897 | 0 | 163 | 1046.5 | 80 | 3907.5 | 0 | 144.5 | 264.5 | 0 | 0 | 6.5 | 0 | Energy Generated | 275.2849 |  | MKWHr
02:00 | 2786 | 1380.5 | 897 | 0 | 162 | 973 | 80 | 3737 | 0 | 136 | 246.5 | 0 | 0 | 1 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2811 | 1370.5 | 897 | 0 | 157 | 951 | 80 | 3654.5 | 0 | 127 | 192.75 | 0 | 0 | 0.5 | 0 | Total Energy Requirement | 275.2849 |  | MKWHr
03:00 | 2836 | 1360.5 | 897 | 0 | 152 | 929 | 80 | 3572 | 0 | 118 | 139 | 0 | 0 | 0 | 0
03:30 | 2971.5 | 1402.5 | 897.5 | 0 | 154 | 881 | 80 | 3537.5 | 0 | 105.5 | 139 | 0 | 0 | 6.5 | 0
04:00 | 3107 | 1444.5 | 898 | 0 | 156 | 833 | 80 | 3503 | 0 | 93 | 139 | 0 | 0 | 13 | 0
04:30 | 2953 | 1395.5 | 897.5 | 0 | 152 | 835.5 | 80 | 3283.5 | 0 | 63.5 | 108 | 0 | 0 | 7 | 0
05:00 | 2799 | 1346.5 | 897 | 0 | 148 | 838 | 80 | 3064 | 0 | 34 | 77 | 0 | 0 | 1 | 0
05:30 | 2469.5 | 1260.75 | 897.5 | 0 | 139 | 642 | 80 | 2755.5 | 0 | 25.5 | 64.5 | 0 | 0 | 5.5 | 0
06:00 | 2140 | 1175 | 898 | 0 | 130 | 446 | 80 | 2447 | 0 | 17 | 52 | 0 | 0 | 10 | 0
06:30 | 2282.5 | 1219 | 897.5 | 0 | 126 | 527 | 80 | 2624.5 | 41.635 | 17 | 52 | 0 | 0 | 36.5 | 0
07:00 | 2425 | 1263 | 897 | 0 | 122 | 608 | 80 | 2802 | 83.27 | 17 | 52 | 0 | 0 | 63 | 0
07:30 | 2446.5 | 1266.5 | 897 | 0 | 128 | 683 | 80 | 2975.5 | 164.805 | 23.5 | 105 | 0 | 0 | 53.5 | 0
08:00 | 2468 | 1270 | 897 | 0 | 134 | 758 | 80 | 3149 | 246.34 | 30 | 158 | 0 | 0 | 44 | 0
08:30 | 2532 | 1247 | 897.5 | 0 | 135 | 755 | 80 | 3313.5 | 350.315 | 48.5 | 197.5 | 0 | 0 | 25 | 0
09:00 | 2596 | 1224 | 898 | 0 | 136 | 752 | 80 | 3478 | 454.29 | 67 | 237 | 0 | 0 | 6 | 0
09:30 | 2655.5 | 1241.75 | 898 | 0 | 137 | 756.5 | 80 | 3555.5 | 502.1 | 71 | 230 | 0 | 0 | 9.5 | 0
10:00 | 2715 | 1259.5 | 898 | 0 | 138 | 761 | 80 | 3633 | 549.91 | 75 | 223 | 0 | 0 | 13 | 0
10:30 | 2842.5 | 1279.5 | 897.5 | 0 | 142 | 803 | 80 | 3595 | 610.7 | 77.5 | 204.5 | 0 | 0 | 8 | 0
11:00 | 2970 | 1299.5 | 897 | 0 | 146 | 845 | 80 | 3557 | 671.49 | 80 | 186 | 0 | 0 | 3 | 0
11:30 | 3080.5 | 1335.25 | 897.5 | 0 | 150 | 854.5 | 80 | 3573 | 707.48 | 92 | 231 | 0 | 0 | 8.5 | 0
12:00 | 3191 | 1371 | 898 | 0 | 154 | 864 | 80 | 3589 | 743.47 | 104 | 276 | 0 | 0 | 14 | 0
12:30 | 3245 | 1396.5 | 897.5 | 0 | 159 | 943 | 80 | 3630.5 | 719.85 | 106.5 | 327 | 0 | 0 | 15 | 0
13:00 | 3299 | 1422 | 897 | 0 | 164 | 1022 | 80 | 3672 | 696.23 | 109 | 378 | 0 | 0 | 16 | 0
13:30 | 3289.5 | 1444 | 897 | 0 | 164 | 1123.5 | 80 | 3822.5 | 648.98 | 117.5 | 405 | 0 | 0 | 18.5 | 0
14:00 | 3280 | 1466 | 897 | 0 | 164 | 1225 | 80 | 3973 | 601.73 | 126 | 432 | 0 | 0 | 21 | 0
14:30 | 3202 | 1458.1 | 897 | 0 | 171 | 1265.5 | 80 | 3997 | 550.025 | 126 | 539.5 | 0 | 0 | 21 | 0
15:00 | 3124 | 1450.2 | 897 | 0 | 178 | 1306 | 80 | 4021 | 498.32 | 126 | 647 | 0 | 0 | 21 | 0
15:30 | 3131 | 1469.2 | 897 | 0 | 170 | 1332.5 | 80 | 4032.5 | 400.19 | 135 | 676 | 0 | 0 | 19.5 | 0
16:00 | 3138 | 1488.2 | 897 | 0 | 162 | 1359 | 80 | 4044 | 302.06 | 144 | 705 | 0 | 0 | 18 | 0
16:30 | 3121.5 | 1467.7 | 897 | 0 | 163 | 1405.5 | 80 | 4112.5 | 213.99 | 151.5 | 814.5 | 0 | 0 | 19.5 | 0
17:00 | 3105 | 1447.2 | 897 | 0 | 164 | 1452 | 80 | 4181 | 125.92 | 159 | 924 | 0 | 0 | 21 | 0
17:30 | 3055.5 | 1441.2 | 897 | 0 | 165 | 1445 | 80 | 4223 | 65.16 | 206 | 1170.25 | 0 | 0 | 21 | 0
18:00 | 3006 | 1435.2 | 897 | 0 | 166 | 1438 | 80 | 4265 | 4.4 | 253 | 1416.5 | 0 | 0 | 21 | 0
18:30 | 3094.5 | 1428.7 | 897 | 0 | 169 | 1451 | 80 | 4305 | 2.2 | 264 | 1506 | 0 | 0 | 16 | 0
19:00 | 3183 | 1422.2 | 897 | 0 | 172 | 1464 | 80 | 4345 | 0 | 275 | 1595.5 | 0 | 0 | 11 | 0
19:30 | 3127 | 1444.5 | 897 | 0 | 166 | 1450 | 80 | 4396 | 0 | 290 | 1537.5 | 0 | 0 | 11 | 0
20:00 | 3123 | 1368.5 | 897 | 0 | 170 | 1451 | 80 | 4418 | 0 | 216 | 1542 | 0 | 0 | 11 | 0
20:30 | 3168 | 1383 | 897 | 0 | 169 | 1453.5 | 80 | 4441.6 | 0 | 205.5 | 1558.5 | 0 | 0 | 10.5 | 0
21:00 | 3213 | 1397.5 | 897 | 0 | 168 | 1456 | 80 | 4465.2 | 0 | 195 | 1575 | 0 | 0 | 10 | 0
21:30 | 3189.5 | 1387.75 | 897.5 | 0 | 169 | 1456.5 | 80 | 4539.7 | 0 | 195 | 1555.5 | 0 | 0 | 5 | 0
22:00 | 3166 | 1378 | 898 | 0 | 170 | 1457 | 80 | 4614.2 | 0 | 195 | 1536 | 0 | 0 | 0 | 0
22:30 | 3166 | 1400.5 | 897.5 | 0 | 169 | 1447.5 | 80 | 4621.2 | 0 | 182 | 1329 | 0 | 0 | 0 | 0
23:00 | 3166 | 1423 | 897 | 0 | 168 | 1438 | 80 | 4628.2 | 0 | 169 | 1122 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 17-03-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 397 | 03:00 | 382 | 15:00 | Madunaghat | 408 | 07:00 | 395 | 00:00
Amtali | 421 | 06:00 | 405 | 14:00 | Meghnaghat | 403 | 06:00 | 385 | 15:00
Ashuganj | 414 | 6:00 | 392 | 14:00 | Payra | 419 | 06:00 | 407 | 16:00
Bhulta | 407 | 06:00 | 385 | 14:00 | Rahanpur | 415 | 06:00 | 396 | 17:00
Bibiana | 407 | 07:00 | 400 | 01:00 | Rampal | 413 | 06:00 | 394 | 14:00
BIPTC | 398 | 04:00 | 389 | 11:00
Bogura | 406 | 06:00 | 379 | 17:00
Gopalganj | 418 | 06:00 | 392 | 14:00
Kaliakoir | 392 | 06:00 | 376 | 15:00
Korerhat | 415 | 06:00 | 396 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 237 | 06:00 | 225 | 14:00 | Jhenaidah | 235 | 01:00 | 218 | 13:00
AKSML | 240 | 06:00 | 227 | 00:00 | Kachua | 238 | 06:00 | 223 | 00:00
Aminbazar | 234 | 5:00 | 225 | 12:00 | Kaliakoir | 241 | 06:00 | 228 | 15:00
Ashuganj | 237 | 06:00 | 225 | 00:00 | Keranigonj | 236 | 06:00 | 223 | 14:00
Ashuganj-400 | 237 | 06:00 | 225 | 00:00 | Khulna(S) | 239 | 06:00 | 221 | 21:00
Baghabari | 235 | 05:00 | 224 | 16:00 | Korerhat | 237 | 06:00 | 225 | 00:00
Barapukuria | 227 | 00:00 | 210 | 17:00 | Madunaghat | 239 | 06:00 | 228 | 00:00
Barapukuria-230 | 227 | 00:00 | 210 | 17:00 | Madunaghat-400 | 239 | 07:00 | 230 | 00:00
Barishal | 236 | 06:00 | 223 | 15:00 | Maniknagar | 235 | 06:00 | 224 | 13:00
Bheramara | 234 | 01:00 | 222 | 08:00 | Meghnaghat | 240 | 05:00 | 232 | 13:00
Bhulta | 238 | 06:00 | 224 | 15:00 | Meghnaghat-400 | 240 | 06:00 | 227 | 00:00
Bibiana | 238 | 07:00 | 231 | 00:00 | Mirsorai | 242 | 06:00 | 232 | 00:00
BIPTC | 237 | 01:00 | 222 | 08:00 | Purbasadipur | 227 | 00:00 | 208 | 16:00
Bogura | 238 | 02:00 | 225 | 17:00 | Rajshahi | 233 | 05:00 | 221 | 08:00
Bogura-400 | 240 | 06:00 | 225 | 17:00 | Rampal | 237 | 06:00 | 221 | 14:00
Borhanuddin | 236 | 04:00 | 227 | 15:00 | Rampur | N/A | N/A | N/A | N/A
BSRM | 236 | 06:00 | 224 | 00:00 | Rampura | 236 | 06:00 | 224 | 14:00
Chowmuhani | 230 | 7:00 | 224 | 16:00 | Shikalbaha | 237 | 07:00 | 229 | 00:00
Cumilla(N) | 237 | 06:00 | 225 | 00:00 | Shyampur | 237 | 06:00 | 224 | 00:00
Faridpur | 233 | 06:00 | 219 | 13:00 | Siddhirganj | 239 | 06:00 | 226 | 00:00
Fenchuganj | 243 | 06:00 | 235 | 00:00 | Sirajgonj | 240 | 05:00 | 230 | 17:00
Feni | 237 | 06:00 | 225 | 00:00 | Sreepur | 228 | 05:00 | 218 | 13:00
Ghorashal | 232 | 07:00 | 225 | 00:00 | Tongi | 237 | 06:00 | 224 | 00:00
Ghorashal-230 | 234 | 06:00 | 222 | 00:00
Gopalganj | 234 | 06:00 | 219 | 14:00
GPH | 232 | 18:00 | 226 | 02:00
Haripur | 237 | 06:00 | 225 | 00:00
Hasnabad | 239 | 21:00 | 224 | 13:00
Hathazari | 238 | 06:00 | 225 | 16:00
Ishurdi | 236 | 01:00 | 225 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 133 | 07:00 | 124 | 13:00 | Madunaghat | 140 | 06:00 | 131 | 00:00
Agargaon | 139 | 06:00 | 132 | 14:00 | Magura | 134 | 01:00 | 119 | 13:00
Agrabad | 137 | 06:00 | 130 | 00:00 | Mahasthangarh | 137 | 05:00 | 127 | 17:00
AKS | 137 | 06:00 | 129 | 00:00 | Maijdee | 133 | 06:00 | 124 | 00:00
Aminbazar | 134 | 03:00 | 129 | 00:00 | Manikganj | 136 | 11:00 | 126 | 17:00
Amnura | 136 | 05:00 | 127 | 16:00 | Maniknagar | 139 | 06:00 | 131 | 14:00
Ashuganj | 142 | 06:00 | 134 | 00:00 | Matarbari | 134 | 06:00 | 111 | 00:00
Ashuganj-230 | 142 | 06:00 | 134 | 00:00 | Matuail | 137 | 18:00 | 132 | 16:00
Bagerhat | 144 | 01:00 | 120 | 18:00 | Metrorail_Motijheel | 139 | 06:00 | 131 | 14:00
Bajitpur | 134 | 03:00 | 127 | 16:00 | Metrorail_Uttara | 134 | 18:00 | 121 | 07:00
Bakerganj | 139 | 06:00 | 130 | 14:00 | Millgate | 141 | 06:00 | 130 | 16:00
Bakulia | 139 | 06:00 | 130 | 00:00 | Mirpur | 138 | 06:00 | 128 | 00:00
Banani | 139 | 05:00 | 130 | 16:00 | Mirzapur | 136 | 06:00 | 127 | 16:00
Bangabhaban | 140 | 06:00 | 131 | 15:00 | Mithapukur | 139 | 00:00 | 126 | 16:00
Barapukuria | 142 | 00:00 | 126 | 17:00 | MI_Cement | 139 | 06:00 | 130 | 13:00
Barguna | 138 | 02:00 | 130 | 14:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 138 | 06:00 | 128 | 17:00 | Mogbazar | 133 | 06:00 | 127 | 13:00
Barishal-230 | 138 | 06:00 | 129 | 14:00 | Mongla | 141 | 02:00 | 121 | 17:00
Baroaulia | 139 | 06:00 | 130 | 00:00 | Motijheel | 140 | 06:00 | 131 | 15:00
Baroirhat | 137 | 06:00 | 128 | 16:00 | Muktagacha | 134 | 06:00 | 122 | 17:00
Bashundhara | 142 | 06:00 | 127 | 13:00 | Munshiganj | 136 | 08:00 | 130 | 13:00
BashundharaCement | 136 | 20:00 | 131 | 09:00 | Muradnagar | 136 | 06:00 | 126 | 00:00
Beanibazar | 134 | 07:00 | 127 | 15:00 | Mymensingh | 136 | 08:00 | 122 | 16:00
Benapole | 140 | 01:00 | 113 | 13:00 | Naogaon | 139 | 02:00 | 126 | 17:00
Bhaluka | 134 | 02:00 | 125 | 13:00 | Narail | 134 | 01:00 | 118 | 13:00
Bhandaria | 135 | 03:00 | 125 | 00:00 | Narinda | 139 | 06:00 | 131 | 14:00
Bhangura | 134 | 02:00 | 126 | 17:00 | Narshingdi | 136 | 06:00 | 125 | 13:00
Bheramara | 136 | 02:00 | 126 | 08:00 | Natore | 135 | 01:00 | 127 | 17:00
Bheramara(GK) | 136 | 05:00 | 127 | 07:00 | Nawabganj | 140 | 06:00 | 130 | 00:00
Bhulta | 130 | 18:00 | 124 | 15:00 | Netrakona | 135 | 02:00 | 120 | 13:00
Bog-Sherpur | 137 | 05:00 | 128 | 15:00 | New | 143 | 06:00 | 130 | 17:00
Bogura | 138 | 02:00 | 130 | 16:00 | Niamatpur | 138 | 06:00 | 130 | 23:00
Bogura-230 | 138 | 02:00 | 130 | 16:00 | Noapara | 138 | 01:00 | 124 | 14:00
Brahmanbaria | 138 | 06:00 | 127 | 14:00 | Pabna | 135 | 05:00 | 127 | 08:00
Cantonment | 140 | 06:00 | 132 | 00:00 | Palashbari | 137 | 00:00 | 124 | 17:00
Chandina | 137 | 06:00 | 129 | 00:00 | Panchagarh | 138 | 18:30 | 125 | 16:00
Chandpur | 136 | 06:00 | 125 | 00:00 | Patiya | 139 | 06:00 | 128 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 140 | 06:00 | 132 | 00:00 | Patuakhali | 136 | 02:00 | 129 | 14:00
Chapai | 137 | 04:00 | 130 | 14:00 | Payra | 138 | 06:00 | 132 | 14:00
Charsaidpur | 137 | 07:00 | 131 | 13:00 | PHP | 135 | 06:00 | 127 | 00:00
Chauddagram | 134 | 06:00 | 126 | 00:00 | Postogola | 138 | 05:00 | 132 | 08:00
Chhatak | 136 | 06:00 | 126 | 00:00 | Pubail | 136 | 19:00 | 131 | 13:00
Chowmuhani | 134 | 06:00 | 125 | 00:00 | Purbachal | 141 | 06:00 | 130 | 16:00
Chuadanga | 134 | 02:00 | 118 | 13:00 | Purbasadipur | 136 | 00:00 | 124 | 16:00
Coxsbazar | 130 | 05:00 | 111 | 23:00 | Rahanpur | 139 | 05:00 | 131 | 17:00
Cumilla(N) | 136 | 06:00 | 129 | 00:00 | Rahanpur-400 | 139 | 05:00 | 132 | 17:00
Cumilla(S) | 133 | 05:00 | 123 | 11:00 | Rahim | 139 | 06:00 | 131 | 13:00
Daganbhuiyan | 134 | 06:00 | 125 | 00:00 | Rajbari | 133 | 06:00 | 123 | 22:00
Daudkandi | 136 | 06:00 | 125 | 00:00 | Rajendrapur | 136 | 06:00 | 126 | 17:00
DhakaUniversity | 136 | 06:00 | 126 | 11:00 | Rajshahi | 133 | 02:00 | 125 | 16:00
Dhamrai | 146 | 06:00 | 133 | 07:00 | Rajshahi-230 | 134 | 02:00 | 127 | 08:00
Dhanmondi | 140.5 | 06:00 | 133 | 14:00 | Ramganj | 132 | 06:00 | 123 | 00:00
Dohazari | 137 | 06:00 | 123 | 00:00 | Rampur | 134 | 05:00 | 130 | 00:00
Faridpur | 134 | 06:00 | 126 | 13:00 | Rampura | 134 | 06:00 | 127 | 13:00
Fatullah | 142 | 06:00 | 128 | 14:00 | Rangamati | 139 | 06:00 | 131 | 00:00
Fenchuganj | 139 | 06:00 | 133 | 00:00 | Rangpur | 140 | 00:00 | 126 | 15:00
Feni | 132 | 06:00 | 125 | 00:00 | Ruppur | 136 | 05:00 | 130 | 6:00
Feni-230 | 133 | 06:00 | 126 | 00:00 | Saidpur | 138 | 00:00 | 124 | 17:00
Ghatail | 133 | 01:00 | 121 | 17:00 | Satkhira | 141 | 01:00 | 121 | 19:00
Ghorashal | 139 | 19:30 | 133 | 19:00 | Satmasjid | 139 | 06:00 | 131 | 14:00
Goalpara | 140 | 01:00 | 127 | 14:00 | Savar | 138 | 06:00 | 127 | 00:00
Gollamari | 141 | 06:00 | 127 | 17:00 | SevenRings | 140 | 06:00 | 133 | 00:00
Gopalganj | 137 | 01:00 | 127 | 16:00 | ShahCement | 138 | 06:00 | 131 | 13:00
Gopalganj-400 | 139 | 06:00 | 130 | 14:00 | Shahjadpur | 137 | 05:00 | 131 | 16:00
Gulshan | 134 | 06:00 | 126 | 14:00 | Shahjibazar | 137 | 06:00 | 126 | 01:00
Halishahar | 135 | 05:00 | 130 | 00:00 | Shahmirpur | 139 | 06:00 | 130 | 00:00
Haripur | 140 | 06:00 | 132 | 14:00 | Shariatpur | 137 | 06:00 | 127 | 14:00
HaripurSBU | 137 | 19:00 | 131 | 10:00 | Sherpur | 138 | 01:00 | 123 | 00:00
Hasnabad | 141 | 06:00 | 131 | 14:00 | Shikalbaha | 125 | 05:00 | 119 | 00:00
Hathazari | 140 | 06:00 | 132 | 00:00 | Shikalbaha-230 | 138 | 07:00 | 131 | 00:00
Hatirjheel | 135 | 06:00 | 127 | 13:00 | Shitalakhya | 139 | 06:00 | 130 | 13:00
Ishurdi | 138 | 02:00 | 131 | 08:00 | Sholosohor | 139 | 06:00 | 131 | 00:00
Jaldhaka | 138 | 00:00 | 121 | 17:00 | Shyampur | 134 | 06:00 | 126 | 13:00
Jamalpur | 140 | 01:00 | 125 | 23:00 | Shyampur-230 | 137 | 06:00 | 129 | 00:00
Jashore | 138 | 01:00 | 116 | 13:00 | Siddhirganj | 138 | 18:00 | 133 | 00:00
Jhenaidah | 135 | 04:00 | 122 | 08:00 | Sirajganj | 133 | 03:00 | 125 | 16:00
Jhenaidah-230 | 137 | 01:00 | 122 | 15:00 | Sonargaon | 137 | 06:00 | 130 | 04:00
Joydebpur | 136 | 18:30 | 129 | 01:00 | Sreemongol | 137 | 06:00 | 127 | 01:00
Joypurhat | 134 | 05:00 | 123 | 17:00 | Sreepur | 137 | 02:00 | 129 | 13:00
Juldah | 136 | 05:00 | 130 | 00:00 | Srinagar | 140 | 06:00 | 130 | 00:00
Kabirpur | 141 | 06:00 | 130 | 16:00 | SSM | 142 | 06:00 | 132 | 00:00
Kachua | 136 | 06:00 | 126 | 00:00 | Sunamganj | 133 | 04:00 | 124 | 22:00
Kaliakoir | 148 | 06:00 | 135 | 14:00 | Sylhet | 136 | 06:00 | 128 | 01:00
Kaliganj | 136 | 01:00 | 121 | 13:00 | Sylhet-132 | 135 | 06:00 | 129 | 00:00
Kallyanpur | 135 | 07:00 | 128 | 14:00 | Tangail | 133 | 06:00 | 123 | 17:00
Kalurghat | 139 | 06:00 | 131 | 00:00 | Taraganj | 139 | 00:00 | 123 | 17:00
Kamrangirchar | 140 | 06:00 | 127 | 00:00 | Tasnim | 138 | 07:00 | 130 | 10:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 137 | 18:30 | 123 | 16:00
Kasba | 135 | 06:00 | 126 | 00:00 | TK | 136 | 06:00 | 131 | 00:00
Kazla | 139 | 07:00 | 131 | 14:00 | Tongi | 145 | 06:00 | 132 | 15:00
Keranigonj | 140 | 06:00 | 130 | 14:00 | Ullahpara | 134 | 05:00 | 126 | 15:00
Khagrachori | 138 | 06:00 | 130 | 00:00 | Ullon | 134 | 06:00 | 127 | 00:00
Khulna | 140 | 01:00 | 126 | 18:00 | Uttara | 135 | 18:00 | 128 | 00:00
Khulna(S) | 141 | 02:00 | 128 | 16:00 | UttaraNew | 134 | 18:00 | 128 | 00:00
Khulshi | 138 | 06:00 | 129 | 00:00 | Zigatola | 137 | 06:00 | 130 | 14:00
Kishoreganj | 132 | 03:00 | 125 | 17:00
Kodda | 136 | 18:30 | 126 | 00:00
Korerhat | 138 | 06:00 | 128 | 13:00
KSRM | 136 | 03:00 | 130 | 00:00
Kulaura | 137 | 04:00 | 131 | 00:00
Kurigram | 140 | 00:00 | 120 | 17:00
Kushtia | 134 | 02:00 | 124 | 08:00
Laksam | 132 | 18:30 | 128 | 00:00
Lakshmipur | 133 | 06:00 | 124 | 00:00
Lalbag | 138 | 18:00 | 130 | 15:00
Lalmonirhat | 138 | 00:00 | 121 | 17:00
Madanganj | 136 | 20:00 | 131 | 09:00
Madaripur | 135 | 02:00 | 129 | 13:00
Madartek | 133 | 06:00 | 126 | 15:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division