## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 19-03-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-03-2026 | during | 19-03-2026 | during | 19-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 6 | 6 | 97.7 | 97.7 | 7 | 7 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 334 | 311 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 250 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 14.7 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 15.5 | 0 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 8 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 45 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 52 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 17 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 16 | 104 | 104 | 0 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 47 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 18 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 330 | 310 | 584 | 584 | 320 | 320 | FGMO
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 340 | 290 | 583 | 583 | 320 | 320 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 70 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1384.5 | 1438.7 | 5947.22 | 5915.22 | 2726.05 | 2798.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 15 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 32 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 80 | 0 | 0 | 0 | 0 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 180 | 220 | 220 | 220 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 15 | 56 | 64 | 56 | 64 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 68 | 68 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 90 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 30 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 4 | 60 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.62 | 0 | 3.51 | 0 | 3.51 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 27 | 50 | 100 | 100 | 25 | 25 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1163 | 1056 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 6 | 1 | 5 | 1 | 5 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 390 | 317 | 320 | 320 | 320 | 320 | Coal shortage
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1958.62 | 2010.5 | 3131.37 | 3135.86 | 2576.01 | 2580.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 203 | 197 | 220 | 220 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 200 | 0 | 150 | 150 | 150 | 150 | Vibration
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 345 | 285 | 342.01 | 342.01 | 342.01 | 342.01 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 20 | 20 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 32 | 32 | 32 | 32 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 97 | 96 | 163 | 163 | 100 | 100 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 150 | 146 | 0 | 0 | 0 | 0 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 16 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 53 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2876.261 | 1119 | 811 | 2471.36 | 2411.36 | 2182.22 | 2122.22
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-03-2026 | during | 19-03-2026 | during | 19-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 23 | 71 | 157.5 | 157.5 | 10 | 10 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.3 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 35 | 60 | 80 | 60 | 80 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 35 | 70 | 115 | 70 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 46.59 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 12 | 12 | From12:00 hrs to24:00 hrs will be dispatching12MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 35 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 196.89 | 141 | 411 | 429 | 216 | 252
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 41 | 41 | 41 | 41 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 159 | 136 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 74 | 75 | 75 | 75 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 0 | 0 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 5 | 82 | 82 | 42 | 42 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 97 | 96 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 310 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 367 | 348 | 385 | 385 | 385 | 385 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1117 | 1059 | 1262 | 1262 | 1094 | 1094
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 897 | 897 | 0 | 0 | 0 | 0 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 216 | 239 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 100 | 1 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 995 | 1015 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2208 | 2152 | 2591.2 | 2506.2 | 1626.1 | 1541.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 125 | 125 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1000 | 1125 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 16 | 150 | 150 | 75 | 75 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 266 | 226 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.66 | 0.01 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1611.66 | 1712.01 | 2162 | 2161 | 1993 | 1992
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 52.02 | 0.12 | 55 | 0 | 55 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 195 | 170 | 220 | 220 | 190 | 190 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 346 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 21 | 21 | 21 | 21 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 60 | 50 | 50 | 50 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.28 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1068.72 | 1331.11 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 55.92 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 101 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1891.94 | 1977.23 | 3185.57 | 2963.87 | 2689.57 | 2467.87
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 53 | 53 | 54 | 54 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.2 | 0.2 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 125 | 1 | 194.26 | 0 | 194.26 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 215.2 | 194.2 | 531.46 | 302 | 457.46 | 228
System Total |  |  |  |  | 28823.2 | 29275.503 | 11702.81 | 11495.64 | 21693.18 | 21086.51 | 15560.41 | 15075.74
Forecast Scenario (19-03-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8700 |  | 0 |  | 8700
|  |  |  | 1:00 | 8600 |  | 0 |  | 8600
|  |  |  | 2:00 | 8400 |  | 0 |  | 8400
|  |  |  | 3:00 | 8600 |  | 0 |  | 8600
|  |  |  | 4:00 | 9300 |  | 0 |  | 9300
|  |  |  | 5:00 | 9000 |  | 0 |  | 9000
|  |  |  | 6:00 | 8700 |  | 0 |  | 8700
|  |  |  | 7:00 | 8900 |  | 0 |  | 8900
|  |  |  | 8:00 | 9100 |  | 0 |  | 9100
|  |  |  | 9:00 | 9700 |  | 0 |  | 9700
|  |  |  | 10:00 | 10100 |  | 0 |  | 10100
|  |  |  | 11:00 | 10100 |  | 0 |  | 10100
|  |  |  | 12:00 | 10700 |  | 0 |  | 10700
|  |  |  | 13:00 | 10980 |  | 0 |  | 10980
|  |  |  | 14:00 | 11160 |  | 0 |  | 11160
|  |  |  | 15:00 | 11130 |  | 0 |  | 11130
|  |  |  | 16:00 | 11000 |  | 0 |  | 11000
|  |  |  | 17:00 | 10940 |  | 0 |  | 10940
|  |  |  | 18:00 | 10700 |  | 0 |  | 10700
|  |  |  | 18:30 | 10600 |  | 0 |  | 10600
|  |  |  | 19:00 | 10510 |  | 0 |  | 10510
|  |  |  | 19:30 | 10710 |  | 0 |  | 10710
|  |  |  | 20:00 | 10610 |  | 0 |  | 10610
|  |  |  | 21:00 | 10410 |  | 0 |  | 10410
|  |  |  | 22:00 | 10200 |  | 0 |  | 10200
|  |  |  | 23:00 | 9800 |  | 0 |  | 9800
Probable Maximum Temperature: |  |  | 30.30°C
Probable Maximum Demand at Day Peak: |  |  | 10700.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 10710.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10710.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 237.34 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:34 hrs on 19-03-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 18-03-2026 | [28 empty] | Date: | 18-03-2026 | [28 empty] | Date: | 18-03-2026 | [28 empty] | Date: | 18-03-2026 | [28 empty] | Date: | 18-03-2026 | [17 empty] | Date: | 18-03-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [17 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 342.010 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 6 | 326 | 0 | 0 | 0 | 17 | 115 | 0 | 15 | 30 | 0 | 17 | 0 | 0 | 0 | 288 | 0 | 0 | 250 | 0 | 0 | 0 | 52 | 18 | 22 | 0 | 350 | 0 | 0 | 55 | 0 | 0 | 51 | 0 | 0 | 25 | 25 | 0 | 80 | 16 | 26 | 580 | 0 | 0 | 50 | 8 | 16 | 225 | 0 | 0 | 0 | 1224 | 0 | 80 | 0 | 0 | 255 | 300 | 51 | 0 | 157 | 0 | 0 | 102 | 34 | 0 | 20 | 0 | 160 | 0 | 0 | 7 | 300 | 0 | 383 | 41 | 0 | 152 | 0 | 17 | 0 | 5 | 30 | 75 | 0 | 97 | 0 | 58 | 48 | 20 | 0 | 0 | 12 | 6350 | 897 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 0 | 0 | 1434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 54 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 125 | 220 | 0 | 0 | 1230 | 15 | 6390.2 | 12740.2 | 87.79
01:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 6 | 331 | 0 | 0 | 0 | 17 | 105 | 0 | 15 | 30 | 17 | 17 | 0 | 0 | 0 | 290 | 0 | 0 | 250 | 0 | 0 | 0 | 52 | 12 | 22 | 0 | 350 | 0 | 0 | 63 | 0 | 2 | 51 | 0 | 0 | 25 | 25 | 0 | 80 | 15 | 26 | 580 | 0 | 0 | 50 | 8 | 17 | 224 | 0 | 0 | 0 | 1100 | 0 | 80 | 0 | 0 | 250 | 245 | 51 | 0 | 143 | 0 | 7 | 102 | 31 | 0 | 20 | 0 | 154 | 0 | 0 | 7 | 300 | 0 | 383 | 41 | 0 | 152 | 0 | 17 | 0 | 5 | 30 | 74 | 0 | 97 | 0 | 59 | 48 | 21 | 0 | 0 | 0 | 6156 | 897 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1106 | 17 | 0 | 0 | 1365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 54 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 125 | 220 | 0 | 0 | 1100 | 16 | 6045 | 12201 | 87.78
02:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 6 | 328 | 0 | 0 | 0 | 17 | 105 | 0 | 15 | 30 | 17 | 17 | 0 | 0 | 0 | 293 | 0 | 0 | 250 | 0 | 0 | 0 | 52 | 12 | 22 | 0 | 350 | 0 | 0 | 64 | 0 | 2 | 51 | 0 | 0 | 25 | 25 | 0 | 80 | 15 | 26 | 580 | 0 | 0 | 50 | 8 | 16 | 226 | 0 | 0 | 0 | 1100 | 0 | 80 | 0 | 0 | 230 | 245 | 51 | 0 | 140 | 0 | 17 | 102 | 32 | 0 | 20 | 0 | 152 | 0 | 0 | 7 | 305 | 0 | 340 | 41 | 0 | 147 | 0 | 17 | 0 | 5 | 30 | 76 | 0 | 97 | 0 | 59 | 48 | 22 | 0 | 0 | 0 | 6104 | 897 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1104 | 17 | 0 | 0 | 1259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 53 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 125 | 220 | 0 | 0 | 1000 | 17 | 5697 | 11801 | 87.77
03:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 6 | 315 | 0 | 0 | 0 | 0 | 105 | 0 | 15 | 30 | 0 | 17 | 0 | 0 | 0 | 292 | 0 | 0 | 250 | 0 | 0 | 0 | 70 | 13 | 22 | 0 | 350 | 0 | 0 | 63 | 0 | 13 | 51 | 0 | 0 | 25 | 25 | 0 | 80 | 15 | 29 | 580 | 0 | 0 | 50 | 8 | 16 | 226 | 0 | 0 | 0 | 1120 | 0 | 80 | 0 | 0 | 150 | 245 | 51 | 0 | 195 | 0 | 0 | 102 | 31 | 0 | 20 | 0 | 152 | 0 | 0 | 7 | 305 | 0 | 340 | 41 | 0 | 136 | 0 | 17 | 0 | 5 | 30 | 75 | 0 | 97 | 0 | 67 | 57 | 23 | 0 | 0 | 0 | 6071 | 897 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 17 | 0 | 0 | 1371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 51 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 125 | 220 | 0 | 0 | 1000 | 15 | 5869 | 11940 | 87.76
04:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 6 | 317 | 0 | 0 | 0 | 0 | 132 | 0 | 0 | 30 | 17 | 17 | 0 | 0 | 0 | 310 | 0 | 17 | 250 | 0 | 0 | 0 | 35 | 13 | 22 | 0 | 350 | 0 | 0 | 61 | 0 | 8 | 51 | 0 | 0 | 25 | 25 | 0 | 80 | 14 | 29 | 580 | 0 | 0 | 50 | 0 | 16 | 226 | 0 | 0 | 0 | 1148 | 0 | 80 | 0 | 0 | 150 | 245 | 51 | 0 | 222 | 0 | 0 | 103 | 31 | 0 | 20 | 0 | 156 | 0 | 0 | 0 | 300 | 0 | 365 | 41 | 0 | 149 | 0 | 17 | 0 | 5 | 30 | 75 | 0 | 97 | 0 | 98 | 57 | 23 | 0 | 0 | 0 | 6160 | 897 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1174 | 17 | 0 | 0 | 1363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 54 | 17 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 125 | 220 | 0 | 0 | 1065 | 2 | 5974 | 12134 | 87.75
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 319 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 350 | 0 | 0 | 30 | 0 | 5 | 51 | 0 | 0 | 25 | 25 | 0 | 80 | 0 | 29 | 580 | 0 | 0 | 33 | 0 | 0 | 226 | 0 | 0 | 0 | 1014 | 0 | 0 | 0 | 0 | 150 | 245 | 51 | 0 | 194 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 148 | 0 | 0 | 0 | 295 | 0 | 309 | 41 | 0 | 150 | 0 | 17 | 0 | 5 | 30 | 75 | 0 | 97 | 0 | 69 | 35 | 23 | 0 | 0 | 0 | 5529 | 897 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 927 | 0 | 0 | 0 | 1212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 125 | 180 | 0 | 0 | 1060 | 0 | 5404 | 10933 | 87.74
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 300 | 0 | 0 | 11 | 0 | 2 | 0 | 0 | 0 | 12 | 25 | 0 | 80 | 0 | 29 | 580 | 0 | 0 | 33 | 0 | 0 | 225 | 0 | 0 | 0 | 874 | 0 | 0 | 0 | 0 | 150 | 250 | 51 | 0 | 150 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 134 | 0 | 0 | 0 | 295 | 0 | 317 | 41 | 0 | 141 | 0 | 17 | 0 | 5 | 30 | 75 | 0 | 96 | 0 | 35 | 35 | 23 | 0 | 0 | 0 | 5038 | 897 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 816 | 0 | 0 | 0 | 1093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 100 | 180 | 0 | 0 | 901 | 0 | 4958 | 9996 | 87.73
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 250 | 0 | 0 | 2 | 0 | 13 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0.46 | 80 | 0 | 17 | 580 | 0 | 0 | 19 | 0 | 0 | 226 | 0 | 0 | 0 | 844 | 3 | 0 | 0 | 0 | 150 | 250 | 51 | 0 | 202 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 128 | 0 | 7 | 0 | 300 | 0 | 317 | 41 | 0 | 138 | 1 | 0 | 0 | 5 | 30 | 75 | 0 | 97 | 0 | 35 | 35 | 23 | 0 | 1.55 | 0 | 5007.01 | 897 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 825 | 0 | 0 | 0 | 1076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.74 | 11 | 0 | 0 | 5.34 | 0 | 0 | 140 | 0 | 0 | 0 | 355 | 0 | 0.5 | 0 | 53 | 0 | 1 | 0 | 0 | 0 | 0 | 0.7 | 6 | 0.05 | 0 | 220 | 100 | 180 | 0 | 0 | 900 | 0 | 4998.33 | 10005.34 | 87.72
08:00 | 0 | 7 | 4 | 0 | 0 | 0 | 0 | 6 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 250 | 0 | 0 | 6 | 0 | 15.5 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 1.38 | 80 | 0 | 20 | 580 | 0 | 0 | 19 | 0 | 0 | 224 | 0 | 0 | 0 | 851 | 9 | 0 | 0 | 0 | 150 | 250 | 51 | 0 | 202 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 122 | 0 | 10 | 0 | 310 | 0 | 328 | 41 | 0 | 141 | 1 | 8 | 0 | 5 | 30 | 76 | 0 | 97 | 0 | 35 | 37 | 23 | 0 | 3.95 | 0 | 5119.83 | 897 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 830 | 0 | 0 | 0 | 1074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.09 | 24 | 0 | 0 | 14.23 | 0 | 0 | 163 | 0 | 0 | 0 | 362 | 0 | 1.2 | 0 | 53 | 0 | 2 | 0 | 0 | 0 | 0 | 1.7 | 22 | 0.25 | 0 | 220 | 100 | 220 | 0 | 0 | 900 | 0 | 5132.47 | 10252.3 | 87.71
09:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 6 | 332 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 250 | 0 | 0 | 20 | 0 | 15.5 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 2.23 | 80 | 0 | 20 | 580 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 860 | 14 | 0 | 0 | 0 | 0 | 320 | 51 | 0 | 212 | 0 | 0 | 99 | 0 | 0 | 20 | 0 | 132 | 0 | 24 | 0 | 315 | 0 | 342 | 41 | 0 | 145 | 6 | 17 | 0 | 5 | 30 | 74 | 0 | 97 | 0 | 65 | 56 | 24 | 0 | 11.46 | 0 | 5289.19 | 896 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 905 | 0 | 0 | 0 | 1066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.55 | 63 | 0 | 0 | 19.08 | 0 | 0 | 193 | 0 | 0 | 0 | 406 | 0 | 2.08 | 0 | 55 | 0 | 15 | 0 | 0 | 0 | 0 | 4.1 | 87 | 0.28 | 0 | 222 | 125 | 220 | 0 | 0 | 900 | 0 | 5446.09 | 10735.28 | 87.7
10:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 6 | 326 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 250 | 0 | 0 | 25 | 0 | 15.5 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 2.84 | 80 | 0 | 20 | 580 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 865 | 18 | 0 | 0 | 0 | 153 | 345 | 51 | 0 | 205 | 0 | 0 | 99 | 0 | 0 | 14 | 0 | 134 | 0 | 58 | 0 | 315 | 0 | 330 | 42 | 0 | 162 | 7 | 17 | 0 | 5 | 30 | 75 | 0 | 97 | 0 | 68 | 58 | 11 | 0.5 | 13.58 | 0 | 5497.42 | 897 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 914 | 0 | 0 | 0 | 1066.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 93 | 0 | 0 | 14.91 | 0 | 0 | 194 | 0 | 0 | 0 | 414 | 0 | 1.69 | 0 | 54 | 0 | 19 | 0 | 0 | 0 | 0 | 5.6 | 111 | 0.43 | 0 | 220 | 125 | 220 | 0 | 0 | 963 | 0 | 5627.97 | 11125.39 | 87.69
11:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 6 | 328 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 250 | 0 | 0 | 29 | 0 | 15.5 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 25 | 3.61 | 80 | 0 | 22 | 390 | 0 | 0 | 29 | 0 | 0 | 220 | 0 | 0 | 0 | 913 | 19 | 0 | 0 | 0 | 166 | 345 | 51 | 0 | 210 | 0 | 0 | 98 | 0 | 0 | 14 | 0 | 146 | 0 | 67 | 0 | 320 | 0 | 340 | 42 | 0 | 160 | 7 | 17 | 0 | 5 | 30 | 75 | 0 | 97 | 0 | 68 | 58 | 16 | 1.3 | 30.72 | 0 | 5489.13 | 897 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 915 | 0 | 0 | 0 | 1064.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.84 | 99 | 0 | 0 | 18.92 | 0 | 0 | 195 | 0 | 0 | 0 | 414 | 0 | 2.51 | 0 | 54 | 0 | 20 | 0 | 0 | 0 | 0 | 6.7 | 87 | 0.73 | 0 | 222 | 125 | 220 | 0 | 0 | 1000 | 0 | 5701.55 | 11190.68 | 87.68
12:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 6 | 334 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 250 | 0 | 0 | 18 | 0 | 15.5 | 22 | 0 | 330 | 0 | 0 | 4 | 0 | 1 | 0 | 0 | 0 | 24 | 27 | 3.62 | 80 | 0 | 0 | 390 | 0 | 0 | 32 | 0 | 0 | 219 | 0 | 0 | 0 | 1163 | 15 | 0 | 0 | 0 | 200 | 345 | 51 | 0 | 203 | 0 | 0 | 97 | 0 | 0 | 20 | 0 | 150 | 0 | 53 | 0 | 320 | 0 | 367 | 42 | 0 | 159 | 6 | 17 | 0 | 5 | 30 | 74 | 0 | 97 | 0 | 68 | 58 | 23 | 1.3 | 46.59 | 0 | 5776.01 | 897 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 995 | 0 | 0 | 0 | 1068.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.02 | 101 | 0 | 0 | 55.92 | 0 | 0 | 195 | 0 | 0 | 0 | 414 | 0 | 5.28 | 0 | 53 | 0 | 30 | 0 | 0 | 0 | 0 | 7.2 | 125 | 0.66 | 0 | 266 | 125 | 220 | 0 | 0 | 1000 | 0 | 5926.8 | 11702.81 | 87.67
13:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 6 | 328 | 0 | 0 | 0 | 13 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 250 | 0 | 0 | 13 | 0 | 15.5 | 22 | 0 | 350 | 0 | 0 | 18 | 0 | 4 | 0 | 0 | 0 | 24 | 30 | 3.38 | 80 | 0 | 30 | 375 | 0 | 0 | 32 | 0 | 0 | 218 | 0 | 0 | 0 | 1175 | 18 | 0 | 0 | 0 | 238 | 342 | 51 | 0 | 210 | 0 | 0 | 96 | 0 | 0 | 20 | 0 | 155 | 0 | 47 | 0 | 310 | 0 | 406 | 42 | 0 | 158 | 10 | 17 | 0 | 5 | 30 | 75 | 0 | 97 | 0 | 68 | 58 | 23 | 2.1 | 27.33 | 6 | 5902.31 | 897 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 1055 | 0 | 0 | 0 | 1088.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.27 | 83 | 0 | 0 | 54.15 | 0 | 0 | 195 | 0 | 0 | 0 | 414 | 0 | 2.35 | 0 | 52 | 0 | 27 | 0 | 0 | 0 | 0 | 7 | 159 | 0.22 | 0 | 282 | 125 | 220 | 0 | 0 | 1010 | 0 | 6002.37 | 11904.68 | 87.66
14:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 6 | 332 | 0 | 0 | 0 | 17 | 52 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 332 | 0 | 0 | 250 | 0 | 0 | 18 | 35 | 12.5 | 22 | 0 | 330 | 0 | 0 | 35 | 0 | 3 | 0 | 0 | 0 | 24 | 32 | 2.96 | 80 | 0 | 29 | 360 | 0 | 0 | 34 | 2 | 0 | 220 | 0 | 0 | 0 | 1161 | 17 | 1 | 0 | 0 | 239 | 300 | 51 | 0 | 175 | 0 | 1 | 97 | 1 | 0 | 20 | 0 | 168 | 0 | 30 | 0 | 310 | 0 | 372 | 42 | 0 | 155 | 9 | 17 | 0 | 5 | 30 | 75 | 0 | 97 | 0 | 68 | 58 | 23 | 1.5 | 28.89 | 10 | 5822.85 | 897 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 1192 | 0 | 0 | 0 | 1319.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.51 | 84 | 0 | 0 | 39.49 | 0 | 0 | 196 | 0 | 0 | 0 | 405 | 0 | 1.75 | 0 | 53 | 0 | 29 | 0 | 0 | 0 | 0 | 5.9 | 130 | 0.24 | 0 | 307 | 125 | 220 | 0 | 0 | 1112 | 0 | 6400.25 | 12223.1 | 87.65
15:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 6 | 308 | 0 | 0 | 17 | 17 | 52 | 0 | 0 | 14 | 0 | 16 | 0 | 0 | 0 | 320 | 0 | 0 | 250 | 0 | 0 | 22 | 52 | 12.5 | 22 | 0 | 330 | 0 | 0 | 49 | 0 | 7 | 0 | 0 | 0 | 24 | 34 | 1.57 | 80 | 0 | 30 | 315 | 0 | 0 | 45 | 24 | 0 | 220 | 0 | 0 | 0 | 1150 | 13 | 12 | 0 | 0 | 200 | 300 | 51 | 0 | 150 | 0 | 15 | 97 | 17 | 0 | 20 | 0 | 166 | 0 | 35 | 0 | 310 | 0 | 366 | 42 | 0 | 135 | 2 | 17 | 0 | 5 | 30 | 76 | 0 | 97 | 0 | 68 | 58 | 33 | 1.2 | 28.1 | 12 | 5791.37 | 897 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 1162 | 0 | 0 | 0 | 1307.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.98 | 68 | 0 | 0 | 25.45 | 0 | 0 | 195 | 0 | 0 | 0 | 390 | 0 | 1.3 | 0 | 53 | 0 | 20 | 0 | 0 | 0 | 0 | 4.7 | 96 | 0.4 | 0 | 274 | 125 | 220 | 0 | 0 | 1190 | 0 | 6331.3 | 12122.67 | 87.64
16:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 6 | 318 | 0 | 0 | 14.3 | 0 | 0 | 0 | 0 | 15 | 0 | 17 | 0 | 0 | 0 | 330 | 0 | 0 | 250 | 0 | 0 | 12 | 52 | 12.5 | 22 | 0 | 360 | 0 | 0 | 60 | 0 | 19 | 0 | 0 | 0 | 24 | 36 | 1.26 | 80 | 0 | 30 | 317 | 0 | 0 | 50 | 25.5 | 0 | 220 | 0 | 0 | 0 | 1106 | 8 | 0 | 0 | 0 | 170 | 300 | 51 | 0 | 148 | 0 | 16 | 96 | 0 | 0 | 20 | 0 | 154 | 0 | 28 | 0 | 305 | 0 | 392 | 42 | 0 | 140 | 2 | 17 | 0 | 5 | 30 | 74 | 0 | 97 | 0 | 68 | 45 | 56 | 0.5 | 4.21 | 12 | 5675.27 | 897 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 1070 | 0 | 0 | 0 | 1390.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.52 | 31 | 0 | 0 | 7.42 | 0 | 0 | 195 | 0 | 0 | 0 | 410 | 0 | 0.22 | 0 | 56 | 0 | 8 | 0 | 0 | 0 | 0 | 3.8 | 73 | 0.26 | 0 | 281 | 125 | 220 | 0 | 0 | 1200 | 0 | 6252.97 | 11928.24 | 87.63
17:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 6 | 310 | 0 | 0 | 15.4 | 0 | 0 | 15 | 45 | 15 | 0 | 48 | 5 | 0 | 0 | 320 | 0 | 17 | 250 | 0 | 0 | 3 | 70 | 12.5 | 22 | 0 | 310 | 0 | 0 | 60 | 0 | 6 | 49 | 0 | 0 | 50 | 38 | 0.47 | 80 | 0 | 30 | 317 | 0 | 0 | 50 | 25.5 | 0 | 191 | 0 | 0 | 0 | 1100 | 3 | 0 | 0 | 0 | 0 | 295 | 51 | 0 | 195 | 0 | 17 | 96 | 0 | 0 | 20 | 0 | 154 | 0 | 9 | 1 | 310 | 0 | 368 | 42 | 0 | 137 | 0 | 17 | 0 | 5 | 30 | 76 | 0 | 96 | 0 | 45 | 45 | 73 | 0 | 1.58 | 0 | 5580.45 | 898 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 1020 | 0 | 0 | 0 | 1388.62 | 0 | 0 | 0 | 20 | 15 | 0 | 60 | 0 | 0 | 5.97 | 9 | 0 | 0 | 2.42 | 0 | 0 | 180 | 0 | 0 | 0 | 347 | 0 | 0.18 | 0 | 54 | 70 | 4 | 70 | 0 | 0 | 0 | 1.4 | 27 | 0.1 | 0 | 260 | 125 | 220 | 0 | 0 | 1190 | 6 | 6220.69 | 11801.14 | 87.62
18:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 6 | 311 | 0 | 0 | 14.7 | 0 | 0 | 0 | 45 | 15 | 0 | 47 | 16 | 0 | 0 | 290 | 0 | 17 | 250 | 0 | 0 | 0 | 70 | 0 | 22 | 0 | 310 | 0 | 0 | 60 | 0 | 6 | 51 | 15 | 0 | 90 | 50 | 0 | 80 | 0 | 30 | 317 | 0 | 0 | 50 | 25.5 | 0 | 180 | 0 | 0 | 0 | 1056 | 0 | 0 | 0 | 0 | 0 | 285 | 51 | 0 | 197 | 0 | 16 | 96 | 0 | 0 | 20 | 0 | 146 | 0 | 0 | 0 | 310 | 0 | 348 | 42 | 0 | 136 | 0 | 17 | 0 | 5 | 30 | 75 | 0 | 96 | 0 | 35 | 35 | 71 | 0 | 0 | 0 | 5460.2 | 897 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1015 | 0 | 0 | 0 | 1331.11 | 0 | 0 | 0 | 35 | 35 | 0 | 60 | 0 | 0 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 53 | 70 | 0 | 70 | 0 | 0 | 0 | 0.2 | 1 | 0.01 | 0 | 226 | 125 | 220 | 0 | 0 | 1125 | 16 | 6035.44 | 11495.64 | 87.61
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 250 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 310 | 0 | 0 | 61 | 0 | 2 | 51 | 15 | 0 | 90 | 50 | 0 | 80 | 0 | 30 | 317 | 0 | 0 | 50 | 8 | 0 | 180 | 0 | 0 | 0 | 950 | 0 | 0 | 0 | 0 | 0 | 300 | 51 | 0 | 197 | 0 | 17 | 51 | 0 | 0 | 20 | 0 | 162 | 0 | 0 | 0 | 265 | 0 | 338 | 42 | 0 | 135 | 0 | 17 | 0 | 0 | 30 | 76 | 0 | 97 | 0 | 35 | 35 | 73 | 0 | 0 | 0 | 5032 | 897 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 905 | 0 | 0 | 0 | 1335.52 | 0 | 0 | 0 | 10 | 35 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 56 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 100 | 180 | 0 | 0 | 1090 | 8 | 5566.52 | 10598.52 | 87.6
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 54 | 0 | 0 | 51 | 0 | 0 | 76 | 50 | 0 | 80 | 0 | 30 | 318 | 0 | 0 | 50 | 8 | 0 | 180 | 0 | 0 | 0 | 914 | 0 | 0 | 0 | 0 | 0 | 285 | 51 | 0 | 188 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 250 | 0 | 312 | 42 | 0 | 136 | 0 | 17 | 0 | 5 | 30 | 75 | 0 | 98 | 0 | 35 | 35 | 73 | 0 | 0 | 0 | 4780 | 897 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 871 | 0 | 0 | 0 | 1314.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 56 | 35 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 100 | 180 | 0 | 0 | 1090 | 0 | 5351.04 | 10131.04
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 51 | 0 | 0 | 51 | 0 | 0 | 62 | 62 | 0 | 80 | 0 | 30 | 318 | 0 | 0 | 50 | 8 | 0 | 180 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 9 | 0 | 285 | 51 | 0 | 186 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 250 | 0 | 322 | 42 | 0 | 135 | 0 | 17 | 0 | 5 | 30 | 76 | 0 | 98 | 0 | 35 | 8 | 73 | 0 | 0 | 0 | 4574 | 897 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 0 | 0 | 0 | 1209.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 100 | 180 | 0 | 0 | 1000 | 0 | 4976.59 | 9550.59 | 87.59
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 62 | 62 | 0 | 80 | 0 | 30 | 319 | 0 | 0 | 39 | 8 | 0 | 224 | 0 | 0 | 0 | 796 | 0 | 0 | 0 | 8 | 0 | 315 | 51 | 0 | 206 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 250 | 0 | 400 | 41 | 0 | 138 | 0 | 17 | 0 | 5 | 30 | 76 | 0 | 98 | 0 | 35 | 8 | 87 | 0 | 0 | 0 | 4793 | 897 | 211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 784 | 0 | 0 | 0 | 1024.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 800 | 0 | 4694.29 | 9487.29 | 87.58
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 310 | 0 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 50 | 62 | 0 | 80 | 0 | 28 | 320 | 0 | 0 | 39 | 8 | 0 | 226 | 0 | 0 | 0 | 724 | 0 | 0 | 0 | 8 | 0 | 280 | 51 | 0 | 189 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 250 | 0 | 360 | 41 | 0 | 137 | 0 | 17 | 0 | 5 | 30 | 75 | 0 | 98 | 0 | 24 | 8 | 105 | 0 | 0 | 0 | 4650 | 897 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 747 | 0 | 0 | 0 | 932.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 600 | 0 | 4430.63 | 9080.63 | 87.57
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 39 | 0 | 0 | 51 | 0 | 0 | 25 | 62 | 0 | 80 | 0 | 28 | 320 | 0 | 0 | 36 | 0 | 0 | 226 | 0 | 0 | 0 | 615 | 0 | 0 | 0 | 9 | 0 | 280 | 51 | 0 | 191 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 124 | 0 | 0 | 0 | 250 | 0 | 323 | 41 | 0 | 139 | 0 | 17 | 0 | 5 | 30 | 75 | 0 | 98 | 0 | 8 | 8 | 105 | 0 | 0 | 0 | 4458 | 897 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 774 | 0 | 0 | 0 | 835.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 4210.87 | 8668.87 | 87.56
Total KWH | 0 | 336000 | 145920 | 0 | 0 | 0 | 0 | 158909.09 | 7754400 | 0 | 0 | 66960 | 92520 | 922464 | 4800 | 145527 | 204209 | 24875 | 237600 | 31680 | 0 | 0 | 7583569 | 0 | 40710 | 6060712 | 0 | 0 | 164971 | 560400 | 238200 | 403200 | 0 | 7984545.45 | 0 | 0 | 851520 | 0 | 72960 | 654059 | 32458 | 0 | 793920 | 808320 | 23863 | 1923420 | 65230 | 336000 | 10705454.55 | 0 | 0 | 958080 | 188886.6 | 75272 | 4897088 | 0 | 0 | 0 | 23438179 | 130275 | 384727 | 0 | 30000 | 2947600 | 6966000 | 1238571 | 0 | 4619000 | 0 | 122880 | 2089633 | 154560 | 0 | 369980 | 0 | 3242880 | 0 | 390582 | 28864 | 7121000 | 0 | 8688000 | 989000 | 0 | 3473836 | 51008 | 381648 | 0 | 122880 | 717088 | 1766000 | 0 | 2334350 | 0 | 1314000 | 1003200 | 943680 | 7900 | 184660 | 59520 | 130860203.69 | 21706181 | 5319360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 552240 | 23076360 | 66720 | 0 | 0 | 28319876 | 0 | 0 | 0 | 91200 | 105408 | 0 | 145776 | 0 | 0 | 312500 | 655920 | 0 | 0 | 257248 | 0 | 0 | 4442191 | 0 | 0 | 0 | 8798545 | 0 | 22560 | 0 | 1264581 | 386120 | 178733 | 391708 | 0 | 0 | 0 | 47424.36 | 959760 | 3318 | 0 | 5498000 | 2791000 | 5236450 | 0 | 0 | 24266181.82 | 100800 | 134996161.18 | 265856364.87

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 18-03-2026
Power Supply Scenario
| Day Peak Generation |  |  | 11702.81 | MW | 12:00 Hr. | Energy Generated |  |  | 265.8564 |  | MKWHr.
| Day Peak Demand |  |  | 11702.81 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11495.64 | MW | 18:00 Hr. | Energy Demand |  |  | 265.8564 |  | MKWHr.
| Evening Peak Demand |  |  | 11495.64 | MW | 18:00 Hr. | Maximum Temperature |  |  | 32.6 |  | °C
| Minimum Generation of the Day |  |  | 8668.87 | MW | 23:00 Hr. | Total Gas Supplied |  |  | 758.27 |  | MMCFD
| Maximum Generation of the Day |  |  | 12740.2 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.7709 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 30.1835 | 0 | 2.8137 | 0 | 0 | 0.16497 | 0 | 0 | 33.1622 | Gas | 106.8024 | Gas | 368211290.138
| Chattogram Zone |  |  | 5.2331 | 34.1436 | 4.4277 | 0 | 1.9234 | 0.15414 | 0 | 0.07296 | 45.955 | Coal | 88.2488 | Coal | 597525555.8621
| Cumilla Zone |  |  | 18.2608 | 0 | 0.69103 | 0 | 0 | 0.39058 | 3.2429 | 0 | 22.5853 | HFO | 11.5969 | HFO | 201359894.61
| Mymensingh Zone |  |  | 0.94368 | 0 | 2.3767 | 0 | 0 | 0.19256 | 0 | 0 | 3.513 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 25.5938 | 0 | 0 | 0 | 0 | 0.051008 | 0 | 0 | 25.6448 | Hydro | 1.9234 | Hydro | 192342
| Khulna Zone |  |  | 5.3194 | 23.0764 | 0.06672 | 0 | 0 | 0.55224 | 21.7062 | 0 | 50.7209 | Solar | 3.943 | Solar | 62883251.482
| Barishal Zone |  |  | 8.0274 | 29.7642 | 0.1008 | 0 | 0 | 0.003318 | 0 | 0 | 37.8957 | Import | 53.2689 | Import | 302992978.49
| Rajshahi Zone |  |  | 13.2407 | 0 | 0.34238 | 0 | 0 | 1.2482 | 28.3199 | 0 | 43.1512 | Wind | 0.07296 | Wind | 1073241.6
| Rangpur Zone |  |  | 0 | 1.2646 | 0.77783 | 0 | 0 | 1.1859 | 0 | 0 | 3.2283
| Total |  |  | 106.8024 | 88.2488 | 11.5969 | 0 | 1.9234 | 3.943 | 53.2689 | 0.07296 | 265.8564
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 368211290.138 |  | Hydro | 192342
|  |  |  | Coal | 597525555.8621 |  | Solar | 62883251.482
|  |  |  | HFO | 201359894.61 |  | Import | 302992978.49
|  |  |  | HSD | 0 |  | Wind | 1073241.6
[5 empty] | Total: | 153,42,38,554 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7062 | Peak Hr Flow | 897.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 40709854.54 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 28.3199 | Peak Hr Flow | 1331.11 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1728 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.2429 | Peak Hr Flow | 146.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2438 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.2689 | Peak Hr Flow | 2374.11 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3372
|  |  |  | Chattogram |  | 0 |  | 1260
|  |  |  | Cumilla |  | 0 |  | 1299
|  |  |  | Mymensingh |  | 0 |  | 802
|  |  |  | Sylhet |  | 0 |  | 386
|  |  |  | Khulna |  | 0 |  | 1602
|  |  |  | Barishal |  | 0 |  | 376
|  |  |  | Rajshahi |  | 0 |  | 1182
|  |  |  | Rangpur |  | 0 |  | 870
|  |  |  | Total |  | 0 |  | 11149
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:35 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- gt
| 09:21 | 12:13 | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Forced S/D Due to 33 kv feeder red hot . | [7 empty] | 15.0MW load
interrup.
| 09:22 | 12:12 | Mahasthangarh 132/33kV S/S 416T MTR 2 HT Forced S/D Due to 33 kv feeder red hot . | [7 empty] | 15.0MW load
interrup.
| 09:29 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- gt
|  | 10:03 | Barishal 230/132kV S/S T-5 HT is restored.
|  | 10:07 | Barishal 230/132kV S/S T-5 LT is restored.
|  | 15:22 | Ghorasal- Ishwardi 230 kV Ckt-2 is restored.
| 16:28 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- GT
| 17:22 |  | Ghorasal- Ishwardi 230 kV Ckt-2 Forced S/D from Ghorashal 230kV end Due to Distance
Realy Trip. Line check Require
| 17:38 | 18:07 | Kabirpur -Tongi 132kV Ckt-1 Tripped from Tongi 230/132/33kV end showing Z1,B-phase,AR
OPERATED relays.
| 17:51 |  | Ghorasal- Ishwardi 230 kV Ckt-2 Tripped from Ishurdi 230/132kV end showing Distance
protection relay relays.
| 18:00 |  | Evening peak generation: 11494 MW
| 18:14 |  | BIPTC S/S 10CF15 Tripped showing 87.1 Differential relay relays Due to 10CF15 tripped by
capacitor unbalance 60/61 instant L2
| 18:25 | 19:57 | Maniknagar 230/132kV S/S Auto Transformer-01(705T) HT Tripped showing REL670 relays Due
to Distance Tripping Zone 1
| 18:25 | 19:57 | Maniknagar-Siddhirganj 230kV Ckt-1 Tripped from Maniknagar 230/132kV end showing REL670
relays Due to Distance Tripping Zone 1 and from Siddhirganj 230/132kV end showing O/C,
Distance Zone-1 Phase A relays Due to Storm
| 18:32 |  | Shyampur-Shyampur(New) 132kV Ckt-2 Tripped from Shyampur 230/132kV end showing Distance | [7 empty] | 34.0MW load
|  |  | relay 21 Trip relay 86.1 Zone-1 SOTF relays Due to Stormy weather | [7 empty] | interrup. Shyampur
230/132kV end
| 18:49 | 21:14 | Brahmanbaria-Narsinghdi 132 kV Ckt-1 Tripped from Brahmanbaria 132/33kV end showing
Distance relay relays.
| 18:56 | 20:47 | Ashuganj-Brahmanbaria 132kV Ckt-1 Tripped from Brahmanbaria 132/33kV end showing Distance
relay relays.
| 19:35 | 22:36 | Daudkandi-Sonargaon 132 kV Ckt-2 Tripped from Sonargaon 132/33kV end showing Line
Distance Relay relays Due to Due to bad weather
| 19:42 | 03:31 | Sonargaon 132/33kV S/S Tr-1 LT Tripped showing TRIP RELAY(MVAJM-25) relays Due to DUE TO | [7 empty] | 4.0MW load
|  |  | BAD WEATHER. T-1 auxiliary TRANSFORMER droup out fuse burst. | [7 empty] | interrup.
| 19:45 | 20:47 | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Tripped showing MiCOM P139 relays Due to Nesco | [7 empty] | 31.0MW load
|  |  | 33 C.T Burst | [7 empty] | interrup.
| 19:45 | 21:40 | Mahasthangarh 132/33kV S/S 406T MTR1 LT Tripped showing Micom P139 relays Due to Nesco 33 | [7 empty] | 31.0MW load
|  |  | C.T Burst | [7 empty] | interrup.
| 19:47 | 20:11 | Cumilla(S) 132/33kV S/S TR-3 LT Tripped showing REF615 relays Due to 33KV PDB Fedder fult | [7 empty] | 54.0MW load
interrup.
| 19:59 | 20:52 | Chandina 132/33kV S/S TR-3 LT Forced S/D Due to Auxiliary TR-2 Post Insulator Red Hot
problem for Raining .
| 20:20 | 22:08 | Munshiganj 132/33kV S/S Transformer-1 LT Tripped showing DIR O/C Trip relays Due to T1 | [7 empty] | 40.0MW load
|  |  | incoming trip at 08:20 for 33kv bus-coupler insulator flashing. | [7 empty] | interrup.
| 20:20 | 22:08 | Munshiganj 132/33kV S/S Transformer-2 LT Tripped showing DIR O/C Trip relays Due to T2 | [7 empty] | 40.0MW load
|  |  | incoming trip at 08:20 for 33kv bus-coupler insulator flashing. | [7 empty] | interrup.
| 20:20 | 20:24 | Mirpur-Uttara 3PH 132kV Ckt-1 Tripped from Mirpur 132/33kV end showing Over Voltage
relays Due to Over Voltage
| 20:23 | 20:56 | Haripur-Madanganj 132kV Ckt-1 Tripped from Haripur 230/132kV end showing Distance Realy | [7 empty] | and 8.0MW load
|  |  | ,zone-1 AN relays. and from Madanganj 132/33kV end showing Distance Relay relays. | [7 empty] | interrup. Madanganj
132/33kV end
| 20:24 | 20:24 | Mirpur-Uttara 3PH 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end.
| 20:28 | 21:46 | Sirajganj 132/33kV S/S Solar Park 1 Tripped showing 1. Line diff Protection 87L 2. Line
Dist protection 21L relays Due to Thundering
| 20:28 | 21:46 | Sirajganj 132/33kV S/S Solar Park 2 Tripped showing 1. Line diff Protection 87L 2. Line
Dist protection relays Due to Thundering.
| 20:42 | 03:30 | Sonargaon 132/33kV S/S Tr-1 HT Tripped showing TRAFO.DIFF.RELAY BACKUP/PROTN.RELAY | [7 empty] | 4.0MW load
|  |  | relays Due to DUE TO BAD WEATHER. T-1 auxiliary TRANSFORMER droup out fuse burst. | [7 empty] | interrup.
| 21:00 |  | Madanganj 132/33kV S/S Madanganj -Summit 55 MW 132 kv Ckt Tripped showing Trip Relay
relays.
| 21:10 | 22:08 | Munshiganj 132/33kV S/S Transformer-1 LT Forced S/D Due to T1 & T2 both sides incoming | [7 empty] | 40.0MW load
|  |  | trip at 08:20 for 33kv bus-coupler insulator flashing. Now T1 x-former is shut down | [7 empty] | interrup.
from 09:10 for maintenance by PBS.
| 21:10 | 22:08 | Munshiganj 132/33kV S/S Transformer-2 LT Forced S/D Due to T1 & T2 both sides incoming | [7 empty] | 40.0MW load
|  |  | trip at 08:20 for 33kv bus-coupler insulator flashing. Now T2 x-former is shut down | [7 empty] | interrup.
from 09:10 for maintenance by PBS.
| 21:13 | 22:31 | Chandina 132/33kV S/S TR-3 LT Forced S/D Due to Auxiliary TR-2 Post Insulator Red Hot
problem for Raining .
| 21:20 | 22:22 | Ishurdi-Pabna 132kV ckt Forced S/D from Ishurdi 132/33kV end Due to La flashing
| 22:00 | 22:20 | Madanganj 132/33kV S/S GT-1 HT Forced S/D Due to Nutral grounding bushing clam flashing | [7 empty] | 12.0MW load
interrup.
| 22:00 | 22:22 | Madanganj 132/33kV S/S GT-1 LT Forced S/D Due to Neutral grounding bushing flashing | [7 empty] | 12.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 22:11 | 22:14 | Kabirpur -Tongi 132kV Ckt-1 Tripped from Tongi 230/132/33kV end showing Z1,B-phase,AR
OPERATED relays.
| 22:40 | 23:37 | Keraniganj-Sreenagar (T at Powerpac 100MW) 132kV Ckt-2 Tripped from Keranigonj
230/132/33kV end showing Distance relay: Zone 1 R-Phase , Trip Relay 86 relays Due to
Thundering
| 22:57 | 23:31 | Gopalganj (O) - Gopalgan (N) Ckt-1 Tripped from Gopalganj 132/33kV end showing Distance-1
A phase relays Due to Zone-1 3.6 km
| 23:02 | 03:56 | Sonargaon 132/33kV S/S OPSL(IEL-2) Tripped showing null relays Due to Due to bus coupler
CB trip
| 23:02 | 03:17 | Daudkandi-Sonargaon 132 kV Ckt-1 Tripped from Sonargaon 132/33kV end showing Null relays
Due to Due to bus coupler CB trip
| 23:02 |  | Daudkandi-Sonargaon 132 kV Ckt-2 Tripped from Sonargaon 132/33kV end showing Line
distance Relay B/B PROTN.Relay-87B relays Due to Due to bad weather
| 01:01 | 02:10 | Sirajganj 132/33kV S/S T3-(435) HT Forced S/D Due to kazipur feeder Bus Ds insulator | [7 empty] | 10.0MW load
|  |  | replace work. | [7 empty] | interrup.
| 01:01 | 02:10 | Sirajganj 132/33kV S/S T3-(435) LT Forced S/D Due to kazipur feeder Bus Ds insulator | [7 empty] | 10.0MW load
|  |  | replace work. | [7 empty] | interrup.
| 01:05 |  | Keranigonj 230/132/33kV S/S 132 kV Hasnabad Ckt. 1 Tripped showing Distance Relayu
Operated relays Due to Bad Weather With Thundering.
| 01:42 | 02:23 | Baroaulia-Hathazari 132 kV Ckt-1 Tripped from Hathazari 230/132/33kV end showing Alstom
Quadrhamo relays Due to Alstome Quadrahmo and from Baroaulia 132/33kV end showing
1.(B) 2.(C) relays Due to Unexpected
| 04:00 |  | Sehri peak generation 8360 MW
| 07:00 |  | Minimum generation 6666 MW
| 07:45 |  | Ashuganj 420 MW CCPP (East) ST was synchronized
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 18-03-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 6 | 158909.09 | Demand "05"MW due to gas restiction by Titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 311 | 7754400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 204209 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 250 | 6060712 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 14.7 | 66960 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 4800 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 24875 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 40710 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 0 | 238200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 403200 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 8 | 145920 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 45 | 145527 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 922464 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 336000 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 31680 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 47 | 237600 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 164971 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 92520 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 310 | 7984545.45 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 290 | 7583569 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 70 | 560400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1438.7 | 33162171.54
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 188886.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 130275 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 958080 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1923420 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 180 | 4897088 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 75272 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 15 | 32458 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 654059 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 793920 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 30 | 336000 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 60 | 851520 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 23863 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 65230 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 808320 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1056 | 23438179 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 6 | 72960 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 317 | 10705454.55 | Coal shortage
Chattogram Area Total |  |  |  |  | 4898.863 | 2010.5 | 45954985.15
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 197 | 4619000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 2947600 | Vibration
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 285 | 6966000 | FGMO ON
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 30000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1238571 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 384727 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 28864 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 96 | 2089633 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 154560 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 146 | 3242880 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 369980 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 16 | 122880 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 390582 | -
Cumilla Area Total |  |  |  |  | 2876.261 | 811 | 22585277
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 71 | 943680 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7900 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 35 | 1003200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 35 | 1314000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 184660 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 59520 | From12:00 hrs to24:00 hrs will be dispatching12MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 141 | 3512960
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 51008 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 989000 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 136 | 3473836 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 75 | 1766000 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 717088 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 5 | 122880 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 96 | 2334350 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 381648 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7121000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 348 | 8688000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | plant will be shutdown due to 3rd Minor Inspection
Sylhet Area Total |  |  |  |  | 2325 | 1059 | 25644810
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 897 | 21706181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 239 | 5319360 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 66720 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 1 | 552240 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1015 | 23076360 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2152 | 50720861
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 125 | 2791000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1125 | 24266181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5236450 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 16 | 100800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 226 | 5498000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0.01 | 3318 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1712.01 | 37895749.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0.12 | 312500 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 170 | 4442191 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 346 | 8798545 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 60 | 145776 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 105408 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 91200 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 22560 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1331.11 | 28319876 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 257248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 655920 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1977.23 | 43151224
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 53 | 1264581 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 391708 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0.2 | 47424.36 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 386120 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 178733 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 1 | 959760 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 194.2 | 3228326.36
Eastern Grid Total |  |  |  |  | 17423.308 | 5460.2 | 130860203.69
Western Grid Total |  |  |  |  | 11852.195 | 6035.44 | 134996161.18
National Grid Total |  |  |  |  | 29275.503 | 11495.64 | 265856364.87
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 18-03-2026
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7118.63 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4031.2 | MW
i) Dhaka area |  |  | 3371.63 |  | MW | i) Khulna area |  |  |  | 1602.5 | MW
ii) Chattogram area |  |  | 1260 |  | MW | ii) Barishal area |  |  |  | 376.3 | MW
iii) Cumilla area |  |  | 1299 |  | MW | iii) Rajshahi area |  |  |  | 1182.4 | MW
iv) Mymensingh area |  |  | 802 |  | MW | iv) Rangpur area |  |  |  | 870 | MW
v) Sylhet area |  |  | 386 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11149.83 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 10 | 19:30 | 67 | Hasnabad | 78 | 00:00 | 133 | Nawabganj | 42.8 | 19:00
2 | AKSML | 10 | 11:00 | 68 | Hathazari | 81 | 19:00 | 134 | Netrakona | 128 | 18:00
3 | Aftabnagar | 28 | 00:00 | 69 | Hatirjheel | 31 | 14:00 | 135 | New | 56 | 08:00
4 | Agargaon | 82 | 18:00 | 70 | Ishurdi | 66 | 19:00 | 136 | Niamatpur | 82 | 13:00
5 | Agrabad | 58 | 19:30 | 71 | Jaldhaka | 74 | 18:00 | 137 | Noapara | 46 | 19:00
6 | Amnura | 33 | 14:00 | 72 | Jamalpur | 100 | 19:00 | 138 | PHP | 8 | 15:00
7 | Ashuganj | 75 | 06:00 | 73 | Jashore | 149 | 21:00 | 139 | Pabna | 88 | 19:00
8 | BSRM | 197 | 10:00 | 74 | Jhenaidah | 107 | 18:30 | 140 | Palashbari | 92 | 18:00
9 | Bagerhat | 80 | 22:00 | 75 | Joydebpur | 108 | 00:00 | 141 | Panchagarh | 54 | 19:00
10 | Bajitpur | 80 | 17:00 | 76 | Joypurhat | 51 | 22:00 | 142 | Patiya | 9 | 00:00
11 | Bakerganj | 10.1 | 22:00 | 77 | Juldah | 15 | 12:00 | 143 | Patuakhali | 61.5 | 22:00
12 | Bakulia | 68 | 19:30 | 78 | KSRM | 11 | 05:00 | 144 | Payra | 28 | 21:00
13 | Banani | 20 | 11:00 | 79 | Kabirpur | 192 | 08:00 | 145 | Postogola | 40 | 00:00
14 | Bangabhaban | 5 | 10:00 | 80 | Kachua | 95 | 19:00 | 146 | Pubail | 22 | 00:00
15 | Barapukuria | 55 | 21:00 | 81 | Kaliganj | 31 | 18:30 | 147 | Purbachal | 20 | 13:00
16 | Barguna | 20 | 21:00 | 82 | Kallyanpur | 87 | 00:00 | 148 | Purbasadipur | 100 | 17:00
17 | Barishal | 87 | 15:00 | 83 | Kalurghat | 45 | 14:00 | 149 | Rahanpur | 32 | 21:00
18 | Barishal-230 | 90 | 21:00 | 84 | Kamrangirchar | 61 | 00:00 | 150 | Rahim | 17 | 01:00
19 | Baroaulia | 64 | 00:00 | 85 | Kaptai | N/A | N/A | 151 | Rajbari | 73 | 19:30
20 | Baroirhat | 59 | 21:00 | 86 | Kasba | 36 | 18:30 | 152 | Rajendrapur | 106 | 00:00
21 | Bashundhara | 141 | 18:00 | 87 | Kazla | 81 | 00:00 | 153 | Rajshahi | 92 | 04:00
22 | BashundharaCement | 14 | 20:00 | 88 | Keranigonj | 70 | 00:00 | 154 | Rajshahi-230 | 80 | 17:00
23 | Beanibazar | 50 | 14:00 | 89 | Khagrachori | 30 | 18:00 | 155 | Ramganj | 100 | 19:00
24 | Benapole | 72 | 21:00 | 90 | Khulna | 48 | 19:00 | 156 | Rampur | 36 | 00:00
25 | Bhaluka | 134 | 16:00 | 91 | Khulshi | 162 | 20:00 | 157 | Rangamati | 16 | 18:30
26 | Bhandaria | 52 | 23:00 | 92 | Kishoreganj | 106 | 16:00 | 158 | Rangpur | 128 | 18:00
27 | Bhangura | 45 | 14:00 | 93 | Kodda | 245 | 00:00 | 159 | Ruppur | 3.6 | 10:00
28 | Bheramara(GK) | 60 | 19:30 | 94 | Kulaura | 30 | 14:00 | 160 | SSM | 0 | 00:00
29 | Bhulta | 195 | 00:00 | 95 | Kurigram | 65 | 18:00 | 161 | Saidpur | 96 | 17:00
30 | Bog-Sherpur | 70 | 04:00 | 96 | Kushtia | 134 | 20:00 | 162 | Satkhira | 136 | 18:30
31 | Bogura | 141 | 04:00 | 97 | Laksam | 28 | 22:00 | 163 | Satmasjid | 79 | 18:00
32 | Borhanuddin | 88 | 21:00 | 98 | Lakshmipur | 45 | 19:30 | 164 | Savar | 158 | 09:00
33 | Brahmanbaria | 113 | 14:00 | 99 | Lalbag | 56 | 00:00 | 165 | SevenRings | 18.73 | 18:00
34 | Cantonment | 123 | 13:00 | 100 | Lalmonirhat | 53 | 17:00 | 166 | ShahCement | 31 | 00:00
35 | Chandina | 19 | 10:00 | 101 | MI_Cement | 16.3 | 08:00 | 167 | Shahjadpur | 77 | 12:00
36 | Chandpur | 72 | 18:30 | 102 | Madanganj | 26 | 00:00 | 168 | Shahjibazar | 95 | 00:00
37 | Chandraghona | 35 | 18:30 | 103 | Madaripur | 104 | 19:00 | 169 | Shahmirpur | 47 | 18:00
38 | Chapai | 65 | 09:00 | 104 | Madartek | 64 | 18:00 | 170 | Shariatpur | 80 | 20:00
39 | Charsaidpur | 39 | 00:00 | 105 | Madunaghat | 46 | 19:00 | 171 | Sherpur | 120 | 18:00
40 | Chauddagram | 72 | 18:30 | 106 | Magura | 67 | 19:30 | 172 | Shikalbaha | 23 | 01:00
41 | Chhatak | 26 | 18:30 | 107 | Mahasthangarh | 72 | 03:00 | 173 | Shitalakhya | 69.4 | 12:00
42 | Chowmuhani | 129 | 20:00 | 108 | Maijdee | 38 | 23:00 | 174 | Sholosohor | 39 | 11:00
43 | Chuadanga | 116 | 19:00 | 109 | Manikganj | 111 | 00:00 | 175 | Shyampur | 152 | 01:00
44 | Coxsbazar | 135 | 21:00 | 110 | Maniknagar | 55 | 13:00 | 176 | Siddhirganj | 95 | 10:00
45 | Cumilla(N) | 114 | 18:30 | 111 | Matarbari | 50 | 03:00 | 177 | Sirajganj | 108 | 13:00
46 | Cumilla(S) | 169 | 14:00 | 112 | Matuail | 55 | 09:00 | 178 | Sonargaon | 134 | 00:00
47 | Daganbhuiyan | 34 | 19:00 | 113 | Metrorail_Motijheel | 14 | 14:00 | 179 | Sreemongol | 56 | 00:00
48 | Daudkandi | 134 | 18:00 | 114 | Metrorail_Uttara | 5 | 17:00 | 180 | Sreepur | 97 | 00:00
49 | DhakaUniversity | 42 | 12:00 | 115 | Millgate | 64 | 08:00 | 181 | Srinagar | 43 | 18:00
50 | Dhamrai | 120 | 00:00 | 116 | Mirpur | 104 | 17:00 | 182 | Sunamganj | 45 | 18:30
51 | Dhanmondi | 83 | 13:00 | 117 | Mirsorai | 8 | 18:30 | 183 | Sylhet | 44 | 14:00
52 | Dohazari | 110 | 19:30 | 118 | Mirzapur | 45 | 03:00 | 184 | Sylhet-132 | 78 | 17:00
53 | Faridpur | 154 | 19:00 | 119 | Mithapukur | 56 | 18:00 | 185 | TK | 23 | 18:30
54 | Fatullah | 78 | 00:00 | 120 | Modern | N/A | N/A | 186 | Tangail | 172 | 03:00
55 | Fenchuganj | 32 | 20:00 | 121 | Mogbazar | 41.8 | 14:00 | 187 | Taraganj | 19 | 18:30
56 | Feni | 95 | 20:00 | 122 | Mongla | 43 | 19:00 | 188 | Tasnim | 20 | 10:00
57 | GPH | 3 | 04:00 | 123 | Motijheel | 30 | 13:00 | 189 | Thakurgaon | 92 | 19:00
58 | Ghatail | 90 | 03:00 | 124 | Muktagacha | 37 | 17:00 | 190 | Tongi | 108 | 00:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 101 | 18:30 | 191 | Ullahpara | 42 | 11:00
60 | Ghorashal-230 | 103 | 00:00 | 126 | Muradnagar | 37 | 18:30 | 192 | Ullon | 44 | 14:00
61 | Goalpara | 36 | 18:30 | 127 | Mymensingh | 151 | 18:00 | 193 | Uttara | 66 | 14:00
62 | Gollamari | 98 | 19:00 | 128 | Naogaon | 106 | 00:00 | 194 | UttaraNew | 24 | 00:00
63 | Gopalganj | 103.8 | 19:30 | 129 | Narail | 63.5 | 21:00 | 195 | Zigatola | 76 | 18:00
64 | Gulshan | 80 | 13:00 | 130 | Narinda | 44 | 13:00
65 | Halishahar | 64 | 19:00 | 131 | Narshingdi | 161 | 00:00
66 | HaripurSBU | 105 | 10:00 | 132 | Natore | 140 | 14:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 18-03-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 12740.2 | 0 |  | 12740.2
1:00 | 12201 | 0 |  | 12201
2:00 | 11801 | 0 |  | 11801
3:00 | 11940 | 0 |  | 11940
4:00 | 12134 | 0 |  | 12134
5:00 | 10933 | 0 |  | 10933
6:00 | 9996 | 0 |  | 9996
7:00 | 10005.34 | 0 |  | 10005.34
8:00 | 10252.3 | 0 |  | 10252.3
9:00 | 10735.28 | 0 |  | 10735.28
10:00 | 11125.39 | 0 |  | 11125.39
11:00 | 11190.68 | 0 |  | 11190.68
12:00 | 11702.81 | 0 |  | 11702.81
13:00 | 11904.68 | 0 |  | 11904.68
14:00 | 12223.1 | 0 |  | 12223.1
15:00 | 12122.67 | 0 |  | 12122.67
16:00 | 11928.24 | 0 |  | 11928.24
17:00 | 11801.14 | 0 |  | 11801.14
18:00 | 11495.64 | 0 |  | 11495.64
19:00 | 10598.52 | 0 |  | 10598.52
19:30 | 10131.04 | 0 |  | 10131.04
20:00 | 9550.59 | 0 |  | 9550.59
21:00 | 9487.29 | 0 |  | 9487.29
22:00 | 9080.63 | 0 |  | 9080.63
23:00 | 8668.87 | 0 |  | 8668.87
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 18-03-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6350 | 6390.2 | 12740.2 | DAILY GENERATION CURVE
00:30 | 6253 | 6217.6 | 12470.6
01:00 | 6156 | 6045 | 12201 | 18-03-2026
01:30 | 6130 | 5871 | 12001
02:00 | 6104 | 5697 | 11801
02:30 | 6087.5 | 5783 | 11870.5
03:00 | 6071 | 5869 | 11940
03:30 | 6115.5 | 5921.5 | 12037
04:00 | 6160 | 5974 | 12134
04:30 | 5844.5 | 5689 | 11533.5
05:00 | 5529 | 5404 | 10933
05:30 | 5283.5 | 5181 | 10464.5
06:00 | 5038 | 4958 | 9996
06:30 | 5022.505 | 4978.165 | 10000.67
07:00 | 5007.01 | 4998.33 | 10005.34
07:30 | 5063.42 | 5065.4 | 10128.82
08:00 | 5119.83 | 5132.47 | 10252.3
08:30 | 5204.51 | 5289.28 | 10493.79
09:00 | 5289.19 | 5446.09 | 10735.28
09:30 | 5393.305 | 5537.03 | 10930.335
10:00 | 5497.42 | 5627.97 | 11125.39
10:30 | 5493.275 | 5664.76 | 11158.035
11:00 | 5489.13 | 5701.55 | 11190.68
11:30 | 5632.57 | 5814.175 | 11446.745
12:00 | 5776.01 | 5926.8 | 11702.81
12:30 | 5839.16 | 5964.585 | 11803.745
13:00 | 5902.31 | 6002.37 | 11904.68
13:30 | 5862.58 | 6201.31 | 12063.89
14:00 | 5822.85 | 6400.25 | 12223.1
14:30 | 5807.11 | 6365.775 | 12172.885
15:00 | 5791.37 | 6331.3 | 12122.67
15:30 | 5733.32 | 6292.135 | 12025.455
16:00 | 5675.27 | 6252.97 | 11928.24
16:30 | 5627.86 | 6236.83 | 11864.69
17:00 | 5580.45 | 6220.69 | 11801.14
17:30 | 5520.325 | 6128.065 | 11648.39
18:00 | 5460.2 | 6035.44 | 11495.64
18:30 | 5246.1 | 5800.98 | 11047.08
19:00 | 5032 | 5566.52 | 10598.52
19:30 | 4780 | 5351.04 | 10131.04
20:00 | 4574 | 4976.59 | 9550.59
20:30 | 4683.5 | 4835.44 | 9518.94 |  | Executive Engineer
21:00 | 4793 | 4694.29 | 9487.29 |  | Network Operation Division
21:30 | 4721.5 | 4562.46 | 9283.96
22:00 | 4650 | 4430.63 | 9080.63
22:30 | 4554 | 4320.75 | 8874.75
23:00 | 4458 | 4210.87 | 8668.87

## En-Curve
QF-LDC-12
Date | 18-03-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3176 | 1475 | 897 | 0 | 160 | 1434 | 80 | 4627.2 | 0 | 169 | 722 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3145 | 1473 | 897 | 0 | 157 | 1399.5 | 80 | 4422.6 | 0 | 169 | 726.5 | 0 | 0 | 1 | 0 | 18-03-2026
01:00 | 3114 | 1471 | 897 | 0 | 154 | 1365 | 80 | 4218 | 0 | 169 | 731 | 0 | 0 | 2 | 0
01:30 | 3051 | 1472.5 | 897 | 0 | 153 | 1312 | 80 | 4127.5 | 0 | 169 | 737 | 0 | 0 | 2 | 0 | Energy Generated | 265.8564 |  | MKWHr
02:00 | 2988 | 1474 | 897 | 0 | 152 | 1259 | 80 | 4037 | 0 | 169 | 743 | 0 | 0 | 2 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2966 | 1470 | 897 | 0 | 152 | 1315 | 80 | 4081 | 0 | 178 | 724 | 0 | 0 | 7.5 | 0 | Total Energy Requirement | 265.8564 |  | MKWHr
03:00 | 2944 | 1466 | 897 | 0 | 152 | 1371 | 80 | 4125 | 0 | 187 | 705 | 0 | 0 | 13 | 0
03:30 | 2973 | 1479 | 897 | 0 | 154 | 1367 | 80 | 4209.5 | 0 | 144.5 | 722.5 | 0 | 0 | 10.5 | 0
04:00 | 3002 | 1492 | 897 | 0 | 156 | 1363 | 80 | 4294 | 0 | 102 | 740 | 0 | 0 | 8 | 0
04:30 | 2960.5 | 1480 | 897 | 0 | 152 | 1287.5 | 80 | 4072.5 | 0 | 76.5 | 521 | 0 | 0 | 6.5 | 0
05:00 | 2919 | 1468 | 897 | 0 | 148 | 1212 | 80 | 3851 | 0 | 51 | 302 | 0 | 0 | 5 | 0
05:30 | 2867.5 | 1423.5 | 897 | 0 | 141 | 1152.5 | 80 | 3647.5 | 0 | 25.5 | 226.5 | 0 | 0 | 3.5 | 0
06:00 | 2816 | 1379 | 897 | 0 | 134 | 1093 | 80 | 3444 | 0 | 0 | 151 | 0 | 0 | 2 | 0
06:30 | 2849.5 | 1363 | 897 | 0 | 131 | 1084.5 | 80 | 3433 | 29.67 | 0 | 132 | 0 | 0 | 1 | 0
07:00 | 2883 | 1347 | 897 | 0 | 128 | 1076 | 80 | 3422 | 59.34 | 0 | 113 | 0 | 0 | 0 | 0
07:30 | 2907 | 1402.75 | 897 | 0 | 125 | 1075 | 80 | 3428 | 94.57 | 5.5 | 114 | 0 | 0 | 0 | 0
08:00 | 2931 | 1458.5 | 897 | 0 | 122 | 1074 | 80 | 3434 | 129.8 | 11 | 115 | 0 | 0 | 0 | 0
08:30 | 2957.5 | 1492.5 | 896.5 | 0 | 127 | 1070 | 80 | 3478 | 223.29 | 18 | 151 | 0 | 0 | 0 | 0
09:00 | 2984 | 1526.5 | 896 | 0 | 132 | 1066 | 80 | 3522 | 316.78 | 25 | 187 | 0 | 0 | 0 | 0
09:30 | 3058 | 1519.5 | 896.5 | 0 | 133 | 1066.17 | 80 | 3559 | 393.165 | 21 | 204 | 0 | 0 | 0 | 0
10:00 | 3132 | 1512.5 | 897 | 0 | 134 | 1066.34 | 80 | 3596 | 469.55 | 17 | 221 | 0 | 0 | 0 | 0
10:30 | 3150 | 1522.5 | 897 | 0 | 140 | 1065.595 | 80 | 3545 | 502.44 | 17 | 238.5 | 0 | 0 | 0 | 0
11:00 | 3168 | 1532.5 | 897 | 0 | 146 | 1064.85 | 80 | 3494 | 535.33 | 17 | 256 | 0 | 0 | 0 | 0
11:30 | 3199.5 | 1519 | 897 | 0 | 148 | 1066.785 | 80 | 3680.5 | 577.96 | 17 | 260.5 | 0 | 0 | 0.5 | 0
12:00 | 3231 | 1505.5 | 897 | 0 | 150 | 1068.72 | 80 | 3867 | 620.59 | 17 | 265 | 0 | 0 | 1 | 0
12:30 | 3268.5 | 1522.5 | 897 | 0 | 152.5 | 1078.55 | 80 | 3908 | 594.195 | 17 | 283 | 0 | 0 | 2.5 | 0
13:00 | 3306 | 1539.5 | 897 | 0 | 155 | 1088.38 | 80 | 3949 | 567.8 | 17 | 301 | 0 | 0 | 4 | 0
13:30 | 3250 | 1524.5 | 897 | 0 | 161.5 | 1203.87 | 80 | 4067 | 516.52 | 34.5 | 325.5 | 0 | 0 | 3.5 | 0
14:00 | 3194 | 1509.5 | 897 | 0 | 168 | 1319.36 | 80 | 4185 | 465.24 | 52 | 350 | 0 | 0 | 3 | 0
14:30 | 3147 | 1494 | 897 | 0 | 167 | 1313.415 | 80 | 4164.5 | 432.47 | 60.5 | 412 | 0 | 0 | 5 | 0
15:00 | 3100 | 1478.5 | 897 | 0 | 166 | 1307.47 | 80 | 4144 | 399.7 | 69 | 474 | 0 | 0 | 7 | 0
15:30 | 3125 | 1498.5 | 897 | 0 | 160 | 1349.11 | 80 | 4087 | 318.445 | 69 | 428.4 | 0 | 0 | 13 | 0
16:00 | 3150 | 1518.5 | 897 | 0 | 154 | 1390.75 | 80 | 4030 | 237.19 | 69 | 382.8 | 0 | 0 | 19 | 0
16:30 | 3027 | 1489.5 | 897.5 | 0 | 154 | 1389.685 | 80 | 3985.5 | 160.655 | 148.5 | 519.85 | 0 | 0 | 12.5 | 0
17:00 | 2904 | 1460.5 | 898 | 0 | 154 | 1388.62 | 80 | 3941 | 84.12 | 228 | 656.9 | 0 | 0 | 6 | 0
17:30 | 2882.5 | 1438.75 | 897.5 | 0 | 150 | 1359.865 | 80 | 3866.5 | 43.225 | 224.5 | 699.55 | 0 | 0 | 6 | 0
18:00 | 2861 | 1417 | 897 | 0 | 146 | 1331.11 | 80 | 3792 | 2.33 | 221 | 742.2 | 0 | 0 | 6 | 0
18:30 | 2740.5 | 1360.5 | 897 | 0 | 154 | 1333.315 | 80 | 3645 | 1.165 | 191 | 640.6 | 0 | 0 | 4 | 0
19:00 | 2620 | 1304 | 897 | 0 | 162 | 1335.52 | 80 | 3498 | 0 | 161 | 539 | 0 | 0 | 2 | 0
19:30 | 2568 | 1275 | 897 | 0 | 136 | 1314.04 | 80 | 3421 | 0 | 51 | 389 | 0 | 0 | 0 | 0
20:00 | 2591 | 1274 | 897 | 0 | 14 | 1209.59 | 80 | 3158 | 0 | 51 | 276 | 0 | 0 | 0 | 0
20:30 | 2750 | 1288 | 897 | 0 | 40 | 1116.94 | 80 | 3026 | 0 | 51 | 270 | 0 | 0 | 0 | 0
21:00 | 2909 | 1302 | 897 | 0 | 66 | 1024.29 | 80 | 2894 | 0 | 51 | 264 | 0 | 0 | 0 | 0
21:30 | 2903.5 | 1297.5 | 897 | 0 | 84 | 978.46 | 80 | 2740 | 0 | 51 | 252.5 | 0 | 0 | 0 | 0
22:00 | 2898 | 1293 | 897 | 0 | 102 | 932.63 | 80 | 2586 | 0 | 51 | 241 | 0 | 0 | 0 | 0
22:30 | 2860.5 | 1287 | 897 | 0 | 113 | 884.25 | 80 | 2492.5 | 0 | 51 | 209.5 | 0 | 0 | 0 | 0
23:00 | 2823 | 1281 | 897 | 0 | 124 | 835.87 | 80 | 2399 | 0 | 51 | 178 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 18-03-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 413 | 23:00 | 385 | 00:00 | Madunaghat | 406 | 19:00 | 397 | 00:00
Amtali | 419 | 23:00 | 406 | 00:00 | Meghnaghat | 416 | 23:00 | 389 | 00:00
Ashuganj | 408 | 6:00 | 397 | 17:00 | Payra | 422 | 23:00 | 408 | 00:00
Bhulta | 409 | 18:30 | 394 | 09:00 | Rahanpur | 414 | 23:00 | 397 | 00:00
Bibiana | 414 | 23:00 | 402 | 14:00 | Rampal | 416 | 23:00 | 396 | 14:00
BIPTC | 397 | 23:00 | 388 | 10:00
Bogura | 401 | 23:00 | 381 | 14:00
Gopalganj | 418 | 23:00 | 393 | 00:00
Kaliakoir | 404 | 23:00 | 379 | 14:00
Korerhat | 413 | 23:00 | 396 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 241 | 20:00 | 228 | 00:00 | Jhenaidah | 234 | 22:00 | 217 | 14:00
AKSML | 234 | 21:00 | 228 | 00:00 | Kachua | 234 | 22:00 | 225 | 00:00
Aminbazar | 242 | 19:30 | 230 | 13:00 | Kaliakoir | 245 | 23:00 | 231 | 00:00
Ashuganj | 238 | 19:00 | 227 | 13:00 | Keranigonj | 239 | 18:30 | 227 | 00:00
Ashuganj-400 | 238 | 19:00 | 227 | 13:00 | Khulna(S) | 237 | 23:00 | 222 | 16:00
Baghabari | 238 | 23:00 | 224 | 14:00 | Korerhat | 235 | 06:00 | 227 | 12:00
Barapukuria | 222 | 06:00 | 209 | 14:00 | Madunaghat | 235 | 18:30 | 229 | 00:00
Barapukuria-230 | 222 | 06:00 | 209 | 14:00 | Madunaghat-400 | 236 | 19:00 | 230 | 00:00
Barishal | 233 | 23:00 | 223 | 00:00 | Maniknagar | 236 | 19:00 | 228 | 13:00
Bheramara | 235 | 05:00 | 222 | 14:00 | Meghnaghat | 245 | 19:00 | 236 | 14:00
Bhulta | 239 | 18:30 | 229 | 00:00 | Meghnaghat-400 | 241 | 18:30 | 230 | 00:00
Bibiana | 239 | 07:00 | 209 | 06:00 | Mirsorai | 242 | 23:00 | 234 | 00:00
BIPTC | 237 | 05:00 | 222 | 14:00 | Purbasadipur | 223 | 02:00 | 207 | 16:00
Bogura | 238 | 22:00 | 225 | 16:00 | Rajshahi | 235 | 21:00 | 220 | 14:00
Bogura-400 | 236 | 06:00 | 225 | 16:00 | Rampal | 236 | 23:00 | 222 | 14:00
Borhanuddin | 237 | 23:00 | 230 | 00:00 | Rampur | N/A | N/A | N/A | N/A
BSRM | 234 | 23:00 | 226 | 00:00 | Rampura | 238 | 18:30 | 228 | 00:00
Chowmuhani | 233 | 21:00 | 226 | 14:00 | Shikalbaha | 234 | 18:00 | 230 | 00:00
Cumilla(N) | 236 | 20:00 | 227 | 00:00 | Shyampur | 238 | 19:00 | 227 | 00:00
Faridpur | 235 | 23:00 | 219 | 00:00 | Siddhirganj | 240 | 18:30 | 229 | 00:00
Fenchuganj | 242 | 19:30 | 235 | 03:00 | Sirajgonj | 241 | 23:00 | 231 | 16:00
Feni | 235 | 21:00 | 227 | 00:00 | Sreepur | 232 | 23:00 | 220 | 16:00
Ghorashal | 244 | 22:00 | 230 | 00:00 | Tongi | 242 | 19:00 | 228 | 10:00
Ghorashal-230 | 239 | 18:30 | 225 | 00:00
Gopalganj | 233 | 23:00 | 219 | 00:00
GPH | 235 | 18:30 | 228 | 00:00
Haripur | 239 | 18:30 | 230 | 12:00
Hasnabad | 240 | 18:00 | 226 | 14:00
Hathazari | 233 | 05:00 | 225 | 13:00
Ishurdi | 238 | 23:00 | 224 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 18:30 | 130 | 00:00 | Madunaghat | 135 | 06:00 | 132 | 00:00
Agargaon | 142 | 18:30 | 134 | 00:00 | Magura | 136 | 22:00 | 119 | 14:00
Agrabad | 134 | 18:00 | 130 | 00:00 | Mahasthangarh | 135 | 06:00 | 126 | 16:00
AKS | 133 | 18:00 | 129 | 00:00 | Maijdee | 130 | 22:00 | 125 | 00:00
Aminbazar | 142 | 19:30 | 132 | 00:00 | Manikganj | 140 | 19:00 | 128 | 00:00
Amnura | 136 | 22:00 | 127 | 14:00 | Maniknagar | 139 | 18:30 | 134 | 00:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 118 | 07:00 | 112 | 01:00
Ashuganj-230 | 144 | 19:00 | 135 | 00:00 | Matuail | 142.3 | 19:00 | 134.5 | 00:00
Bagerhat | 133 | 23:00 | 122 | 19:00 | Metrorail_Motijheel | 139 | 18:30 | 134 | 00:00
Bajitpur | 137 | 18:00 | 128 | 13:00 | Metrorail_Uttara | 141 | 20:00 | 130 | 00:00
Bakerganj | 135 | 23:00 | 129 | 14:00 | Millgate | 142 | 18:30 | 132 | 00:00
Bakulia | 134 | 18:00 | 130 | 12:00 | Mirpur | 141 | 18:30 | 131 | 02:00
Banani | 143 | 18:30 | 132 | 00:00 | Mirzapur | 140 | 18:30 | 129 | 00:00
Bangabhaban | 139 | 20:00 | 134 | 13:00 | Mithapukur | 134 | 06:00 | 123 | 16:00
Barapukuria | 137 | 06:00 | 126 | 14:00 | MI_Cement | 142.7 | 20:00 | 132 | 01:00
Barguna | 134 | 07:00 | 129 | 14:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 135 | 23:00 | 129 | 15:00 | Mogbazar | 136 | 18:30 | 130 | 0:00
Barishal-230 | 135 | 23:00 | 128 | 16:00 | Mongla | 135 | 06:00 | 122 | 18:30
Baroaulia | 134 | 08:00 | 131 | 00:00 | Motijheel | 139 | 20:00 | 134 | 14:00
Baroirhat | 133 | 18:00 | 129 | 00:00 | Muktagacha | 135 | 17:00 | 125 | 00:00
Bashundhara | 143 | 18:30 | 130 | 00:00 | Munshiganj | 141 | 18:30 | 132 | 00:00
BashundharaCement | 142 | 18:30 | 135 | 09:00 | Muradnagar | 138 | 21:00 | 128 | 00:00
Beanibazar | 132 | 20:00 | 126 | 14:00 | Mymensingh | 136 | 17:00 | 123 | 08:00
Benapole | 135 | 23:00 | 113 | 14:00 | Naogaon | 140 | 22:00 | 125 | 14:00
Bhaluka | 137 | 17:00 | 128 | 14:00 | Narail | 136 | 06:00 | 119 | 14:00
Bhandaria | 131 | 06:00 | 123 | 16:00 | Narinda | 0 | 00:00 | N/A | N/A
Bhangura | 137 | 21:00 | 126 | 14:00 | Narshingdi | 140 | 18:30 | 128 | 00:00
Bheramara | 137 | 22:00 | 130 | 14:00 | Natore | 136 | 21:00 | 126 | 14:00
Bheramara(GK) | 138 | 22:00 | 130 | 14:00 | Nawabganj | 142 | 20:00 | 132 | 00:00
Bhulta | 137 | 19:00 | 128 | 00:00 | Netrakona | 134 | 23:00 | 122 | 14:00
Bog-Sherpur | 137 | 22:00 | 127 | 14:00 | New | 143 | 18:30 | 133 | 00:00
Bogura | 137 | 21:00 | 129 | 16:00 | Niamatpur | 138 | 23:00 | 130 | 00:00
Bogura-230 | 137 | 06:00 | 129 | 16:00 | Noapara | 137 | 23:00 | 126 | 15:00
Brahmanbaria | 137 | 23:00 | 127 | 19:00 | Pabna | 138 | 21:00 | 128 | 14:00
Cantonment | 142 | 18:30 | 134 | 00:00 | Palashbari | 131 | 05:00 | 123 | 14:00
Chandina | 138 | 20:00 | 130 | 14:00 | Panchagarh | 137 | 18:30 | 125 | 14:00
Chandpur | 131 | 22:00 | 127 | 00:00 | Patiya | 132 | 17:00 | 128 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 136 | 18:00 | 132 | 00:00 | Patuakhali | 134 | 23:00 | 129 | 14:00
Chapai | 137 | 23:00 | 131 | 00:00 | Payra | 138 | 23:00 | 132 | 00:00
Charsaidpur | 142 | 18:30 | 133 | 00:00 | PHP | 133 | 21:00 | 128 | 00:00
Chauddagram | 134 | 21:00 | 127 | 00:00 | Postogola | 144 | 20:00 | 135 | 00:00
Chhatak | 131 | 06:00 | 125 | 16:00 | Pubail | 146 | 18:00 | 133 | 12:00
Chowmuhani | 131 | 22:00 | 125 | 00:00 | Purbachal | 142 | 18:30 | 132 | 00:00
Chuadanga | 137 | 22:00 | 116 | 14:00 | Purbasadipur | 132 | 02:00 | 122 | 16:00
Coxsbazar | 118 | 08:00 | 111 | 13:00 | Rahanpur | 139 | 00:00 | 133 | 01:00
Cumilla(N) | 137 | 21:00 | 130 | 00:00 | Rahanpur-400 | 139 | 22:00 | 133 | 00:00
Cumilla(S) | 138 | 20:00 | 122 | 16:00 | Rahim | 141 | 18:00 | 135 | 00:00
Daganbhuiyan | 131 | 21:00 | 126 | 00:00 | Rajbari | 136 | 23:00 | 124 | 00:00
Daudkandi | 139 | 21:00 | 126 | 00:00 | Rajendrapur | 139 | 18:30 | 128 | 14:00
DhakaUniversity | 135 | 18:30 | 130 | 00:00 | Rajshahi | 136 | 21:00 | 124 | 14:00
Dhamrai | 142 | 18:00 | 131 | 17:00 | Rajshahi-230 | 136 | 21:00 | 126 | 14:00
Dhanmondi | 143 | 18:30 | 135 | 00:00 | Ramganj | 128 | 20:00 | 123 | 00:00
Dohazari | 127 | 05:00 | 123 | 00:00 | Rampur | 135 | 18:00 | 130 | 00:00
Faridpur | 136 | 23:00 | 126 | 00:00 | Rampura | 134 | 06:00 | 130 | 00:00
Fatullah | 142 | 18:30 | 131 | 00:00 | Rangamati | 135 | 22:00 | 131 | 00:00
Fenchuganj | 137 | 19:30 | 132 | 16:00 | Rangpur | 133 | 06:00 | 124 | 14:00
Feni | 131 | 22:00 | 126 | 00:00 | Ruppur | 138 | 21:00 | 131 | 13:00
Feni-230 | 132 | 21:00 | 127 | 00:00 | Saidpur | 134 | 06:00 | 123 | 14:00
Ghatail | 136 | 23:00 | 123 | 00:00 | Satkhira | 135 | 05:00 | 123 | 18:30
Ghorashal | 145 | 19:30 | 135 | 14:00 | Satmasjid | 140 | 19:00 | 134 | 00:00
Goalpara | 139 | 06:00 | 128 | 16:00 | Savar | 141 | 20:00 | 130 | 00:00
Gollamari | 139 | 06:00 | 130 | 14:00 | SevenRings | 146 | 19:00 | 135 | 11:00
Gopalganj | 140 | 23:00 | 128 | 00:00 | ShahCement | 142 | 18:30 | 133 | 00:00
Gopalganj-400 | 140 | 23:00 | 130 | 00:00 | Shahjadpur | 140 | 21:00 | 131 | 15:00
Gulshan | 134 | 18:30 | 130 | 00:00 | Shahjibazar | 135 | 20:00 | 126 | 16:00
Halishahar | 136 | 18:30 | 131 | 00:00 | Shahmirpur | 135 | 18:00 | 130 | 13:00
Haripur | 141 | 18:30 | 134 | 00:00 | Shariatpur | 138 | 23:00 | 127 | 00:00
HaripurSBU | 141 | 18:30 | 135 | 01:00 | Sherpur | 131 | 04:00 | 118 | 18:00
Hasnabad | 144 | 20:00 | 135 | 00:00 | Shikalbaha | 125 | 06:00 | 119 | 00:00
Hathazari | 135 | 04:00 | 132 | 00:00 | Shikalbaha-230 | 137 | 23:00 | 131 | 00:00
Hatirjheel | 135 | 18:30 | 130 | 00:00 | Shitalakhya | 142.7 | 20:00 | 132 | 01:00
Ishurdi | 140 | 22:00 | 131 | 16:00 | Sholosohor | 135 | 18:00 | 131 | 00:00
Jaldhaka | 131 | 06:00 | 121 | 14:00 | Shyampur | 138 | 18:30 | 130 | 02:00
Jamalpur | 133 | 04:00 | 123 | 18:00 | Shyampur-230 | 137 | 18:30 | 131 | 00:00
Jashore | 137 | 23:00 | 115 | 13:00 | Siddhirganj | 142 | 18:30 | 135 | 00:00
Jhenaidah | 138 | 22:00 | 121 | 14:00 | Sirajganj | 136 | 22:00 | 125 | 14:00
Jhenaidah-230 | 136 | 06:00 | 122 | 14:00 | Sonargaon | 142 | 19:00 | 134 | 00:00
Joydebpur | 144 | 18:30 | 127 | 10:00 | Sreemongol | 135 | 20:00 | 128 | 00:00
Joypurhat | 133 | 22:00 | 123 | 16:00 | Sreepur | 140 | 18:30 | 131 | 16:00
Juldah | 136 | 18:30 | 130 | 00:00 | Srinagar | 140 | 18:30 | 132 | 00:00
Kabirpur | 146 | 18:00 | 133 | 00:00 | SSM | 138 | 00:00 | 136 | 14:00
Kachua | 132 | 20:00 | 127 | 13:00 | Sunamganj | 128 | 06:00 | 124 | 00:00
Kaliakoir | 144 | 18:00 | 136 | 19:00 | Sylhet | 132 | 06:00 | 128 | 00:00
Kaliganj | 136 | 22:00 | 120 | 14:00 | Sylhet-132 | 132 | 19:30 | 128 | 14:00
Kallyanpur | 142 | 19:30 | 131 | 00:00 | Tangail | 137 | 17:00 | 126 | 07:00
Kalurghat | 135 | 17:00 | 132 | 11:00 | Taraganj | 133 | 01:00 | 122 | 14:00
Kamrangirchar | 141 | 18:30 | 130 | 00:00 | Tasnim | 142 | 19:00 | 132 | 00:00
Kaptai | 137 | 16:00 | 135 | 15:00 | Thakurgaon | 136 | 18:30 | 122 | 14:00
Kasba | 138 | 19:30 | 128 | 00:00 | TK | 135 | 17:00 | 132 | 00:00
Kazla | 140 | 21:00 | 134 | 13:00 | Tongi | 139 | 19:00 | 135 | 11:00
Keranigonj | 143 | 20:00 | 133 | 00:00 | Ullahpara | 137 | 23:00 | 126 | 14:00
Khagrachori | 135 | 22:00 | 130 | 00:00 | Ullon | 134 | 06:00 | 130 | 00:00
Khulna | 138 | 23:00 | 128 | 15:00 | Uttara | 140 | 20:00 | 130 | 00:00
Khulna(S) | 139 | 06:00 | 130 | 14:00 | UttaraNew | 141 | 20:00 | 131 | 00:00
Khulshi | 133 | 18:00 | 129 | 00:00 | Zigatola | 142 | 19:30 | 133 | 00:00
Kishoreganj | 139 | 19:00 | 125 | 16:00
Kodda | 141 | 18:00 | 127 | 06:00
Korerhat | 136 | 23:00 | 131 | 00:00
KSRM | 136 | 23:00 | 131 | 12:00
Kulaura | 137 | 20:00 | 131 | 14:00
Kurigram | 129 | 06:00 | 116 | 16:00
Kushtia | 139 | 22:00 | 126 | 14:00
Laksam | 132 | 19:30 | 127 | 16:00
Lakshmipur | 130 | 21:00 | 124 | 00:00
Lalbag | 141 | 18:30 | 133 | 00:00
Lalmonirhat | 130 | 06:00 | 120 | 13:00
Madanganj | 142 | 18:30 | 135 | 09:00
Madaripur | 139 | 23:00 | 129 | 00:00
Madartek | 134 | 18:30 | 130 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division