## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 19-03-2026 | [28 empty] | Date: | 19-03-2026 | [28 empty] | Date: | 19-03-2026 | [28 empty] | Date: | 19-03-2026 | [28 empty] | Date: | 19-03-2026 | [17 empty] | Date: | 19-03-2026
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [17 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 342.010 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 12 | 0 | 0 | 51 | 0 | 0 | 12 | 36 | 0 | 80 | 0 | 29 | 320 | 0 | 0 | 39 | 0 | 0 | 181 | 0 | 0 | 0 | 605 | 0 | 0 | 0 | 11 | 0 | 200 | 0 | 0 | 133 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 250 | 0 | 318 | 29 | 0 | 135 | 0 | 17 | 0 | 5 | 20 | 40 | 0 | 98 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 3950 | 896 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740 | 0 | 0 | 0 | 833.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 90 | 180 | 0 | 0 | 500 | 0 | 3989.23 | 7939.23 | 87.55
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 12 | 0 | 4 | 34 | 0 | 0 | 12 | 24 | 0 | 40 | 0 | 28 | 320 | 0 | 0 | 39 | 0 | 0 | 181 | 0 | 0 | 0 | 602 | 0 | 0 | 0 | 14 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 240 | 0 | 318 | 30 | 0 | 120 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 98 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 3618 | 796 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 762 | 0 | 0 | 0 | 811.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 45 | 180 | 0 | 0 | 500 | 0 | 3812.53 | 7430.53 | 87.54
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 12 | 0 | 0 | 34 | 0 | 0 | 12 | 24 | 0 | 40 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 605 | 0 | 0 | 0 | 11 | 0 | 200 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 165 | 0 | 340 | 30 | 0 | 133 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 98 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 3609 | 614 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767 | 0 | 0 | 0 | 811.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 45 | 180 | 0 | 0 | 500 | 0 | 3683.53 | 7292.53 | 87.53
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 40 | 0 | 10 | 320 | 0 | 0 | 1 | 0 | 0 | 181 | 0 | 0 | 0 | 605 | 0 | 0 | 0 | 13 | 0 | 345 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 165 | 0 | 352 | 41 | 0 | 144 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 98 | 0 | 4 | 8 | 106 | 0 | 0 | 0 | 3908 | 614 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 776 | 0 | 0 | 0 | 816.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 50 | 220 | 0 | 0 | 500 | 0 | 3795.17 | 7703.17 | 87.52
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 12 | 0 | 40 | 0 | 15 | 320 | 0 | 0 | 6 | 0 | 0 | 181 | 0 | 0 | 0 | 700 | 0 | 0 | 0 | 13 | 0 | 325 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 88 | 0 | 0 | 0 | 165 | 0 | 328 | 41 | 0 | 158 | 0 | 0 | 0 | 52 | 30 | 0 | 0 | 98 | 0 | 16 | 16 | 107 | 0 | 0 | 0 | 4235 | 614 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 940 | 0 | 0 | 0 | 857.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 65 | 220 | 0 | 0 | 530 | 0 | 4125.32 | 8360.32 | 87.51
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 12 | 0 | 40 | 0 | 15 | 320 | 0 | 0 | 6 | 0 | 0 | 181 | 0 | 0 | 0 | 604 | 0 | 0 | 0 | 13 | 0 | 260 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 84 | 0 | 0 | 0 | 165 | 0 | 329 | 41 | 0 | 153 | 0 | 0 | 0 | 5 | 30 | 0 | 0 | 98 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 3879 | 522 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 761 | 0 | 0 | 0 | 824.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 65 | 180 | 0 | 0 | 500 | 0 | 3659.81 | 7538.81 | 87.5
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 605 | 0 | 0 | 0 | 13 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 82 | 0 | 0 | 0 | 165 | 0 | 310 | 30 | 0 | 120 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 98 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 3433 | 421 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 741 | 0 | 0 | 0 | 819.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 45 | 180 | 0 | 0 | 500 | 0 | 3361.5 | 6794.5 | 87.49
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 168 | 0 | 0 | 4 | 0 | 12 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.47 | 30 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 609 | 2 | 0 | 0 | 13 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 84 | 0 | 10 | 0 | 165 | 0 | 337 | 29 | 0 | 120 | 2 | 0 | 0 | 0 | 7 | 0 | 0 | 98 | 0 | 0 | 0 | 73 | 0.2 | 6.29 | 0 | 3429.96 | 271 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.42 | 761 | 0 | 0 | 0 | 821.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.18 | 10 | 0 | 0 | 6.54 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0.18 | 0 | 55 | 0 | 3 | 0 | 0 | 0 | 0 | 0.2 | 21 | 0.07 | 0 | 140 | 45 | 180 | 0 | 0 | 500 | 0 | 3239.19 | 6669.15 | 87.48
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 168 | 0 | 0 | 11 | 0 | 12 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.49 | 30 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 608 | 9 | 0 | 0 | 25 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 76 | 0 | 30 | 0 | 165 | 0 | 325 | 29 | 0 | 137 | 5 | 0 | 0 | 0 | 7 | 0 | 0 | 98 | 0 | 0 | 0 | 106 | 0.8 | 19.22 | 0 | 3558.51 | 421 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.25 | 758 | 0 | 0 | 0 | 822.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.38 | 41 | 0 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 1.87 | 0 | 55 | 0 | 11 | 0 | 0 | 0 | 0 | 2.2 | 67 | 0.2 | 0 | 140 | 45 | 180 | 0 | 0 | 500 | 0 | 3526.78 | 7085.29 | 87.47
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 168 | 0 | 0 | 19 | 0 | 13 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.46 | 30 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 608 | 13 | 0 | 0 | 50 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 84 | 0 | 46 | 0 | 165 | 0 | 340 | 29 | 0 | 141 | 8 | 0 | 0 | 0 | 7 | 0 | 0 | 98 | 0 | 0 | 0 | 110 | 1.1 | 32.57 | 0 | 3688.13 | 592 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 770 | 0 | 0 | 0 | 825.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.56 | 34 | 0 | 0 | 42.06 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 3.61 | 0 | 55 | 0 | 20 | 0 | 0 | 0 | 0 | 4.2 | 113 | 0.37 | 0 | 140 | 45 | 180 | 0 | 0 | 500 | 0 | 3825.38 | 7513.51 | 87.46
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 168 | 0 | 0 | 28 | 0 | 8 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 3.2 | 30 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 605 | 17 | 0 | 0 | 50 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 90 | 0 | 62 | 0 | 165 | 0 | 337 | 30 | 0 | 139 | 10 | 0 | 0 | 0 | 7 | 0 | 0 | 98 | 0 | 0 | 0 | 157 | 1.4 | 41.84 | 0 | 3752.44 | 893 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 760 | 0 | 0 | 0 | 820.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.51 | 36 | 0 | 0 | 52.81 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 4.59 | 0 | 56 | 0 | 28 | 0 | 0 | 0 | 0 | 5.6 | 143 | 0.51 | 0 | 140 | 45 | 180 | 0 | 0 | 500 | 0 | 4198.77 | 7951.21 | 87.45
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 230 | 0 | 0 | 25 | 0 | 8 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 3.62 | 30 | 0 | 0 | 320 | 0 | 0 | 15 | 0 | 0 | 182 | 0 | 0 | 0 | 608 | 19 | 0 | 0 | 100 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 96 | 0 | 69 | 0 | 200 | 0 | 357 | 30 | 0 | 142 | 12 | 0 | 0 | 0 | 7 | 0 | 0 | 98 | 0 | 0 | 0 | 156 | 2.2 | 48.3 | 0 | 4038.12 | 896 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 772 | 0 | 0 | 0 | 835.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.32 | 102 | 0 | 0 | 61.83 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 5.5 | 0 | 56 | 0 | 32 | 0 | 0 | 0 | 0 | 6.3 | 118 | 0.6 | 0 | 140 | 45 | 180 | 0 | 0 | 500 | 0 | 4316.92 | 8355.04 | 87.44
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 230 | 0 | 0 | 32 | 0 | 8 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 12 | 36 | 3.81 | 80 | 0 | 0 | 320 | 0 | 0 | 28 | 0 | 0 | 182 | 0 | 0 | 0 | 608 | 19 | 0 | 0 | 150 | 0 | 250 | 1 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 112 | 0 | 73 | 0 | 275 | 0 | 363 | 42 | 0 | 147 | 12 | 0 | 0 | 10 | 20 | 0 | 0 | 98 | 0 | 8 | 8 | 156 | 2 | 35.75 | 0 | 4448.56 | 896 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 802 | 0 | 0 | 0 | 842.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.37 | 113 | 0 | 0 | 36.47 | 0 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 2.87 | 0 | 56 | 0 | 19 | 0 | 0 | 0 | 0 | 6.6 | 150 | 0.63 | 0 | 140 | 45 | 180 | 0 | 0 | 500 | 0 | 4563.95 | 9012.51 | 87.43
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 310 | 0 | 0 | 31 | 0 | 8 | 7 | 0 | 370 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 24 | 25 | 3.57 | 80 | 0 | 2 | 320 | 0 | 0 | 34 | 0 | 0 | 216 | 0 | 0 | 0 | 639 | 17 | 0 | 0 | 150 | 0 | 340 | 10 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 110 | 0 | 69 | 0 | 310 | 0 | 396 | 42 | 0 | 149 | 9 | 0 | 0 | 35 | 30 | 0 | 0 | 98 | 0 | 8 | 8 | 156 | 2 | 26.79 | 0 | 4931.36 | 896 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 820 | 0 | 0 | 0 | 831.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.03 | 100 | 0 | 0 | 61.38 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.74 | 0 | 56 | 0 | 23 | 0 | 0 | 0 | 0 | 6.9 | 137 | 0.61 | 0 | 192 | 60 | 220 | 0 | 0 | 520 | 0 | 4778.35 | 9709.71 | 87.42
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 327 | 0 | 0 | 16 | 35 | 8 | 7 | 0 | 340 | 0 | 0 | 12 | 0 | 13 | 0 | 0 | 0 | 24 | 25 | 3.07 | 80 | 0 | 7 | 320 | 0 | 0 | 45 | 0 | 0 | 217 | 0 | 0 | 0 | 710 | 17 | 0 | 0 | 300 | 0 | 345 | 36 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 124 | 0 | 62 | 0 | 320 | 0 | 370 | 42 | 0 | 155 | 10 | 8 | 0 | 80 | 30 | 0 | 0 | 96 | 0 | 24 | 8 | 155 | 2 | 45.42 | 0 | 5309.49 | 896 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 809 | 0 | 0 | 0 | 912.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.45 | 56 | 0 | 0 | 47.11 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.14 | 0 | 55 | 0 | 27 | 0 | 0 | 0 | 0 | 5.3 | 166 | 0.54 | 0 | 220 | 60 | 220 | 0 | 0 | 634 | 0 | 5028.37 | 10337.86 | 87.41
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 326 | 0 | 0 | 8 | 35 | 8 | 7 | 0 | 370 | 0 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 24 | 25 | 2.26 | 80 | 0 | 12 | 320 | 0 | 0 | 50 | 0 | 0 | 217 | 0 | 0 | 0 | 710 | 12 | 0 | 0 | 300 | 0 | 342 | 51 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 124 | 0 | 49 | 0 | 320 | 0 | 375 | 42 | 0 | 155 | 7 | 17 | 0 | 82 | 30 | 0 | 0 | 96 | 0 | 24 | 8 | 155 | 1.4 | 28.29 | 0 | 5342.95 | 896 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 820 | 0 | 0 | 0 | 915.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.86 | 67 | 0 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.8 | 0 | 55 | 0 | 23 | 0 | 0 | 0 | 0 | 4.6 | 115 | 0.45 | 0 | 220 | 60 | 220 | 0 | 0 | 650 | 0 | 4944.52 | 10287.47 | 87.4
16:00 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 51 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 328 | 0 | 0 | 0 | 52 | 8 | 7 | 0 | 360 | 0 | 0 | 12 | 0 | 7 | 0 | 0 | 0 | 50 | 25 | 1.39 | 80 | 0 | 12 | 320 | 0 | 0 | 50 | 0 | 0 | 218 | 0 | 0 | 0 | 710 | 7 | 0 | 0 | 325 | 0 | 342 | 51 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 130 | 0 | 30 | 0 | 320 | 0 | 394 | 42 | 0 | 143 | 3 | 17 | 0 | 82 | 20 | 0 | 0 | 96 | 0 | 24 | 8 | 155 | 0.6 | 23.76 | 0 | 5490.75 | 896 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 815 | 0 | 0 | 0 | 919.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.47 | 41 | 0 | 0 | 26.86 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 2.42 | 0 | 55 | 0 | 6 | 0 | 0 | 0 | 0 | 2.4 | 80 | 0.26 | 0 | 221 | 60 | 220 | 0 | 0 | 650 | 0 | 4823.86 | 10314.61 | 87.39
17:00 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 52 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 328 | 0 | 0 | 0 | 52 | 8 | 7 | 0 | 375 | 0 | 0 | 12 | 0 | 6 | 17 | 0 | 0 | 50 | 50 | 0.46 | 80 | 0 | 21 | 320 | 0 | 0 | 50 | 0 | 0 | 218 | 0 | 0 | 0 | 870 | 3 | 0 | 0 | 325 | 0 | 345 | 51 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 122 | 0 | 11 | 0 | 325 | 0 | 394 | 42 | 0 | 146 | 1 | 17 | 0 | 82 | 20 | 0 | 0 | 96 | 0 | 30 | 8 | 155 | 0.2 | 7.79 | 0 | 5717.45 | 896 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 900 | 0 | 0 | 0 | 920.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.55 | 19 | 0 | 0 | 9.12 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0.86 | 0 | 56 | 0 | 3 | 0 | 0 | 0 | 0 | 1.1 | 30 | 0.09 | 0 | 254 | 60 | 220 | 0 | 0 | 680 | 0 | 4845.67 | 10563.12 | 87.38
18:00 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 52 | 369 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 329 | 0 | 0 | 0 | 52 | 8 | 7 | 0 | 375 | 0 | 0 | 12 | 0 | 1 | 17 | 0 | 0 | 12 | 12 | 0 | 80 | 0 | 29 | 320 | 0 | 0 | 50 | 0 | 0 | 220 | 0 | 0 | 0 | 1025 | 0 | 0 | 0 | 370 | 0 | 345 | 51 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 126 | 0 | 0 | 7 | 325 | 0 | 394 | 42 | 0 | 154 | 0 | 17 | 0 | 82 | 30 | 17 | 0 | 96 | 0 | 94 | 75 | 155 | 0 | 0.24 | 0 | 6019.24 | 896 | 394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 990 | 0 | 0 | 0 | 1114.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.02 | 0 | 56 | 0 | 1 | 0 | 0 | 0 | 0 | 0.2 | 3 | 0 | 0 | 282 | 100 | 220 | 0 | 0 | 855 | 0 | 5326.72 | 11345.96 | 87.37
19:00 | 0 | 8 | 0 | 100 | 0 | 0 | 0 | 53 | 333 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 333 | 0 | 0 | 0 | 70 | 8 | 7 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 12 | 12 | 0 | 80 | 0 | 29 | 320 | 0 | 0 | 32 | 0 | 0 | 221 | 0 | 0 | 0 | 1118 | 0 | 0 | 0 | 335 | 0 | 345 | 51 | 0 | 195 | 0 | 0 | 42 | 0 | 0 | 20 | 0 | 132 | 0 | 0 | 7 | 315 | 0 | 338 | 42 | 0 | 141 | 0 | 17 | 0 | 82 | 30 | 75 | 0 | 96 | 0 | 75 | 45 | 158 | 0 | 0 | 5 | 5954 | 896 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1001 | 0 | 0 | 0 | 1236.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 0 | 1000 | 0 | 5634.52 | 11588.52 | 87.36
19:30 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 53 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 333 | 0 | 0 | 0 | 35 | 8 | 7 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 320 | 0 | 0 | 19 | 0 | 0 | 223 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 345 | 0 | 345 | 51 | 0 | 200 | 0 | 0 | 98 | 0 | 0 | 20 | 0 | 128 | 0 | 0 | 0 | 315 | 0 | 340 | 42 | 0 | 137 | 0 | 17 | 0 | 82 | 30 | 75 | 0 | 96 | 0 | 35 | 24 | 159 | 0 | 0 | 0 | 5854 | 896 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 957 | 0 | 0 | 0 | 1164.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 120 | 220 | 0 | 0 | 1060 | 0 | 5550.51 | 11404.51
20:00 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 53 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 334 | 0 | 0 | 0 | 35 | 8 | 12 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 320 | 0 | 0 | 19 | 0 | 0 | 224 | 0 | 0 | 0 | 1050 | 0 | 0 | 0 | 355 | 0 | 345 | 51 | 0 | 204 | 0 | 0 | 98 | 0 | 0 | 20 | 0 | 124 | 0 | 0 | 0 | 315 | 0 | 340 | 41 | 0 | 139 | 0 | 17 | 0 | 82 | 30 | 75 | 0 | 96 | 0 | 35 | 24 | 159 | 0 | 0 | 0 | 5832 | 896 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 946 | 0 | 0 | 0 | 1129.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 56 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 125 | 220 | 0 | 0 | 1070 | 0 | 5558.27 | 11390.27 | 87.36
21:00 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 53 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 333 | 0 | 0 | 0 | 35 | 8 | 12 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 320 | 0 | 0 | 12 | 0 | 0 | 224 | 0 | 0 | 0 | 1069 | 0 | 0 | 0 | 365 | 0 | 355 | 51 | 0 | 210 | 0 | 0 | 99 | 0 | 0 | 20 | 0 | 130 | 0 | 0 | 0 | 320 | 0 | 392 | 41 | 0 | 155 | 0 | 17 | 0 | 82 | 30 | 75 | 0 | 96 | 0 | 35 | 8 | 159 | 0 | 0 | 0 | 5982 | 896 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1053 | 0 | 0 | 0 | 1129.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 125 | 220 | 0 | 0 | 1080 | 0 | 5648.91 | 11630.91 | 87.35
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 342 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 300 | 0 | 0 | 0 | 35 | 8 | 12 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 320 | 0 | 0 | 2 | 0 | 0 | 224 | 0 | 0 | 0 | 1102 | 0 | 0 | 0 | 360 | 0 | 355 | 51 | 0 | 203 | 0 | 0 | 99 | 0 | 0 | 20 | 0 | 132 | 0 | 0 | 0 | 320 | 0 | 392 | 41 | 0 | 161 | 0 | 17 | 0 | 82 | 30 | 75 | 0 | 96 | 0 | 16 | 8 | 159 | 0 | 0 | 0 | 5823 | 896 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1101 | 0 | 0 | 0 | 1130.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 125 | 220 | 0 | 0 | 1105 | 0 | 5728.51 | 11551.51 | 87.35
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 311 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 300 | 0 | 0 | 0 | 35 | 8 | 12 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 320 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 393 | 0 | 330 | 51 | 0 | 192 | 0 | 0 | 99 | 0 | 0 | 20 | 0 | 136 | 0 | 0 | 0 | 315 | 0 | 370 | 41 | 0 | 155 | 0 | 17 | 0 | 82 | 30 | 74 | 0 | 96 | 0 | 16 | 8 | 160 | 0 | 0 | 0 | 5706 | 896 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1079 | 0 | 0 | 0 | 1117.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 125 | 220 | 0 | 0 | 1120 | 0 | 5680.52 | 11386.52 | 87.34
Total KWH | 0 | 15360 | 0 | 570500 | 0 | 0 | 0 | 471500 | 7887600 | 0 | 44800 | 0 | 0 | 29232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7765881 | 0 | 0 | 6032903 | 0 | 0 | 185999 | 446400 | 253200 | 118080 | 0 | 7872272.73 | 0 | 0 | 106560 | 0 | 97440 | 282004 | 0 | 0 | 220800 | 293760 | 25438 | 1424700 | 0 | 346560 | 7723636.36 | 0 | 0 | 524160 | 0 | 0 | 4741262 | 0 | 0 | 0 | 18294543 | 126225 | 0 | 0 | 4288000 | 0 | 6954000 | 572058 | 0 | 4460000 | 0 | 0 | 497141 | 0 | 0 | 247500 | 0 | 2502720 | 0 | 513527 | 10832 | 6045000 | 0 | 8739000 | 870000 | 0 | 3492655 | 83378 | 381648 | 0 | 976320 | 484416 | 448000 | 0 | 2335690 | 0 | 460800 | 249600 | 3045120 | 12800 | 332660 | 8160 | 113911841.09 | 18288727 | 7485408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 546480 | 20647280 | 0 | 0 | 0 | 22283040 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317512 | 608710 | 0 | 0 | 406512 | 0 | 0 | 192782 | 0 | 0 | 0 | 8410472 | 0 | 35880 | 0 | 1304727 | 0 | 213125 | 14092 | 0 | 0 | 0 | 44815.2 | 1152000 | 4290 | 0 | 4778000 | 1705000 | 5070260 | 0 | 0 | 16795636.36 | 0 | 110304748.56 | 224216589.65

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 20-03-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-03-2026 | during | 20-03-2026 | during | 20-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 100 | 150 | 150 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 53 | 97.7 | 97.7 | 7 | 7 | Demand "05"MW due to gas restiction by Titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 335 | 358 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 230 | 333 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 8 | 8 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 12 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 340 | 340 | 584 | 584 | 320 | 320 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 295 | 335 | 583 | 583 | 320 | 320 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 35 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1240 | 1574 | 5837.22 | 5805.22 | 2726.05 | 2798.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 28 | 12 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 80 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 182 | 224 | 220 | 220 | 220 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 56 | 64 | 56 | 64 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 68 | 68 | 68 | 68 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 29 | 40 | 40 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.81 | 0 | 3.61 | 0 | 3.61 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 36 | 0 | 100 | 100 | 25 | 25 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 608 | 1069 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 10 | 0 | 2 | 3 | 2 | 3 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 320 | 320 | 400 | 320 | 320 | 320 | Coal shortage
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1298.81 | 1768 | 3344.47 | 3250.86 | 2657.11 | 2650.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 140 | 210 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 250 | 355 | 342.01 | 342.01 | 342.01 | 342.01 | Able to ON FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 150 | 365 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0.01 | 0.01 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 20 | 20 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 1 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 32 | 32 | 32 | 32 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 99 | 163 | 163 | 100 | 100 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 112 | 130 | 84 | 82 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 7 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 73 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2876.261 | 733 | 1230 | 2411.36 | 2344.36 | 2197.22 | 2132.22
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-03-2026 | during | 20-03-2026 | during | 20-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 156 | 159 | 157.5 | 157.5 | 10 | 10 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.2 | 0 | 1.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 8 | 60 | 80 | 60 | 80 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 8 | 35 | 70 | 115 | 70 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 35.75 | 0 | 39.75 | 0 | 39.75 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 12 | 12 | From12:00 hrs to24:00 hrs will be dispatching12MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 35 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 209.75 | 202 | 404.95 | 429 | 209.95 | 252
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 41 | 41 | 41 | 41 | 41 | plant availability zero
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 147 | 155 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 75 | 100 | 100 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 20 | 30 | 30 | 30 | 0 | 0 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 82 | 83 | 83 | 42 | 42 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 98 | 96 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 17 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 275 | 320 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 363 | 392 | 400 | 400 | 385 | 385 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | plant will be shutdown due to 3rd Minor Inspection
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 967 | 1208 | 1303 | 1303 | 1094 | 1094
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 896 | 896 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 255 | 398 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 68 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 802 | 1053 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2021 | 2347 | 3591.2 | 3506.2 | 2836.1 | 2751.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 45 | 125 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 500 | 1080 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 75 | 75 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 140 | 277 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.63 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 865.63 | 1702 | 2162 | 2161 | 1993 | 1992
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 57.37 | 0 | 58.5 | 0 | 58.5 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 190 | 190 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 394 | 414 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 21 | 21 | 21 | 21 | machine problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 50 | 50 | 50 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.87 | 0 | 5.8 | 0 | 5.8 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 842.01 | 1129.91 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 36.47 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 113 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1445.72 | 1543.91 | 3189.17 | 2963.87 | 2693.17 | 2467.87
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 56 | 56 | 55 | 55 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.6 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 19 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 150 | 0 | 194 | 0 | 194 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 231.6 | 56 | 532.2 | 303 | 457.2 | 228
System Total |  |  |  |  | 28823.2 | 29275.503 | 9012.51 | 11630.91 | 22775.57 | 22066.51 | 16863.8 | 16365.74
Forecast Scenario (20-03-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 10900 |  | 0 |  | 10900
|  |  |  | 1:00 | 10230 |  | 0 |  | 10230
|  |  |  | 2:00 | 9930 |  | 0 |  | 9930
|  |  |  | 3:00 | 10180 |  | 0 |  | 10180
|  |  |  | 4:00 | 10670 |  | 0 |  | 10670
|  |  |  | 5:00 | 9680 |  | 0 |  | 9680
|  |  |  | 6:00 | 8780 |  | 0 |  | 8780
|  |  |  | 7:00 | 8480 |  | 0 |  | 8480
|  |  |  | 8:00 | 8730 |  | 0 |  | 8730
|  |  |  | 9:00 | 9000 |  | 0 |  | 9000
|  |  |  | 10:00 | 9270 |  | 0 |  | 9270
|  |  |  | 11:00 | 9510 |  | 0 |  | 9510
|  |  |  | 12:00 | 10000 |  | 0 |  | 10000
|  |  |  | 13:00 | 10540 |  | 0 |  | 10540
|  |  |  | 14:00 | 11010 |  | 0 |  | 11010
|  |  |  | 15:00 | 10790 |  | 0 |  | 10790
|  |  |  | 16:00 | 10660 |  | 0 |  | 10660
|  |  |  | 17:00 | 10740 |  | 0 |  | 10740
|  |  |  | 18:00 | 11370 |  | 0 |  | 11370
|  |  |  | 18:30 | 11400 |  | 0 |  | 11400
|  |  |  | 19:00 | 11450 |  | 0 |  | 11450
|  |  |  | 19:30 | 11100 |  | 0 |  | 11100
|  |  |  | 20:00 | 10930 |  | 0 |  | 10930
|  |  |  | 21:00 | 11000 |  | 0 |  | 11000
|  |  |  | 22:00 | 10930 |  | 0 |  | 10930
|  |  |  | 23:00 | 10670 |  | 0 |  | 10670
Probable Maximum Temperature: |  |  | 31.00°C
Probable Maximum Demand at Day Peak: |  |  | 10000.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11450.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11450.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 245.45 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:37 hrs on 20-03-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 19-03-2026
Power Supply Scenario
| Day Peak Generation |  |  | 9012.51 | MW | 12:00 Hr. | Energy Generated |  |  | 224.2166 |  | MKWHr.
| Day Peak Demand |  |  | 9012.51 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11630.91 | MW | 21:00 Hr. | Energy Demand |  |  | 224.2166 |  | MKWHr.
| Evening Peak Demand |  |  | 11630.91 | MW | 21:00 Hr. | Maximum Temperature |  |  | 30.5 |  | °C
| Minimum Generation of the Day |  |  | 6669.15 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 818.46 |  | MMCFD
| Maximum Generation of the Day |  |  | 11630.91 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 5.3252 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 31.0167 | 0 | 0.49099 | 0 | 0 | 0.186 | 0 | 0 | 31.6937 | Gas | 102.805 | Gas | 355607061.1441
| Chattogram Zone |  |  | 5.0878 | 26.0182 | 1.4273 | 0 | 1.4247 | 0.15166 | 0 | 0.09744 | 34.2071 | Coal | 69.5438 | Coal | 473617809.5996
| Cumilla Zone |  |  | 17.0187 | 0 | 0.010832 | 0 | 0 | 0.51353 | 2.5027 | 0 | 20.0458 | HFO | 2.6618 | HFO | 46899454.04
| Mymensingh Zone |  |  | 3.0451 | 0 | 0.71856 | 0 | 0 | 0.34546 | 0 | 0 | 4.1091 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.7727 | 0 | 0 | 0 | 0 | 0.083378 | 0 | 0 | 23.8561 | Hydro | 1.4247 | Hydro | 142470
| Khulna Zone |  |  | 7.4854 | 20.6473 | 0 | 0 | 0 | 0.54648 | 18.2887 | 0 | 46.9679 | Solar | 4.6094 | Solar | 73686341.63
| Barishal Zone |  |  | 6.7753 | 21.5736 | 0 | 0 | 0 | 0.00429 | 0 | 0 | 28.3532 | Import | 43.0745 | Import | 242610269.35
| Rajshahi Zone |  |  | 8.6033 | 0 | 0 | 0 | 0 | 1.3686 | 22.283 | 0 | 32.2549 | Wind | 0.09744 | Wind | 1433342.4
| Rangpur Zone |  |  | 0 | 1.3047 | 0.014092 | 0 | 0 | 1.4099 | 0 | 0 | 2.7288
| Total |  |  | 102.805 | 69.5438 | 2.6618 | 0 | 1.4247 | 4.6094 | 43.0745 | 0.09744 | 224.2166
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 355607061.1441 |  | Hydro | 142470
|  |  |  | Coal | 473617809.5996 |  | Solar | 73686341.63
|  |  |  | HFO | 46899454.04 |  | Import | 242610269.35
|  |  |  | HSD | 0 |  | Wind | 1433342.4
[5 empty] | Total: | 119,39,96,748 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 18.2887 | Peak Hr Flow | 896.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 26035436.36 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 22.283 | Peak Hr Flow | 1129.91 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1412 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.5027 | Peak Hr Flow | 130.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1597 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 43.0745 | Peak Hr Flow | 2155.91 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3220
|  |  |  | Chattogram |  | 0 |  | 1278
|  |  |  | Cumilla |  | 0 |  | 1233
|  |  |  | Mymensingh |  | 0 |  | 976
|  |  |  | Sylhet |  | 0 |  | 469
|  |  |  | Khulna |  | 0 |  | 1637
|  |  |  | Barishal |  | 0 |  | 430
|  |  |  | Rajshahi |  | 0 |  | 1243
|  |  |  | Rangpur |  | 0 |  | 742
|  |  |  | Total |  | 0 |  | 11228
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Rangpur 20 MW GTPP |  |  | 20
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 20
|  |  |  | Total Unavailable Capacity |  |  |  | 320
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:25 | 10:57 | BIPTC S/S 10CF15 Forced S/D Due to Shutdown is taken for emergency maintenance
| 08:38 | 11:10 | Ishurdi 132/33kV S/S 132/33 kV T-3 LT Scheduled S/D | [7 empty] | 15.0MW load
interrup.
| 08:38 | 11:09 | Ishurdi 132/33kV S/S 132/33 kV T-3 HT Scheduled S/D | [7 empty] | 15.0MW load
interrup.
| 08:55 | 10:34 | Mahasthangarh 132/33kV S/S 406T MTR1 HT Forced S/D Due to 33 KV Bus-1 work | [7 empty] | 15.0MW load
interrup.
| 08:55 | 10:34 | Mahasthangarh 132/33kV S/S 406T MTR1 LT Forced S/D Due to 33 KV Bus-1 work | [7 empty] | 15.0MW load
interrup.
| 09:09 |  | BIPTC S/S 10CF16 Tripped showing 87.1 Differential Relay relays Due to Tripped by
differential protection Y phase OPTD.
| 09:34 | 10:59 | Ramganj 132/33kV S/S Transformer-01 HT Scheduled S/D Due to 33 KV PBS Feeder Red hot
maintenance work at 33 kv Bus Ds
| 09:34 | 10:59 | Ramganj 132/33kV S/S Transformer-01 LT Scheduled S/D Due to 33 KV PBS Feeder Red hot
maintenance work at 33 kv Bus Ds
| 10:49 | 11:30 | Sherpur 132/33kV S/S Transformer- 01 HT Scheduled S/D Due to OLTC oil Fill.
| 10:49 | 11:31 | Sherpur 132/33kV S/S Transformer- 01 LT Scheduled S/D Due to OLTC oil Fill.
| 11:32 | 11:59 | Sherpur 132/33kV S/S Transformer- 02 LT Scheduled S/D Due to OLTC oil Fill
| 11:32 | 11:58 | Sherpur 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to OLTC oil Fill
| 12:00 |  | Day peak 9008 MW
| 12:35 | 13:34 | Mahasthangarh 132/33kV S/S 406T MTR1 HT Tripped showing Differential relay ,Micom P741 | [7 empty] | 20.0MW load
|  |  | relays Due to Nesco 33 kv feeder Fault. | [7 empty] | interrup.
| 12:35 | 13:37 | Mahasthangarh 132/33kV S/S 406T MTR1 LT Tripped showing over curent P142 relays Due to | [7 empty] | 20.0MW load
|  |  | Nesco 33 kv feeder Fault. | [7 empty] | interrup.
| 12:35 | 12:52 | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Tripped showing OVER Current P142 relays Due to | [7 empty] | 20.0MW load
|  |  | Nesco 33 kv feeder Fault. | [7 empty] | interrup.
| 13:47 | 15:32 | Ashuganj-Kishoreganj 132kV Ckt-1 Scheduled S/D from Bajitpur 132/33kV end Due to Tree
trimming.
| 14:18 | 15:56 | Dhamrai 132/33kV S/S Transformer-2 HT Scheduled S/D Due to PBS work
| 14:18 | 15:56 | Dhamrai 132/33kV S/S Transformer-2 LT Scheduled S/D Due to PBS work
| 14:22 | 15:27 | Munshiganj 132/33kV S/S Transformer-2 LT Project Work S/D Due to Maintenance by pbs bus-2
| 14:22 | 15:26 | Munshiganj 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Maintenance by pbs bus-2
| 14:28 | 15:51 | Dhamrai 132/33kV S/S 33 KV Bus Section-02 Scheduled S/D Due to PBS WORK
|  | 14:49 | Keranigonj 230/132/33kV S/S 132 kV Hasnabad Ckt. 1 is restored.
| 15:02 | 21:42 | Bhulta 400/230kV S/S 400kV Bus-1 Forced S/D
| 15:12 |  | Ghorashal unit-7 GT was sync.
| 15:37 | 16:29 | Kabirpur -Tongi 132kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to for Nest
romove
| 17:35 |  | Shahjibazar 330 MW CCPP GT was sync.
| 17:48 | 05:08 | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) Forced S/D Due to As per NLDC"s
instruction
| 18:44 |  | Chandpur CCPP GT was sync.
| 19:50 | 20:11 | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to TR-01(A+B) 33kV Side CT Redhot | [7 empty] | 5.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 19:52 | 20:10 | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to TR-01(A+B) 33kV Side CT Redhot | [7 empty] | 5.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 21:03 |  | JERA Meghnaghat Power Limited 718 MW CCPP GT2 was sync.
| 21:05 | 00:41 | Kabirpur 132/33kV S/S XFR, T-2 LT Forced S/D Due to Red hot at 33 kV bus DS of TR-2 | [7 empty] | 24.0MW load
interrup.
| 21:06 | 00:38 | Kabirpur 132/33kV S/S XFR, T-2 HT Forced S/D Due to Red hot at 33 kV Bus DS of TR -2 | [7 empty] | 24.0MW load
interrup.
| 22:14 | 23:21 | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to TR-01(A+B) 33kV Side CT Redhot | [7 empty] | 5.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 22:14 | 23:19 | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to TR-01(A+B) 33kV Side CT Redhot | [7 empty] | 5.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 05:00 | 05:20 | Jaldhaka-Saidpur 132kV Ckt-1 Tripped from Saidpur 132/33kV end showing Distance relay
zone 2 relays Due to Distance relay
| 06:15 | 06:28 | Saidpur 132/33kV S/S TR-4 (414T) LT Tripped showing Siemens relays Due to O/C
| 06:30 | 07:14 | Mithapukur-Rangpur Confidence( 100MW ) 132kV Ckt-1 Tripped from Mithapukur 132/33kV end
showing O/C L 1,2 86 LO RELAY relays Due to None
| 07:00 |  | Minimum Generation: 7852 MW.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 19-03-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 100 | 570500 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 53 | 471500 | Demand "05"MW due to gas restiction by Titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 358 | 7887600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 333 | 6032903 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 8 | 253200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 12 | 118080 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 29232 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 15360 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 185999 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 340 | 7872272.73 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 335 | 7765881 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 44800 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 35 | 446400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1574 | 31693727.73
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 126225 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 12 | 524160 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1424700 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 224 | 4741262 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 282004 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 220800 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 29 | 346560 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 106560 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 25438 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 293760 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1069 | 18294543 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 97440 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 320 | 7723636.36 | Coal shortage
Chattogram Area Total |  |  |  |  | 4898.863 | 1768 | 34207088.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 210 | 4460000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Vibration
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 355 | 6954000 | Able to ON FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 365 | 4288000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 572058 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 10832 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 99 | 497141 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 130 | 2502720 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 247500 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 513527 | -
Cumilla Area Total |  |  |  |  | 2876.261 | 1230 | 20045778
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 159 | 3045120 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 8 | 249600 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 35 | 460800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 332660 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 8160 | From12:00 hrs to24:00 hrs will be dispatching12MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 202 | 4109140
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 83378 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 870000 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3492655 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 75 | 448000 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 484416 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 976320 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 96 | 2335690 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 381648 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 6045000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 392 | 8739000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2325 | 1208 | 23856107
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 896 | 18288727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 398 | 7485408 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 546480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1053 | 20647280 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2347 | 46967895
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 125 | 1705000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1080 | 16795636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5070260 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 277 | 4778000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4290 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1702 | 28353186.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 317512 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 192782 | Plant is running to NLDC demand with low gas press
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 8410472 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 35880 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1129.91 | 22283040 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 406512 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 608710 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1543.91 | 32254908
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 56 | 1304727 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 14092 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 44815.2 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 0 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 213125 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1152000 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 56 | 2728759.2
Eastern Grid Total |  |  |  |  | 17423.308 | 5982 | 113911841.09
Western Grid Total |  |  |  |  | 11852.195 | 5648.91 | 110304748.56
National Grid Total |  |  |  |  | 29275.503 | 11630.91 | 224216589.65
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 19-03-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7176.54 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4050.92 | MW
i) Dhaka area |  |  | 3220.04 |  | MW | i) Khulna area |  |  |  | 1636.6 | MW
ii) Chattogram area |  |  | 1278.5 |  | MW | ii) Barishal area |  |  |  | 429.72 | MW
iii) Cumilla area |  |  | 1233 |  | MW | iii) Rajshahi area |  |  |  | 1242.6 | MW
iv) Mymensingh area |  |  | 976 |  | MW | iv) Rangpur area |  |  |  | 742 | MW
v) Sylhet area |  |  | 469 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11227.46 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 7 | 04:00 | 67 | Hasnabad | 50 | 19:30 | 133 | Nawabganj | 50.2 | 21:00
2 | AKSML | 7 | 04:00 | 68 | Hathazari | 76 | 00:00 | 134 | Netrakona | 122 | 18:00
3 | Aftabnagar | 26 | 18:00 | 69 | Hatirjheel | 26 | 14:00 | 135 | New | 34 | 18:00
4 | Agargaon | 73 | 21:00 | 70 | Ishurdi | 57 | 19:30 | 136 | Niamatpur | 90 | 21:00
5 | Agrabad | 54 | 00:00 | 71 | Jaldhaka | 68 | 18:00 | 137 | Noapara | 39 | 21:00
6 | Amnura | 35 | 21:00 | 72 | Jamalpur | 112 | 18:00 | 138 | PHP | 9 | 14:00
7 | Ashuganj | 83 | 15:00 | 73 | Jashore | 147 | 21:00 | 139 | Pabna | 79 | 03:00
8 | BSRM | 197 | 05:00 | 74 | Jhenaidah | 95 | 18:30 | 140 | Palashbari | 96 | 18:00
9 | Bagerhat | 82 | 21:00 | 75 | Joydebpur | 69 | 18:30 | 141 | Panchagarh | 52 | 18:00
10 | Bajitpur | 76 | 18:30 | 76 | Joypurhat | 52 | 21:00 | 142 | Patiya | 9 | 00:00
11 | Bakerganj | 10.36 | 22:00 | 77 | Juldah | 20 | 17:00 | 143 | Patuakhali | 63 | 19:30
12 | Bakulia | 73 | 19:00 | 78 | KSRM | 10 | 17:00 | 144 | Payra | 28 | 22:00
13 | Banani | 13.2 | 20:00 | 79 | Kabirpur | 98 | 18:00 | 145 | Postogola | 33 | 18:30
14 | Bangabhaban | 4 | 10:00 | 80 | Kachua | 87 | 18:00 | 146 | Pubail | 16 | 18:00
15 | Barapukuria | 50 | 04:00 | 81 | Kaliganj | 29 | 21:00 | 147 | Purbachal | 20 | 18:00
16 | Barguna | 20 | 22:00 | 82 | Kallyanpur | 78 | 18:30 | 148 | Purbasadipur | 95 | 13:00
17 | Barishal | 87 | 19:30 | 83 | Kalurghat | 40 | 00:00 | 149 | Rahanpur | 33 | 22:00
18 | Barishal-230 | 96 | 21:00 | 84 | Kamrangirchar | 41 | 00:00 | 150 | Rahim | 1 | 00:00
19 | Baroaulia | 61 | 00:00 | 85 | Kaptai | N/A | N/A | 151 | Rajbari | 65 | 19:00
20 | Baroirhat | 56 | 19:30 | 86 | Kasba | 32 | 22:00 | 152 | Rajendrapur | 83 | 22:00
21 | Bashundhara | 119 | 19:00 | 87 | Kazla | 64 | 18:00 | 153 | Rajshahi | 85 | 18:30
22 | BashundharaCement | 1 | 12:00 | 88 | Keranigonj | 65 | 14:00 | 154 | Rajshahi-230 | 74 | 19:00
23 | Beanibazar | 56 | 18:30 | 89 | Khagrachori | 38 | 18:30 | 155 | Ramganj | 96 | 22:00
24 | Benapole | 68 | 21:00 | 90 | Khulna | 57 | 19:30 | 156 | Rampur | 34 | 00:00
25 | Bhaluka | 105 | 18:00 | 91 | Khulshi | 152 | 19:00 | 157 | Rangamati | 16 | 18:30
26 | Bhandaria | 50 | 21:00 | 92 | Kishoreganj | 118 | 21:00 | 158 | Rangpur | 126 | 18:00
27 | Bhangura | 31 | 18:00 | 93 | Kodda | 127 | 18:00 | 159 | Ruppur | 2.4 | 11:00
28 | Bheramara(GK) | 51 | 21:00 | 94 | Kulaura | 35 | 18:30 | 160 | SSM | 0 | 00:00
29 | Bhulta | 106 | 10:00 | 95 | Kurigram | 67 | 18:00 | 161 | Saidpur | 85 | 18:00
30 | Bog-Sherpur | 62 | 19:00 | 96 | Kushtia | 105 | 20:00 | 162 | Satkhira | 137 | 21:00
31 | Bogura | 131 | 22:00 | 97 | Laksam | 30 | 13:00 | 163 | Satmasjid | 67 | 18:00
32 | Borhanuddin | 91 | 19:00 | 98 | Lakshmipur | 49 | 20:00 | 164 | Savar | 106 | 18:00
33 | Brahmanbaria | 116 | 22:00 | 99 | Lalbag | 30 | 00:00 | 165 | SevenRings | 15.44 | 08:00
34 | Cantonment | 108 | 19:00 | 100 | Lalmonirhat | 52 | 18:00 | 166 | ShahCement | 22 | 23:00
35 | Chandina | 25 | 15:00 | 101 | MI_Cement | 16.3 | 08:00 | 167 | Shahjadpur | 59 | 18:00
36 | Chandpur | 72 | 18:30 | 102 | Madanganj | 27 | 17:00 | 168 | Shahjibazar | 103 | 18:30
37 | Chandraghona | 34 | 19:30 | 103 | Madaripur | 103 | 21:00 | 169 | Shahmirpur | 44 | 00:00
38 | Chapai | 66 | 03:00 | 104 | Madartek | 56 | 18:00 | 170 | Shariatpur | 75 | 18:30
39 | Charsaidpur | 22 | 17:00 | 105 | Madunaghat | 50 | 21:00 | 171 | Sherpur | 134 | 18:00
40 | Chauddagram | 71 | 18:30 | 106 | Magura | 61 | 18:30 | 172 | Shikalbaha | 26.5 | 21:00
41 | Chhatak | 28 | 21:00 | 107 | Mahasthangarh | 66 | 21:00 | 173 | Shitalakhya | 48.6 | 19:00
42 | Chowmuhani | 130 | 19:30 | 108 | Maijdee | 41 | 18:30 | 174 | Sholosohor | 34 | 00:00
43 | Chuadanga | 107 | 19:00 | 109 | Manikganj | 95 | 22:00 | 175 | Shyampur | 77 | 14:00
44 | Coxsbazar | 132 | 22:00 | 110 | Maniknagar | 50 | 18:00 | 176 | Siddhirganj | 68 | 18:00
45 | Cumilla(N) | 100 | 22:00 | 111 | Matarbari | 49 | 03:00 | 177 | Sirajganj | 88 | 21:00
46 | Cumilla(S) | 135 | 23:00 | 112 | Matuail | 31 | 22:00 | 178 | Sonargaon | 50 | 19:30
47 | Daganbhuiyan | 32 | 00:00 | 113 | Metrorail_Motijheel | 15 | 13:00 | 179 | Sreemongol | 58 | 19:00
48 | Daudkandi | 105 | 18:30 | 114 | Metrorail_Uttara | 5 | 16:00 | 180 | Sreepur | 57 | 18:00
49 | DhakaUniversity | 32 | 13:00 | 115 | Millgate | 38 | 00:00 | 181 | Srinagar | 41.6 | 21:00
50 | Dhamrai | 64 | 18:00 | 116 | Mirpur | 92 | 19:30 | 182 | Sunamganj | 47 | 21:00
51 | Dhanmondi | 70 | 20:00 | 117 | Mirsorai | 7 | 19:30 | 183 | Sylhet | 43 | 20:00
52 | Dohazari | 107 | 00:00 | 118 | Mirzapur | 44 | 20:00 | 184 | Sylhet-132 | 82 | 15:00
53 | Faridpur | 134 | 21:00 | 119 | Mithapukur | 55 | 18:00 | 185 | TK | 23 | 00:00
54 | Fatullah | 47 | 23:00 | 120 | Modern | N/A | N/A | 186 | Tangail | 150 | 18:30
55 | Fenchuganj | 30 | 00:00 | 121 | Mogbazar | 32.7 | 19:00 | 187 | Taraganj | 16 | 10:00
56 | Feni | 95 | 18:30 | 122 | Mongla | 29 | 01:00 | 188 | Tasnim | 23 | 16:00
57 | GPH | 2 | 03:00 | 123 | Motijheel | 26 | 19:30 | 189 | Thakurgaon | 88 | 19:00
58 | Ghatail | 90 | 18:00 | 124 | Muktagacha | 40 | 18:00 | 190 | Tongi | 85 | 18:30
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 98 | 16:00 | 191 | Ullahpara | 34 | 21:00
60 | Ghorashal-230 | 74 | 20:00 | 126 | Muradnagar | 35 | 21:00 | 192 | Ullon | 40 | 21:00
61 | Goalpara | 39 | 21:00 | 127 | Mymensingh | 188 | 18:00 | 193 | Uttara | 58 | 20:00
62 | Gollamari | 74 | 19:00 | 128 | Naogaon | 104 | 22:00 | 194 | UttaraNew | 21 | 18:00
63 | Gopalganj | 102.6 | 21:00 | 129 | Narail | 55 | 21:00 | 195 | Zigatola | 64 | 18:00
64 | Gulshan | 66 | 19:00 | 130 | Narinda | 36 | 19:00
65 | Halishahar | 54 | 00:00 | 131 | Narshingdi | 96 | 23:00
66 | HaripurSBU | 75 | 16:00 | 132 | Natore | 129 | 22:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 19-03-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 7939.23 | 0 |  | 7939.23
1:00 | 7430.53 | 0 |  | 7430.53
2:00 | 7292.53 | 0 |  | 7292.53
3:00 | 7703.17 | 0 |  | 7703.17
4:00 | 8360.32 | 0 |  | 8360.32
5:00 | 7538.81 | 0 |  | 7538.81
6:00 | 6794.5 | 0 |  | 6794.5
7:00 | 6669.15 | 0 |  | 6669.15
8:00 | 7085.29 | 0 |  | 7085.29
9:00 | 7513.51 | 0 |  | 7513.51
10:00 | 7951.21 | 0 |  | 7951.21
11:00 | 8355.04 | 0 |  | 8355.04
12:00 | 9012.51 | 0 |  | 9012.51
13:00 | 9709.71 | 0 |  | 9709.71
14:00 | 10337.86 | 0 |  | 10337.86
15:00 | 10287.47 | 0 |  | 10287.47
16:00 | 10314.61 | 0 |  | 10314.61
17:00 | 10563.12 | 0 |  | 10563.12
18:00 | 11345.96 | 0 |  | 11345.96
19:00 | 11588.52 | 0 |  | 11588.52
19:30 | 11404.51 | 0 |  | 11404.51
20:00 | 11390.27 | 0 |  | 11390.27
21:00 | 11630.91 | 0 |  | 11630.91
22:00 | 11551.51 | 0 |  | 11551.51
23:00 | 11386.52 | 0 |  | 11386.52
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 19-03-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 3950 | 3989.23 | 7939.23 | DAILY GENERATION CURVE
00:30 | 3784 | 3900.88 | 7684.88
01:00 | 3618 | 3812.53 | 7430.53 | 19-03-2026
01:30 | 3613.5 | 3748.03 | 7361.53
02:00 | 3609 | 3683.53 | 7292.53
02:30 | 3758.5 | 3739.35 | 7497.85
03:00 | 3908 | 3795.17 | 7703.17
03:30 | 4071.5 | 3960.245 | 8031.745
04:00 | 4235 | 4125.32 | 8360.32
04:30 | 4057 | 3892.565 | 7949.565
05:00 | 3879 | 3659.81 | 7538.81
05:30 | 3656 | 3510.655 | 7166.655
06:00 | 3433 | 3361.5 | 6794.5
06:30 | 3431.48 | 3300.345 | 6731.825
07:00 | 3429.96 | 3239.19 | 6669.15
07:30 | 3494.235 | 3382.985 | 6877.22
08:00 | 3558.51 | 3526.78 | 7085.29
08:30 | 3623.32 | 3676.08 | 7299.4
09:00 | 3688.13 | 3825.38 | 7513.51
09:30 | 3720.285 | 4012.075 | 7732.36
10:00 | 3752.44 | 4198.77 | 7951.21
10:30 | 3895.28 | 4257.845 | 8153.125
11:00 | 4038.12 | 4316.92 | 8355.04
11:30 | 4243.34 | 4440.435 | 8683.775
12:00 | 4448.56 | 4563.95 | 9012.51
12:30 | 4689.96 | 4671.15 | 9361.11
13:00 | 4931.36 | 4778.35 | 9709.71
13:30 | 5120.425 | 4903.36 | 10023.785
14:00 | 5309.49 | 5028.37 | 10337.86
14:30 | 5326.22 | 4986.445 | 10312.665
15:00 | 5342.95 | 4944.52 | 10287.47
15:30 | 5416.85 | 4884.19 | 10301.04
16:00 | 5490.75 | 4823.86 | 10314.61
16:30 | 5604.1 | 4834.765 | 10438.865
17:00 | 5717.45 | 4845.67 | 10563.12
17:30 | 5868.345 | 5086.195 | 10954.54
18:00 | 6019.24 | 5326.72 | 11345.96
18:30 | 5986.62 | 5480.62 | 11467.24
19:00 | 5954 | 5634.52 | 11588.52
19:30 | 5854 | 5550.51 | 11404.51
20:00 | 5832 | 5558.27 | 11390.27
20:30 | 5907 | 5603.59 | 11510.59 |  | Executive Engineer
21:00 | 5982 | 5648.91 | 11630.91 |  | Network Operation Division
21:30 | 5902.5 | 5688.71 | 11591.21
22:00 | 5823 | 5728.51 | 11551.51
22:30 | 5764.5 | 5704.515 | 11469.015
23:00 | 5706 | 5680.52 | 11386.52

## En-Curve
QF-LDC-12
Date | 19-03-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2329 | 1206 | 896 | 0 | 90 | 833.23 | 80 | 2355 | 0 | 51 | 99 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2205 | 1169.5 | 846 | 0 | 79 | 822.38 | 60 | 2365.5 | 0 | 42.5 | 93 | 0 | 0 | 2 | 0 | 19-03-2026
01:00 | 2081 | 1133 | 796 | 0 | 68 | 811.53 | 40 | 2376 | 0 | 34 | 87 | 0 | 0 | 4 | 0
01:30 | 2145 | 1105.5 | 705 | 0 | 71 | 811.53 | 40 | 2380 | 0 | 34 | 67.5 | 0 | 0 | 2 | 0 | Energy Generated | 224.2166 |  | MKWHr
02:00 | 2209 | 1078 | 614 | 0 | 74 | 811.53 | 40 | 2384 | 0 | 34 | 48 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2352.5 | 1151 | 614 | 0 | 77 | 813.85 | 40 | 2390 | 0 | 17 | 36.5 | 0 | 0 | 6 | 0 | Total Energy Requirement | 224.2166 |  | MKWHr
03:00 | 2496 | 1224 | 614 | 0 | 80 | 816.17 | 40 | 2396 | 0 | 0 | 25 | 0 | 0 | 12 | 0
03:30 | 2535.5 | 1328.5 | 614 | 0 | 84 | 836.745 | 40 | 2540.5 | 0 | 0 | 37.5 | 0 | 0 | 15 | 0
04:00 | 2575 | 1433 | 614 | 0 | 88 | 857.32 | 40 | 2685 | 0 | 0 | 50 | 0 | 0 | 18 | 0
04:30 | 2503 | 1332 | 568 | 0 | 86 | 841.065 | 40 | 2532.5 | 0 | 0 | 34 | 0 | 0 | 13 | 0
05:00 | 2431 | 1231 | 522 | 0 | 84 | 824.81 | 40 | 2380 | 0 | 0 | 18 | 0 | 0 | 8 | 0
05:30 | 2224 | 1146.5 | 471.5 | 0 | 83 | 822.155 | 35 | 2370.5 | 0 | 0 | 9 | 0 | 0 | 5 | 0
06:00 | 2017 | 1062 | 421 | 0 | 82 | 819.5 | 30 | 2361 | 0 | 0 | 0 | 0 | 0 | 2 | 0
06:30 | 1996 | 1042 | 346 | 0 | 83 | 820.55 | 30 | 2373 | 40.275 | 0 | 0 | 0 | 0 | 1 | 0
07:00 | 1975 | 1022 | 271 | 0 | 84 | 821.6 | 30 | 2385 | 80.55 | 0 | 0 | 0 | 0 | 0 | 0
07:30 | 2001 | 1039 | 346 | 0 | 80 | 821.99 | 30 | 2383 | 176.23 | 0 | 0 | 0 | 0 | 0 | 0
08:00 | 2027 | 1056 | 421 | 0 | 76 | 822.38 | 30 | 2381 | 271.91 | 0 | 0 | 0 | 0 | 0 | 0
08:30 | 2057.5 | 1063.5 | 506.5 | 0 | 80 | 823.98 | 30 | 2387 | 350.92 | 0 | 0 | 0 | 0 | 0 | 0
09:00 | 2088 | 1071 | 592 | 0 | 84 | 825.58 | 30 | 2393 | 429.93 | 0 | 0 | 0 | 0 | 0 | 0
09:30 | 2105.5 | 1062.5 | 742.5 | 0 | 87 | 823.165 | 30 | 2387 | 493.695 | 0 | 0 | 0 | 0 | 1 | 0
10:00 | 2123 | 1054 | 893 | 0 | 90 | 820.75 | 30 | 2381 | 557.46 | 0 | 0 | 0 | 0 | 2 | 0
10:30 | 2217 | 1108 | 894.5 | 0 | 93 | 828.06 | 30 | 2388.5 | 584.565 | 0 | 7.5 | 0 | 0 | 2 | 0
11:00 | 2311 | 1162 | 896 | 0 | 96 | 835.37 | 30 | 2396 | 611.67 | 0 | 15 | 0 | 0 | 2 | 0
11:30 | 2485.5 | 1212.5 | 896 | 0 | 104 | 838.69 | 55 | 2411 | 621.585 | 0 | 53.5 | 0 | 0 | 6 | 0
12:00 | 2660 | 1263 | 896 | 0 | 112 | 842.01 | 80 | 2426 | 631.5 | 0 | 92 | 0 | 0 | 10 | 0
12:30 | 2875 | 1355.5 | 896 | 0 | 111 | 836.85 | 80 | 2486.5 | 615.26 | 0 | 95.5 | 0 | 0 | 9.5 | 0
13:00 | 3090 | 1448 | 896 | 0 | 110 | 831.69 | 80 | 2547 | 599.02 | 0 | 99 | 0 | 0 | 9 | 0
13:30 | 3192.5 | 1487 | 896 | 0 | 117 | 872.26 | 80 | 2647.5 | 584.525 | 17.5 | 118.5 | 0 | 0 | 11 | 0
14:00 | 3295 | 1526 | 896 | 0 | 124 | 912.83 | 80 | 2748 | 570.03 | 35 | 138 | 0 | 0 | 13 | 0
14:30 | 3295 | 1564 | 896 | 0 | 124 | 914.29 | 80 | 2761.5 | 489.875 | 35 | 140.5 | 0 | 0 | 12.5 | 0
15:00 | 3295 | 1602 | 896 | 0 | 124 | 915.75 | 80 | 2775 | 409.72 | 35 | 143 | 0 | 0 | 12 | 0
15:30 | 3345.5 | 1607.5 | 896 | 0 | 127 | 917.6 | 80 | 2773 | 345.44 | 43.5 | 156 | 0 | 0 | 9.5 | 0
16:00 | 3396 | 1613 | 896 | 0 | 130 | 919.45 | 80 | 2771 | 281.16 | 52 | 169 | 0 | 0 | 7 | 0
16:30 | 3410.5 | 1635.5 | 896 | 0 | 126 | 920.2 | 80 | 2925.5 | 193.665 | 60.5 | 184.5 | 0 | 0 | 6.5 | 0
17:00 | 3425 | 1658 | 896 | 0 | 122 | 920.95 | 80 | 3080 | 106.17 | 69 | 200 | 0 | 0 | 6 | 0
17:30 | 3507 | 1664 | 896 | 0 | 124 | 1017.615 | 80 | 3304 | 55.925 | 72.5 | 230 | 0 | 0 | 3.5 | 0
18:00 | 3589 | 1670 | 896 | 0 | 126 | 1114.28 | 80 | 3528 | 5.68 | 76 | 260 | 0 | 0 | 1 | 0
18:30 | 3575 | 1621.5 | 896 | 0 | 129 | 1175.4 | 80 | 3665 | 2.84 | 93 | 229 | 0 | 0 | 0.5 | 0
19:00 | 3561 | 1573 | 896 | 0 | 132 | 1236.52 | 80 | 3802 | 0 | 110 | 198 | 0 | 0 | 0 | 0
19:30 | 3644 | 1575 | 896 | 0 | 128 | 1164.51 | 80 | 3770 | 0 | 69 | 78 | 0 | 0 | 0 | 0
20:00 | 3664 | 1596 | 896 | 0 | 124 | 1129.27 | 80 | 3720 | 0 | 69 | 112 | 0 | 0 | 0 | 0
20:30 | 3719 | 1619 | 896 | 0 | 127 | 1129.59 | 80 | 3787.5 | 0 | 69 | 83.5 | 0 | 0 | 0 | 0
21:00 | 3774 | 1642 | 896 | 0 | 130 | 1129.91 | 80 | 3855 | 0 | 69 | 55 | 0 | 0 | 0 | 0
21:30 | 3695 | 1640 | 896 | 0 | 131 | 1130.21 | 80 | 3909.5 | 0 | 69 | 40.5 | 0 | 0 | 0 | 0
22:00 | 3616 | 1638 | 896 | 0 | 132 | 1130.51 | 80 | 3964 | 0 | 69 | 26 | 0 | 0 | 0 | 0
22:30 | 3578.5 | 1606.5 | 896 | 0 | 134 | 1124.015 | 80 | 3956 | 0 | 69 | 25 | 0 | 0 | 0 | 0
23:00 | 3541 | 1575 | 896 | 0 | 136 | 1117.52 | 80 | 3948 | 0 | 69 | 24 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 19-03-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 416 | 08:00 | 399 | 22:00 | Madunaghat | 412 | 02:00 | 398 | 23:00
Amtali | 426 | 04:00 | 411 | 22:00 | Meghnaghat | 420 | 01:00 | 405 | 13:00
Ashuganj | 409 | 6:00 | 402 | 13:00 | Payra | 422 | 00:00 | 414 | 19:00
Bhulta | 407 | 01:00 | 397 | 13:00 | Rahanpur | 420 | 06:00 | 404 | 19:00
Bibiana | 416 | 00:00 | 405 | 22:00 | Rampal | 418 | 06:00 | 400 | 19:00
BIPTC | 408 | 05:00 | 390 | 13:00
Bogura | 410 | 06:00 | 390 | 19:00
Gopalganj | 420 | 06:00 | 402 | 21:00
Kaliakoir | 408 | 01:00 | 377 | 00:00
Korerhat | 421 | 01:00 | 402 | 21:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 243 | 01:00 | 232 | 18:00 | Jhenaidah | 238 | 06:00 | 217 | 21:00
AKSML | 239 | 02:00 | 228 | 21:00 | Kachua | 241 | 06:00 | 224 | 22:00
Aminbazar | 242 | 00:00 | 232 | 21:00 | Kaliakoir | 248 | 06:00 | 230 | 00:00
Ashuganj | 239 | 04:00 | 230 | 13:00 | Keranigonj | 241 | 06:00 | 230 | 18:00
Ashuganj-400 | 239 | 04:00 | 230 | 13:00 | Khulna(S) | 241 | 06:00 | 222 | 19:00
Baghabari | 241 | 05:00 | 228 | 17:00 | Korerhat | 241 | 01:00 | 226 | 22:00
Barapukuria | 229 | 06:00 | 210 | 18:00 | Madunaghat | 240 | 02:00 | 229 | 21:00
Barapukuria-230 | 229 | 06:00 | 210 | 18:00 | Madunaghat-400 | 240 | 03:00 | 230 | 23:00
Barishal | 238 | 01:00 | 225 | 22:00 | Maniknagar | 237 | 01:00 | 229 | 18:00
Bheramara | 239 | 07:00 | 221 | 18:00 | Meghnaghat | 244 | 06:00 | 233 | 18:30
Bhulta | 239 | 06:00 | 230 | 13:00 | Meghnaghat-400 | 239 | 01:00 | 228 | 13:00
Bibiana | 243 | 01:00 | 233 | 21:00 | Mirsorai | 246 | 02:00 | 224 | 01:00
BIPTC | 239 | 05:00 | 221 | 18:00 | Purbasadipur | 230 | 06:00 | 215 | 18:00
Bogura | 244 | 06:00 | 230 | 18:00 | Rajshahi | 236 | 06:00 | 219 | 18:00
Bogura-400 | 243 | 06:00 | 230 | 18:00 | Rampal | 239 | 06:00 | 223 | 21:00
Borhanuddin | 240 | 02:00 | 229 | 22:00 | Rampur | N/A | N/A | N/A | N/A
BSRM | 240 | 01:00 | 226 | 10:00 | Rampura | 237 | 00:00 | 230 | 18:00
Chowmuhani | 236 | 10:00 | 225 | 19:00 | Shikalbaha | 238 | 02:00 | 228 | 19:30
Cumilla(N) | 239 | 05:00 | 227 | 18:00 | Shyampur | 239 | 01:00 | 229 | 18:00
Faridpur | 235 | 00:00 | 223 | 21:00 | Siddhirganj | 239 | 07:00 | 231 | 13:00
Fenchuganj | 244 | 06:00 | 237 | 21:00 | Sirajgonj | 245 | 05:00 | 234 | 18:00
Feni | 242 | 01:00 | 227 | 18:00 | Sreepur | 236 | 06:00 | 225 | 14:00
Ghorashal | 245 | 01:00 | 230 | 15:00 | Tongi | 243 | 04:00 | 233 | 23:00
Ghorashal-230 | 241 | 06:00 | 229 | 22:00
Gopalganj | 235 | 01:00 | 223 | 21:00
GPH | 240 | 02:00 | 228 | 22:00
Haripur | 240 | 03:00 | 230 | 18:00
Hasnabad | 240 | 01:00 | 230 | 15:00
Hathazari | 238 | 02:00 | 227 | 22:00
Ishurdi | 240 | 06:00 | 225 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 01:00 | 130 | 13:00 | Madunaghat | 140 | 02:00 | 132 | 22:00
Agargaon | 140 | 01:00 | 134 | 15:00 | Magura | 137 | 06:00 | 121 | 19:00
Agrabad | 137 | 02:00 | 130 | 22:00 | Mahasthangarh | 139 | 05:00 | 127 | 18:00
AKS | 136 | 01:00 | 129 | 19:30 | Maijdee | 137 | 01:00 | 124 | 18:30
Aminbazar | 142 | 00:00 | 135 | 18:00 | Manikganj | 137 | 05:00 | 127 | 22:00
Amnura | 139 | 05:00 | 127 | 21:00 | Maniknagar | 141 | 01:00 | 129 | 13:00
Ashuganj | 143 | 03:00 | 135 | 11:00 | Matarbari | 121 | 07:00 | 110 | 18:30
Ashuganj-230 | 143 | 03:00 | 135 | 11:00 | Matuail | 141.7 | 01:00 | 136 | 18:00
Bagerhat | 138 | 00:00 | 122 | 19:30 | Metrorail_Motijheel | 141 | 01:00 | 129 | 13:00
Bajitpur | 137 | 00:00 | 126 | 14:00 | Metrorail_Uttara | 140 | 06:00 | 131 | 22:00
Bakerganj | 138 | 02:00 | 130 | 19:00 | Millgate | 140 | 01:00 | 132 | 18:00
Bakulia | 134 | 03:00 | 129 | 22:00 | Mirpur | 142 | 01:00 | 134 | 22:00
Banani | 140 | 04:00 | 131 | 22:00 | Mirzapur | 138 | 01:00 | 127 | 22:00
Bangabhaban | 140 | 00:00 | 128 | 18:00 | Mithapukur | 137 | 06:00 | 124 | 18:00
Barapukuria | 142 | 06:00 | 126 | 18:00 | MI_Cement | 143.4 | 01:00 | 135 | 22:00
Barguna | 140 | 01:00 | 129 | 22:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 140 | 01:00 | 130 | 22:00 | Mogbazar | 136 | 07:00 | 130 | 18:00
Barishal-230 | 139 | 01:00 | 129 | 22:00 | Mongla | 138 | 05:00 | 124 | 18:30
Baroaulia | 138 | 02:00 | 131 | 19:00 | Motijheel | 140 | 00:00 | 128 | 18:00
Baroirhat | 138 | 02:00 | 130 | 19:30 | Muktagacha | 133 | 00:00 | 124 | 17:00
Bashundhara | 140 | 05:00 | 129 | 21:00 | Munshiganj | 141 | 00:00 | 134 | 18:00
BashundharaCement | 142 | 00:00 | 136 | 16:00 | Muradnagar | 140 | 01:00 | 129 | 18:30
Beanibazar | 133 | 05:00 | 127 | 22:00 | Mymensingh | 135 | 00:00 | 121 | 18:00
Benapole | 136 | 06:00 | 114 | 21:00 | Naogaon | 142 | 05:00 | 128 | 18:00
Bhaluka | 138 | 00:00 | 128 | 18:00 | Narail | 138 | 06:00 | 120 | 21:00
Bhandaria | 141 | 01:00 | 124 | 22:00 | Narinda | 141 | 01:00 | 129 | 13:00
Bhangura | 139 | 06:00 | 129 | 18:00 | Narshingdi | 137 | 01:00 | 132 | 18:00
Bheramara | 138 | 06:00 | 130 | 18:00 | Natore | 138 | 06:00 | 127 | 18:00
Bheramara(GK) | 138 | 05:00 | 130 | 18:00 | Nawabganj | 138 | 01:00 | 129 | 18:00
Bhulta | 134 | 05:00 | 129 | 21:00 | Netrakona | 133 | 00:00 | 119 | 18:00
Bog-Sherpur | 140 | 06:00 | 130 | 18:00 | New | 141 | 07:00 | 133 | 15:00
Bogura | 141 | 06:00 | 130 | 18:00 | Niamatpur | 140 | 01:00 | 134 | 18:00
Bogura-230 | 141 | 06:00 | 131 | 18:00 | Noapara | 139 | 06:00 | 125 | 19:30
Brahmanbaria | 139 | 01:00 | 131 | 22:00 | Pabna | 138 | 05:00 | 129 | 18:00
Cantonment | 140 | 01:00 | 133 | 21:00 | Palashbari | 136 | 06:00 | 124 | 18:00
Chandina | 141 | 01:00 | 130 | 22:00 | Panchagarh | 140 | 06:00 | 129 | 12:00
Chandpur | 139 | 01:00 | 123 | 18:30 | Patiya | 134 | 03:00 | 128 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 139 | 03:00 | 132 | 21:00 | Patuakhali | 138 | 01:00 | 130 | 18:30
Chapai | 138 | 01:00 | 133 | 19:30 | Payra | 140 | 01:00 | 135 | 17:00
Charsaidpur | 142 | 00:00 | 136 | 13:00 | PHP | 137 | 01:00 | 129 | 18:00
Chauddagram | 138 | 01:00 | 128 | 00:00 | Postogola | 144 | 01:00 | 136 | 22:00
Chhatak | 132 | 05:00 | 126 | 13:00 | Pubail | 145 | 04:00 | 137 | 21:00
Chowmuhani | 137 | 01:00 | 125 | 17:00 | Purbachal | 140 | 01:00 | 132 | 18:00
Chuadanga | 135 | 05:00 | 119 | 19:00 | Purbasadipur | 137 | 06:00 | 126 | 16:00
Coxsbazar | 120 | 16:00 | 110 | 22:00 | Rahanpur | 140 | 02:00 | 135 | 18:00
Cumilla(N) | 140 | 04:00 | 131 | 18:00 | Rahanpur-400 | 141 | 05:00 | 135 | 19:00
Cumilla(S) | 138 | 05:00 | 124 | 16:00 | Rahim | 140 | 00:00 | 136 | 14:00
Daganbhuiyan | 137 | 01:00 | 126 | 18:30 | Rajbari | 137 | 00:00 | 127 | 21:00
Daudkandi | 139 | 06:00 | 127 | 21:00 | Rajendrapur | 142 | 01:00 | 131 | 13:00
DhakaUniversity | 135 | 01:00 | 130 | 13:00 | Rajshahi | 135 | 05:00 | 125 | 21:00
Dhamrai | 139 | 00:00 | 133 | 18:00 | Rajshahi-230 | 136 | 05:00 | 126 | 18:00
Dhanmondi | 142 | 00:00 | 137 | 13:00 | Ramganj | 137 | 01:00 | 122 | 18:00
Dohazari | 129 | 05:00 | 123 | 22:00 | Rampur | 136 | 02:00 | 130 | 22:00
Faridpur | 136 | 00:00 | 129 | 21:00 | Rampura | 134 | 00:00 | 130 | 13:00
Fatullah | 143 | 00:00 | 133 | 18:00 | Rangamati | 138 | 04:00 | 131 | 18:30
Fenchuganj | 138 | 05:00 | 134 | 13:00 | Rangpur | 137 | 05:00 | 126 | 18:00
Feni | 136 | 01:00 | 127 | 18:00 | Ruppur | 139 | 03:00 | 130 | 21:00
Feni-230 | 136 | 01:00 | 127 | 18:00 | Saidpur | 138 | 06:00 | 126 | 18:00
Ghatail | 135 | 00:00 | 122 | 17:00 | Satkhira | 138 | 06:00 | 121 | 20:00
Ghorashal | 145 | 01:00 | 138 | 16:00 | Satmasjid | 140 | 00:00 | 133 | 22:00
Goalpara | 142 | 06:00 | 128 | 18:30 | Savar | 141 | 01:00 | 133 | 18:00
Gollamari | 142 | 06:00 | 129 | 19:00 | SevenRings | 146 | 01:00 | 138 | 17:00
Gopalganj | 140 | 00:00 | 129 | 18:00 | ShahCement | 142 | 00:00 | 136 | 12:00
Gopalganj-400 | 140 | 00:00 | 132 | 21:00 | Shahjadpur | 142 | 04:00 | 133 | 18:00
Gulshan | 134 | 03:00 | 129 | 13:00 | Shahjibazar | 138 | 02:00 | 131 | 13:00
Halishahar | 137 | 02:00 | 130 | 22:00 | Shahmirpur | 136 | 01:00 | 130 | 23:00
Haripur | 141 | 07:00 | 136 | 21:00 | Shariatpur | 140 | 00:00 | 129 | 21:00
HaripurSBU | 141 | 01:00 | 136 | 14:00 | Sherpur | 130 | 18:00 | 113 | 13:00
Hasnabad | 144 | 00:00 | 137 | 23:00 | Shikalbaha | 126 | 02:00 | 119 | 13:00
Hathazari | 140 | 02:00 | 133 | 19:30 | Shikalbaha-230 | 137 | 03:00 | 132 | 13:00
Hatirjheel | 135 | 01:00 | 130 | 13:00 | Shitalakhya | 143.4 | 01:00 | 135 | 23:00
Ishurdi | 140 | 05:00 | 132 | 18:00 | Sholosohor | 138 | 02:00 | 131 | 21:00
Jaldhaka | 135 | 05:00 | 121 | 18:00 | Shyampur | 138 | 00:00 | 129 | 21:00
Jamalpur | 135 | 18:30 | 117 | 13:00 | Shyampur-230 | 138 | 01:00 | 133 | 18:00
Jashore | 138 | 06:00 | 117 | 13:00 | Siddhirganj | 142 | 00:00 | 136 | 22:00
Jhenaidah | 137 | 05:00 | 123 | 18:00 | Sirajganj | 138 | 06:00 | 128 | 22:00
Jhenaidah-230 | 138 | 06:00 | 123 | 21:00 | Sonargaon | 142 | 00:00 | 135 | 21:00
Joydebpur | 142 | 05:00 | 133 | 18:00 | Sreemongol | 137 | 01:00 | 131 | 13:00
Joypurhat | 137 | 06:00 | 125 | 18:00 | Sreepur | 142 | 06:00 | 133 | 13:00
Juldah | 135 | 05:00 | 130 | 21:00 | Srinagar | 138 | 01:00 | 129 | 22:00
Kabirpur | 140 | 02:00 | 130 | 22:00 | SSM | 138 | 00:00 | 135 | 12:00
Kachua | 138 | 06:00 | 126 | 23:00 | Sunamganj | 130 | 05:00 | 124 | 12:00
Kaliakoir | 141 | 01:00 | 134 | 16:00 | Sylhet | 134 | 07:00 | 129 | 13:00
Kaliganj | 137 | 06:00 | 121 | 21:00 | Sylhet-132 | 132 | 01:00 | 129 | 12:00
Kallyanpur | 141 | 00:00 | 136 | 14:00 | Tangail | 135 | 00:00 | 123 | 13:00
Kalurghat | 139 | 02:00 | 133 | 18:30 | Taraganj | 137 | 06:00 | 126 | 21:00
Kamrangirchar | 141 | 01:00 | 130 | 18:00 | Tasnim | 142 | 00:00 | 135 | 21:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 139 | 06:00 | 126 | 18:00
Kasba | 139 | 00:00 | 128 | 18:00 | TK | 137 | 04:00 | 131 | 21:00
Kazla | 141 | 01:00 | 129 | 14:00 | Tongi | 141 | 04:00 | 134 | 19:30
Keranigonj | 138 | 01:00 | 130 | 18:00 | Ullahpara | 139 | 05:00 | 129 | 18:00
Khagrachori | 139 | 03:00 | 130 | 18:00 | Ullon | 136 | 05:00 | 130 | 13:00
Khulna | 141 | 06:00 | 128 | 18:30 | Uttara | 142 | 01:00 | 134 | 21:00
Khulna(S) | 142 | 06:00 | 129 | 19:30 | UttaraNew | 140 | 06:00 | 131 | 22:00
Khulshi | 136 | 02:00 | 129 | 22:00 | Zigatola | 138 | 01:00 | 130 | 18:00
Kishoreganj | 137 | 00:00 | 124 | 13:00
Kodda | 142 | 01:00 | 130 | 21:00
Korerhat | 139 | 01:00 | 131 | 21:00
KSRM | 136 | 04:00 | 131 | 19:00
Kulaura | 137 | 02:00 | 132 | 13:00
Kurigram | 134 | 06:00 | 116 | 18:00
Kushtia | 138 | 06:00 | 127 | 21:00
Laksam | 139 | 01:00 | 126 | 18:00
Lakshmipur | 137 | 01:00 | 124 | 18:00
Lalbag | 139 | 06:00 | 130 | 22:00
Lalmonirhat | 130 | 13:00 | 117 | 18:00
Madanganj | 142 | 00:00 | 136 | 16:00
Madaripur | 140 | 00:00 | 129 | 23:00
Madartek | 133 | 00:00 | 129 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division