## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 21-03-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-03-2026 | during | 21-03-2026 | during | 21-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 20 | 110 | 365 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 45 | 97.7 | 97.7 | 7 | 7 | On test
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 289 | 342 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 225 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 39 | 210 | 210 | 0 | 1 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 240 | 260 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 8 | 5 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 12 | 5 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 19 | 0 | 18 | 0 | 18 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 310 | 455 | 584 | 584 | 320 | 584 | FGMO
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 320 | 320 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 250 | 210 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 0 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1148 | 1696 | 6038.22 | 6020.22 | 2712.05 | 3063.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 10 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 80 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 181 | 225 | 220 | 225 | 220 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 56 | 64 | 56 | 64 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 68 | 68 | 68 | 68 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 13 | 40 | 40 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0 | 0 | 3.81 | 0 | 3.81 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 25 | 25 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 147 | 147 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 605 | 310 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 33 | 7 | 0 | 7 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 320 | 140 | 320 | 320 | 320 | 320 | Coal shortage
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1146 | 801 | 3269.67 | 3252.86 | 2662.31 | 2665.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 130 | 211 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 230 | 325 | 342.01 | 342.01 | 342.01 | 342.01 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 220 | 369 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 20 | 20 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 0 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 16 | 16 | 32 | 32 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 103 | 163 | 163 | 100 | 100 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 180 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 96 | 46 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 5 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 104 | 104 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 28 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2876.261 | 774 | 1110 | 2385.36 | 2324.36 | 2187.22 | 2132.22
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-03-2026 | during | 21-03-2026 | during | 21-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 107 | 163 | 157.5 | 157.5 | 10 | 10 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0 | 0 | 0.7 | 0 | 0.7 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 0 | 0 | 60 | 80 | 60 | 80 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 0 | 0 | 70 | 115 | 70 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 1.02 | 0 | 45.12 | 0 | 45.12 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 35 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 108.02 | 163 | 409.82 | 429 | 214.82 | 252
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 28 | 41 | 41 | 41 | 41 | 41 | plant availability zero
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 140 | 162 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 22 | 100 | 100 | 100 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 0 | 0 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 31 | 82 | 82 | 42 | 42 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 96 | 96 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 20 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 240 | 330 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 320 | 373 | 0 | 0 | 0 | 0 | Due to Gas Field Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 883 | 1183 | 902 | 902 | 709 | 709
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 691 | 893 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 200 | 330 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 43 | 0 | 70 | 0 | 70 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 785 | 366 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1719 | 1589 | 3582.2 | 3512.2 | 2821.1 | 2751.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 90 | 125 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 500 | 480 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 180 | 180 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 75 | 75 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 140 | 140 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.32 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 910.32 | 925 | 2162 | 2161 | 1993 | 1992
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 30.65 | 0 | 58 | 0 | 58 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 190 | 190 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 200 | 389 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 21 | 21 | 21 | 21 | machine problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 70 | 70 | 50 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.96 | 0 | 5.8 | 0 | 5.8 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 832.42 | 848 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 20.8 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 57 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1142.83 | 1237 | 3208.67 | 2983.87 | 2692.67 | 2467.87
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 56 | 54 | 55 | 55 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.7 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 21 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 23 | 0 | 122 | 0 | 122 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 103.7 | 54 | 460.2 | 303 | 385.2 | 228
System Total |  |  |  |  | 28823.2 | 29275.503 | 7934.87 | 8758 | 22418.14 | 21888.51 | 16377.37 | 16260.74
Forecast Scenario (21-03-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8660 |  | 0 |  | 8660
|  |  |  | 1:00 | 8400 |  | 0 |  | 8400
|  |  |  | 2:00 | 8060 |  | 0 |  | 8060
|  |  |  | 3:00 | 7660 |  | 0 |  | 7660
|  |  |  | 4:00 | 7280 |  | 0 |  | 7280
|  |  |  | 5:00 | 7160 |  | 0 |  | 7160
|  |  |  | 6:00 | 7030 |  | 0 |  | 7030
|  |  |  | 7:00 | 7360 |  | 0 |  | 7360
|  |  |  | 8:00 | 7000 |  | 0 |  | 7000
|  |  |  | 9:00 | 6600 |  | 0 |  | 6600
|  |  |  | 10:00 | 6600 |  | 0 |  | 6600
|  |  |  | 11:00 | 6800 |  | 0 |  | 6800
|  |  |  | 12:00 | 7200 |  | 0 |  | 7200
|  |  |  | 13:00 | 7500 |  | 0 |  | 7500
|  |  |  | 14:00 | 7700 |  | 0 |  | 7700
|  |  |  | 15:00 | 7600 |  | 0 |  | 7600
|  |  |  | 16:00 | 7400 |  | 0 |  | 7400
|  |  |  | 17:00 | 7100 |  | 0 |  | 7100
|  |  |  | 18:00 | 6900 |  | 0 |  | 6900
|  |  |  | 18:30 | 8000 |  | 0 |  | 8000
|  |  |  | 19:00 | 8796 |  | 0 |  | 8796
|  |  |  | 19:30 | 9050 |  | 0 |  | 9050
|  |  |  | 20:00 | 8900 |  | 0 |  | 8900
|  |  |  | 21:00 | 9200 |  | 0 |  | 9200
|  |  |  | 22:00 | 9300 |  | 0 |  | 9300
|  |  |  | 23:00 | 9400 |  | 0 |  | 9400
Probable Maximum Temperature: |  |  | 30.50°C
Probable Maximum Demand at Day Peak: |  |  | 7200.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 9200.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 9200.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 185.606 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:26 hrs on 21-03-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 20-03-2026 | [28 empty] | Date: | 20-03-2026 | [28 empty] | Date: | 20-03-2026 | [28 empty] | Date: | 20-03-2026 | [28 empty] | Date: | 20-03-2026 | [17 empty] | Date: | 20-03-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [17 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 342.010 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 306 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 8 | 12 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 320 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 987 | 0 | 0 | 0 | 345 | 0 | 342 | 51 | 0 | 198 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 134 | 0 | 0 | 0 | 310 | 0 | 390 | 41 | 0 | 152 | 0 | 17 | 0 | 5 | 30 | 75 | 0 | 96 | 0 | 16 | 8 | 160 | 0 | 0 | 0 | 5481 | 896 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 993 | 0 | 0 | 0 | 1027.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 125 | 220 | 0 | 0 | 1050 | 0 | 5426.75 | 10907.75 | 87.34
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 298 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 8 | 12 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 320 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 935 | 0 | 0 | 0 | 325 | 0 | 325 | 51 | 0 | 191 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 126 | 0 | 0 | 0 | 310 | 0 | 366 | 41 | 0 | 150 | 0 | 17 | 0 | 5 | 30 | 74 | 0 | 96 | 0 | 16 | 8 | 160 | 0 | 0 | 0 | 5365 | 896 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 861 | 0 | 0 | 0 | 987.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244 | 125 | 220 | 0 | 0 | 1000 | 0 | 5179.84 | 10544.84 | 87.33
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 289 | 0 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 8 | 12 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 320 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 870 | 0 | 0 | 0 | 300 | 0 | 320 | 51 | 0 | 188 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 122 | 0 | 0 | 0 | 305 | 0 | 360 | 41 | 0 | 142 | 0 | 17 | 0 | 5 | 30 | 75 | 0 | 96 | 0 | 16 | 8 | 161 | 0 | 0 | 0 | 5324 | 896 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 855 | 0 | 0 | 0 | 914.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 125 | 220 | 0 | 0 | 900 | 0 | 4929.7 | 10253.7 | 87.33
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 290 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 8 | 12 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 320 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 850 | 0 | 0 | 0 | 300 | 0 | 355 | 51 | 0 | 194 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 118 | 0 | 0 | 0 | 305 | 0 | 376 | 41 | 0 | 133 | 0 | 17 | 0 | 5 | 30 | 76 | 0 | 96 | 0 | 16 | 8 | 161 | 0 | 0 | 0 | 5389 | 896 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 894 | 0 | 0 | 0 | 920.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 125 | 220 | 0 | 0 | 896 | 0 | 4957.86 | 10346.86 | 87.32
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 325 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 8 | 12 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 320 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 894 | 0 | 0 | 0 | 325 | 0 | 325 | 51 | 0 | 189 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 124 | 0 | 0 | 0 | 300 | 0 | 357 | 41 | 0 | 152 | 0 | 17 | 0 | 5 | 30 | 74 | 0 | 96 | 0 | 25 | 5 | 161 | 0 | 0 | 0 | 5618 | 896 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 882 | 0 | 0 | 0 | 917.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 125 | 220 | 0 | 0 | 900 | 0 | 4991.04 | 10609.04 | 87.32
05:00 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 50 | 288 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 8 | 12 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 674 | 0 | 0 | 0 | 310 | 0 | 300 | 51 | 0 | 199 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 114 | 0 | 0 | 0 | 315 | 0 | 352 | 41 | 0 | 143 | 0 | 0 | 0 | 0 | 30 | 75 | 0 | 97 | 0 | 35 | 35 | 162 | 0 | 0 | 0 | 4997 | 896 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 774 | 0 | 0 | 0 | 832.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 625 | 0 | 4327.04 | 9324.04 | 87.31
06:00 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 285 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 8 | 12 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 80 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 606 | 0 | 0 | 0 | 220 | 0 | 265 | 0 | 0 | 140 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 305 | 0 | 352 | 28 | 0 | 135 | 0 | 0 | 0 | 0 | 30 | 75 | 0 | 96 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 4496.01 | 893 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 736 | 0 | 0 | 0 | 834.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3838.13 | 8334.14 | 87.31
07:00 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 285 | 0 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 240 | 0 | 0 | 3 | 0 | 8 | 12 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 30 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 606 | 3 | 0 | 0 | 220 | 0 | 230 | 0 | 0 | 130 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 104 | 0 | 6 | 0 | 240 | 0 | 352 | 29 | 0 | 137 | 1 | 0 | 0 | 0 | 30 | 23 | 0 | 96 | 0 | 0 | 0 | 130 | 0.2 | 1.39 | 0 | 4261.89 | 591 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.17 | 770 | 0 | 0 | 0 | 835.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.03 | 9 | 0 | 0 | 4.65 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0.41 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0.09 | 0 | 140 | 100 | 180 | 0 | 0 | 495 | 0 | 3592.83 | 7854.72 | 87.3
08:00 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 285 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 240 | 0 | 0 | 11 | 0 | 10 | 12 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.14 | 30 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 605 | 9 | 0 | 0 | 220 | 0 | 230 | 0 | 0 | 130 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 96 | 0 | 19 | 0 | 240 | 0 | 342 | 28 | 0 | 137 | 4 | 0 | 0 | 0 | 30 | 24 | 0 | 96 | 0 | 0 | 0 | 130 | 0 | 15.54 | 0 | 4265.68 | 591 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.64 | 777 | 0 | 0 | 0 | 831.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.39 | 28 | 0 | 0 | 12.72 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 1.25 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 9 | 0.17 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3670.11 | 7935.79 | 87.3
09:00 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 289 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 19 | 0 | 8 | 12 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 605 | 10 | 0 | 0 | 220 | 0 | 230 | 0 | 0 | 130 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 96 | 0 | 28 | 0 | 240 | 0 | 320 | 28 | 0 | 140 | 7 | 0 | 0 | 0 | 30 | 22 | 0 | 96 | 0 | 0 | 0 | 107 | 0 | 1.02 | 0 | 4059.02 | 691 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 785 | 0 | 0 | 0 | 832.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.65 | 57 | 0 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 1.96 | 0 | 56 | 0 | 21 | 0 | 0 | 0 | 0 | 3.7 | 23 | 0.32 | 0 | 140 | 90 | 180 | 0 | 0 | 500 | 0 | 3875.85 | 7934.87 | 87.29
10:00 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 309 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 18 | 0 | 5 | 7 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 605 | 16 | 0 | 0 | 220 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 102 | 0 | 27 | 0 | 240 | 0 | 318 | 28 | 0 | 138 | 9 | 0 | 0 | 0 | 7 | 22 | 0 | 96 | 0 | 0 | 0 | 107 | 0 | 3.93 | 0 | 3935.93 | 640 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 766 | 0 | 0 | 0 | 832.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.32 | 85 | 0 | 0 | 1.64 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 53 | 0 | 26 | 0 | 0 | 0 | 0 | 5.4 | 152 | 0.39 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3950.21 | 7886.14 | 87.29
11:00 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 294 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.65 | 30 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 605 | 10 | 0 | 0 | 210 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 110 | 0 | 67 | 0 | 210 | 0 | 312 | 28 | 0 | 134 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 96 | 0 | 0 | 0 | 107 | 0 | 0.57 | 0 | 3772.22 | 483 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 753 | 0 | 0 | 0 | 830.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.89 | 97 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 52 | 0 | 30 | 0 | 0 | 0 | 0 | 6.5 | 101 | 0.48 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3727.99 | 7500.21 | 87.28
12:00 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 289 | 0 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 30 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 588 | 7 | 0 | 0 | 210 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 50 | 0 | 0 | 10 | 0 | 114 | 0 | 20 | 0 | 175 | 0 | 310 | 28 | 0 | 139 | 0 | 0 | 0 | 0 | 17 | 23 | 0 | 96 | 0 | 0 | 0 | 110 | 2.2 | 8.01 | 0 | 3666.84 | 703 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 766 | 0 | 0 | 0 | 820.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58 | 20 | 0 | 0 | 5.46 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0.55 | 0 | 53 | 0 | 30 | 0 | 0 | 0 | 0 | 7 | 75 | 0.6 | 0 | 140 | 100 | 180 | 0 | 0 | 490 | 0 | 3810.28 | 7477.12 | 87.28
13:00 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 320 | 0 | 282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1.52 | 40 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 335 | 16 | 0 | 0 | 250 | 0 | 342 | 0 | 0 | 208 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 62 | 0 | 45 | 0 | 175 | 0 | 334 | 28 | 0 | 146 | 1 | 0 | 0 | 0 | 17 | 22 | 0 | 96 | 0 | 0 | 0 | 123 | 2 | 5.26 | 0 | 3898.78 | 893 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 793 | 0 | 0 | 0 | 838.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.82 | 75 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.8 | 0 | 53 | 0 | 20 | 0 | 0 | 0 | 0 | 6.5 | 183 | 0.7 | 0 | 140 | 100 | 220 | 0 | 0 | 485 | 0 | 4535.64 | 8434.42 | 87.27
14:00 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 316 | 0 | 268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 3.3 | 40 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 310 | 16 | 0 | 0 | 250 | 0 | 300 | 0 | 0 | 194 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 70 | 0 | 41 | 0 | 175 | 0 | 300 | 28 | 0 | 153 | 0 | 0 | 0 | 0 | 17 | 25 | 0 | 96 | 0 | 0 | 0 | 164 | 0.8 | 6.85 | 0 | 3796.95 | 518 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 756 | 0 | 0 | 0 | 814.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 3.99 | 0 | 53 | 0 | 29 | 0 | 0 | 0 | 0 | 6.5 | 162 | 0.25 | 0 | 140 | 100 | 220 | 0 | 0 | 485 | 0 | 3971.94 | 7768.89 | 87.27
15:00 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 0 | 297 | 0 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 4 | 0 | 5 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 2.17 | 40 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 310 | 13 | 0 | 0 | 220 | 0 | 210 | 0 | 0 | 130 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 68 | 0 | 10 | 0 | 240 | 0 | 287 | 32 | 0 | 135 | 1 | 0 | 0 | 0 | 17 | 23 | 0 | 96 | 0 | 0 | 0 | 109 | 0.8 | 4.02 | 0 | 3507.99 | 418 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 750 | 0 | 0 | 0 | 815.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 32 | 0 | 0 | 40.09 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 2.5 | 0 | 54 | 0 | 20 | 0 | 0 | 0 | 0 | 4.9 | 97 | 0.02 | 0 | 140 | 100 | 180 | 0 | 0 | 480 | 0 | 3632.63 | 7140.62 | 87.26
16:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 284 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 310 | 8 | 0 | 0 | 220 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 80 | 0 | 3 | 0 | 210 | 0 | 345 | 32 | 0 | 120 | 1 | 0 | 0 | 0 | 17 | 23 | 0 | 96 | 0 | 0 | 0 | 109 | 0.8 | 4.82 | 0 | 3591.62 | 475 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 750 | 0 | 0 | 0 | 830.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.31 | 42 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 2.26 | 0 | 54 | 0 | 13 | 0 | 0 | 0 | 0 | 1.8 | 81 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 480 | 0 | 3568.04 | 7159.66 | 87.26
17:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 6 | 315 | 0 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 310 | 3 | 0 | 0 | 280 | 0 | 290 | 0 | 0 | 206 | 0 | 0 | 50 | 0 | 0 | 5 | 0 | 42 | 0 | 1 | 0 | 175 | 0 | 366 | 32 | 0 | 130 | 1 | 4 | 0 | 0 | 17 | 23 | 0 | 96 | 0 | 0 | 0 | 161 | 0 | 6.97 | 0 | 4077.97 | 705 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 350 | 0 | 0 | 0 | 827.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.8 | 10 | 0 | 0 | 3.55 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.33 | 0 | 54 | 0 | 5 | 0 | 0 | 0 | 0 | 0.6 | 34 | 0.01 | 0 | 140 | 100 | 180 | 0 | 0 | 480 | 0 | 3537.58 | 7615.55 | 87.25
18:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 6 | 371 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 6 | 140 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 347 | 0 | 342 | 6 | 0 | 219 | 0 | 0 | 50 | 0 | 0 | 12 | 0 | 36 | 0 | 0 | 0 | 315 | 0 | 400 | 32 | 0 | 156 | 0 | 8 | 0 | 5 | 17 | 70 | 0 | 96 | 0 | 32 | 8 | 160 | 0 | 0 | 0 | 4659 | 892 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 836.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.01 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 140 | 125 | 220 | 0 | 0 | 480 | 0 | 3813.57 | 8472.57 | 87.25
19:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 22 | 301 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 13 | 140 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 330 | 0 | 290 | 16 | 0 | 192 | 0 | 0 | 104 | 0 | 0 | 11 | 0 | 32 | 0 | 0 | 0 | 310 | 0 | 358 | 41 | 0 | 149 | 0 | 17 | 0 | 83 | 30 | 100 | 0 | 96 | 0 | 8 | 0 | 161 | 0 | 0 | 0 | 4641 | 893 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 125 | 180 | 0 | 0 | 530 | 0 | 3782 | 8423 | 87.24
19:30 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 22 | 317 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 260 | 11 | 0 | 0 | 0 | 5 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 13 | 140 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 347 | 0 | 305 | 51 | 0 | 198 | 0 | 0 | 104 | 0 | 0 | 6 | 0 | 42 | 0 | 0 | 0 | 315 | 0 | 352 | 41 | 0 | 152 | 0 | 17 | 0 | 30 | 30 | 100 | 0 | 96 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 4651 | 893 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 125 | 180 | 0 | 0 | 480 | 0 | 3727 | 8378
20:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 39 | 313 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 260 | 40 | 0 | 0 | 0 | 5 | 0 | 0 | 440 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 13 | 140 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 360 | 0 | 320 | 51 | 0 | 208 | 0 | 0 | 103 | 0 | 0 | 6 | 0 | 46 | 0 | 0 | 0 | 310 | 0 | 369 | 41 | 0 | 155 | 0 | 17 | 0 | 30 | 30 | 100 | 0 | 96 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 4741 | 893 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 125 | 180 | 0 | 0 | 480 | 0 | 3777 | 8518 | 87.24
21:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 45 | 342 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 260 | 39 | 0 | 0 | 0 | 5 | 5 | 0 | 455 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 13 | 140 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 369 | 0 | 325 | 51 | 0 | 211 | 0 | 0 | 103 | 0 | 0 | 5 | 0 | 46 | 0 | 0 | 0 | 330 | 0 | 373 | 41 | 0 | 162 | 0 | 20 | 0 | 31 | 30 | 100 | 0 | 96 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 4953 | 893 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 125 | 180 | 0 | 0 | 480 | 0 | 3805 | 8758 | 87.23
22:00 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 54 | 331 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 40 | 0 | 0 | 0 | 5 | 5 | 0 | 480 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 13 | 140 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 345 | 0 | 300 | 51 | 0 | 201 | 0 | 0 | 104 | 0 | 0 | 5 | 0 | 50 | 0 | 0 | 0 | 325 | 0 | 341 | 41 | 0 | 160 | 0 | 20 | 0 | 31 | 30 | 99 | 0 | 96 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 5032 | 893 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 125 | 180 | 0 | 0 | 480 | 0 | 3753 | 8785 | 87.23
23:00 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 54 | 307 | 0 | 289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 260 | 40 | 0 | 0 | 0 | 5 | 5 | 0 | 470 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 325 | 0 | 290 | 0 | 0 | 190 | 0 | 0 | 105 | 0 | 0 | 5 | 0 | 48 | 0 | 0 | 0 | 310 | 0 | 320 | 41 | 0 | 152 | 0 | 6 | 0 | 0 | 30 | 100 | 0 | 96 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 4767 | 893 | 283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 125 | 180 | 0 | 0 | 480 | 0 | 3685 | 8452 | 87.22
Total KWH | 0 | 0 | 0 | 1645982 | 0 | 0 | 0 | 461045.46 | 7426800 | 0 | 5383000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1823000 | 0 | 2120901 | 0 | 0 | 5827784 | 211000 | 0 | 68725 | 75600 | 202800 | 160920 | 0 | 8404090.91 | 0 | 0 | 0 | 0 | 264960 | 167377 | 0 | 0 | 0 | 0 | 15004 | 1416360 | 0 | 169440 | 5461818.18 | 0 | 0 | 0 | 0 | 0 | 4712760 | 0 | 0 | 0 | 12692726 | 119475 | 0 | 0 | 6792000 | 0 | 6830000 | 517646 | 0 | 4345000 | 0 | 0 | 1709979 | 0 | 0 | 296070 | 0 | 1971840 | 0 | 254882 | 0 | 6425000 | 0 | 8342000 | 826000 | 0 | 3458781.82 | 24591 | 186024 | 0 | 209280 | 587904 | 1294700 | 0 | 2314400 | 0 | 181200 | 86400 | 3386880 | 8250 | 68220 | 0 | 108948616.37 | 18470545 | 6728544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460080 | 16058182 | 0 | 0 | 0 | 19946546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148792 | 445410 | 0 | 0 | 199488 | 0 | 0 | 0 | 0 | 0 | 0 | 7691200 | 0 | 14580 | 0 | 1274618 | 0 | 186341 | 0 | 0 | 0 | 0 | 41371.2 | 826560 | 2791 | 0 | 3731000 | 2663000 | 4832040 | 0 | 0 | 14660363.64 | 0 | 98381451.84 | 207330068.21

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 20-03-2026
Power Supply Scenario
| Day Peak Generation |  |  | 7934.87 | MW | 09:00 Hr. | Energy Generated |  |  | 207.3301 |  | MKWHr.
| Day Peak Demand |  |  | 7934.87 | MW | 09:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 8758 | MW | 21:00 Hr. | Energy Demand |  |  | 207.3301 |  | MKWHr.
| Evening Peak Demand |  |  | 8758 | MW | 21:00 Hr. | Maximum Temperature |  |  | 31 |  | °C
| Minimum Generation of the Day |  |  | 7140.62 | MW | 15:00 Hr. | Total Gas Supplied |  |  | 779.81 |  | MMCFD
| Maximum Generation of the Day |  |  | 10907.75 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 4.9448 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.6673 | 0 | 0.0756 | 0 | 0 | 0.068725 | 0 | 0 | 33.8116 | Gas | 107.986 | Gas | 375997941.2401
| Chattogram Zone |  |  | 4.8822 | 18.1545 | 0.16738 | 0 | 1.4164 | 0.13448 | 0 | 0.26496 | 25.0199 | Coal | 53.8787 | Coal | 366713952.3166
| Cumilla Zone |  |  | 20.4907 | 0 | 0 | 0 | 0 | 0.25488 | 1.9718 | 0 | 22.7174 | HFO | 0.51058 | HFO | 9013881.3
| Mymensingh Zone |  |  | 3.3869 | 0 | 0.2676 | 0 | 0 | 0.07647 | 0 | 0 | 3.7309 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.6441 | 0 | 0 | 0 | 0 | 0.024591 | 0 | 0 | 23.6687 | Hydro | 1.4164 | Hydro | 141636
| Khulna Zone |  |  | 6.7285 | 16.0582 | 0 | 0 | 0 | 0.46008 | 18.4705 | 0 | 41.7174 | Solar | 2.8846 | Solar | 46661962.8
| Barishal Zone |  |  | 7.495 | 18.3914 | 0 | 0 | 0 | 0.002791 | 0 | 0 | 25.8892 | Import | 40.3889 | Import | 222773792.59
| Rajshahi Zone |  |  | 7.6912 | 0 | 0 | 0 | 0 | 0.80827 | 19.9465 | 0 | 28.446 | Wind | 0.26496 | Wind | 3897561.6
| Rangpur Zone |  |  | 0 | 1.2746 | 0 | 0 | 0 | 1.0543 | 0 | 0 | 2.3289
| Total |  |  | 107.986 | 53.8787 | 0.51058 | 0 | 1.4164 | 2.8846 | 40.3889 | 0.26496 | 207.3301
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 375997941.2401 |  | Hydro | 141636
|  |  |  | Coal | 366713952.3166 |  | Solar | 46661962.8
|  |  |  | HFO | 9013881.3 |  | Import | 222773792.59
|  |  |  | HSD | 0 |  | Wind | 3897561.6
[5 empty] | Total: | 102,52,00,727 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 18.4705 | Peak Hr Flow | 893.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 20855818.18 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 19.9465 | Peak Hr Flow | 848.00 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 649 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.9718 | Peak Hr Flow | 46.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1604 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 40.3889 | Peak Hr Flow | 1787.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 2507
|  |  |  | Chattogram |  | 0 |  | 916
|  |  |  | Cumilla |  | 0 |  | 872
|  |  |  | Mymensingh |  | 0 |  | 744
|  |  |  | Sylhet |  | 0 |  | 389
|  |  |  | Khulna |  | 0 |  | 1043
|  |  |  | Barishal |  | 0 |  | 300
|  |  |  | Rajshahi |  | 0 |  | 1038
|  |  |  | Rangpur |  | 0 |  | 637
|  |  |  | Total |  | 0 |  | 8446
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:05 |  | Meghnaghat CCPP(Summit)-2 Shutdown with remarks:- ST
| 08:13 |  | Meghnaghat CCPP(Summit)-2 GT Shutdown with remarks:- None
| 08:15 |  | Meghnaghat CCPP(Summit)-2 Shutdown with remarks:- GT
| 09:00 |  | Day Peak Generation: 7931 MW.
| 10:24 |  | Ghorashal unit-7 ST was sync.
| 10:51 | 11:27 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Tripped from Shahjibazar 132/33kV end showing
Distance relay relays Due to Heavy rain With Thundering
| 10:58 | 11:27 | Brahmanbaria-Shahjibazar 132 kV Ckt-1 Tripped from Shahjibazar 132/33kV end showing
Distance Relay relays Due to Heavy Rain With Thundering
|  | 11:04 | Rampal 400/230kV S/S Bus Reactor is restored.
|  | 11:15 | Rampal 400/230kV S/S Gopalganj Line-1 Reactor is restored.
| 11:20 | 11:36 | Hasnabad 132/33kV S/S 132/33kV 424 T-5 LT Tripped showing Over current and Earth Fault | [7 empty] | 15.0MW load
|  |  | relays Due to 33kv pangaon and Nawabganj-2 feeder fault | [7 empty] | interrup.
| 11:20 | 11:36 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT Tripped showing E/F, O/C and 33kv master trip | [7 empty] | 15.0MW load
|  |  | OPDG relays Due to 33kv pangaon and Nawabganj-2 feeder fault | [7 empty] | interrup.
| 11:20 | 11:36 | Hasnabad 132/33kV S/S 33kv Main Bus Tripped showing Over current and Earth fault relays | [7 empty] | 30.0MW load
|  |  | Due to 33kv pangaon and Nawabganj-2 feeder fault | [7 empty] | interrup.
| 11:26 | 12:05 | Narshingdi 132/33kV S/S T-2 HT Tripped showing RET 670 relays Due to Mechanical trip
| 11:26 | 12:06 | Narshingdi 132/33kV S/S T-2 LT Tripped showing REF 630 relays Due to Inter trip
| 11:29 |  | Matarbari 2*600 MW (CPGCBL) Unit-1 was shutdown
| 13:01 |  | SS Power unit-1 was shutdown.
| 13:23 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized with remarks:- GT-2
| 15:03 | 18:52 | Madaripur 132/33kV S/S T3-426T HT Forced S/D Due to Due to fault | [7 empty] | 20.0MW load
interrup.
| 15:03 | 18:52 | Madaripur 132/33kV S/S T3-426T LT Forced S/D Due to Due to fault | [7 empty] | 20.0MW load
interrup.
| 15:20 | 15:52 | Baroaulia-Hathazari 132 kV Ckt-1 Tripped from Hathazari 230/132/33kV end showing Alstom
Quadramho relays. and from Baroaulia 132/33kV end showing 1.(B) 2.(C) relays Due to
Unexpected
| 15:38 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized with remarks:- ST
| 15:38 |  | Meghnaghat 450 MW CCPP ST was sync.
| 15:40 | 20:05 | Bagerhat-Bhandaria 132 kV Ckt-1 Tripped from Bagerhat 132/33kV end showing Distance Relay
relays Due to OV
| 15:52 | 17:55 | Mongla 132/33kV S/S T-2 LT Tripped showing Over Current/Earth Fault relays Due to Due to | [7 empty] | 9.0MW load
|  |  | 33 KV Bus PT Blast | [7 empty] | interrup.
| 16:06 | 16:07 | Cumilla(S) 132/33kV S/S TR-1 LT Scheduled S/D Due to Bus Shifting Tripura to Bd
| 16:07 | 16:07 | Cumilla(S) 132/33kV S/S TR-1 HT Scheduled S/D Due to Bus Shifting Tripura to Bd
| 16:12 | 16:13 | Cumilla(S) 132/33kV S/S TR-3 LT Scheduled S/D Due to Bus Shifting Tripura to Bd
| 16:12 | 16:13 | Cumilla(S) 132/33kV S/S TR-3 HT Scheduled S/D Due to Bus Shifting Tripura to Bd
| 16:16 | 16:37 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing Non relays Due to Madhabpur-3 Feeder
OC/EF fault.
| 16:26 | 16:56 | Dohazari-Sikalbaha 132 kV Ckt-1 Tripped from Dohazari 132/33kV end showing Siemens O/C
Relay: General Peak/trip,R-phase trip,Y-phase trip,B-phase trip.Distance Relay:Zone-01
(A,B) relays Due to ***Tripped portion: Dohazari to Patiya. Stormy Weather
| 16:36 | 18:26 | Barishal 132/33kV S/S T-2 (415T) LT Tripped showing Inst. O/c, Deff. O/C relays Due to | [7 empty] | 12.0MW load
|  |  | Pbs Charbaria 33kV feeder bus loop fault | [7 empty] | interrup.
| 16:36 | 17:06 | Barishal 132/33kV S/S T-1 (405T) LT Tripped showing Inst. O/C, Deff. O/C relays Due to | [7 empty] | 22.0MW load
|  |  | T-1 & T-2 33kV trip for pbs Charbaria 33kV bus loop fault | [7 empty] | interrup.
| 16:52 |  | Rampal 1320 MW (BIFPCL) unit-1 was shut down due to low demand caused by bad weather.
| 16:58 | 17:27 | Goalpara-Labanchura 132kV Ckt-2 Tripped from Goalpara 132/33kV end showing distance
relay relays Due to distance trip bagerhat-2 zone-1 trip bagerhat-2 phace -c,
circuit km-28km
| 17:14 |  | JERA Meghnaghat Power Limited 718 MW CCPP tripped.
| 17:56 | 20:02 | Kalurghat 132/33kV S/S TRFO-01(506T) LT Tripped showing REF615,RET650,RET 670 relays Due
to Fault by bpdb
| 19:10 | 20:48 | Kaliakoir-Tongi 230kV Ckt-2 Tripped from Tongi 230/132/33kV end showing LBB protection
relays Due to 230 kv bus 2, B phase PT Blast
| 19:10 | 20:50 | Kodda(300MW)-Tongi 230kV Ckt-1 Tripped from Tongi 230/132/33kV end showing 86 R1 R2,
phase OPTD main 2 dist. Prot. relays Due to 230 kv bus 2, B phase PT Blast
| 19:27 |  | Siddhirganj 2*120 MW GT-2 was sync.
| 20:42 | 23:48 | Hasnabad 132/33kV S/S 132/33kV 424 T-5 HT Scheduled S/D Due to Red hot at 33 kv bus
isolator
| 20:42 | 23:48 | Hasnabad 132/33kV S/S 132/33kV 424 T-5 LT Scheduled S/D Due to Red hot at 33 kv bus
isolator
| 20:42 | 23:48 | Hasnabad 132/33kV S/S 33kv Main Bus Scheduled S/D Due to Red hot at 33kv main bus
isolator of Transformer-5
| 21:10 | 21:25 | Tongi 230/132/33kV S/S 230 kV Bus-2 Tripped showing High impedance, phase R T,
Supervison relay relays Due to 230 kv bus 2, B phase PT Blast
| 22:15 | 23:08 | Kabirpur -Tongi 132kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Bird nest
remove
| 23:09 | 23:23 | Joypurhat-Naogaon 132kV Ckt-1 Tripped from Joypurhat 132/33kV end showing distance
relays Due to over Voltage
| 23:10 | 23:45 | Bogura(New)-Naogaon 132 kV Ckt-1 Tripped from Naogaon 132/33kV end showing 51 relays Due
to Deractional Earth Fault (Whether: Thunderstorm and storm)
| 23:10 | 00:22 | Kabirpur -Tongi 132kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Nest
remove
| 23:57 | 00:40 | Rangpur 132/33kV S/S Rangpur-GTPS Forced S/D Due to Emergency Demand of GTPS End
| 00:06 | 05:46 | Bogura 230/132kV S/S Confidance UN-2 Tripped showing Over Voltage Trip relays Due to Over
Voltage .
| 00:06 | 05:46 | Bogura 230/132kV S/S Confidance UN-2 Tripped showing Over Voltage Trip relays Due to Over
Voltage .
| 00:46 | 01:30 | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT Tripped showing 67 relays Due to 67 | [7 empty] | 20.0MW load
interrup.
| 00:46 | 01:26 | Rajshahi 132/33kV S/S Transformer T-2(415T) LT Tripped showing 67 relays Due to Mohonpur | [7 empty] | 10.0MW load
|  |  | Feeder Faulty | [7 empty] | interrup.
| 00:46 | 01:24 | Rajshahi 132/33kV S/S Transformer T-2(415T) HT Tripped showing Trip Relay relays Due to | [7 empty] | 10.0MW load
|  |  | Mohonpur Feeder Faulty | [7 empty] | interrup.
| 01:27 | 01:53 | Rajshahi 132/33kV S/S Transformer T-2(415T) LT Tripped showing 67 relays Due to Mohonpur
Feeder Faulty
| 01:27 | 01:50 | Rajshahi 132/33kV S/S Transformer T-2(415T) HT Tripped showing 67 relays Due to Mohonpur
Feeder Faulty
| 02:08 |  | Bibiyana-III 400 MW CCPP Shutdown with remarks:- ST
| 02:25 | 03:25 | Saidpur 132/33kV S/S TR-5 (434T) HT Tripped showing O/C. and E/F Relay relays Due to For
33kv Trillion gold feeder trail.
| 02:25 | 03:26 | Saidpur 132/33kV S/S TR-5 (434T) LT Tripped showing No Relay relays.
| 03:14 |  | Bibiyana-III 400 MW CCPP Shutdown with remarks:- GT
| 03:15 | 03:33 | Faridpur 132/33kV S/S Transformer-1 LT Tripped showing 33kV over current and Earth Fault. | [7 empty] | 36.0MW load
|  |  | relays Due to 33kV Khalil Mondol feeder fault | [7 empty] | interrup.
| 03:15 | 03:33 | Faridpur 132/33kV S/S Transformer-2 LT Tripped showing 33kV o/c & E/F relays Due to 33kV | [7 empty] | 36.0MW load
|  |  | khalil mondol feeder fault. | [7 empty] | interrup.
| 03:50 |  | Khulna (C) S/S Tr-3 405T HT Tripped showing No relay. relays Due to E/F Inst 33kv side | [7 empty] | 8.0MW load
|  |  | Chandanimahal feeder fault. | [7 empty] | interrup.
| 03:59 |  | Lalmonirhat-Rangpur 132 kV Ckt-2 Tripped from Kurigram 132/33kV end showing Z1,Distance
Protection(P443) relays Due to PT Burn(B-phase)
| 04:00 |  | Minimum Generation: 6114 MW
| 04:20 |  | Bagerhat-Bhandaria 132 kV Ckt-1 Tripped from Bagerhat 132/33kV end showing Distance
relays Due to Over voltage
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 20-03-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 110 | 1645982 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 45 | 461045.46 | Demand "05"MW due to gas restiction by Titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 342 | 7426800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 1823000 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 39 | 211000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 260 | 5827784 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 5 | 202800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 5 | 160920 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 0 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 68725 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 455 | 8404090.91 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 2120901 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 210 | 5383000 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 0 | 75600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1696 | 33811648.37
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 119475 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1416360 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 225 | 4712760 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 167377 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 13 | 169440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 15004 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 310 | 12692726 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 33 | 264960 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 140 | 5461818.18 | Coal shortage
Chattogram Area Total |  |  |  |  | 4898.863 | 801 | 25019920.18
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 211 | 4345000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 325 | 6830000 | Able to ON FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 369 | 6792000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 517646 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 103 | 1709979 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 46 | 1971840 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 5 | 296070 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 254882 | -
Cumilla Area Total |  |  |  |  | 2876.261 | 1110 | 22717417
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 163 | 3386880 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8250 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 0 | 86400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 0 | 181200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 68220 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | From12:00 hrs to24:00 hrs will be dispatching12MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 163 | 3730950
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 24591 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 826000 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 162 | 3458781.82 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 100 | 1294700 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 587904 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 31 | 209280 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 96 | 2314400 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 20 | 186024 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 330 | 6425000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 373 | 8342000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | plant will be shutdown due to 3rd Minor Inspection
Sylhet Area Total |  |  |  |  | 2325 | 1183 | 23668680.82
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 893 | 18470545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 330 | 6728544 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 460080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 366 | 16058182 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1589 | 41717351
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 125 | 2663000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 480 | 14660363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 180 | 4832040 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 140 | 3731000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2791 | -
Barishal Area Total |  |  |  |  | 3481.04 | 925 | 25889194.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 148792 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 389 | 7691200 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | machine problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 14580 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 848 | 19946546 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 199488 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 445410 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1237 | 28446016
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 54 | 1274618 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 41371.2 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 0 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 186341 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 826560 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 54 | 2328890.2
Eastern Grid Total |  |  |  |  | 17423.308 | 4953 | 108948616.37
Western Grid Total |  |  |  |  | 11852.195 | 3805 | 98381451.84
National Grid Total |  |  |  |  | 29275.503 | 8758 | 207330068.21
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 20-03-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 5427.06 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3017 | MW
i) Dhaka area |  |  | 2506.56 |  | MW | i) Khulna area |  |  |  | 1042.6 | MW
ii) Chattogram area |  |  | 915.5 |  | MW | ii) Barishal area |  |  |  | 299.8 | MW
iii) Cumilla area |  |  | 872 |  | MW | iii) Rajshahi area |  |  |  | 1037.6 | MW
iv) Mymensingh area |  |  | 744 |  | MW | iv) Rangpur area |  |  |  | 637 | MW
v) Sylhet area |  |  | 389 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 8444.06 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 9 | 17:00 | 67 | Hasnabad | 46 | 01:00 | 133 | Nawabganj | 44.2 | 00:00
2 | AKSML | 7 | 04:00 | 68 | Hathazari | 70 | 23:00 | 134 | Netrakona | 112 | 18:00
3 | Aftabnagar | 24 | 00:00 | 69 | Hatirjheel | 24 | 00:00 | 135 | New | 30 | 00:00
4 | Agargaon | 68 | 00:00 | 70 | Ishurdi | 51 | 03:00 | 136 | Niamatpur | 89 | 03:00
5 | Agrabad | 54 | 00:00 | 71 | Jaldhaka | 68 | 18:00 | 137 | Noapara | 34 | 00:00
6 | Amnura | 34 | 08:00 | 72 | Jamalpur | 98 | 03:00 | 138 | PHP | 6 | 01:00
7 | Ashuganj | 57 | 04:00 | 73 | Jashore | 134 | 01:00 | 139 | Pabna | 75 | 03:00
8 | BSRM | 199 | 00:00 | 74 | Jhenaidah | 87 | 13:00 | 140 | Palashbari | 92 | 18:00
9 | Bagerhat | 72 | 00:00 | 75 | Joydebpur | 64 | 13:00 | 141 | Panchagarh | 47 | 18:00
10 | Bajitpur | 68 | 18:00 | 76 | Joypurhat | 50 | 00:00 | 142 | Patiya | 9 | 00:00
11 | Bakerganj | 9.12 | 00:00 | 77 | Juldah | 15 | 00:00 | 143 | Patuakhali | 59.5 | 00:00
12 | Bakulia | 68 | 00:00 | 78 | KSRM | 10 | 10:00 | 144 | Payra | 26 | 00:00
13 | Banani | 11.2 | 11:00 | 79 | Kabirpur | 102 | 01:00 | 145 | Postogola | 33 | 00:00
14 | Bangabhaban | 3 | 00:00 | 80 | Kachua | 87 | 00:00 | 146 | Pubail | 19 | 13:00
15 | Barapukuria | 48 | 04:00 | 81 | Kaliganj | 28 | 13:00 | 147 | Purbachal | 20 | 00:00
16 | Barguna | 18 | 00:00 | 82 | Kallyanpur | 75 | 00:00 | 148 | Purbasadipur | 91 | 13:00
17 | Barishal | 79 | 13:00 | 83 | Kalurghat | 23 | 00:00 | 149 | Rahanpur | 32 | 00:00
18 | Barishal-230 | 84 | 00:00 | 84 | Kamrangirchar | 37 | 00:00 | 150 | Rahim | 1 | 00:00
19 | Baroaulia | 45 | 04:00 | 85 | Kaptai | N/A | N/A | 151 | Rajbari | 73 | 04:00
20 | Baroirhat | 53 | 13:00 | 86 | Kasba | 30 | 00:00 | 152 | Rajendrapur | 79 | 00:00
21 | Bashundhara | 109 | 00:00 | 87 | Kazla | 64 | 00:00 | 153 | Rajshahi | 94 | 03:00
22 | BashundharaCement | 0 | 00:00 | 88 | Keranigonj | 60 | 00:00 | 154 | Rajshahi-230 | 73 | 00:00
23 | Beanibazar | 50 | 00:00 | 89 | Khagrachori | 26 | 13:00 | 155 | Ramganj | 92 | 00:00
24 | Benapole | 64 | 13:00 | 90 | Khulna | 50 | 00:00 | 156 | Rampur | 32 | 02:00
25 | Bhaluka | 89 | 00:00 | 91 | Khulshi | 150 | 00:00 | 157 | Rangamati | 14 | 19:30
26 | Bhandaria | 48 | 00:00 | 92 | Kishoreganj | 107 | 00:00 | 158 | Rangpur | 120 | 18:00
27 | Bhangura | 36 | 03:00 | 93 | Kodda | 112 | 00:00 | 159 | Ruppur | 2.4 | 09:00
28 | Bheramara(GK) | 47 | 03:00 | 94 | Kulaura | 32 | 00:00 | 160 | SSM | 0 | 00:00
29 | Bhulta | 97 | 00:00 | 95 | Kurigram | 64 | 03:00 | 161 | Saidpur | 70 | 18:00
30 | Bog-Sherpur | 60 | 03:00 | 96 | Kushtia | 104 | 03:00 | 162 | Satkhira | 125 | 00:00
31 | Bogura | 121 | 00:00 | 97 | Laksam | 28 | 00:00 | 163 | Satmasjid | 62 | 00:00
32 | Borhanuddin | 89 | 00:00 | 98 | Lakshmipur | 47 | 00:00 | 164 | Savar | 96 | 00:00
33 | Brahmanbaria | 107 | 00:00 | 99 | Lalbag | 20 | 00:00 | 165 | SevenRings | 2.36 | 01:00
34 | Cantonment | 96 | 00:00 | 100 | Lalmonirhat | 44 | 18:00 | 166 | ShahCement | 22 | 11:00
35 | Chandina | 18 | 16:00 | 101 | MI_Cement | 13.3 | 00:00 | 167 | Shahjadpur | 52 | 08:00
36 | Chandpur | 68 | 00:00 | 102 | Madanganj | 24 | 00:00 | 168 | Shahjibazar | 89 | 00:00
37 | Chandraghona | 32 | 13:00 | 103 | Madaripur | 97 | 00:00 | 169 | Shahmirpur | 41 | 00:00
38 | Chapai | 64 | 00:00 | 104 | Madartek | 54 | 00:00 | 170 | Shariatpur | 74 | 00:00
39 | Charsaidpur | 13 | 11:00 | 105 | Madunaghat | 47 | 00:00 | 171 | Sherpur | 112 | 18:00
40 | Chauddagram | 65 | 00:00 | 106 | Magura | 52 | 00:00 | 172 | Shikalbaha | 24.5 | 01:00
41 | Chhatak | 26 | 00:00 | 107 | Mahasthangarh | 65 | 19:00 | 173 | Shitalakhya | 46.2 | 00:00
42 | Chowmuhani | 127 | 13:00 | 108 | Maijdee | 39 | 00:00 | 174 | Sholosohor | 29 | 22:00
43 | Chuadanga | 114 | 03:00 | 109 | Manikganj | 88 | 01:00 | 175 | Shyampur | 73 | 01:00
44 | Coxsbazar | 130 | 00:00 | 110 | Maniknagar | 49 | 00:00 | 176 | Siddhirganj | 63 | 00:00
45 | Cumilla(N) | 92 | 00:00 | 111 | Matarbari | 50 | 03:00 | 177 | Sirajganj | 90 | 04:00
46 | Cumilla(S) | 125 | 01:00 | 112 | Matuail | 30 | 00:00 | 178 | Sonargaon | 45 | 01:00
47 | Daganbhuiyan | 33 | 21:00 | 113 | Metrorail_Motijheel | 13 | 16:00 | 179 | Sreemongol | 51 | 01:00
48 | Daudkandi | 99 | 00:00 | 114 | Metrorail_Uttara | 4 | 17:00 | 180 | Sreepur | 45 | 01:00
49 | DhakaUniversity | 24 | 11:00 | 115 | Millgate | 35 | 00:00 | 181 | Srinagar | 38 | 13:00
50 | Dhamrai | 60 | 00:00 | 116 | Mirpur | 85 | 00:00 | 182 | Sunamganj | 42 | 00:00
51 | Dhanmondi | 63 | 00:00 | 117 | Mirsorai | 7 | 00:00 | 183 | Sylhet | 46 | 13:00
52 | Dohazari | 105 | 22:00 | 118 | Mirzapur | 40 | 00:00 | 184 | Sylhet-132 | 77 | 00:00
53 | Faridpur | 125 | 00:00 | 119 | Mithapukur | 54 | 04:00 | 185 | TK | 21 | 19:30
54 | Fatullah | 48 | 00:00 | 120 | Modern | N/A | N/A | 186 | Tangail | 142 | 03:00
55 | Fenchuganj | 35 | 13:00 | 121 | Mogbazar | 29.4 | 11:00 | 187 | Taraganj | 14 | 03:00
56 | Feni | 87 | 13:00 | 122 | Mongla | 23 | 00:00 | 188 | Tasnim | 7 | 16:00
57 | GPH | 1 | 00:00 | 123 | Motijheel | 24 | 00:00 | 189 | Thakurgaon | 81 | 18:00
58 | Ghatail | 90 | 03:00 | 124 | Muktagacha | 31 | 03:00 | 190 | Tongi | 85 | 00:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 86 | 00:00 | 191 | Ullahpara | 39 | 03:00
60 | Ghorashal-230 | 71 | 00:00 | 126 | Muradnagar | 30 | 00:00 | 192 | Ullon | 38 | 00:00
61 | Goalpara | 36 | 00:00 | 127 | Mymensingh | 155 | 04:00 | 193 | Uttara | 50 | 00:00
62 | Gollamari | 64 | 00:00 | 128 | Naogaon | 101 | 04:00 | 194 | UttaraNew | 20 | 00:00
63 | Gopalganj | 87 | 00:00 | 129 | Narail | 54 | 13:00 | 195 | Zigatola | 62 | 00:00
64 | Gulshan | 58 | 11:00 | 130 | Narinda | 35 | 00:00
65 | Halishahar | 49 | 00:00 | 131 | Narshingdi | 94 | 00:00
66 | HaripurSBU | 75 | 00:00 | 132 | Natore | 129 | 04:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 20-03-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 10907.75 | 0 |  | 10907.75
1:00 | 10544.84 | 0 |  | 10544.84
2:00 | 10253.7 | 0 |  | 10253.7
3:00 | 10346.86 | 0 |  | 10346.86
4:00 | 10609.04 | 0 |  | 10609.04
5:00 | 9324.04 | 0 |  | 9324.04
6:00 | 8334.14 | 0 |  | 8334.14
7:00 | 7854.72 | 0 |  | 7854.72
8:00 | 7935.79 | 0 |  | 7935.79
9:00 | 7934.87 | 0 |  | 7934.87
10:00 | 7886.14 | 0 |  | 7886.14
11:00 | 7500.21 | 0 |  | 7500.21
12:00 | 7477.12 | 0 |  | 7477.12
13:00 | 8434.42 | 0 |  | 8434.42
14:00 | 7768.89 | 0 |  | 7768.89
15:00 | 7140.62 | 0 |  | 7140.62
16:00 | 7159.66 | 0 |  | 7159.66
17:00 | 7615.55 | 0 |  | 7615.55
18:00 | 8472.57 | 0 |  | 8472.57
19:00 | 8423 | 0 |  | 8423
19:30 | 8378 | 0 |  | 8378
20:00 | 8518 | 0 |  | 8518
21:00 | 8758 | 0 |  | 8758
22:00 | 8785 | 0 |  | 8785
23:00 | 8452 | 0 |  | 8452
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 20-03-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5481 | 5426.75 | 10907.75 | DAILY GENERATION CURVE
00:30 | 5423 | 5303.295 | 10726.295
01:00 | 5365 | 5179.84 | 10544.84 | 20-03-2026
01:30 | 5344.5 | 5054.77 | 10399.27
02:00 | 5324 | 4929.7 | 10253.7
02:30 | 5356.5 | 4943.78 | 10300.28
03:00 | 5389 | 4957.86 | 10346.86
03:30 | 5503.5 | 4974.45 | 10477.95
04:00 | 5618 | 4991.04 | 10609.04
04:30 | 5307.5 | 4659.04 | 9966.54
05:00 | 4997 | 4327.04 | 9324.04
05:30 | 4746.505 | 4082.585 | 8829.09
06:00 | 4496.01 | 3838.13 | 8334.14
06:30 | 4378.95 | 3715.48 | 8094.43
07:00 | 4261.89 | 3592.83 | 7854.72
07:30 | 4263.785 | 3631.47 | 7895.255
08:00 | 4265.68 | 3670.11 | 7935.79
08:30 | 4162.35 | 3772.98 | 7935.33
09:00 | 4059.02 | 3875.85 | 7934.87
09:30 | 3997.475 | 3913.03 | 7910.505
10:00 | 3935.93 | 3950.21 | 7886.14
10:30 | 3854.075 | 3839.1 | 7693.175
11:00 | 3772.22 | 3727.99 | 7500.21
11:30 | 3719.53 | 3769.135 | 7488.665
12:00 | 3666.84 | 3810.28 | 7477.12
12:30 | 3782.81 | 4172.96 | 7955.77
13:00 | 3898.78 | 4535.64 | 8434.42
13:30 | 3847.865 | 4253.79 | 8101.655
14:00 | 3796.95 | 3971.94 | 7768.89
14:30 | 3652.47 | 3802.285 | 7454.755
15:00 | 3507.99 | 3632.63 | 7140.62
15:30 | 3549.805 | 3600.335 | 7150.14
16:00 | 3591.62 | 3568.04 | 7159.66
16:30 | 3834.795 | 3552.81 | 7387.605
17:00 | 4077.97 | 3537.58 | 7615.55
17:30 | 4368.485 | 3675.575 | 8044.06
18:00 | 4659 | 3813.57 | 8472.57
18:30 | 4650 | 3797.785 | 8447.785
19:00 | 4641 | 3782 | 8423
19:30 | 4651 | 3727 | 8378
20:00 | 4741 | 3777 | 8518
20:30 | 4847 | 3791 | 8638 |  | Executive Engineer
21:00 | 4953 | 3805 | 8758 |  | Network Operation Division
21:30 | 4992.5 | 3779 | 8771.5
22:00 | 5032 | 3753 | 8785
22:30 | 4899.5 | 3719 | 8618.5
23:00 | 4767 | 3685 | 8452

## En-Curve
QF-LDC-12
Date | 20-03-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3545 | 1496 | 896 | 0 | 134 | 1027.75 | 80 | 3654 | 0 | 51 | 24 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3496.5 | 1506.5 | 896 | 0 | 130 | 1007.795 | 80 | 3534.5 | 0 | 51 | 24 | 0 | 0 | 0 | 0 | 20-03-2026
01:00 | 3448 | 1517 | 896 | 0 | 126 | 987.84 | 80 | 3415 | 0 | 51 | 24 | 0 | 0 | 0 | 0
01:30 | 3418.5 | 1553.5 | 896 | 0 | 124 | 951.27 | 80 | 3301 | 0 | 51 | 24 | 0 | 0 | 0 | 0 | Energy Generated | 207.3301 |  | MKWHr
02:00 | 3389 | 1590 | 896 | 0 | 122 | 914.7 | 80 | 3187 | 0 | 51 | 24 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3421.5 | 1605.5 | 896 | 0 | 120 | 917.78 | 80 | 3184.5 | 0 | 51 | 24 | 0 | 0 | 0 | 0 | Total Energy Requirement | 207.3301 |  | MKWHr
03:00 | 3454 | 1621 | 896 | 0 | 118 | 920.86 | 80 | 3182 | 0 | 51 | 24 | 0 | 0 | 0 | 0
03:30 | 3464.5 | 1705.5 | 896 | 0 | 121 | 918.95 | 80 | 3214 | 0 | 51 | 27 | 0 | 0 | 0 | 0
04:00 | 3475 | 1790 | 896 | 0 | 124 | 917.04 | 80 | 3246 | 0 | 51 | 30 | 0 | 0 | 0 | 0
04:30 | 3322.5 | 1682 | 896 | 0 | 119 | 874.54 | 80 | 2917 | 0 | 25.5 | 50 | 0 | 0 | 0 | 0
05:00 | 3170 | 1574 | 896 | 0 | 114 | 832.04 | 80 | 2588 | 0 | 0 | 70 | 0 | 0 | 0 | 0
05:30 | 2907.5 | 1494.5 | 894.5 | 0 | 112 | 833.085 | 80 | 2472.5 | 0.005 | 0 | 35 | 0 | 0 | 0 | 0
06:00 | 2645 | 1415 | 893 | 0 | 110 | 834.13 | 80 | 2357 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0
06:30 | 2580.5 | 1383 | 742 | 0 | 107 | 834.655 | 55 | 2371.5 | 20.775 | 0 | 0 | 0 | 0 | 0 | 0
07:00 | 2516 | 1351 | 591 | 0 | 104 | 835.18 | 30 | 2386 | 41.54 | 0 | 0 | 0 | 0 | 0 | 0
07:30 | 2511 | 1340 | 591 | 0 | 100 | 833.26 | 30 | 2391.5 | 98.495 | 0 | 0 | 0 | 0 | 0 | 0
08:00 | 2506 | 1329 | 591 | 0 | 96 | 831.34 | 30 | 2397 | 155.45 | 0 | 0 | 0 | 0 | 0 | 0
08:30 | 2479.5 | 1244.5 | 641 | 0 | 96 | 831.88 | 30 | 2401.5 | 210.95 | 0 | 0 | 0 | 0 | 0 | 0
09:00 | 2453 | 1160 | 691 | 0 | 96 | 832.42 | 30 | 2406 | 266.45 | 0 | 0 | 0 | 0 | 0 | 0
09:30 | 2385.5 | 1142.5 | 665.5 | 0 | 99 | 832.44 | 30 | 2395 | 360.565 | 0 | 0 | 0 | 0 | 0 | 0
10:00 | 2318 | 1125 | 640 | 0 | 102 | 832.46 | 30 | 2384 | 454.68 | 0 | 0 | 0 | 0 | 0 | 0
10:30 | 2316.5 | 1098.5 | 561.5 | 0 | 106 | 831.29 | 30 | 2317 | 432.385 | 0 | 0 | 0 | 0 | 0 | 0
11:00 | 2315 | 1072 | 483 | 0 | 110 | 830.12 | 30 | 2250 | 410.09 | 0 | 0 | 0 | 0 | 0 | 0
11:30 | 2336 | 1046 | 593 | 0 | 112 | 825.105 | 30 | 2216.5 | 330.06 | 0 | 0 | 0 | 0 | 0 | 0
12:00 | 2357 | 1020 | 703 | 0 | 114 | 820.09 | 30 | 2183 | 250.03 | 0 | 0 | 0 | 0 | 0 | 0
12:30 | 2670.5 | 1111.5 | 798 | 0 | 88 | 829.455 | 35 | 2068 | 354.815 | 0 | 0 | 0 | 0 | 0.5 | 0
13:00 | 2984 | 1203 | 893 | 0 | 62 | 838.82 | 40 | 1953 | 459.6 | 0 | 0 | 0 | 0 | 1 | 0
13:30 | 2910 | 1202 | 705.5 | 0 | 66 | 826.76 | 40 | 1920 | 428.895 | 0 | 0 | 0 | 0 | 2.5 | 0
14:00 | 2836 | 1201 | 518 | 0 | 70 | 814.7 | 40 | 1887 | 398.19 | 0 | 0 | 0 | 0 | 4 | 0
14:30 | 2657 | 1175 | 468 | 0 | 69 | 814.89 | 40 | 1880.5 | 339.365 | 0 | 0 | 0 | 0 | 11 | 0
15:00 | 2478 | 1149 | 418 | 0 | 68 | 815.08 | 40 | 1874 | 280.54 | 0 | 0 | 0 | 0 | 18 | 0
15:30 | 2461.5 | 1176 | 446.5 | 0 | 74 | 822.875 | 40 | 1874 | 240.765 | 0 | 0 | 0 | 0 | 14.5 | 0
16:00 | 2445 | 1203 | 475 | 0 | 80 | 830.67 | 40 | 1874 | 200.99 | 0 | 0 | 0 | 0 | 11 | 0
16:30 | 2773.5 | 1272 | 590 | 0 | 61 | 828.98 | 40 | 1674 | 140.125 | 0 | 0 | 0 | 0 | 8 | 0
17:00 | 3102 | 1341 | 705 | 0 | 42 | 827.29 | 40 | 1474 | 79.26 | 0 | 0 | 0 | 0 | 5 | 0
17:30 | 3347.5 | 1408.5 | 798.5 | 0 | 39 | 831.775 | 60 | 1484 | 40.785 | 0 | 20 | 0 | 0 | 14 | 0
18:00 | 3593 | 1476 | 892 | 0 | 36 | 836.26 | 80 | 1494 | 2.31 | 0 | 40 | 0 | 0 | 23 | 0
18:30 | 3495 | 1498 | 892.5 | 0 | 34 | 820.13 | 80 | 1560.5 | 1.155 | 0 | 24 | 0 | 0 | 42.5 | 0
19:00 | 3397 | 1520 | 893 | 0 | 32 | 804 | 80 | 1627 | 0 | 0 | 8 | 0 | 0 | 62 | 0
19:30 | 3477 | 1505 | 893 | 0 | 42 | 818 | 80 | 1498 | 0 | 0 | 0 | 0 | 0 | 65 | 0
20:00 | 3575 | 1541 | 893 | 0 | 46 | 842 | 80 | 1477 | 0 | 0 | 0 | 0 | 0 | 64 | 0
20:30 | 3603 | 1639 | 893 | 0 | 46 | 845 | 80 | 1483.5 | 0 | 0 | 0 | 0 | 0 | 48.5 | 0
21:00 | 3631 | 1737 | 893 | 0 | 46 | 848 | 80 | 1490 | 0 | 0 | 0 | 0 | 0 | 33 | 0
21:30 | 3605 | 1797.5 | 893 | 0 | 48 | 836.5 | 80 | 1485.5 | 0 | 0 | 0 | 0 | 0 | 26 | 0
22:00 | 3579 | 1858 | 893 | 0 | 50 | 825 | 80 | 1481 | 0 | 0 | 0 | 0 | 0 | 19 | 0
22:30 | 3484.5 | 1779.5 | 893 | 0 | 49 | 824.5 | 80 | 1489 | 0 | 0 | 0 | 0 | 0 | 19 | 0
23:00 | 3390 | 1701 | 893 | 0 | 48 | 824 | 80 | 1497 | 0 | 0 | 0 | 0 | 0 | 19 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 20-03-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 416 | 16:00 | 403 | 00:00 | Madunaghat | 410 | 17:00 | 399 | 00:00
Amtali | 422 | 08:00 | 415 | 01:00 | Meghnaghat | 418 | 16:00 | 408 | 02:00
Ashuganj | 413 | 8:00 | 407 | 1:00 | Payra | 422 | 16:00 | 415 | 00:00
Bhulta | 409 | 15:00 | 399 | 00:00 | Rahanpur | 420 | 05:00 | 405 | 18:00
Bibiana | 418 | 12:00 | 407 | 01:00 | Rampal | 415 | 06:00 | 403 | 00:00
BIPTC | 406 | 14:00 | 391 | 13:00
Bogura | 409 | 05:00 | 395 | 18:00
Gopalganj | 418 | 15:00 | 406 | 00:00
Kaliakoir | 413 | 11:00 | 394 | 00:00
Korerhat | 417 | 15:00 | 404 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 240 | 08:00 | 234 | 00:00 | Jhenaidah | 236 | 15:00 | 223 | 00:00
AKSML | 237 | 16:00 | 229 | 00:00 | Kachua | 239 | 14:00 | 225 | 00:00
Aminbazar | 240 | 07:00 | 234 | 00:00 | Kaliakoir | 245 | 10:00 | 237 | 18:00
Ashuganj | 238 | 12:00 | 229 | 11:00 | Keranigonj | 238 | 08:00 | 232 | 00:00
Ashuganj-400 | 238 | 12:00 | 229 | 11:00 | Khulna(S) | 239 | 06:00 | 228 | 00:00
Baghabari | 239 | 10:00 | 230 | 00:00 | Korerhat | 238 | 15:00 | 228 | 00:00
Barapukuria | 234 | 07:00 | 217 | 02:00 | Madunaghat | 238 | 16:00 | 230 | 00:00
Barapukuria-230 | 234 | 07:00 | 217 | 02:00 | Madunaghat-400 | 238 | 16:00 | 231 | 00:00
Barishal | 237 | 15:00 | 227 | 00:00 | Maniknagar | 238 | 15:00 | 229 | 00:00
Bheramara | 237 | 16:00 | 225 | 00:00 | Meghnaghat | 244 | 13:00 | 235 | 00:00
Bhulta | 238 | 15:00 | 231 | 00:00 | Meghnaghat-400 | 238 | 16:00 | 230 | 03:00
Bibiana | 242 | 08:00 | 234 | 00:00 | Mirsorai | 246 | 15:00 | 236 | 00:00
BIPTC | 238 | 16:00 | 227 | 00:00 | Purbasadipur | 235 | 07:00 | 215 | 18:00
Bogura | 243 | 05:00 | 234 | 18:00 | Rajshahi | 234 | 06:00 | 223 | 00:00
Bogura-400 | 242 | 07:00 | 233 | 04:00 | Rampal | 237 | 06:00 | 227 | 00:00
Borhanuddin | 239 | 15:00 | 231 | 00:00 | Rampur | N/A | N/A | N/A | N/A
BSRM | 239 | 16:00 | 228 | 00:00 | Rampura | 238 | 15:00 | 231 | 00:00
Chowmuhani | 239 | 15:00 | 236 | 18:00 | Shikalbaha | 236 | 16:00 | 229 | 00:00
Cumilla(N) | 237 | 15:00 | 229 | 00:00 | Shyampur | 239 | 15:00 | 230 | 00:00
Faridpur | 235 | 15:00 | 225 | 00:00 | Siddhirganj | 239 | 15:00 | 231 | 00:00
Fenchuganj | 243 | 12:00 | 238 | 00:00 | Sirajgonj | 244 | 10:00 | 237 | 00:00
Feni | 239 | 15:00 | 228 | 00:00 | Sreepur | 236 | 11:00 | 228 | 02:00
Ghorashal | 240 | 16:00 | 230 | 05:00 | Tongi | 241 | 09:00 | 233 | 00:00
Ghorashal-230 | 238 | 11:00 | 231 | 00:00
Gopalganj | 234 | 15:00 | 213 | 20:00
GPH | 239 | 16:00 | 229 | 00:00
Haripur | 240 | 12:00 | 232 | 00:00
Hasnabad | 238 | 07:00 | 232 | 00:00
Hathazari | 238 | 17:00 | 228 | 00:00
Ishurdi | 238 | 10:00 | 229 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 15:00 | 130 | 00:00 | Madunaghat | 138 | 16:00 | 132 | 00:00
Agargaon | 139 | 08:00 | 134 | 18:00 | Magura | 136 | 15:00 | 124 | 00:00
Agrabad | 137 | 16:00 | 131 | 00:00 | Mahasthangarh | 139 | 07:00 | 130 | 18:00
AKS | 136 | 19:00 | 130 | 00:00 | Maijdee | 135 | 15:00 | 125 | 00:00
Aminbazar | 140 | 06:00 | 130 | 15:00 | Manikganj | 136 | 11:00 | 130 | 01:00
Amnura | 138 | 04:00 | 130 | 00:00 | Maniknagar | 134 | 12:00 | 129 | 00:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 127 | 18:30 | 110 | 00:00
Ashuganj-230 | 145 | 11:00 | 138 | 00:00 | Matuail | 142 | 12:00 | 137 | 00:00
Bagerhat | 142 | 16:00 | 127 | 00:00 | Metrorail_Motijheel | 134 | 12:00 | 129 | 00:00
Bajitpur | 137 | 10:00 | 130 | 00:00 | Metrorail_Uttara | 137 | 08:00 | 132 | 00:00
Bakerganj | 138 | 16:00 | 131 | 00:00 | Millgate | 138 | 08:00 | 133 | 00:00
Bakulia | 139 | 15:00 | 130 | 00:00 | Mirpur | 139 | 07:00 | 135 | 18:00
Banani | 138 | 08:00 | 134 | 00:00 | Mirzapur | 139 | 11:00 | 129 | 03:00
Bangabhaban | 134 | 15:00 | 129 | 00:00 | Mithapukur | 140 | 08:00 | 127 | 17:00
Barapukuria | 142 | 05:00 | 127 | 17:00 | MI_Cement | 141 | 08:00 | 135 | 01:00
Barguna | 140 | 17:00 | 131 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 140 | 16:00 | 131 | 00:00 | Mogbazar | 136 | 15:00 | 134 | 00:00
Barishal-230 | 138 | 15:00 | 131 | 00:00 | Mongla | 142 | 17:00 | 128 | 00:00
Baroaulia | 138 | 16:00 | 132 | 00:00 | Motijheel | 134 | 15:00 | 129 | 00:00
Baroirhat | 137 | 16:00 | 131 | 00:00 | Muktagacha | 140 | 10:00 | 129 | 00:00
Bashundhara | 138 | 11:00 | 129 | 00:00 | Munshiganj | 141 | 12:00 | 134 | 20:00
BashundharaCement | 143 | 12:00 | 136 | 00:00 | Muradnagar | 138 | 12:00 | 130 | 00:00
Beanibazar | 134 | 10:00 | 128 | 00:00 | Mymensingh | 141 | 10:00 | 124 | 04:00
Benapole | 137 | 15:00 | 119 | 00:00 | Naogaon | 140 | 05:00 | 130 | 00:00
Bhaluka | 140 | 10:00 | 130 | 03:00 | Narail | 137 | 14:00 | 125 | 00:00
Bhandaria | 140 | 16:00 | 126 | 00:00 | Narinda | 134 | 12:00 | 129 | 00:00
Bhangura | 137 | 11:00 | 129 | 00:00 | Narshingdi | 139 | 11:00 | 132 | 00:00
Bheramara | 137 | 08:00 | 132 | 00:00 | Natore | 135 | 05:00 | 130 | 00:00
Bheramara(GK) | 137 | 07:00 | 131 | 03:00 | Nawabganj | 136 | 12:00 | 130 | 00:00
Bhulta | 135 | 12:00 | 130 | 00:00 | Netrakona | 137 | 10:00 | 124 | 00:00
Bog-Sherpur | 139 | 07:00 | 133 | 00:00 | New | 138 | 07:00 | 134 | 00:00
Bogura | 140 | 06:00 | 133 | 18:00 | Niamatpur | 140 | 05:00 | 135 | 03:00
Bogura-230 | 140 | 05:00 | 134 | 18:00 | Noapara | 140 | 15:00 | 129 | 00:00
Brahmanbaria | 138 | 14:00 | 131 | 00:00 | Pabna | 137 | 16:00 | 131 | 04:00
Cantonment | 138 | 06:00 | 134 | 00:00 | Palashbari | 138 | 07:00 | 127 | 00:00
Chandina | 138 | 12:00 | 131 | 00:00 | Panchagarh | 139 | 05:00 | 128 | 11:00
Chandpur | 135 | 14:00 | 125 | 00:00 | Patiya | 137 | 18:00 | 128 | 09:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 140 | 16:00 | 133 | 00:00 | Patuakhali | 138 | 16:00 | 130 | 00:00
Chapai | 139 | 05:00 | 134 | 12:00 | Payra | 139 | 16:00 | 136 | 00:00
Charsaidpur | 142 | 12:00 | 136 | 00:00 | PHP | 136 | 15:00 | 130 | 00:00
Chauddagram | 137 | 15:00 | 128 | 00:00 | Postogola | 142 | 12:00 | 138 | 00:00
Chhatak | 133 | 10:00 | 126 | 00:00 | Pubail | 145 | 11:00 | 138 | 01:00
Chowmuhani | 134 | 15:00 | 125 | 00:00 | Purbachal | 138 | 11:00 | 133 | 00:00
Chuadanga | 134 | 06:00 | 122 | 03:00 | Purbasadipur | 138 | 07:00 | 127 | 17:00
Coxsbazar | 125 | 19:00 | 111 | 00:00 | Rahanpur | 140 | 03:00 | 136 | 18:00
Cumilla(N) | 139 | 14:00 | 132 | 00:00 | Rahanpur-400 | 141 | 05:00 | 136 | 13:00
Cumilla(S) | 138 | 16:00 | 126 | 11:00 | Rahim | 142 | 12:00 | 135 | 20:00
Daganbhuiyan | 135 | 15:00 | 127 | 00:00 | Rajbari | 135 | 14:00 | 129 | 00:00
Daudkandi | 139 | 12:00 | 128 | 00:00 | Rajendrapur | 143 | 11:00 | 134 | 00:00
DhakaUniversity | 135 | 12:00 | 131 | 00:00 | Rajshahi | 134 | 02:00 | 129 | 00:00
Dhamrai | 138 | 06:00 | 134 | 00:00 | Rajshahi-230 | 135 | 06:00 | 129 | 00:00
Dhanmondi | 143 | 12:00 | 136.7 | 18:00 | Ramganj | 135 | 15:00 | 123 | 00:00
Dohazari | 134 | 18:30 | 124 | 00:00 | Rampur | 138 | 19:00 | 131 | 00:00
Faridpur | 136 | 12:00 | 130 | 00:00 | Rampura | 135 | 15:00 | 131 | 00:00
Fatullah | 142 | 15:00 | 134 | 00:00 | Rangamati | 139 | 16:00 | 131 | 00:00
Fenchuganj | 138 | 11:00 | 134 | 00:00 | Rangpur | 140 | 07:00 | 128 | 13:00
Feni | 135 | 15:00 | 127 | 00:00 | Ruppur | 138 | 10:00 | 132 | 00:00
Feni-230 | 135 | 15:00 | 128 | 00:00 | Saidpur | 139 | 07:00 | 127 | 13:00
Ghatail | 140 | 10:00 | 126 | 17:00 | Satkhira | 141 | 17:00 | 127 | 00:00
Ghorashal | 144 | 10:00 | 138 | 00:00 | Satmasjid | 137 | 06:00 | 133 | 07:00
Goalpara | 143 | 17:00 | 132 | 00:00 | Savar | 139 | 06:00 | 134 | 18:00
Gollamari | 141 | 14:00 | 133 | 00:00 | SevenRings | 145 | 11:00 | 139 | 00:00
Gopalganj | 141 | 16:00 | 132 | 00:00 | ShahCement | 142 | 12:00 | 133 | 06:00
Gopalganj-400 | 140 | 15:00 | 134 | 00:00 | Shahjadpur | 140 | 02:00 | 134 | 00:00
Gulshan | 134 | 15:00 | 130 | 00:00 | Shahjibazar | 139 | 11:00 | 130 | 00:00
Halishahar | 138 | 17:00 | 131 | 00:00 | Shahmirpur | 138 | 17:00 | 130 | 00:00
Haripur | 142 | 12:00 | 136 | 18:00 | Shariatpur | 139 | 15:00 | 130 | 00:00
HaripurSBU | 142 | 12:00 | 136 | 00:00 | Sherpur | 137 | 08:00 | 116 | 04:00
Hasnabad | 142 | 12:00 | 137 | 00:00 | Shikalbaha | 127 | 17:00 | 120 | 00:00
Hathazari | 139 | 17:00 | 133 | 00:00 | Shikalbaha-230 | 138 | 16:00 | 130 | 18:30
Hatirjheel | 135 | 15:00 | 131 | 00:00 | Shitalakhya | 141 | 08:00 | 135 | 01:00
Ishurdi | 139 | 08:00 | 134 | 00:00 | Sholosohor | 138 | 16:00 | 132 | 00:00
Jaldhaka | 138 | 07:00 | 124 | 17:00 | Shyampur | 138 | 19:00 | 129 | 00:00
Jamalpur | 137 | 09:00 | 120 | 03:00 | Shyampur-230 | 138 | 08:00 | 134 | 00:00
Jashore | 139 | 15:00 | 124 | 13:00 | Siddhirganj | 142 | 12:00 | 127 | 00:00
Jhenaidah | 137 | 15:00 | 126 | 00:00 | Sirajganj | 137 | 10:00 | 130 | 04:00
Jhenaidah-230 | 136 | 06:00 | 127 | 00:00 | Sonargaon | 142 | 12:00 | 136 | 00:00
Joydebpur | 144 | 11:00 | 135 | 00:00 | Sreemongol | 138 | 11:00 | 130 | 00:00
Joypurhat | 136 | 08:00 | 128 | 00:00 | Sreepur | 143 | 11:00 | 136 | 01:00
Juldah | 138 | 16:00 | 131 | 00:00 | Srinagar | 136 | 12:00 | 131 | 00:00
Kabirpur | 140 | 11:00 | 131 | 00:00 | SSM | 140 | 05:00 | 138 | 00:00
Kachua | 136 | 14:00 | 126 | 00:00 | Sunamganj | 133 | 11:00 | 125 | 00:00
Kaliakoir | 141 | 10:00 | 134 | 03:00 | Sylhet | 134 | 11:00 | 130 | 00:00
Kaliganj | 138 | 15:00 | 126 | 00:00 | Sylhet-132 | 133 | 11:00 | 129 | 00:00
Kallyanpur | 140 | 11:00 | 132 | 22:00 | Tangail | 139 | 10:00 | 123 | 04:00
Kalurghat | 139 | 16:00 | 133 | 00:00 | Taraganj | 139 | 07:00 | 127 | 13:00
Kamrangirchar | 139 | 11:00 | 130 | 00:00 | Tasnim | 142 | 12:00 | 135 | 00:00
Kaptai | 140 | 16:00 | 135 | 2:00 | Thakurgaon | 138 | 07:00 | 127 | 11:00
Kasba | 139 | 12:00 | 129 | 00:00 | TK | 139 | 16:00 | 132 | 00:00
Kazla | 138 | 00:00 | 129 | 01:00 | Tongi | 139 | 08:00 | 134 | 00:00
Keranigonj | 137 | 12:00 | 131 | 00:00 | Ullahpara | 138 | 10:00 | 130 | 03:00
Khagrachori | 139 | 16:00 | 131 | 00:00 | Ullon | 135 | 18:30 | 131 | 00:00
Khulna | 141 | 16:00 | 132 | 00:00 | Uttara | 140 | 11:00 | 135 | 18:00
Khulna(S) | 142 | 16:00 | 133 | 00:00 | UttaraNew | 137 | 08:00 | 132 | 00:00
Khulshi | 136 | 18:30 | 130 | 00:00 | Zigatola | 136 | 12:00 | 132 | 00:00
Kishoreganj | 137 | 10:00 | 130 | 00:00
Kodda | 143 | 11:00 | 129 | 04:00
Korerhat | 138 | 15:00 | 131 | 00:00
KSRM | 138 | 18:30 | 132 | 00:00
Kulaura | 138 | 14:00 | 133 | 00:00
Kurigram | 140 | 07:00 | 120 | 17:00
Kushtia | 136 | 23:00 | 129 | 00:00
Laksam | 136 | 14:00 | 126 | 00:00
Lakshmipur | 135 | 15:00 | 125 | 00:00
Lalbag | 135 | 09:00 | 130 | 00:00
Lalmonirhat | 137 | 08:00 | 126 | 00:00
Madanganj | 143 | 12:00 | 136 | 00:00
Madaripur | 139 | 16:00 | 129 | 00:00
Madartek | 134 | 18:30 | 130 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division