## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 24-03-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-03-2026 | during | 24-03-2026 | during | 24-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 190 | 189 | 365 | 365 | 0 | 0 | GBC 1 and 3 under maintenance
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 93 | 97.7 | 97.7 | 7 | 7 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 313 | 343 | 412 | 412 | 412 | 412 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 160 | 225 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 40 | 81 | 210 | 210 | 0 | 210 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 230 | 335 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 49 | 49 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 7 | 10 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 7 | 7 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 104 | -
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 146 | 146 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 33 | 0 | 33 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 350 | 460 | 584 | 584 | 584 | 584 | FGMO
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 320 | 320 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 292 | 251 | 718 | 718 | 718 | 718 | FGMO
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 17 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1622 | 2011 | 5823.22 | 5790.22 | 3709.05 | 3990.05
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 80 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 182 | 223 | 220 | 220 | 220 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 56 | 64 | 56 | 64 | -
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 68 | 68 | 68 | 68 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 21 | 40 | 40 | 5 | 14 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 68 | 68 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.01 | 0 | 3.53 | 0 | 3.53 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 25 | 25 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 147 | 147 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 305 | 321 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 6 | 5 | 8 | 5 | 8 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 147 | 150 | 935 | 935 | 320 | 320 | U-1 Under Maintenance
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 741.01 | 818 | 3883.39 | 3870.86 | 2661.03 | 2657.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 199 | 199 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 315 | 295 | 342.01 | 342.01 | 342.01 | 342.01 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 310 | 393 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 42 | 41.65 | 41.65 | 46 | 46 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 25 | 55 | 55 | 20 | 20 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 102 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 0 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 16 | 16 | 32 | 32 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 100 | 163 | 163 | 100 | 100 | ST Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 180 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 42 | 48 | 84 | 80 | 84 | 80 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | -
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 104 | 104 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 62 | 0 | 75 | 0 | 75 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2876.261 | 998 | 1275 | 2405.36 | 2326.36 | 2177.21 | 2098.21
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-03-2026 | during | 24-03-2026 | during | 24-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 160 | 161 | 157.5 | 157.5 | 10 | 10 | GT-4 Under Maintenance
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 0 | 25 | 60 | 80 | 60 | 80 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 0 | 35 | 70 | 115 | 70 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 51.68 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 35 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 212.88 | 221 | 416.1 | 429 | 221.1 | 252
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 41 | 42 | 42 | 41 | 41 | GT-1 Under Maintenance
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 142 | 155 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 20 | 30 | 30 | 30 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 80 | 83 | 83 | 42 | 42 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 96 | 97 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 20 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 275 | 315 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 182 | 394 | 385 | 385 | 385 | 385 | -
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 768 | 1132 | 1189 | 1189 | 1094 | 1094
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 523 | 710 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 280 | 384 | 410 | 410 | 410 | 410 | -
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 79 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 374 | 539 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1256 | 1633 | 3602.2 | 3512.2 | 2841.1 | 2751.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 16 | 16 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 100 | 125 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 500 | 680 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 75 | 75 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 140 | 233 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.69 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 920.69 | 1258 | 2162 | 2161 | 1993 | 1992
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 47.47 | 0 | 61 | 0 | 61 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | IGV Not open
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 190 | 190 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 270 | 358 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 21 | 21 | 21 | 21 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 70 | 70 | 50 | 50 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.66 | 0 | 6 | 0 | 6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 829.46 | 1076.5 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 29.18 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 105 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1283.77 | 1434.5 | 3211.87 | 2983.87 | 2695.87 | 2467.87
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7 | 0 | 6.2 | 0 | 6.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 208 | 0 | 200 | 0 | 200 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 245 | 0 | 464.2 | 228 | 464.2 | 228
System Total |  |  |  |  | 28823.2 | 29275.503 | 8047.35 | 9782.5 | 23157.34 | 22490.51 | 17856.56 | 17530.73
Forecast Scenario (24-03-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8850 |  | 0 |  | 8850
|  |  |  | 1:00 | 8410 |  | 0 |  | 8410
|  |  |  | 2:00 | 7970 |  | 0 |  | 7970
|  |  |  | 3:00 | 7740 |  | 0 |  | 7740
|  |  |  | 4:00 | 7440 |  | 0 |  | 7440
|  |  |  | 5:00 | 7330 |  | 0 |  | 7330
|  |  |  | 6:00 | 7310 |  | 0 |  | 7310
|  |  |  | 7:00 | 7760 |  | 0 |  | 7760
|  |  |  | 8:00 | 8260 |  | 0 |  | 8260
|  |  |  | 9:00 | 8200 |  | 0 |  | 8200
|  |  |  | 10:00 | 8020 |  | 0 |  | 8020
|  |  |  | 11:00 | 8220 |  | 0 |  | 8220
|  |  |  | 12:00 | 8740 |  | 0 |  | 8740
|  |  |  | 13:00 | 9430 |  | 0 |  | 9430
|  |  |  | 14:00 | 9520 |  | 0 |  | 9520
|  |  |  | 15:00 | 9060 |  | 0 |  | 9060
|  |  |  | 16:00 | 8430 |  | 0 |  | 8430
|  |  |  | 17:00 | 8300 |  | 0 |  | 8300
|  |  |  | 18:00 | 8990 |  | 0 |  | 8990
|  |  |  | 18:30 | 10100 |  | 0 |  | 10100
|  |  |  | 19:00 | 10420 |  | 0 |  | 10420
|  |  |  | 19:30 | 10480 |  | 0 |  | 10480
|  |  |  | 20:00 | 10370 |  | 0 |  | 10370
|  |  |  | 21:00 | 10290 |  | 0 |  | 10290
|  |  |  | 22:00 | 10150 |  | 0 |  | 10150
|  |  |  | 23:00 | 9800 |  | 0 |  | 9800
Probable Maximum Temperature: |  |  | 31.00°C
Probable Maximum Demand at Day Peak: |  |  | 8740.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 10480.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10480.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 209.01 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:26 hrs on 24-03-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 23-03-2026 | [28 empty] | Date: | 23-03-2026 | [28 empty] | Date: | 23-03-2026 | [28 empty] | Date: | 23-03-2026 | [28 empty] | Date: | 23-03-2026 | [17 empty] | Date: | 23-03-2026
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [17 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 342.010 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 103 | 317 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 250 | 40 | 0 | 0 | 0 | 7 | 10 | 0 | 530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 330 | 0 | 330 | 0 | 0 | 188 | 0 | 0 | 104 | 0 | 0 | 20 | 0 | 44 | 0 | 0 | 0 | 305 | 0 | 72 | 41 | 0 | 148 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 96 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 4578 | 695 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 829.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 125 | 220 | 0 | 0 | 500 | 0 | 3575.1 | 8153.1 | 86.81
01:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 103 | 317 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 250 | 40 | 0 | 0 | 0 | 5 | 10 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 280 | 0 | 290 | 0 | 0 | 192 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 42 | 0 | 0 | 0 | 310 | 0 | 72 | 41 | 0 | 136 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 96 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 4148 | 743 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 835.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3566.23 | 7714.23 | 86.8
02:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 307 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 250 | 40 | 0 | 0 | 0 | 5 | 10 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 280 | 0 | 305 | 0 | 0 | 196 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 40 | 0 | 0 | 0 | 310 | 0 | 92 | 41 | 0 | 136 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 96 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 4081 | 383 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 832.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3189.85 | 7270.85 | 86.79
03:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 331 | 0 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 250 | 40 | 0 | 0 | 0 | 5 | 10 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 230 | 0 | 295 | 0 | 0 | 196 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 38 | 0 | 0 | 0 | 310 | 0 | 92 | 41 | 0 | 139 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 96 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 3991 | 233 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 834.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3050.9 | 7041.9 | 86.78
04:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 312 | 0 | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 250 | 40 | 0 | 0 | 0 | 5 | 10 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 230 | 0 | 250 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 38 | 0 | 0 | 0 | 310 | 0 | 92 | 33 | 0 | 136 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 96 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 3799 | 243 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 833.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 2948.99 | 6747.99 | 86.77
05:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 307 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 250 | 40 | 0 | 0 | 0 | 5 | 10 | 0 | 310 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 230 | 0 | 250 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 36 | 0 | 0 | 0 | 305 | 0 | 92 | 33 | 0 | 135 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 96 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 3787 | 243 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 833.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 2848.83 | 6635.83 | 86.76
06:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 310 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 250 | 40 | 0 | 0 | 0 | 5 | 10 | 0 | 310 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 230 | 0 | 250 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 0 | 8 | 0 | 36 | 0 | 0 | 0 | 305 | 0 | 92 | 33 | 0 | 137 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 96 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 3767 | 244 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 833.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 2852.01 | 6619.01 | 86.75
07:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 320 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 250 | 40 | 0 | 1 | 0 | 7 | 10 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57 | 80 | 0 | 2 | 148 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 305 | 3 | 0 | 0 | 280 | 0 | 315 | 0 | 0 | 183 | 0 | 0 | 50 | 0 | 0 | 19 | 0 | 38 | 0 | 11 | 0 | 315 | 0 | 92 | 33 | 0 | 141 | 2 | 0 | 0 | 0 | 17 | 0 | 0 | 96 | 0 | 0 | 0 | 164 | 0.2 | 6.1 | 0 | 4080.87 | 243 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.03 | 385 | 0 | 0 | 0 | 834.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.74 | 4 | 0 | 0 | 5.82 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0.55 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.3 | 22 | 0.08 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 2981.72 | 7062.59 | 86.74
08:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 320 | 0 | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 250 | 40 | 0 | 13 | 0 | 7 | 10 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.62 | 80 | 0 | 2 | 147 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 305 | 9 | 0 | 0 | 290 | 0 | 295 | 0 | 0 | 191 | 0 | 0 | 50 | 0 | 0 | 19 | 0 | 36 | 0 | 30 | 0 | 315 | 0 | 92 | 33 | 0 | 141 | 5 | 0 | 0 | 0 | 17 | 0 | 0 | 96 | 0 | 0 | 0 | 164 | 0.8 | 20.69 | 0 | 4158.11 | 522 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.03 | 362 | 0 | 0 | 0 | 828.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.09 | 37 | 0 | 0 | 23.24 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 2.01 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 2.9 | 76 | 0.22 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3401.99 | 7560.1 | 86.73
09:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 304 | 0 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 250 | 40 | 0 | 13 | 0 | 7 | 10 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.59 | 80 | 0 | 1 | 147 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 305 | 15 | 0 | 0 | 315 | 0 | 300 | 0 | 0 | 140 | 0 | 0 | 50 | 0 | 0 | 19 | 0 | 36 | 0 | 47 | 0 | 310 | 0 | 99 | 32 | 0 | 136 | 8 | 0 | 0 | 0 | 17 | 0 | 0 | 96 | 0 | 0 | 0 | 163 | 1.4 | 33.11 | 0 | 4082.1 | 522 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 380 | 0 | 0 | 0 | 830.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.2 | 40 | 0 | 0 | 36.15 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 3.5 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 5 | 134 | 0.39 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3417.5 | 7499.6 | 86.72
10:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 317 | 0 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 230 | 40 | 0 | 13 | 0 | 7 | 10 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.37 | 80 | 0 | 2 | 147 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 305 | 18 | 0 | 0 | 230 | 0 | 230 | 0 | 0 | 180 | 0 | 0 | 50 | 0 | 0 | 19 | 0 | 34 | 0 | 32 | 0 | 275 | 0 | 98.8 | 32 | 0 | 141 | 4 | 0 | 0 | 0 | 20 | 0 | 0 | 96 | 0 | 0 | 0 | 160 | 1.8 | 44.47 | 0 | 3910.44 | 522 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 392 | 0 | 0 | 0 | 835.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.2 | 42 | 0 | 0 | 50.92 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 4.47 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 6.3 | 100 | 0.53 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3417.48 | 7327.92 | 86.72
11:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 320 | 0 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 230 | 40 | 0 | 14 | 0 | 7 | 7 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.71 | 80 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 305 | 20 | 0 | 0 | 230 | 0 | 230 | 0 | 0 | 204 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 40 | 0 | 69 | 0 | 250 | 0 | 141 | 32 | 0 | 152 | 8 | 0 | 0 | 0 | 20 | 0 | 0 | 96 | 0 | 0 | 0 | 159 | 2.4 | 34.98 | 0 | 4002.09 | 523 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 381 | 0 | 0 | 0 | 827.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.77 | 102 | 0 | 0 | 38.17 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 2.98 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 6.7 | 143 | 0.62 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3526.6 | 7528.69 | 86.71
12:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 313 | 0 | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 230 | 40 | 0 | 33 | 0 | 7 | 7 | 0 | 350 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 4.01 | 80 | 0 | 2 | 147 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 305 | 20 | 0 | 0 | 310 | 0 | 315 | 0 | 0 | 199 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 42 | 0 | 62 | 0 | 275 | 0 | 182 | 41 | 0 | 142 | 4 | 8 | 0 | 0 | 20 | 0 | 0 | 96 | 0 | 0 | 0 | 160 | 1.2 | 51.68 | 0 | 4341.89 | 523 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 374 | 0 | 0 | 0 | 829.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.47 | 105 | 0 | 0 | 29.18 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 2.66 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 7 | 208 | 0.69 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3705.46 | 8047.35 | 86.71
13:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 346 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 230 | 99 | 0 | 16 | 0 | 7 | 7 | 0 | 410 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3.19 | 80 | 0 | 16 | 147 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 305 | 19 | 0 | 0 | 350 | 0 | 345 | 0 | 0 | 204 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 46 | 0 | 71 | 0 | 310 | 0 | 232 | 41 | 0 | 149 | 4 | 20 | 0 | 0 | 20 | 0 | 0 | 96 | 0 | 0 | 0 | 158 | 2.5 | 50.41 | 0 | 4730.1 | 523 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 379 | 0 | 0 | 0 | 833.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.65 | 91 | 0 | 0 | 63.54 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.24 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 7.3 | 152 | 0.63 | 0 | 140 | 115 | 220 | 0 | 0 | 500 | 0 | 4003.37 | 8733.47 | 86.7
14:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 26 | 318 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 40 | 0 | 29 | 0 | 7 | 7 | 0 | 400 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 1.01 | 80 | 0 | 21 | 180 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 305 | 17 | 0 | 8 | 298 | 0 | 290 | 13 | 0 | 187 | 20 | 0 | 98 | 0 | 0 | 20 | 0 | 48 | 0 | 59 | 0 | 310 | 0 | 287 | 41 | 0 | 146 | 6 | 20 | 0 | 80 | 30 | 0 | 0 | 96 | 0 | 0 | 0 | 158 | 1.5 | 19.88 | 0 | 4886.39 | 522 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 374 | 0 | 0 | 0 | 826.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.02 | 78 | 0 | 0 | 54.84 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 4.04 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 4.4 | 190 | 0.59 | 0 | 140 | 125 | 220 | 0 | 0 | 535 | 0 | 3933.81 | 8820.2 | 86.7
15:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 26 | 292 | 0 | 242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 335 | 40 | 0 | 22 | 0 | 10 | 7 | 0 | 400 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0.85 | 80 | 0 | 21 | 180 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 305 | 14 | 0 | 8 | 298 | 0 | 285 | 20 | 0 | 192 | 20 | 0 | 98 | 0 | 0 | 20 | 0 | 44 | 0 | 21 | 0 | 305 | 0 | 335 | 41 | 0 | 133 | 9 | 8 | 0 | 80 | 30 | 0 | 0 | 96 | 0 | 12 | 16 | 157 | 0.6 | 37.86 | 0 | 4838.31 | 383 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 370 | 0 | 0 | 0 | 833.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.27 | 22 | 0 | 0 | 45.59 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 2.51 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 4.7 | 152 | 0.35 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3521.77 | 8360.08 | 86.69
16:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 7 | 294 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 290 | 40 | 0 | 15 | 0 | 10 | 7 | 0 | 310 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0.79 | 80 | 0 | 5 | 150 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 305 | 9 | 0 | 8 | 314 | 0 | 305 | 5 | 5 | 199 | 5 | 0 | 50 | 0 | 0 | 20 | 0 | 40 | 0 | 29 | 0 | 310 | 0 | 391 | 33 | 0 | 134 | 5 | 8 | 0 | 5 | 20 | 0 | 0 | 96 | 0 | 24 | 16 | 157 | 0.9 | 18.79 | 0 | 4547.48 | 241 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 378 | 0 | 0 | 0 | 831.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.69 | 36 | 0 | 0 | 26.95 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 2.36 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 3.7 | 94 | 0.14 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3185.34 | 7732.82 | 86.69
17:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 7 | 313 | 0 | 257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 280 | 40 | 0 | 5 | 0 | 10 | 7 | 0 | 315 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0.28 | 80 | 0 | 5 | 150 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 305 | 3 | 0 | 8 | 318 | 0 | 305 | 5 | 5 | 203 | 5 | 0 | 51 | 0 | 0 | 20 | 0 | 40 | 0 | 10 | 0 | 315 | 0 | 394 | 33 | 0 | 140 | 2 | 8 | 0 | 5 | 20 | 0 | 0 | 96 | 0 | 24 | 16 | 157 | 0.3 | 6.5 | 0 | 4527.08 | 241 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 384 | 0 | 0 | 0 | 835.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.76 | 18 | 0 | 0 | 9.91 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0.85 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 1.7 | 41 | 0.87 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3075.86 | 7602.94 | 86.68
18:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 50 | 311 | 0 | 283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 40 | 0 | 0 | 0 | 10 | 7 | 0 | 405 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 20 | 208 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 390 | 0 | 0 | 45 | 350 | 0 | 330 | 17 | 5 | 202 | 38 | 0 | 50 | 0 | 0 | 20 | 0 | 44 | 0 | 0 | 0 | 315 | 0 | 394 | 33 | 0 | 140 | 0 | 8 | 0 | 5 | 20 | 0 | 0 | 96 | 0 | 24 | 16 | 159 | 0 | 0.03 | 0 | 4996.03 | 240 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 490 | 0 | 0 | 0 | 938.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 3 | 0 | 0 | 181 | 100 | 180 | 0 | 0 | 522 | 0 | 3300.41 | 8296.44 | 86.67
19:00 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 87 | 333 | 0 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 335 | 109 | 0 | 0 | 17 | 10 | 7 | 0 | 420 | 0 | 0 | 0 | 0 | 7 | 17 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 21 | 150 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 400 | 0 | 0 | 102 | 332 | 0 | 300 | 51 | 21 | 195 | 42 | 0 | 100 | 0 | 0 | 20 | 0 | 48 | 0 | 0 | 0 | 310 | 0 | 394 | 41 | 0 | 155 | 0 | 20 | 0 | 80 | 30 | 0 | 0 | 96 | 0 | 35 | 35 | 160 | 0 | 0 | 0 | 5402 | 678 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 601 | 0 | 0 | 0 | 1082.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 125 | 220 | 0 | 0 | 624 | 0 | 4318.34 | 9720.34 | 86.66
19:30 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 93 | 343 | 0 | 251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 81 | 0 | 0 | 17 | 10 | 7 | 0 | 460 | 0 | 0 | 0 | 0 | 6 | 17 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 21 | 150 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 321 | 0 | 0 | 102 | 393 | 0 | 295 | 51 | 25 | 199 | 42 | 0 | 100 | 0 | 0 | 20 | 0 | 48 | 0 | 0 | 0 | 315 | 0 | 394 | 41 | 0 | 155 | 0 | 20 | 0 | 80 | 30 | 0 | 0 | 97 | 0 | 35 | 25 | 161 | 0 | 0 | 0 | 5457 | 710 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539 | 0 | 0 | 0 | 1076.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 125 | 220 | 0 | 0 | 680 | 0 | 4325.5 | 9782.5
20:00 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 95 | 335 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 144 | 0 | 0 | 0 | 10 | 7 | 0 | 530 | 0 | 0 | 0 | 0 | 7 | 17 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 21 | 150 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 308 | 0 | 0 | 65 | 370 | 0 | 340 | 51 | 23 | 175 | 42 | 0 | 102 | 0 | 0 | 20 | 0 | 48 | 0 | 0 | 0 | 315 | 0 | 394 | 41 | 0 | 156 | 0 | 20 | 0 | 80 | 30 | 0 | 0 | 96 | 0 | 35 | 16 | 160 | 0 | 0 | 0 | 5552 | 709 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 457 | 0 | 0 | 0 | 1031.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 125 | 220 | 0 | 0 | 680 | 0 | 4124.77 | 9676.77 | 86.65
21:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 95 | 334 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 209 | 0 | 0 | 0 | 10 | 7 | 0 | 530 | 0 | 0 | 0 | 0 | 11 | 17 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 23 | 150 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 307 | 0 | 0 | 8 | 260 | 0 | 330 | 51 | 5 | 192 | 20 | 0 | 102 | 0 | 0 | 20 | 0 | 48 | 0 | 0 | 0 | 310 | 0 | 394 | 41 | 0 | 155 | 0 | 20 | 0 | 80 | 30 | 0 | 0 | 96 | 0 | 8 | 8 | 162 | 0 | 0 | 0 | 5381 | 710 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 452 | 0 | 0 | 0 | 1030.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 125 | 220 | 0 | 0 | 718 | 0 | 4214.44 | 9595.44 | 86.64
22:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 93 | 330 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 209 | 0 | 0 | 0 | 10 | 7 | 0 | 530 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 23 | 150 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 280 | 0 | 330 | 51 | 0 | 192 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 48 | 0 | 0 | 0 | 310 | 0 | 394 | 41 | 0 | 154 | 0 | 20 | 0 | 80 | 30 | 0 | 0 | 96 | 0 | 8 | 8 | 163 | 0 | 0 | 0 | 5336 | 710 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 0 | 0 | 986.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 125 | 220 | 0 | 0 | 750 | 0 | 4123.18 | 9459.18 | 86.63
23:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 90 | 322 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 209 | 0 | 0 | 0 | 10 | 7 | 0 | 450 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 150 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 300 | 0 | 305 | 51 | 0 | 196 | 0 | 0 | 102 | 0 | 0 | 14 | 0 | 48 | 0 | 0 | 0 | 310 | 0 | 394 | 41 | 0 | 152 | 0 | 20 | 0 | 80 | 30 | 0 | 0 | 96 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 5234 | 710 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 820.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 125 | 220 | 0 | 0 | 650 | 0 | 3828.22 | 9062.22 | 86.62
Total KWH | 0 | 0 | 0 | 4548991 | 0 | 0 | 0 | 771545.46 | 7776000 | 0 | 6822870 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4627300 | 0 | 0 | 0 | 0 | 6766394 | 1912000 | 0 | 183242 | 9600 | 225000 | 221760 | 0 | 9389090.91 | 0 | 0 | 0 | 0 | 81600 | 42048 | 0 | 0 | 0 | 0 | 22441 | 1922160 | 0 | 246720 | 3781818.18 | 0 | 0 | 0 | 0 | 0 | 4372313 | 0 | 0 | 0 | 7532727 | 148500 | 0 | 267636 | 7039000 | 0 | 7212000 | 397988 | 67680 | 4635000 | 200232 | 0 | 1652596 | 0 | 0 | 454970 | 0 | 1000320 | 0 | 444736 | 0 | 7419000 | 0 | 5574000 | 888000 | 0 | 3449372.73 | 69020 | 206736 | 0 | 632640 | 534720 | 0 | 0 | 2311050 | 0 | 204000 | 139200 | 3419520 | 13250 | 323970 | 0 | 109960757.28 | 11170909 | 7622496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 599760 | 9541818 | 0 | 0 | 0 | 20956363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333944 | 565240 | 0 | 0 | 375008 | 0 | 0 | 0 | 0 | 0 | 0 | 7912000 | 0 | 33360 | 0 | 0 | 0 | 255797 | 0 | 0 | 0 | 0 | 47476.2 | 1346400 | 4354 | 0 | 3687000 | 2590000 | 5040100 | 0 | 0 | 13802181.82 | 0 | 85884207.02 | 195844964.3

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 23-03-2026
Power Supply Scenario
| Day Peak Generation |  |  | 8047.35 | MW | 12:00 Hr. | Energy Generated |  |  | 195.845 |  | MKWHr.
| Day Peak Demand |  |  | 8047.35 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 9782.5 | MW | 19:30 Hr. | Energy Demand |  |  | 195.845 |  | MKWHr.
| Evening Peak Demand |  |  | 9782.5 | MW | 19:30 Hr. | Maximum Temperature |  |  | 29.9 |  | °C
| Minimum Generation of the Day |  |  | 6619.01 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 887.51 |  | MMCFD
| Maximum Generation of the Day |  |  | 9782.5 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 4.8522 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 43.061 | 0 | 0.0096 | 0 | 0 | 0.18324 | 0 | 0 | 43.2538 | Gas | 117.2067 | Gas | 415720427.0473
| Chattogram Zone |  |  | 4.619 | 11.3145 | 0.042048 | 0 | 1.9222 | 0.17094 | 0 | 0.0816 | 18.1503 | Coal | 38.3455 | Coal | 256756101.366
| Cumilla Zone |  |  | 21.9271 | 0 | 0 | 0 | 0 | 0.44474 | 1.0003 | 0 | 23.3722 | HFO | 0.39485 | HFO | 6582427.2
| Mymensingh Zone |  |  | 3.4195 | 0 | 0.3432 | 0 | 0 | 0.33722 | 0 | 0 | 4.0999 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 21.0155 | 0 | 0 | 0 | 0 | 0.06902 | 0 | 0 | 21.0845 | Hydro | 1.9222 | Hydro | 192216
| Khulna Zone |  |  | 7.6225 | 9.5418 | 0 | 0 | 0 | 0.59976 | 11.1709 | 0 | 28.935 | Solar | 4.7665 | Solar | 77379595.87
| Barishal Zone |  |  | 7.6301 | 17.4892 | 0 | 0 | 0 | 0.004354 | 0 | 0 | 25.1236 | Import | 33.1276 | Import | 192449024.92
| Rajshahi Zone |  |  | 7.912 | 0 | 0 | 0 | 0 | 1.3076 | 20.9564 | 0 | 30.1759 | Wind | 0.0816 | Wind | 1200336
| Rangpur Zone |  |  | 0 | 0 | 0 | 0 | 0 | 1.6497 | 0 | 0 | 1.6497
| Total |  |  | 117.2067 | 38.3455 | 0.39485 | 0 | 1.9222 | 4.7665 | 33.1276 | 0.0816 | 195.845
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 415720427.0473 |  | Hydro | 192216
|  |  |  | Coal | 256756101.366 |  | Solar | 77379595.87
|  |  |  | HFO | 6582427.2 |  | Import | 192449024.92
|  |  |  | HSD | 0 |  | Wind | 1200336
[5 empty] | Total: | 95,02,80,128 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 65236.37 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 11.1709 | Peak Hr Flow | 710.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 15263472.73 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 20.9564 | Peak Hr Flow | 1076.50 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 789 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0003 | Peak Hr Flow | 48.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 911 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 33.1276 | Peak Hr Flow | 1834.50 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 2516
|  |  |  | Chattogram |  | 0 |  | 1188
|  |  |  | Cumilla |  | 0 |  | 1018
|  |  |  | Mymensingh |  | 0 |  | 911
|  |  |  | Sylhet |  | 0 |  | 405
|  |  |  | Khulna |  | 0 |  | 1320
|  |  |  | Barishal |  | 0 |  | 341
|  |  |  | Rajshahi |  | 0 |  | 1047
|  |  |  | Rangpur |  | 0 |  | 677
|  |  |  | Total |  | 0 |  | 9423
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:35 | Sylhet 132/33kV S/S T4 HT is restored.
|  | 08:36 | Sylhet 132/33kV S/S T4 LT is restored.
| 08:55 | 12:42 | Bashundhara-Rampura 132 kV Ckt-1 Scheduled S/D from Rampura 230/132kV end Due to Annual
maintenance
| 09:42 |  | Bibiyana-3 400 MW CCPP ST was sync.
| 09:42 |  | Bibiyana-III 400 MW CCPP Synchronized with remarks:- STG
| 12:00 |  | Day Peak Generation: 8044 MW.
|  | 12:29 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T LT is restored.
| 19:30 |  | Evening peak generation: 9782 MW
| 02:32 |  | Haripur-Rahim Steel 132 kV ckt tripped showing distance zone-1, O/C and E/F relay.
| 06:00 |  | Minimum Generation: 7382 MW
| 06:26 |  | Sirajgonj 225MW CCPP Unit-3 Synchronized with remarks:- GT
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 23-03-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 189 | 4548991 | plant availability zero
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 93 | 771545.46 | On test
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 343 | 7776000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4627300 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 81 | 1912000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 6766394 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 10 | 225000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 7 | 221760 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 0 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 183242 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 460 | 9389090.91 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 251 | 6822870 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 17 | 9600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2011 | 43253793.37
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 148500 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1922160 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 223 | 4372313 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 42048 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 21 | 246720 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22441 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 321 | 7532727 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 6 | 81600 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 150 | 3781818.18 | Coal shortage
Chattogram Area Total |  |  |  |  | 4898.863 | 818 | 18150327.18
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 199 | 4635000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 295 | 7212000 | Able to ON FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 7039000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 42 | 200232 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 25 | 67680 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 102 | 267636 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 397988 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 1652596 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 48 | 1000320 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 454970 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 444736 | -
Cumilla Area Total |  |  |  |  | 2876.261 | 1275 | 23372158
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 161 | 3419520 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13250 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 25 | 139200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 35 | 204000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 323970 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | From12:00 hrs to24:00 hrs will be dispatching12MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 221 | 4099940
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 69020 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 888000 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3449372.73 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 534720 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 632640 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 97 | 2311050 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 20 | 206736 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7419000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 394 | 5574000 | Due to Air Filter DP High FGMO not available.
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1132 | 21084538.73
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 710 | 11170909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 384 | 7622496 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 599760 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 539 | 9541818 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1633 | 28934983
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 125 | 2590000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 680 | 13802181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5040100 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 233 | 3687000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4354 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1258 | 25123635.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 333944 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 358 | 7912000 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | machine problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 33360 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1076.5 | 20956363 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 375008 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 565240 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1434.5 | 30175915
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 47476.2 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 0 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 255797 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1346400 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 0 | 1649673.2
Eastern Grid Total |  |  |  |  | 17423.308 | 5457 | 109960757.28
Western Grid Total |  |  |  |  | 11852.195 | 4325.5 | 85884207.02
National Grid Total |  |  |  |  | 29275.503 | 9782.5 | 195844964.3
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 23-03-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6037.7 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3384.6 | MW
i) Dhaka area |  |  | 2515.7 |  | MW | i) Khulna area |  |  |  | 1320 | MW
ii) Chattogram area |  |  | 1188 |  | MW | ii) Barishal area |  |  |  | 341 | MW
iii) Cumilla area |  |  | 1018 |  | MW | iii) Rajshahi area |  |  |  | 1046.6 | MW
iv) Mymensingh area |  |  | 911 |  | MW | iv) Rangpur area |  |  |  | 677 | MW
v) Sylhet area |  |  | 405 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 9422.3 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 35 | 21:00 | 133 | Nawabganj | 41.8 | 14:00
2 | AKSML | 18 | 19:00 | 68 | Hathazari | 61 | 19:00 | 134 | Netrakona | 118 | 18:30
3 | Aftabnagar | 20 | 00:00 | 69 | Hatirjheel | 16 | 14:00 | 135 | New | 26 | 19:00
4 | Agargaon | 57 | 13:00 | 70 | Ishurdi | 46 | 19:00 | 136 | Niamatpur | 66 | 19:00
5 | Agrabad | 44 | 11:00 | 71 | Jaldhaka | 58 | 19:00 | 137 | Noapara | 30 | 19:00
6 | Amnura | 25 | 13:00 | 72 | Jamalpur | 97 | 19:00 | 138 | PHP | 10 | 17:00
7 | Ashuganj | 43 | 13:00 | 73 | Jashore | 115 | 19:00 | 139 | Pabna | 62 | 19:00
8 | BSRM | 201 | 23:00 | 74 | Jhenaidah | 93 | 19:30 | 140 | Palashbari | 84 | 19:00
9 | Bagerhat | 63 | 19:00 | 75 | Joydebpur | 57 | 18:30 | 141 | Panchagarh | 39 | 19:30
10 | Bajitpur | 74 | 18:30 | 76 | Joypurhat | 44 | 19:00 | 142 | Patiya | 8 | 19:00
11 | Bakerganj | 8.4 | 21:00 | 77 | Juldah | 17.5 | 15:00 | 143 | Patuakhali | 50 | 22:00
12 | Bakulia | 53 | 21:00 | 78 | KSRM | 5.5 | 18:00 | 144 | Payra | 24 | 00:00
13 | Banani | 10.2 | 19:30 | 79 | Kabirpur | 90 | 18:00 | 145 | Postogola | 25 | 23:00
14 | Bangabhaban | 3 | 00:00 | 80 | Kachua | 71 | 18:30 | 146 | Pubail | 13 | 13:00
15 | Barapukuria | 42 | 21:00 | 81 | Kaliganj | 24 | 18:30 | 147 | Purbachal | 17 | 18:30
16 | Barguna | 16 | 21:00 | 82 | Kallyanpur | 63 | 21:00 | 148 | Purbasadipur | 73 | 19:00
17 | Barishal | 68 | 21:00 | 83 | Kalurghat | 18 | 00:00 | 149 | Rahanpur | 27 | 19:30
18 | Barishal-230 | 74 | 19:00 | 84 | Kamrangirchar | 28 | 13:00 | 150 | Rahim | 1 | 02:00
19 | Baroaulia | 48 | 19:00 | 85 | Kaptai | N/A | N/A | 151 | Rajbari | 54 | 19:00
20 | Baroirhat | 42 | 18:30 | 86 | Kasba | 27 | 19:00 | 152 | Rajendrapur | 70 | 20:00
21 | Bashundhara | 93 | 13:00 | 87 | Kazla | 39 | 22:00 | 153 | Rajshahi | 86 | 19:00
22 | BashundharaCement | 0 | 00:00 | 88 | Keranigonj | 50 | 14:00 | 154 | Rajshahi-230 | 50 | 13:00
23 | Beanibazar | 46 | 18:30 | 89 | Khagrachori | 26 | 19:00 | 155 | Ramganj | 78 | 18:30
24 | Benapole | 58 | 19:00 | 90 | Khulna | 38 | 13:00 | 156 | Rampur | 28 | 21:00
25 | Bhaluka | 96 | 19:00 | 91 | Khulshi | 130 | 21:00 | 157 | Rangamati | 13 | 12:00
26 | Bhandaria | 42 | 21:00 | 92 | Kishoreganj | 104 | 18:30 | 158 | Rangpur | 100 | 19:00
27 | Bhangura | 30 | 08:00 | 93 | Kodda | 106 | 18:30 | 159 | Ruppur | 5.2 | 06:00
28 | Bheramara(GK) | 43 | 19:00 | 94 | Kulaura | 28 | 18:30 | 160 | SSM | 0 | 00:00
29 | Bhulta | 77 | 19:30 | 95 | Kurigram | 50 | 08:00 | 161 | Saidpur | 61 | 19:00
30 | Bog-Sherpur | 56 | 19:00 | 96 | Kushtia | 91 | 19:00 | 162 | Satkhira | 114 | 19:00
31 | Bogura | 110 | 21:00 | 97 | Laksam | 25 | 21:00 | 163 | Satmasjid | 53 | 14:00
32 | Borhanuddin | 76 | 21:00 | 98 | Lakshmipur | 26 | 14:00 | 164 | Savar | 82 | 22:00
33 | Brahmanbaria | 101 | 19:00 | 99 | Lalbag | 15 | 13:00 | 165 | SevenRings | 5.11 | 12:00
34 | Cantonment | 86 | 13:00 | 100 | Lalmonirhat | 46 | 19:00 | 166 | ShahCement | 39 | 09:00
35 | Chandina | 14 | 23:00 | 101 | MI_Cement | 1.3 | 12:00 | 167 | Shahjadpur | 53 | 19:00
36 | Chandpur | 56 | 13:00 | 102 | Madanganj | 22 | 13:00 | 168 | Shahjibazar | 92 | 21:00
37 | Chandraghona | 31 | 18:30 | 103 | Madaripur | 74 | 22:00 | 169 | Shahmirpur | 36 | 19:30
38 | Chapai | 50 | 20:00 | 104 | Madartek | 44 | 13:00 | 170 | Shariatpur | 64 | 22:00
39 | Charsaidpur | 22 | 18:30 | 105 | Madunaghat | 41 | 19:00 | 171 | Sherpur | 118 | 19:00
40 | Chauddagram | 59 | 18:30 | 106 | Magura | 54 | 19:00 | 172 | Shikalbaha | 17 | 19:00
41 | Chhatak | 24 | 18:30 | 107 | Mahasthangarh | 57 | 19:00 | 173 | Shitalakhya | 33.9 | 14:00
42 | Chowmuhani | 113 | 19:00 | 108 | Maijdee | 39 | 21:00 | 174 | Sholosohor | 24 | 00:00
43 | Chuadanga | 89 | 18:30 | 109 | Manikganj | 80 | 19:00 | 175 | Shyampur | 33 | 23:00
44 | Coxsbazar | 116 | 19:00 | 110 | Maniknagar | 38 | 14:00 | 176 | Siddhirganj | 53 | 13:00
45 | Cumilla(N) | 85 | 18:30 | 111 | Matarbari | 44 | 18:30 | 177 | Sirajganj | 76 | 19:00
46 | Cumilla(S) | 103 | 19:00 | 112 | Matuail | 24 | 22:00 | 178 | Sonargaon | 41 | 19:00
47 | Daganbhuiyan | 31 | 00:00 | 113 | Metrorail_Motijheel | 20 | 13:00 | 179 | Sreemongol | 53 | 19:30
48 | Daudkandi | 92 | 21:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sreepur | 48 | 19:00
49 | DhakaUniversity | 18 | 12:00 | 115 | Millgate | 30 | 21:00 | 181 | Srinagar | 36.4 | 14:00
50 | Dhamrai | 56 | 21:00 | 116 | Mirpur | 71 | 14:00 | 182 | Sunamganj | 41 | 19:00
51 | Dhanmondi | 41.2 | 19:30 | 117 | Mirsorai | 7 | 21:00 | 183 | Sylhet | 41 | 18:30
52 | Dohazari | 91 | 20:00 | 118 | Mirzapur | 38 | 13:00 | 184 | Sylhet-132 | 66 | 18:30
53 | Faridpur | 104 | 19:30 | 119 | Mithapukur | 54 | 08:00 | 185 | TK | 17 | 00:00
54 | Fatullah | 39 | 23:00 | 120 | Modern | N/A | N/A | 186 | Tangail | 128 | 18:30
55 | Fenchuganj | 27 | 18:30 | 121 | Mogbazar | 24.8 | 13:00 | 187 | Taraganj | 15 | 19:00
56 | Feni | 72 | 18:30 | 122 | Mongla | 20 | 18:30 | 188 | Tasnim | 16 | 16:00
57 | GPH | 75 | 19:30 | 123 | Motijheel | 19 | 19:00 | 189 | Thakurgaon | 73 | 19:30
58 | Ghatail | 76 | 19:00 | 124 | Muktagacha | 29 | 18:30 | 190 | Tongi | 57 | 21:00
59 | Ghorashal | 57 | 09:00 | 125 | Munshiganj | 72 | 14:00 | 191 | Ullahpara | 30 | 07:00
60 | Ghorashal-230 | 56 | 21:00 | 126 | Muradnagar | 30 | 20:00 | 192 | Ullon | 31 | 13:00
61 | Goalpara | 27 | 13:00 | 127 | Mymensingh | 150 | 18:30 | 193 | Uttara | 43 | 19:00
62 | Gollamari | 64 | 13:00 | 128 | Naogaon | 85 | 20:00 | 194 | UttaraNew | 17 | 21:00
63 | Gopalganj | 84 | 19:00 | 129 | Narail | 48 | 19:00 | 195 | Zigatola | 51 | 13:00
64 | Gulshan | 50 | 13:00 | 130 | Narinda | 24 | 13:00
65 | Halishahar | 48.5 | 19:00 | 131 | Narshingdi | 102 | 21:00
66 | HaripurSBU | 52 | 23:00 | 132 | Natore | 119 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 23-03-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 8153.1 | 0 |  | 8153.1
1:00 | 7714.23 | 0 |  | 7714.23
2:00 | 7270.85 | 0 |  | 7270.85
3:00 | 7041.9 | 0 |  | 7041.9
4:00 | 6747.99 | 0 |  | 6747.99
5:00 | 6635.83 | 0 |  | 6635.83
6:00 | 6619.01 | 0 |  | 6619.01
7:00 | 7062.59 | 0 |  | 7062.59
8:00 | 7560.1 | 0 |  | 7560.1
9:00 | 7499.6 | 0 |  | 7499.6
10:00 | 7327.92 | 0 |  | 7327.92
11:00 | 7528.69 | 0 |  | 7528.69
12:00 | 8047.35 | 0 |  | 8047.35
13:00 | 8733.47 | 0 |  | 8733.47
14:00 | 8820.2 | 0 |  | 8820.2
15:00 | 8360.08 | 0 |  | 8360.08
16:00 | 7732.82 | 0 |  | 7732.82
17:00 | 7602.94 | 0 |  | 7602.94
18:00 | 8296.44 | 0 |  | 8296.44
19:00 | 9720.34 | 0 |  | 9720.34
19:30 | 9782.5 | 0 |  | 9782.5
20:00 | 9676.77 | 0 |  | 9676.77
21:00 | 9595.44 | 0 |  | 9595.44
22:00 | 9459.18 | 0 |  | 9459.18
23:00 | 9062.22 | 0 |  | 9062.22
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 23-03-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4578 | 3575.1 | 8153.1 | DAILY GENERATION CURVE
00:30 | 4363 | 3570.665 | 7933.665
01:00 | 4148 | 3566.23 | 7714.23 | 23-03-2026
01:30 | 4114.5 | 3378.04 | 7492.54
02:00 | 4081 | 3189.85 | 7270.85
02:30 | 4036 | 3120.375 | 7156.375
03:00 | 3991 | 3050.9 | 7041.9
03:30 | 3895 | 2999.945 | 6894.945
04:00 | 3799 | 2948.99 | 6747.99
04:30 | 3793 | 2898.91 | 6691.91
05:00 | 3787 | 2848.83 | 6635.83
05:30 | 3777 | 2850.42 | 6627.42
06:00 | 3767 | 2852.01 | 6619.01
06:30 | 3923.935 | 2916.865 | 6840.8
07:00 | 4080.87 | 2981.72 | 7062.59
07:30 | 4119.49 | 3191.855 | 7311.345
08:00 | 4158.11 | 3401.99 | 7560.1
08:30 | 4120.105 | 3409.745 | 7529.85
09:00 | 4082.1 | 3417.5 | 7499.6
09:30 | 3996.27 | 3417.49 | 7413.76
10:00 | 3910.44 | 3417.48 | 7327.92
10:30 | 3956.265 | 3472.04 | 7428.305
11:00 | 4002.09 | 3526.6 | 7528.69
11:30 | 4171.99 | 3616.03 | 7788.02
12:00 | 4341.89 | 3705.46 | 8047.35
12:30 | 4535.995 | 3854.415 | 8390.41
13:00 | 4730.1 | 4003.37 | 8733.47
13:30 | 4808.245 | 3968.59 | 8776.835
14:00 | 4886.39 | 3933.81 | 8820.2
14:30 | 4862.35 | 3727.79 | 8590.14
15:00 | 4838.31 | 3521.77 | 8360.08
15:30 | 4692.895 | 3353.555 | 8046.45
16:00 | 4547.48 | 3185.34 | 7732.82
16:30 | 4537.28 | 3130.6 | 7667.88
17:00 | 4527.08 | 3075.86 | 7602.94
17:30 | 4761.555 | 3188.135 | 7949.69
18:00 | 4996.03 | 3300.41 | 8296.44
18:30 | 5199.015 | 3809.375 | 9008.39
19:00 | 5402 | 4318.34 | 9720.34
19:30 | 5457 | 4325.5 | 9782.5
20:00 | 5552 | 4124.77 | 9676.77
20:30 | 5466.5 | 4169.605 | 9636.105 |  | Executive Engineer
21:00 | 5381 | 4214.44 | 9595.44 |  | Network Operation Division
21:30 | 5358.5 | 4168.81 | 9527.31
22:00 | 5336 | 4123.18 | 9459.18
22:30 | 5285 | 3975.7 | 9260.7
23:00 | 5234 | 3828.22 | 9062.22

## En-Curve
QF-LDC-12
Date | 23-03-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3192 | 1853 | 695 | 0 | 44 | 829.1 | 80 | 1460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3058.5 | 1738.5 | 719 | 0 | 43 | 832.165 | 80 | 1462.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23-03-2026
01:00 | 2925 | 1624 | 743 | 0 | 42 | 835.23 | 80 | 1465 | 0 | 0 | 0 | 0 | 0 | 0 | 0
01:30 | 2932.5 | 1577.5 | 563 | 0 | 41 | 834.04 | 80 | 1464.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Generated | 195.845 |  | MKWHr
02:00 | 2940 | 1531 | 383 | 0 | 40 | 832.85 | 80 | 1464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2924.5 | 1504.5 | 308 | 0 | 39 | 833.875 | 80 | 1466.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total Energy Requirement | 195.845 |  | MKWHr
03:00 | 2909 | 1478 | 233 | 0 | 38 | 834.9 | 80 | 1469 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2794.5 | 1440.5 | 238 | 0 | 38 | 834.445 | 80 | 1469.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:00 | 2680 | 1403 | 243 | 0 | 38 | 833.99 | 80 | 1470 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2629 | 1399 | 243 | 0 | 37 | 833.91 | 80 | 1468.5 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0
05:00 | 2578 | 1395 | 243 | 0 | 36 | 833.83 | 80 | 1467 | 0 | 0 | 0 | 0 | 0 | 3 | 0
05:30 | 2580 | 1382.5 | 243.5 | 0 | 36 | 833.42 | 80 | 1468 | 0 | 0 | 0 | 0 | 0 | 4 | 0
06:00 | 2582 | 1370 | 244 | 0 | 36 | 833.01 | 80 | 1469 | 0 | 0 | 0 | 0 | 0 | 5 | 0
06:30 | 2722 | 1412 | 243.5 | 0 | 37 | 833.605 | 80 | 1473.5 | 36.695 | 0 | 0 | 0 | 0 | 2.5 | 0
07:00 | 2862 | 1454 | 243 | 0 | 38 | 834.2 | 80 | 1478 | 73.39 | 0 | 0 | 0 | 0 | 0 | 0
07:30 | 2868.5 | 1467 | 382.5 | 0 | 37 | 831.35 | 80 | 1466 | 178.995 | 0 | 0 | 0 | 0 | 0 | 0
08:00 | 2875 | 1480 | 522 | 0 | 36 | 828.5 | 80 | 1454 | 284.6 | 0 | 0 | 0 | 0 | 0 | 0
08:30 | 2796.5 | 1438 | 522 | 0 | 36 | 829.38 | 80 | 1463 | 364.97 | 0 | 0 | 0 | 0 | 0 | 0
09:00 | 2718 | 1396 | 522 | 0 | 36 | 830.26 | 80 | 1472 | 445.34 | 0 | 0 | 0 | 0 | 0 | 0
09:30 | 2646.9 | 1374 | 522 | 0 | 35 | 832.66 | 80 | 1478 | 445.2 | 0 | 0 | 0 | 0 | 0 | 0
10:00 | 2575.8 | 1352 | 522 | 0 | 34 | 835.06 | 80 | 1484 | 445.06 | 0 | 0 | 0 | 0 | 0 | 0
10:30 | 2609.9 | 1343 | 522.5 | 0 | 37 | 831.21 | 80 | 1478.5 | 526.195 | 0 | 0 | 0 | 0 | 0 | 0
11:00 | 2644 | 1334 | 523 | 0 | 40 | 827.36 | 80 | 1473 | 607.33 | 0 | 0 | 0 | 0 | 0 | 0
11:30 | 2811 | 1388.5 | 523 | 0 | 41 | 828.41 | 80 | 1469.5 | 646.11 | 0 | 0 | 0 | 0 | 0.5 | 0
12:00 | 2978 | 1443 | 523 | 0 | 42 | 829.46 | 80 | 1466 | 684.89 | 0 | 0 | 0 | 0 | 1 | 0
12:30 | 3236 | 1533 | 523 | 0 | 44 | 831.235 | 80 | 1468.5 | 672.675 | 0 | 0 | 0 | 0 | 2 | 0
13:00 | 3494 | 1623 | 523 | 0 | 46 | 833.01 | 80 | 1471 | 660.46 | 0 | 0 | 0 | 0 | 3 | 0
13:30 | 3461.5 | 1683 | 522.5 | 0 | 47 | 829.965 | 80 | 1502.5 | 643.87 | 0 | 0 | 0 | 0 | 6.5 | 0
14:00 | 3429 | 1743 | 522 | 0 | 48 | 826.92 | 80 | 1534 | 627.28 | 0 | 0 | 0 | 0 | 10 | 0
14:30 | 3410 | 1691.5 | 452.5 | 0 | 46 | 830.135 | 80 | 1514.5 | 543.005 | 0 | 14 | 0 | 0 | 8.5 | 0
15:00 | 3391 | 1640 | 383 | 0 | 44 | 833.35 | 80 | 1495 | 458.73 | 0 | 28 | 0 | 0 | 7 | 0
15:30 | 3319 | 1544.5 | 312 | 0 | 42 | 832.425 | 80 | 1484 | 390.025 | 0 | 34 | 0 | 0 | 8.5 | 0
16:00 | 3247 | 1449 | 241 | 0 | 40 | 831.5 | 80 | 1473 | 321.32 | 0 | 40 | 0 | 0 | 10 | 0
16:30 | 3263.5 | 1458 | 241 | 0 | 40 | 833.635 | 80 | 1476 | 224.745 | 0 | 40 | 0 | 0 | 11 | 0
17:00 | 3280 | 1467 | 241 | 0 | 40 | 835.77 | 80 | 1479 | 128.17 | 0 | 40 | 0 | 0 | 12 | 0
17:30 | 3349 | 1601 | 240.5 | 0 | 42 | 887.27 | 80 | 1635 | 66.42 | 0 | 40 | 0 | 0 | 8.5 | 0
18:00 | 3418 | 1735 | 240 | 0 | 44 | 938.77 | 80 | 1791 | 4.67 | 0 | 40 | 0 | 0 | 5 | 0
18:30 | 3564.5 | 1845.5 | 459 | 0 | 46 | 1010.555 | 80 | 1922.5 | 2.335 | 17 | 55 | 0 | 0 | 6 | 0
19:00 | 3711 | 1956 | 678 | 0 | 48 | 1082.34 | 80 | 2054 | 0 | 34 | 70 | 0 | 0 | 7 | 0
19:30 | 3790 | 2055 | 710 | 0 | 48 | 1076.5 | 80 | 1923 | 0 | 34 | 60 | 0 | 0 | 6 | 0
20:00 | 3831 | 2133 | 709 | 0 | 48 | 1031.77 | 80 | 1769 | 0 | 17 | 51 | 0 | 0 | 7 | 0
20:30 | 3831 | 2093.5 | 709.5 | 0 | 48 | 1031.105 | 80 | 1783.5 | 0 | 17 | 33.5 | 0 | 0 | 9 | 0
21:00 | 3831 | 2054 | 710 | 0 | 48 | 1030.44 | 80 | 1798 | 0 | 17 | 16 | 0 | 0 | 11 | 0
21:30 | 3825.5 | 2043.5 | 710 | 0 | 48 | 1008.31 | 80 | 1780 | 0 | 8.5 | 16 | 0 | 0 | 7.5 | 0
22:00 | 3820 | 2033 | 710 | 0 | 48 | 986.18 | 80 | 1762 | 0 | 0 | 16 | 0 | 0 | 4 | 0
22:30 | 3817.5 | 1996.5 | 710 | 0 | 48 | 903.2 | 80 | 1695 | 0 | 0 | 8 | 0 | 0 | 2.5 | 0
23:00 | 3815 | 1960 | 710 | 0 | 48 | 820.22 | 80 | 1628 | 0 | 0 | 0 | 0 | 0 | 1 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 23-03-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 422 | 06:00 | 411 | 12:00 | Madunaghat | 412 | 07:00 | 406 | 19:00
Amtali | 423 | 03:00 | 417 | 19:00 | Meghnaghat | 422 | 04:00 | 414 | 13:00
Ashuganj | 417 | 4:00 | 409 | 13:00 | Payra | 424 | 05:00 | 418 | 18:30
Bhulta | 414 | 04:00 | 405 | 13:00 | Rahanpur | 421 | 05:00 | 406 | 19:00
Bibiana | 419 | 17:00 | 415 | 02:00 | Rampal | 416 | 03:00 | 405 | 19:00
BIPTC | 409 | 02:00 | 395 | 19:00
Bogura | 417 | 04:00 | 399 | 19:30
Gopalganj | 422 | 04:00 | 412 | 18:30
Kaliakoir | 415 | 04:00 | 408 | 13:00
Korerhat | 418 | 04:00 | 412 | 18:30
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 241 | 03:00 | 235 | 13:00 | Jhenaidah | 241 | 04:00 | 226 | 19:00
AKSML | 238 | 06:00 | 233 | 13:00 | Kachua | 239 | 05:00 | 232 | 18:30
Aminbazar | 242 | 05:00 | 236 | 13:00 | Kaliakoir | 244 | 03:00 | 238 | 13:00
Ashuganj | 244 | 04:00 | 234 | 13:00 | Keranigonj | 241 | 06:00 | 235 | 13:00
Ashuganj-400 | 244 | 04:00 | 234 | 13:00 | Khulna(S) | 244 | 05:00 | 231 | 19:00
Baghabari | 241 | 05:00 | 234 | 17:00 | Korerhat | 238 | 05:00 | 233 | 18:30
Barapukuria | 234 | 05:00 | 215 | 19:00 | Madunaghat | 239 | 05:00 | 234 | 18:30
Barapukuria-230 | 234 | 05:00 | 215 | 19:00 | Madunaghat-400 | 239 | 06:00 | 235 | 19:00
Barishal | 237 | 04:00 | 232 | 18:30 | Maniknagar | 240 | 02:00 | 236 | 13:00
Bheramara | 242 | 03:00 | 229 | 19:00 | Meghnaghat | 245 | 04:00 | 241 | 14:00
Bhulta | 242 | 04:00 | 237 | 13:00 | Meghnaghat-400 | 240 | 04:00 | 234 | 12:00
Bibiana | 243 | 08:00 | 237 | 18:30 | Mirsorai | 243 | 03:00 | 238 | 18:30
BIPTC | 243 | 04:00 | 229 | 18:30 | Purbasadipur | 233 | 05:00 | 216 | 19:00
Bogura | 242 | 05:00 | 230 | 19:00 | Rajshahi | 240 | 04:00 | 226 | 19:00
Bogura-400 | 241 | 05:00 | 229 | 19:00 | Rampal | 241 | 06:00 | 230 | 19:00
Borhanuddin | 238 | 03:00 | 234 | 18:00 | Rampur | N/A | N/A | N/A | N/A
BSRM | 238 | 04:00 | 233 | 18:30 | Rampura | 241 | 05:00 | 237 | 13:00
Chowmuhani | 239 | 7:00 | 234 | 18:30 | Shikalbaha | 238 | 06:00 | 233 | 19:00
Cumilla(N) | 238 | 06:00 | 233 | 13:00 | Shyampur | 240 | 06:00 | 235 | 13:00
Faridpur | 237 | 04:00 | 230 | 13:00 | Siddhirganj | 242 | 04:00 | 238 | 12:00
Fenchuganj | 245 | 06:00 | 240 | 01:00 | Sirajgonj | 246 | 04:00 | 239 | 13:00
Feni | 239 | 04:00 | 234 | 13:00 | Sreepur | 237 | 06:00 | 228 | 18:30
Ghorashal | 242 | 00:00 | 240 | 07:00 | Tongi | 243 | 04:00 | 238 | 13:00
Ghorashal-230 | 240 | 02:00 | 234 | 13:00
Gopalganj | 235 | 03:00 | 234 | 13:00
GPH | 239 | 06:00 | 234 | 18:30
Haripur | 241 | 03:00 | 237 | 13:00
Hasnabad | 241 | 05:00 | 236 | 15:00
Hathazari | 237 | 06:00 | 234 | 18:30
Ishurdi | 243 | 03:00 | 232 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 01:00 | 134 | 12:00 | Madunaghat | 139 | 05:00 | 135 | 18:30
Agargaon | 139 | 04:00 | 135 | 13:00 | Magura | 138 | 06:00 | 126 | 19:00
Agrabad | 138 | 06:00 | 133 | 18:30 | Mahasthangarh | 139 | 03:00 | 130 | 18:30
AKS | 135 | 00:00 | 133 | 06:00 | Maijdee | 133 | 03:00 | 129 | 18:30
Aminbazar | 141 | 05:00 | 137 | 12:00 | Manikganj | 137 | 03:00 | 133 | 22:00
Amnura | 139 | 01:00 | 131 | 19:00 | Maniknagar | 136 | 01:00 | 134 | 12:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 126 | 10:00 | 117 | 18:30
Ashuganj-230 | 145 | 05:00 | 140 | 13:00 | Matuail | 140 | 06:00 | 137 | 14:00
Bagerhat | 138 | 06:00 | 127 | 19:00 | Metrorail_Motijheel | 136 | 01:00 | 134 | 12:00
Bajitpur | 136 | 04:00 | 130 | 17:00 | Metrorail_Uttara | 140 | 03:00 | 136 | 13:00
Bakerganj | 138 | 03:00 | 134 | 19:00 | Millgate | 139 | 01:00 | 136 | 12:00
Bakulia | 137 | 03:00 | 135 | 00:00 | Mirpur | 140 | 02:00 | 136 | 13:00
Banani | 140 | 04:00 | 136 | 13:00 | Mirzapur | 137 | 04:00 | 130 | 14:00
Bangabhaban | 136 | 03:00 | 133 | 13:00 | Mithapukur | 135 | 04:00 | 126 | 18:30
Barapukuria | 133 | 05:00 | 122 | 19:00 | MI_Cement | 140 | 04:00 | 136.5 | 13:00
Barguna | 138 | 05:00 | 135 | 13:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 139 | 04:00 | 135 | 13:00 | Mogbazar | 138 | 03:00 | 135 | 11:00
Barishal-230 | 139 | 01:00 | 134 | 18:30 | Mongla | 138 | 04:00 | 129 | 19:00
Baroaulia | 140 | 05:00 | 135 | 18:30 | Motijheel | 136 | 03:00 | 133 | 13:00
Baroirhat | 137 | 07:00 | 134 | 13:00 | Muktagacha | 136 | 03:00 | 121 | 14:00
Bashundhara | 140 | 03:00 | 134 | 12:00 | Munshiganj | 138 | 01:00 | 135 | 13:00
BashundharaCement | 138 | 00:00 | 136 | 04:00 | Muradnagar | 137 | 03:00 | 133 | 13:00
Beanibazar | 133 | 03:00 | 130 | 18:30 | Mymensingh | 135 | 06:00 | 120 | 14:00
Benapole | 136 | 03:00 | 120 | 19:00 | Naogaon | 142 | 03:00 | 128 | 19:00
Bhaluka | 138 | 05:00 | 132 | 13:00 | Narail | 138 | 03:00 | 124 | 19:00
Bhandaria | 137 | 07:00 | 132 | 14:00 | Narinda | 136 | 01:00 | 134 | 12:00
Bhangura | 139 | 04:00 | 132 | 19:00 | Narshingdi | 135 | 05:00 | 134 | 18:30
Bheramara | 140 | 04:00 | 134 | 19:00 | Natore | 137 | 07:00 | 131 | 19:00
Bheramara(GK) | 140 | 03:00 | 134 | 19:00 | Nawabganj | 138 | 06:00 | 133 | 13:00
Bhulta | 134 | 00:00 | 133 | 13:00 | Netrakona | 133 | 06:00 | 124 | 08:00
Bog-Sherpur | 140 | 03:00 | 132 | 19:00 | New | 140 | 03:00 | 136 | 13:00
Bogura | 140 | 03:00 | 134 | 18:00 | Niamatpur | 140 | 03:00 | 135 | 19:00
Bogura-230 | 140 | 03:00 | 132 | 18:30 | Noapara | 138 | 02:00 | 129 | 19:00
Brahmanbaria | 139 | 06:00 | 135 | 13:00 | Pabna | 140 | 04:00 | 133 | 19:00
Cantonment | 139 | 06:00 | 134 | 13:00 | Palashbari | 133 | 03:00 | 126 | 19:00
Chandina | 139 | 05:00 | 135 | 13:00 | Panchagarh | 136 | 05:00 | 128 | 18:30
Chandpur | 134 | 04:00 | 131 | 12:00 | Patiya | 136 | 04:00 | 132 | 20:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 139 | 04:00 | 135 | 18:30 | Patuakhali | 136 | 00:00 | 134 | 10:00
Chapai | 139 | 03:00 | 135 | 18:30 | Payra | 139 | 00:00 | 137 | 18:30
Charsaidpur | 139 | 06:00 | 136 | 05:00 | PHP | 136 | 03:00 | 133 | 13:00
Chauddagram | 135 | 02:00 | 132 | 14:00 | Postogola | 140 | 00:00 | 137 | 13:00
Chhatak | 133 | 05:00 | 128 | 18:30 | Pubail | 145 | 04:00 | 140 | 13:00
Chowmuhani | 134 | 06:00 | 129 | 20:00 | Purbachal | 141 | 04:00 | 136 | 13:00
Chuadanga | 135 | 01:00 | 125 | 19:00 | Purbasadipur | 134 | 04:00 | 125 | 19:00
Coxsbazar | 126 | 09:00 | 116 | 18:30 | Rahanpur | 141 | 04:00 | 136 | 19:00
Cumilla(N) | 139 | 06:00 | 135 | 12:00 | Rahanpur-400 | 141 | 02:00 | 136 | 19:00
Cumilla(S) | 137 | 04:00 | 130 | 16:00 | Rahim | 138 | 00:00 | 136 | 11:00
Daganbhuiyan | 135 | 06:00 | 131 | 13:00 | Rajbari | 137 | 03:00 | 132 | 14:00
Daudkandi | 136 | 05:00 | 131 | 13:00 | Rajendrapur | 140 | 01:00 | 135 | 18:00
DhakaUniversity | 137 | 05:00 | 134 | 13:00 | Rajshahi | 138 | 06:00 | 130 | 18:30
Dhamrai | 138 | 03:00 | 135 | 18:30 | Rajshahi-230 | 138 | 03:00 | 131 | 19:00
Dhanmondi | 141 | 03:00 | 138 | 13:00 | Ramganj | 132 | 04:00 | 128 | 18:30
Dohazari | 134 | 08:00 | 127 | 19:00 | Rampur | 138 | 05:00 | 134 | 19:30
Faridpur | 137 | 04:00 | 133 | 19:00 | Rampura | 137 | 06:00 | 134 | 13:00
Fatullah | 141 | 06:00 | 137 | 13:00 | Rangamati | 138 | 05:00 | 135 | 13:00
Fenchuganj | 139 | 06:00 | 136 | 12:00 | Rangpur | 134 | 05:00 | 124 | 19:00
Feni | 134 | 03:00 | 131 | 12:00 | Ruppur | 141 | 05:00 | 134 | 19:00
Feni-230 | 135 | 06:00 | 131 | 13:00 | Saidpur | 133 | 00:00 | 124 | 18:30
Ghatail | 134 | 06:00 | 122 | 14:00 | Satkhira | 137 | 04:00 | 125 | 19:00
Ghorashal | 145 | 03:00 | 140 | 15:00 | Satmasjid | 138 | 01:00 | 135 | 14:00
Goalpara | 141 | 05:00 | 130 | 14:00 | Savar | 139 | 05:00 | 135 | 13:00
Gollamari | 141 | 06:00 | 132 | 19:00 | SevenRings | 145 | 03:00 | 141 | 13:00
Gopalganj | 139 | 03:00 | 132 | 19:00 | ShahCement | 139 | 06:00 | 136 | 13:00
Gopalganj-400 | 141 | 06:00 | 136 | 18:30 | Shahjadpur | 141 | 00:00 | 137 | 18:30
Gulshan | 136 | 01:00 | 133 | 13:00 | Shahjibazar | 138 | 15:00 | 134 | 13:00
Halishahar | 138 | 03:00 | 134 | 18:30 | Shahmirpur | 138 | 10:00 | 134 | 19:00
Haripur | 139 | 01:00 | 137 | 09:00 | Shariatpur | 140 | 05:00 | 134 | 18:30
HaripurSBU | 139 | 01:00 | 136 | 13:00 | Sherpur | 132 | 05:00 | 111 | 09:00
Hasnabad | 140 | 00:00 | 138 | 12:00 | Shikalbaha | 128 | 06:00 | 123 | 18:00
Hathazari | 139 | 06:00 | 135 | 18:30 | Shikalbaha-230 | 138 | 02:00 | 135 | 19:00
Hatirjheel | 137 | 02:00 | 134 | 13:00 | Shitalakhya | 140 | 04:00 | 136.5 | 13:00
Ishurdi | 142 | 03:00 | 136 | 18:30 | Sholosohor | 137 | 01:00 | 135 | 13:00
Jaldhaka | 131 | 04:00 | 119 | 19:00 | Shyampur | 139 | 01:00 | 136 | 06:00
Jamalpur | 135 | 05:00 | 113 | 14:00 | Shyampur-230 | 140 | 03:00 | 137 | 13:00
Jashore | 137 | 04:00 | 122 | 19:00 | Siddhirganj | 139 | 00:00 | 137 | 13:00
Jhenaidah | 138 | 02:00 | 128 | 19:00 | Sirajganj | 138 | 02:00 | 130 | 19:00
Jhenaidah-230 | 140 | 05:00 | 129 | 19:00 | Sonargaon | 138 | 00:00 | 136 | 12:00
Joydebpur | 141 | 00:00 | 138 | 14:00 | Sreemongol | 137 | 22:00 | 133 | 18:00
Joypurhat | 135 | 02:00 | 127 | 19:00 | Sreepur | 142 | 05:00 | 136 | 18:30
Juldah | 138 | 09:00 | 134 | 19:30 | Srinagar | 137 | 03:00 | 134 | 12:00
Kabirpur | 141 | 03:00 | 130 | 13:00 | SSM | 141 | 08:00 | 140 | 00:00
Kachua | 135 | 03:00 | 131 | 18:30 | Sunamganj | 131 | 04:00 | 126 | 18:00
Kaliakoir | 140 | 02:00 | 136 | 12:00 | Sylhet | 134 | 05:00 | 131 | 18:30
Kaliganj | 139 | 03:00 | 128 | 18:30 | Sylhet-132 | 133 | 03:00 | 132 | 00:00
Kallyanpur | 139 | 01:00 | 136 | 13:00 | Tangail | 134 | 05:00 | 125 | 14:00
Kalurghat | 139 | 06:00 | 135 | 18:30 | Taraganj | 132 | 03:00 | 121 | 19:00
Kamrangirchar | 140 | 05:00 | 134 | 13:00 | Tasnim | 139 | 05:00 | 136 | 13:00
Kaptai | 140 | 5:00 | 138 | 1:00 | Thakurgaon | 135 | 05:00 | 126 | 18:30
Kasba | 137 | 04:00 | 132 | 18:30 | TK | 139 | 04:00 | 135 | 18:30
Kazla | 136 | 02:00 | 134 | 13:00 | Tongi | 141 | 04:00 | 138 | 13:00
Keranigonj | 138 | 04:00 | 134 | 13:00 | Ullahpara | 140 | 02:00 | 133 | 18:30
Khagrachori | 138 | 04:00 | 132 | 18:30 | Ullon | 136 | 00:00 | 133 | 13:00
Khulna | 140 | 04:00 | 131 | 18:30 | Uttara | 141 | 05:00 | 136 | 13:00
Khulna(S) | 140 | 05:00 | 131 | 19:00 | UttaraNew | 140 | 03:00 | 136 | 13:00
Khulshi | 137 | 04:00 | 133 | 18:30 | Zigatola | 138 | 06:00 | 134 | 08:00
Kishoreganj | 135 | 06:00 | 128 | 18:30
Kodda | 142 | 06:00 | 132 | 12:00
Korerhat | 139 | 07:00 | 135 | 00:00
KSRM | 139 | 02:00 | 135 | 18:30
Kulaura | 138 | 06:00 | 135 | 13:00
Kurigram | 130 | 06:00 | 120 | 08:00
Kushtia | 139 | 06:00 | 131 | 19:00
Laksam | 134 | 04:00 | 131 | 03:00
Lakshmipur | 133 | 04:00 | 130 | 13:00
Lalbag | 137 | 01:00 | 127 | 02:00
Lalmonirhat | 130 | 03:00 | 115 | 19:00
Madanganj | 138 | 00:00 | 136 | 04:00
Madaripur | 138 | 00:00 | 135 | 19:00
Madartek | 137 | 06:00 | 134 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division