## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 25-03-2026 | [28 empty] | Date: | 25-03-2026 | [28 empty] | Date: | 25-03-2026 | [28 empty] | Date: | 25-03-2026 | [28 empty] | Date: | 25-03-2026 | [17 empty] | Date: | 25-03-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [17 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 342.010 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 43 | 333 | 0 | 537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 12 | 17 | 0 | 530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 190 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 325 | 0 | 330 | 51 | 0 | 187 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 114 | 0 | 0 | 0 | 315 | 0 | 358 | 41 | 0 | 154 | 0 | 20 | 0 | 5 | 20 | 90 | 0 | 96 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 5528 | 898 | 379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 405 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 125 | 220 | 0 | 0 | 700 | 0 | 4348 | 9876 | 96.34
01:00 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 41 | 315 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 12 | 17 | 0 | 530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 29 | 150 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 320 | 0 | 334 | 51 | 0 | 184 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 110 | 0 | 0 | 0 | 305 | 0 | 347 | 41 | 0 | 143 | 0 | 20 | 0 | 5 | 20 | 90 | 0 | 97 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 5239 | 898 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 404 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 125 | 220 | 0 | 0 | 560 | 0 | 4178 | 9417 | 86.33
02:00 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 7 | 323 | 0 | 474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 7 | 17 | 0 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 7 | 150 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 305 | 0 | 290 | 5 | 0 | 190 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 106 | 0 | 0 | 0 | 315 | 0 | 363 | 27 | 0 | 136 | 0 | 20 | 0 | 5 | 20 | 89 | 0 | 97 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 4881 | 898 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 354 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 125 | 220 | 0 | 0 | 500 | 0 | 4021 | 8902 | 86.32
03:00 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 301 | 0 | 458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 7 | 17 | 0 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 150 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 300 | 0 | 290 | 0 | 0 | 178 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 104 | 0 | 0 | 0 | 310 | 0 | 331 | 27 | 0 | 135 | 0 | 20 | 0 | 0 | 20 | 91 | 0 | 96 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 4681 | 898 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 351 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3929 | 8610 | 86.31
04:00 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 298 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 7 | 17 | 0 | 400 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 150 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 280 | 0 | 290 | 0 | 0 | 140 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 100 | 0 | 0 | 0 | 310 | 0 | 317 | 26 | 0 | 134 | 0 | 20 | 0 | 0 | 20 | 91 | 0 | 96 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 4531 | 898 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 346 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3909 | 8440 | 86.3
05:00 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 295 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 7 | 17 | 0 | 400 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 230 | 0 | 290 | 0 | 0 | 140 | 0 | 0 | 50 | 0 | 0 | 18 | 0 | 98 | 0 | 0 | 0 | 305 | 0 | 320 | 26 | 0 | 133 | 0 | 0 | 0 | 0 | 20 | 26 | 0 | 96 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 4322 | 886 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 347 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3875 | 8197 | 86.29
06:00 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 296 | 0 | 448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 7 | 12 | 0 | 310 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0.01 | 40 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 230 | 0 | 300 | 0 | 0 | 140 | 0 | 0 | 50 | 0 | 0 | 18 | 0 | 96 | 0 | 0 | 0 | 305 | 0 | 320 | 26 | 0 | 134 | 0 | 0 | 0 | 0 | 20 | 24 | 0 | 96 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 4237.01 | 886 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 345 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 3875 | 8112.01 | 86.28
07:00 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 319 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 2 | 0 | 7 | 12 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52 | 40 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 306 | 3 | 0 | 0 | 230 | 0 | 310 | 0 | 0 | 192 | 0 | 0 | 50 | 0 | 0 | 18 | 0 | 92 | 0 | 12 | 0 | 320 | 0 | 364 | 26 | 0 | 142 | 2 | 0 | 0 | 0 | 20 | 25 | 0 | 96 | 0 | 0 | 0 | 163 | 0.1 | 4.29 | 0 | 4596.91 | 886 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 390 | 0 | 0 | 0 | 833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.63 | 13 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 143 | 0 | 385 | 0 | 0.35 | 0 | 55 | 0 | 2 | 0 | 0 | 0 | 0 | 0.8 | 11 | 0.06 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 4008.84 | 8605.75 | 86.27
08:00 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 335 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 6 | 0 | 7 | 12 | 0 | 530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 40 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 309 | 9 | 0 | 0 | 307 | 0 | 335 | 0 | 0 | 190 | 0 | 0 | 50 | 0 | 0 | 18 | 0 | 66 | 0 | 30 | 0 | 310 | 0 | 360 | 26 | 0 | 138 | 5 | 0 | 0 | 0 | 20 | 24 | 0 | 96 | 0 | 0 | 0 | 163 | 0.4 | 8.17 | 0 | 4893.07 | 886 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 375 | 0 | 0 | 0 | 830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.73 | 34 | 0 | 0 | 12.39 | 0 | 0 | 0 | 0 | 160 | 0 | 400 | 0 | 1.43 | 0 | 53 | 0 | 6 | 0 | 0 | 0 | 0 | 2.7 | 41 | 0.22 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 4138.47 | 9031.54 | 86.26
09:00 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 337 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 15 | 0 | 15 | 12 | 0 | 530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.08 | 40 | 0 | 2 | 150 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 306 | 14 | 0 | 0 | 309 | 0 | 330 | 0 | 0 | 195 | 0 | 0 | 50 | 0 | 0 | 18 | 0 | 70 | 0 | 49 | 0 | 315 | 0 | 376 | 26 | 0 | 137 | 7 | 0 | 0 | 0 | 20 | 25 | 0 | 96 | 0 | 16 | 8 | 163 | 1.1 | 13.74 | 0 | 4995.92 | 886 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 375 | 0 | 0 | 0 | 825.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.99 | 69 | 0 | 0 | 18.69 | 0 | 0 | 0 | 0 | 159 | 0 | 402 | 0 | 3.16 | 0 | 52 | 0 | 12 | 0 | 0 | 0 | 0 | 4.9 | 51 | 0.37 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 4233.31 | 9229.23 | 86.25
10:00 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 333 | 0 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 20 | 0 | 13 | 12 | 0 | 530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | 40 | 0 | 2 | 150 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 308 | 17 | 0 | 0 | 312 | 0 | 340 | 0 | 0 | 198 | 0 | 0 | 50 | 0 | 0 | 14 | 0 | 100 | 0 | 49 | 0 | 310 | 0 | 380 | 41 | 0 | 137 | 7 | 0 | 0 | 0 | 20 | 24 | 0 | 96 | 0 | 16 | 8 | 160 | 1.8 | 22.88 | 0 | 5068.78 | 886 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 374 | 0 | 0 | 0 | 829.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.69 | 76 | 0 | 0 | 46.9 | 0 | 0 | 0 | 0 | 159 | 0 | 408 | 0 | 3.35 | 0 | 52 | 0 | 12 | 0 | 0 | 0 | 0 | 6.1 | 65 | 0.52 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 4336 | 9404.78 | 86.24
11:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 339 | 0 | 484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 28 | 0 | 13 | 12 | 0 | 560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.57 | 40 | 0 | 3 | 150 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 308 | 19 | 0 | 0 | 320 | 0 | 340 | 0 | 0 | 202 | 0 | 0 | 51 | 0 | 0 | 14 | 0 | 88 | 0 | 70 | 0 | 315 | 0 | 406 | 41 | 0 | 140 | 11 | 0 | 0 | 0 | 20 | 25 | 0 | 96 | 0 | 16 | 8 | 159 | 1.1 | 39.46 | 0 | 5207.13 | 886 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 379 | 0 | 0 | 0 | 838.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.52 | 97 | 0 | 0 | 53.93 | 0 | 0 | 0 | 0 | 163 | 0 | 414 | 0 | 4.26 | 0 | 52 | 0 | 30 | 0 | 0 | 0 | 0 | 7.1 | 139 | 0.61 | 0 | 140 | 100 | 180 | 0 | 0 | 500 | 0 | 4510.94 | 9718.07 | 86.23
12:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 346 | 0 | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 31 | 0 | 13 | 12 | 0 | 560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.63 | 40 | 0 | 3 | 210 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 332 | 19 | 0 | 2 | 356 | 0 | 0 | 18 | 1 | 205 | 0 | 0 | 97 | 0 | 0 | 20 | 0 | 100 | 0 | 71 | 0 | 315 | 0 | 406 | 41 | 0 | 147 | 12 | 8 | 0 | 5 | 20 | 75 | 0 | 96 | 0 | 16 | 8 | 156 | 2.4 | 41.31 | 0 | 5368.34 | 886 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 420 | 0 | 0 | 0 | 858.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.41 | 108 | 0 | 0 | 50.45 | 0 | 0 | 0 | 0 | 197 | 0 | 412 | 0 | 5.78 | 0 | 52 | 0 | 30 | 0 | 0 | 0 | 0 | 7.7 | 134 | 0.64 | 0 | 184 | 125 | 220 | 0 | 0 | 515 | 0 | 4743.83 | 10112.17 | 86.22
13:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 353 | 0 | 642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 30 | 0 | 13 | 12 | 0 | 567 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 3.4 | 40 | 0 | 3 | 290 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 445 | 19 | 0 | 97 | 359 | 0 | 0 | 51 | 23 | 208 | 39 | 0 | 97 | 0 | 0 | 20 | 0 | 106 | 0 | 67 | 0 | 325 | 0 | 407 | 42 | 0 | 157 | 10 | 17 | 0 | 5 | 30 | 100 | 0 | 96 | 0 | 16 | 8 | 155 | 2.2 | 28.29 | 0 | 5849.89 | 886 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 440 | 0 | 0 | 0 | 979 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 53.05 | 102 | 0 | 0 | 44.77 | 0 | 0 | 0 | 0 | 195 | 0 | 411 | 0 | 3.58 | 0 | 53 | 0 | 15 | 0 | 0 | 0 | 0 | 7.7 | 187 | 0.62 | 0 | 222 | 125 | 220 | 0 | 0 | 750 | 0 | 5208.72 | 11058.61 | 86.21
14:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 345 | 0 | 635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 26 | 0 | 13 | 12 | 0 | 530 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 2.97 | 40 | 0 | 8 | 355 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 500 | 17 | 0 | 150 | 328 | 0 | 0 | 51 | 43 | 193 | 42 | 0 | 97 | 0 | 0 | 20 | 0 | 112 | 0 | 56 | 0 | 320 | 0 | 374 | 42 | 0 | 156 | 9 | 17 | 0 | 5 | 30 | 100 | 0 | 96 | 0 | 20 | 16 | 156 | 1.4 | 45.4 | 0 | 5926.77 | 886 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 428 | 0 | 0 | 0 | 959.4 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 46.38 | 91 | 0 | 0 | 49.31 | 0 | 0 | 0 | 0 | 191 | 0 | 400 | 0 | 2.23 | 0 | 53 | 0 | 30 | 0 | 0 | 0 | 0 | 6.3 | 181 | 0.53 | 0 | 244 | 125 | 220 | 0 | 0 | 950 | 0 | 5355.15 | 11281.92 | 86.2
15:00 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 332 | 0 | 635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 21 | 0 | 13 | 12 | 0 | 530 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 2.25 | 40 | 0 | 11 | 355 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 500 | 13 | 0 | 172 | 320 | 0 | 0 | 51 | 48 | 193 | 40 | 0 | 96 | 0 | 0 | 20 | 0 | 124 | 0 | 45 | 0 | 315 | 0 | 345 | 42 | 0 | 154 | 7 | 17 | 0 | 5 | 30 | 100 | 0 | 95 | 0 | 24 | 16 | 156 | 0.4 | 28.75 | 0 | 5871.4 | 887 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 360 | 0 | 0 | 0 | 948.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.55 | 64 | 0 | 0 | 37.82 | 0 | 0 | 0 | 0 | 185 | 0 | 364 | 0 | 1.78 | 0 | 53 | 0 | 27 | 0 | 0 | 0 | 0 | 5.5 | 149 | 0.44 | 0 | 242 | 120 | 220 | 0 | 0 | 1000 | 0 | 5126.2 | 10997.6 | 86.19
16:00 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 335 | 0 | 451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 4 | 0 | 13 | 12 | 0 | 530 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1.32 | 40 | 0 | 11 | 355 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 451 | 8 | 0 | 180 | 340 | 0 | 0 | 51 | 47 | 202 | 42 | 0 | 94 | 0 | 0 | 20 | 0 | 118 | 0 | 27 | 0 | 310 | 0 | 368 | 42 | 0 | 138 | 4 | 17 | 0 | 5 | 30 | 100 | 0 | 95 | 0 | 24 | 16 | 156 | 1 | 4.97 | 0 | 5607.29 | 886 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 374 | 0 | 0 | 0 | 873.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.61 | 42 | 0 | 0 | 11.82 | 0 | 0 | 0 | 0 | 187 | 0 | 370 | 0 | 1.37 | 0 | 53 | 0 | 17 | 0 | 0 | 0 | 0 | 3.2 | 82 | 0.28 | 0 | 248 | 120 | 220 | 0 | 0 | 900 | 0 | 4817.96 | 10425.25 | 86.18
17:00 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 321 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 5 | 0 | 13 | 12 | 0 | 450 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0.46 | 40 | 0 | 14 | 355 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 450 | 3 | 0 | 180 | 320 | 0 | 44 | 51 | 46 | 195 | 42 | 0 | 95 | 0 | 0 | 20 | 0 | 116 | 0 | 10 | 0 | 315 | 0 | 366 | 42 | 0 | 140 | 0 | 20 | 0 | 5 | 30 | 100 | 0 | 95 | 0 | 24 | 16 | 156 | 0.3 | 11.02 | 0 | 5310.78 | 886 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 372 | 0 | 0 | 0 | 867.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.67 | 13 | 0 | 0 | 10.4 | 0 | 0 | 0 | 0 | 190 | 0 | 359 | 0 | 0.91 | 0 | 53 | 0 | 7 | 0 | 0 | 0 | 0 | 1.2 | 31 | 0.1 | 0 | 247 | 120 | 220 | 0 | 0 | 900 | 0 | 4687.52 | 9998.3 | 86.17
18:00 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 316 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 13 | 12 | 0 | 475 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 13 | 355 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 454 | 0 | 0 | 128 | 340 | 0 | 90 | 51 | 0 | 203 | 5 | 0 | 97 | 0 | 0 | 20 | 0 | 122 | 0 | 1 | 0 | 310 | 0 | 397 | 42 | 0 | 135 | 0 | 20 | 0 | 5 | 30 | 100 | 0 | 95 | 0 | 24 | 16 | 156 | 0 | 0.32 | 0 | 5310.32 | 886 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 371 | 0 | 0 | 0 | 869.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96 | 0 | 0 | 0 | 0.63 | 0 | 0 | 0 | 0 | 183 | 0 | 387 | 0 | 0.05 | 0 | 52 | 0 | 1 | 0 | 0 | 0 | 0 | 0.2 | 3 | 0.01 | 0 | 248 | 120 | 220 | 0 | 0 | 900 | 0 | 4615 | 9925.32 | 86.16
19:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 313 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 17 | 0 | 12 | 0 | 530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 8 | 470 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 593 | 0 | 0 | 55 | 290 | 0 | 85 | 51 | 5 | 192 | 42 | 0 | 98 | 0 | 0 | 20 | 0 | 132 | 0 | 0 | 0 | 320 | 0 | 364 | 42 | 0 | 153 | 0 | 20 | 0 | 5 | 30 | 99 | 0 | 96 | 0 | 35 | 35 | 157 | 0 | 0 | 0 | 5567 | 886 | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 598 | 0 | 0 | 0 | 1221.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 414 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 0 | 980 | 0 | 5383.74 | 10950.74 | 86.16
19:30 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 294 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 13 | 470 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 575 | 0 | 0 | 55 | 290 | 0 | 85 | 51 | 5 | 193 | 42 | 0 | 99 | 0 | 0 | 20 | 0 | 128 | 0 | 0 | 0 | 310 | 0 | 367 | 42 | 0 | 136 | 0 | 20 | 0 | 5 | 30 | 99 | 0 | 95 | 0 | 24 | 24 | 159 | 0 | 0 | 0 | 5335 | 886 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 592 | 0 | 0 | 0 | 1215.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 351 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261 | 100 | 180 | 0 | 0 | 1055 | 0 | 5244.07 | 10579.07
20:00 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 291 | 0 | 284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 14 | 470 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 525 | 0 | 0 | 8 | 280 | 0 | 55 | 51 | 5 | 216 | 39 | 0 | 98 | 0 | 0 | 20 | 0 | 128 | 0 | 0 | 0 | 305 | 0 | 367 | 42 | 0 | 134 | 0 | 20 | 0 | 5 | 30 | 100 | 0 | 95 | 0 | 16 | 16 | 159 | 0 | 0 | 0 | 5193 | 886 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 573 | 0 | 0 | 0 | 1214.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 348 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259 | 100 | 180 | 0 | 0 | 1065 | 0 | 5215.07 | 10408.07 | 86.15
21:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 318 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 11 | 14 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 20 | 470 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 520 | 0 | 0 | 8 | 280 | 0 | 30 | 51 | 5 | 200 | 40 | 0 | 102 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 305 | 0 | 390 | 42 | 0 | 137 | 0 | 20 | 0 | 5 | 30 | 99 | 0 | 95 | 0 | 16 | 8 | 159 | 0 | 0 | 0 | 5219 | 886 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 522 | 0 | 0 | 0 | 1122.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 373 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 100 | 180 | 0 | 0 | 1100 | 0 | 5139.62 | 10358.62 | 86.15
22:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 317 | 0 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 11 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 20 | 470 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 520 | 0 | 0 | 8 | 300 | 0 | 20 | 51 | 5 | 195 | 42 | 0 | 103 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 310 | 0 | 384 | 42 | 0 | 137 | 0 | 20 | 0 | 5 | 30 | 100 | 0 | 95 | 0 | 16 | 8 | 160 | 0 | 0 | 0 | 5181 | 886 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 524 | 0 | 0 | 0 | 1018.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 356 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 100 | 180 | 0 | 0 | 1115 | 0 | 5036.57 | 10217.57 | 86.14
23:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 343 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 11 | 18 | 0 | 445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 470 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 526 | 0 | 0 | 8 | 350 | 0 | 29 | 40 | 5 | 206 | 42 | 0 | 51 | 0 | 0 | 8 | 0 | 110 | 0 | 0 | 0 | 320 | 0 | 392 | 41 | 0 | 150 | 0 | 0 | 0 | 5 | 17 | 100 | 0 | 95 | 0 | 16 | 8 | 160 | 0 | 0 | 0 | 5215 | 886 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 534 | 0 | 0 | 0 | 977.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 414 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221 | 110 | 220 | 0 | 0 | 1030 | 0 | 5017.75 | 10232.75 | 86.14
Total KWH | 0 | 0 | 0 | 4569100 | 0 | 0 | 0 | 0 | 7876800 | 0 | 10636470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4919800 | 0 | 0 | 0 | 0 | 7230785 | 0 | 0 | 192665 | 27600 | 249000 | 351720 | 0 | 11506818.18 | 0 | 0 | 0 | 0 | 46080 | 0 | 0 | 0 | 0 | 0 | 25203 | 1024980 | 0 | 257760 | 6538181.82 | 0 | 0 | 0 | 0 | 0 | 5069589 | 0 | 0 | 0 | 9730908 | 142020 | 0 | 986909 | 7484500 | 0 | 4138000 | 733760 | 252480 | 4677000 | 427392 | 0 | 1959517 | 0 | 0 | 386160 | 0 | 2493120 | 0 | 474009 | 0 | 7602000 | 0 | 9054000 | 878000 | 0 | 3415500 | 68890 | 304128 | 0 | 76800 | 579072 | 1785000 | 0 | 2298920 | 0 | 351600 | 213600 | 3456960 | 10250 | 244130 | 0 | 124747177 | 21493090 | 9055872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 634320 | 10072728 | 0 | 0 | 0 | 21895984 | 0 | 0 | 100000 | 0 | 0 | 0 | 0 | 0 | 0 | 334400 | 677760 | 0 | 0 | 325504 | 0 | 0 | 0 | 0 | 4382591 | 0 | 9246836 | 0 | 27120 | 0 | 1224436 | 608 | 201230 | 0 | 0 | 0 | 0 | 50604.72 | 1053360 | 3996 | 0 | 4800000 | 2663000 | 5138990 | 0 | 0 | 18516363.64 | 0 | 111898793.36 | 236645970.36

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 26-03-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 25-03-2026 | during | 26-03-2026 | during | 26-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 190 | 192 | 190 | 190 | 0 | 0 | GBC 1 and 3 under maintenance
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 7 | 7 | On test
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 346 | 313 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 327 | 320 | 335 | 335 | 335 | 335
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 13 | 0 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 12 | 12 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 560 | 530 | 584 | 584 | 584 | 584 | FGMO
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 624 | 300 | 718 | 718 | 300 | 300 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 17 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2328 | 1909 | 5876.22 | 5845.22 | 3593.02 | 3562.02
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 221 | 220 | 220 | 220 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 56 | 64 | 56 | 64 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 68 | 68 | 68 | 68 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 3 | 8 | 40 | 40 | 40 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.63 | 0 | 4.01 | 0 | 4.01 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 332 | 593 | 1224 | 1224 | 612 | 612 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 3 | 12 | 3 | 12 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 210 | 470 | 1045 | 1045 | 320 | 320 | Unit 1 Under Maintenance
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 821.63 | 1332 | 3991.87 | 3984.86 | 2130.51 | 2123.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 205 | 192 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 0 | 85 | 342.01 | 342.01 | 306 | 306 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 356 | 290 | 393 | 393 | 363 | 363 | FGMO
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 42 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 1 | 5 | 55 | 55 | 20 | 20 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 2 | 55 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 18 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 16 | 16 | 16 | 16 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 97 | 98 | 163 | 163 | 100 | 100 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 100 | 132 | 84 | 82 | 84 | 82 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 71 | 0 | 74 | 0 | 74 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2876.261 | 870 | 970 | 2404.36 | 2328.36 | 2074.2 | 1998.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 25-03-2026 | during | 26-03-2026 | during | 26-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 156 | 157 | 157.5 | 157.5 | 10 | 10 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.4 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 35 | 60 | 80 | 60 | 80 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 16 | 35 | 70 | 115 | 70 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 41.31 | 0 | 45.12 | 0 | 45.12 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 12 | 12 | From12:00 hrs to24:00 hrs will be dispatching12MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 35 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 223.71 | 227 | 411.12 | 429 | 216.12 | 252
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 42 | 41 | 41 | 41 | 41 | plant availability zero
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 147 | 153 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 75 | 99 | 100 | 100 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 20 | 30 | 30 | 30 | 0 | 0 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 5 | 83 | 83 | 42 | 42 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 96 | 96 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 20 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 320 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 406 | 364 | 385 | 385 | 357 | 357 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1125 | 1129 | 1288 | 1288 | 1016 | 1016
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 886 | 886 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 388 | 389 | 410 | 410 | 410 | 410 | -
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 93 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 420 | 598 | 1234.2 | 1234.2 | 617 | 617 | Low demand for EID holidays
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1787 | 1873 | 3597.2 | 3512.2 | 2219.1 | 2134.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 125 | 120 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 515 | 980 | 1244 | 1244 | 1184 | 1184 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 75 | 75 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 184 | 307 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.64 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1044.64 | 1627 | 2162 | 2161 | 1933 | 1932
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 56.41 | 0 | 62 | 0 | 62 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 197 | 196 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 412 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 22 | 22 | 21 | 21 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 50 | 50 | 50 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.78 | 0 | 6 | 0 | 6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 858.85 | 1221.74 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 50.45 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 108 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1688.49 | 1831.74 | 3154.87 | 2925.87 | 2616.49 | 2387.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 52 | 52 | 55 | 55 | 55 | 55 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.7 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 134 | 0 | 179.62 | 0 | 179.62 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 223.7 | 52 | 517.82 | 303 | 497.82 | 283
System Total |  |  |  |  | 28823.2 | 29275.503 | 10112.17 | 10950.74 | 23403.46 | 22777.51 | 16296.26 | 15688.31
Forecast Scenario (26-03-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9870 |  | 0 |  | 9870
|  |  |  | 1:00 | 9370 |  | 0 |  | 9370
|  |  |  | 2:00 | 8800 |  | 0 |  | 8800
|  |  |  | 3:00 | 8460 |  | 0 |  | 8460
|  |  |  | 4:00 | 8240 |  | 0 |  | 8240
|  |  |  | 5:00 | 7950 |  | 0 |  | 7950
|  |  |  | 6:00 | 7810 |  | 0 |  | 7810
|  |  |  | 7:00 | 8250 |  | 0 |  | 8250
|  |  |  | 8:00 | 8630 |  | 0 |  | 8630
|  |  |  | 9:00 | 8630 |  | 0 |  | 8630
|  |  |  | 10:00 | 8900 |  | 0 |  | 8900
|  |  |  | 11:00 | 9160 |  | 0 |  | 9160
|  |  |  | 12:00 | 9500 |  | 0 |  | 9500
|  |  |  | 13:00 | 10400 |  | 0 |  | 10400
|  |  |  | 14:00 | 10580 |  | 0 |  | 10580
|  |  |  | 15:00 | 10240 |  | 0 |  | 10240
|  |  |  | 16:00 | 9620 |  | 0 |  | 9620
|  |  |  | 17:00 | 9150 |  | 0 |  | 9150
|  |  |  | 18:00 | 9030 |  | 0 |  | 9030
|  |  |  | 18:30 | 9500 |  | 0 |  | 9500
|  |  |  | 19:00 | 10000 |  | 0 |  | 10000
|  |  |  | 19:30 | 9630 |  | 0 |  | 9630
|  |  |  | 20:00 | 9460 |  | 0 |  | 9460
|  |  |  | 21:00 | 9410 |  | 0 |  | 9410
|  |  |  | 22:00 | 9250 |  | 0 |  | 9250
|  |  |  | 23:00 | 9150 |  | 0 |  | 9150
Probable Maximum Temperature:
Probable Maximum Demand at Day Peak: |  |  | 9500.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 10000.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10000.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 219.86 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:38 hrs on 26-03-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 25-03-2026
Power Supply Scenario
| Day Peak Generation |  |  | 10112.17 | MW | 12:00 Hr. | Energy Generated |  |  | 236.646 |  | MKWHr.
| Day Peak Demand |  |  | 10112.17 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 10950.74 | MW | 19:00 Hr. | Energy Demand |  |  | 236.646 |  | MKWHr.
| Evening Peak Demand |  |  | 10950.74 | MW | 19:00 Hr. | Maximum Temperature |  |  | 32.4 |  | °C
| Minimum Generation of the Day |  |  | 8112.01 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 926.73 |  | MMCFD
| Maximum Generation of the Day |  |  | 11281.92 | MW | 14:00 Hr. | Production Cost per KWHr |  |  | 4.832 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 47.3405 | 0 | 0.0276 | 0 | 0 | 0.19267 | 0 | 0 | 47.5608 | Gas | 133.7512 | Gas | 468196812.5606
| Chattogram Zone |  |  | 5.3273 | 16.2691 | 0 | 0 | 1.025 | 0.16722 | 0 | 0.04608 | 22.8347 | Coal | 50.8826 | Coal | 341321658.6858
| Cumilla Zone |  |  | 21.0457 | 0 | 0 | 0 | 0 | 0.47401 | 2.4931 | 0 | 24.0128 | HFO | 0.59341 | HFO | 9766091.52
| Mymensingh Zone |  |  | 3.457 | 0 | 0.5652 | 0 | 0 | 0.25438 | 0 | 0 | 4.2765 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 25.9934 | 0 | 0 | 0 | 0 | 0.06889 | 0 | 0 | 26.0623 | Hydro | 1.025 | Hydro | 102498
| Khulna Zone |  |  | 9.0559 | 10.0727 | 0 | 0 | 0 | 0.63432 | 21.4931 | 0 | 41.256 | Solar | 4.4655 | Solar | 71146295.134
| Barishal Zone |  |  | 7.802 | 23.3164 | 0 | 0 | 0 | 0.003996 | 0 | 0 | 31.1223 | Import | 45.8822 | Import | 252268958.26
| Rajshahi Zone |  |  | 13.7294 | 0 | 0 | 0 | 0 | 1.3648 | 21.896 | 0 | 36.9902 | Wind | 0.04608 | Wind | 677836.8
| Rangpur Zone |  |  | 0 | 1.2244 | 0.000608 | 0 | 0 | 1.3052 | 0 | 0 | 2.5302
| Total |  |  | 133.7512 | 50.8826 | 0.59341 | 0 | 1.025 | 4.4655 | 45.8822 | 0.04608 | 236.646
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 468196812.5606 |  | Hydro | 102498
|  |  |  | Coal | 341321658.6858 |  | Solar | 71146295.134
|  |  |  | HFO | 9766091.52 |  | Import | 252268958.26
|  |  |  | HSD | 0 |  | Wind | 677836.8
[5 empty] | Total: | 114,34,80,150 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.4931 | Peak Hr Flow | 886.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 22377254.59 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 21.896 | Peak Hr Flow | 1221.74 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1019 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.4931 | Peak Hr Flow | 132.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1427 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 45.8822 | Peak Hr Flow | 2239.74 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 2554
|  |  |  | Chattogram |  | 0 |  | 1292
|  |  |  | Cumilla |  | 0 |  | 1182
|  |  |  | Mymensingh |  | 0 |  | 891
|  |  |  | Sylhet |  | 0 |  | 482
|  |  |  | Khulna |  | 0 |  | 1697
|  |  |  | Barishal |  | 0 |  | 428
|  |  |  | Rajshahi |  | 0 |  | 1276
|  |  |  | Rangpur |  | 0 |  | 770
|  |  |  | Total |  | 0 |  | 10572
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:28 | 12:07 | Chandraghona-Kaptai 132 kV Ckt-1 Forced S/D from Chandraghona 132/33kV end Due to OPGW
work
| 08:55 | 12:20 | Chandraghona-Kaptai 132 kV Ckt-2 Forced S/D from Chandraghona 132/33kV end Due to OPGW
work
|  | 09:23 | Borhanuddin 230/33kV S/S Tr-Load HT is restored.
|  | 09:30 | Khulna (C) S/S TR-1 425T HT is restored.
|  | 09:31 | Khulna (C) S/S TR-1 425T LT is restored.
|  | 09:53 | Cumilla(S) 132/33kV S/S TR-2 HT is restored.
|  | 09:54 | Cumilla(S) 132/33kV S/S TR-2 LT is restored.
| 11:11 | 12:20 | Shahjadpur-Ullahpara 132kV Ckt-1 Scheduled S/D from Ullahpara 132/33kV end Due to Red hot
maintenance work.
| 11:36 | 13:09 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) LT Scheduled S/D | [7 empty] | 10.0MW load
interrup.
| 11:37 | 13:07 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT Scheduled S/D | [7 empty] | 10.0MW load
interrup.
| 11:45 |  | Ashuganj 450 MW CCPP(South) Tripped with remarks:- Plant
| 12:00 |  | Day peak Generation : 10107 MW
| 12:15 |  | Baghabari 71 MW was sync.
| 12:21 | 13:21 | Sirajganj-Ullahpara 132KV Ckt-2 Forced S/D from Sirajganj 132/33kV end Due to Read hot
maintenance at Ullapara SS end and from Ullahpara 132/33kV end Due to Red hot maintenance
work.
|  | 12:32 | Shahjadpur 132/33kV S/S T-1(405T) HT is restored.
| 16:26 |  | JERA Meghnaghat Power Limited 718 MW CCPP GT2 was shutdown.
| 16:55 |  | Ashuganj South 360 MW CCPP GT was sync.
| 16:55 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 17:38 | 18:22 | Brahmanbaria 132/33kV S/S Aux. Tr-2 (PGCB) LT Tripped showing O/C relays. | [7 empty] | 1.2MW load
interrup.
| 17:38 | 18:20 | Brahmanbaria 132/33kV S/S 402T LT Tripped showing O/C &E/F relays. | [7 empty] | 40.0MW load
interrup.
| 18:59 | 20:55 | Aminbazar-Keraniganj 230kV Ckt-1 Tripped from Keranigonj 230/132/33kV end showing 86.1
relays Due to 67N Directional Earth Fault trip. and from Aminbazar 400/230/132kV end
showing REL316*4 REL 521 relays Due to Trip
| 19:00 |  | Evening Peak Generation: 10950 MW.
| 19:25 | 19:42 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Overcurrent protection relay P142 relays
Due to Due to 33 kv PBS Feeders fault
| 23:39 | 00:22 | Nawabganj 132/33kV S/S TR-2 LT Forced S/D Due to 33 kv Incomer -2 shutdown for redhot | [7 empty] | 15.0MW load
|  |  | maintenance on R phase. | [7 empty] | interrup.
| 00:26 | 02:05 | Nawabganj 132/33kV S/S 33kV Bus Section-1 Forced S/D Due to 33 kv Incomer -1 & Bus-01 | [7 empty] | 10.0MW load
|  |  | shutdown for redhot maintenance on R & Y phase. | [7 empty] | interrup.
| 01:06 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- ST
| 06:00 |  | Minimum Generation: 8443 MW
| 07:30 | 07:37 | Satkhira 132/33kV S/S Transformer-1 (T-1) LT Tripped showing Over current relay relays | [7 empty] | 80.0MW load
|  |  | Due to Due to 33 kv kajirhat feeder fault | [7 empty] | interrup.
| 07:40 |  | Daudkandi 132/33kV S/S Transformer-3 LT Tripped showing Overcurrent relay relays Due to | [7 empty] | 20.0MW load
|  |  | Flashing at 33KV switchyard near to Palli Bidyut Feeder-10 breaker. | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 25-03-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 192 | 4569100 | GBC 1 and 3 under maintenance
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 313 | 7876800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4919800 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 320 | 7230785 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 0 | 249000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 12 | 351720 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 0 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 192665 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 530 | 11506818.18 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 300 | 10636470 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 17 | 27600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1909 | 47560758.18
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 142020 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 1024980 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 221 | 5069589 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 8 | 257760 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 25203 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 593 | 9730908 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 46080 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 470 | 6538181.82 | Plant availability less
Chattogram Area Total |  |  |  |  | 4898.863 | 1332 | 22834721.82
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 192 | 4677000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 85 | 4138000 | Able to ON FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 290 | 7484500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 42 | 427392 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 252480 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 55 | 986909 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 733760 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 98 | 1959517 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 132 | 2493120 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 386160 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 474009 | -
Cumilla Area Total |  |  |  |  | 2876.261 | 970 | 24012847
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 157 | 3456960 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10250 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 35 | 213600 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 35 | 351600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 244130 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | From12:00 hrs to24:00 hrs will be dispatching12MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 227 | 4276540
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 68890 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 878000 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 153 | 3415500 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 99 | 1785000 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 579072 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 5 | 76800 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 96 | 2298920 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 20 | 304128 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7602000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 364 | 9054000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1129 | 26062310
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 886 | 21493090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 389 | 9055872 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 634320 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 598 | 10072728 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1873 | 41256010
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2663000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 980 | 18516363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5138990 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 4800000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3996 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1627 | 31122349.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 334400 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 100000 | Machine Standby
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 196 | 4382591 | Plant is running as per NLDC demand
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9246836 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 27120 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1221.74 | 21895984 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 325504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 677760 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1831.74 | 36990195
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 52 | 1224436 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 50604.72 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 608 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 201230 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1053360 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 52 | 2530238.72
Eastern Grid Total |  |  |  |  | 17423.308 | 5567 | 124747177
Western Grid Total |  |  |  |  | 11852.195 | 5383.74 | 111898793.36
National Grid Total |  |  |  |  | 29275.503 | 10950.74 | 236645970.36
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 25-03-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6400.97 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4170.8 | MW
i) Dhaka area |  |  | 2554.47 |  | MW | i) Khulna area |  |  |  | 1697 | MW
ii) Chattogram area |  |  | 1291.5 |  | MW | ii) Barishal area |  |  |  | 427.6 | MW
iii) Cumilla area |  |  | 1182 |  | MW | iii) Rajshahi area |  |  |  | 1276.2 | MW
iv) Mymensingh area |  |  | 891 |  | MW | iv) Rangpur area |  |  |  | 770 | MW
v) Sylhet area |  |  | 482 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10571.77 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 52 | 18:30 | 133 | Natore | 139 | 19:00
2 | AKSML | 19.2 | 17:00 | 68 | Hathazari | 69 | 18:30 | 134 | Nawabganj | 48.4 | 14:00
3 | Aftabnagar | 24 | 13:00 | 69 | Hatirjheel | 25 | 14:00 | 135 | Netrakona | 121 | 18:30
4 | Agargaon | 81 | 13:00 | 70 | Ishurdi | 63 | 19:00 | 136 | New | 32.8 | 18:30
5 | Agrabad | 48 | 13:00 | 71 | Jaldhaka | 61 | 19:00 | 137 | Niamatpur | 82 | 18:30
6 | Amnura | 36 | 19:00 | 72 | Jamalpur | 106 | 19:00 | 138 | Noapara | 40 | 19:00
7 | Ashuganj | 61 | 13:00 | 73 | Jashore | 138 | 19:00 | 139 | PHP | 12 | 11:00
8 | BSRM | 190 | 01:00 | 74 | Jhenaidah | 104 | 19:00 | 140 | Pabna | 80 | 19:00
9 | Bagerhat | 83 | 19:30 | 75 | Joydebpur | 74 | 13:00 | 141 | Palashbari | 104 | 13:00
10 | Bajitpur | 58 | 23:00 | 76 | Joypurhat | 53 | 19:30 | 142 | Panchagarh | 47 | 19:00
11 | Bakerganj | 9.6 | 19:00 | 77 | Juldah | 18 | 10:00 | 143 | Patiya | 9 | 18:30
12 | Bakulia | 64 | 22:00 | 78 | KSRM | 10 | 16:00 | 144 | Patuakhali | 57.6 | 21:00
13 | Banani | 16 | 13:00 | 79 | Kabirpur | 123 | 17:00 | 145 | Payra | 30 | 21:00
14 | Bangabhaban | 15 | 10:00 | 80 | Kachua | 89 | 19:00 | 146 | Postogola | 31 | 14:00
15 | Barapukuria | 53 | 19:00 | 81 | Kaliganj | 29 | 18:30 | 147 | Pubail | 19 | 14:00
16 | Barguna | 18 | 19:00 | 82 | Kallyanpur | 75 | 13:00 | 148 | Purbachal | 21 | 18:30
17 | Barishal | 87 | 13:00 | 83 | Kalurghat | 24 | 21:00 | 149 | Purbasadipur | 89 | 19:00
18 | Barishal-230 | 96 | 19:00 | 84 | Kamrangirchar | 36 | 13:00 | 150 | Rahanpur | 28 | 19:30
19 | Baroaulia | 60 | 11:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 1 | 01:00
20 | Baroirhat | 59 | 18:30 | 86 | Kasba | 30 | 14:00 | 152 | Rajbari | 72 | 19:00
21 | Bashundhara | 116 | 13:00 | 87 | Kazla | 61 | 15:00 | 153 | Rajendrapur | 85 | 14:00
22 | BashundharaCement | 12 | 11:00 | 88 | Keranigonj | 52 | 22:00 | 154 | Rajshahi | 102 | 19:00
23 | Beanibazar | 54 | 18:30 | 89 | Khagrachori | 32 | 18:30 | 155 | Rajshahi-230 | 68 | 13:00
24 | Benapole | 68 | 19:30 | 90 | Khulna | 50 | 13:00 | 156 | Ramganj | 98 | 20:00
25 | Bhaluka | 118 | 14:00 | 91 | Khulshi | 144 | 16:00 | 157 | Rampur | 32 | 21:00
26 | Bhandaria | 50 | 21:00 | 92 | Kishoreganj | 104 | 14:00 | 158 | Rangamati | 17 | 20:00
27 | Bhangura | 38 | 13:00 | 93 | Kodda | 148 | 18:30 | 159 | Rangpur | 109 | 14:00
28 | Bheramara(GK) | 60 | 19:00 | 94 | Kulaura | 35 | 18:30 | 160 | Ruppur | 4 | 15:00
29 | Bhulta | 98 | 18:30 | 95 | Kurigram | 58 | 19:00 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 68 | 20:00 | 96 | Kushtia | 130 | 18:30 | 162 | Saidpur | 72 | 19:00
31 | Bogura | 137 | 20:00 | 97 | Laksam | 28 | 18:30 | 163 | Satkhira | 134 | 19:00
32 | Borhanuddin | 91 | 22:00 | 98 | Lakshmipur | 30 | 00:00 | 164 | Satmasjid | 67 | 14:00
33 | Brahmanbaria | 111 | 13:00 | 99 | Lalbag | 19 | 16:00 | 165 | Savar | 104 | 15:00
34 | Cantonment | 118 | 13:00 | 100 | Lalmonirhat | 44 | 18:30 | 166 | SevenRings | 5.49 | 02:00
35 | Chandina | 24 | 09:00 | 101 | MI_Cement | 16.7 | 17:00 | 167 | ShahCement | 37 | 12:00
36 | Chandpur | 72 | 19:00 | 102 | Madanganj | 32 | 15:00 | 168 | Shahjadpur | 60 | 14:00
37 | Chandraghona | 35 | 18:30 | 103 | Madaripur | 98 | 20:00 | 169 | Shahjibazar | 103 | 19:00
38 | Chapai | 63 | 19:30 | 104 | Madartek | 51 | 13:00 | 170 | Shahmirpur | 52 | 02:00
39 | Charsaidpur | 31 | 15:00 | 105 | Madunaghat | 47 | 18:00 | 171 | Shariatpur | 78 | 20:00
40 | Chauddagram | 73 | 18:30 | 106 | Magura | 64 | 18:30 | 172 | Sherpur | 118 | 18:30
41 | Chhatak | 27 | 20:00 | 107 | Mahasthangarh | 66 | 19:00 | 173 | Shikalbaha | 25 | 19:00
42 | Chowmuhani | 136 | 19:00 | 108 | Maijdee | 43 | 21:00 | 174 | Shitalakhya | 49 | 15:00
43 | Chuadanga | 116 | 19:00 | 109 | Manikganj | 89 | 15:00 | 175 | Sholosohor | 32 | 21:00
44 | Coxsbazar | 142 | 19:30 | 110 | Maniknagar | 50 | 13:00 | 176 | Shyampur | 80 | 17:00
45 | Cumilla(N) | 111 | 13:00 | 111 | Matarbari | 50 | 19:00 | 177 | Siddhirganj | 68 | 14:00
46 | Cumilla(S) | 133 | 18:30 | 112 | Matuail | 28 | 19:00 | 178 | Sirajganj | 88 | 13:00
47 | Daganbhuiyan | 31 | 21:00 | 113 | Metrorail_Motijheel | 20 | 10:00 | 179 | Sonargaon | 79 | 13:00
48 | Daudkandi | 110 | 19:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sreemongol | 66 | 18:30
49 | DhakaUniversity | 36 | 13:00 | 115 | Millgate | 49 | 17:00 | 181 | Sreepur | 78 | 15:00
50 | Dhamrai | 78 | 17:00 | 116 | Mirpur | 90 | 14:00 | 182 | Srinagar | 43 | 14:00
51 | Dhanmondi | 69.3 | 14:00 | 117 | Mirsorai | 9 | 18:00 | 183 | Sunamganj | 47 | 18:30
52 | Dohazari | 101 | 20:00 | 118 | Mirzapur | 46 | 13:00 | 184 | Sylhet | 45 | 18:30
53 | Faridpur | 132 | 19:00 | 119 | Mithapukur | 54 | 18:30 | 185 | Sylhet-132 | 84 | 18:30
54 | Fatullah | 44 | 18:30 | 120 | Modern | N/A | N/A | 186 | TK | 20 | 19:30
55 | Fenchuganj | 31 | 18:30 | 121 | Mogbazar | 42.4 | 14:00 | 187 | Tangail | 148 | 14:00
56 | Feni | 90 | 18:30 | 122 | Mongla | 49 | 18:30 | 188 | Taraganj | 18 | 19:00
57 | GPH | 76 | 10:00 | 123 | Motijheel | 28 | 13:00 | 189 | Tasnim | 18 | 19:30
58 | Ghatail | 84 | 14:00 | 124 | Muktagacha | 32 | 18:30 | 190 | Thakurgaon | 81 | 19:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 90 | 13:00 | 191 | Tongi | 64 | 13:00
60 | Ghorashal-230 | 79 | 19:00 | 126 | Muradnagar | 32 | 15:00 | 192 | Ullahpara | 39 | 14:00
61 | Goalpara | 36 | 13:00 | 127 | Mymensingh | 156 | 18:30 | 193 | Ullon | 36 | 13:00
62 | Gollamari | 82 | 20:00 | 128 | Nabinagar | 6 | 14:00 | 194 | Uttara | 54 | 18:00
63 | Gopalganj | 105 | 19:30 | 129 | Naogaon | 111 | 21:00 | 195 | UttaraNew | 20 | 14:00
64 | Gulshan | 84 | 13:00 | 130 | Narail | 57.5 | 19:30 | 196 | Zigatola | 66 | 13:00
65 | Halishahar | 54.5 | 18:30 | 131 | Narinda | 33 | 13:00
66 | HaripurSBU | 90 | 13:00 | 132 | Narshingdi | 102 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 25-03-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 9876 | 0 |  | 9876
1:00 | 9417 | 0 |  | 9417
2:00 | 8902 | 0 |  | 8902
3:00 | 8610 | 0 |  | 8610
4:00 | 8440 | 0 |  | 8440
5:00 | 8197 | 0 |  | 8197
6:00 | 8112.01 | 0 |  | 8112.01
7:00 | 8605.75 | 0 |  | 8605.75
8:00 | 9031.54 | 0 |  | 9031.54
9:00 | 9229.23 | 0 |  | 9229.23
10:00 | 9404.78 | 0 |  | 9404.78
11:00 | 9718.07 | 0 |  | 9718.07
12:00 | 10112.17 | 0 |  | 10112.17
13:00 | 11058.61 | 0 |  | 11058.61
14:00 | 11281.92 | 0 |  | 11281.92
15:00 | 10997.6 | 0 |  | 10997.6
16:00 | 10425.25 | 0 |  | 10425.25
17:00 | 9998.3 | 0 |  | 9998.3
18:00 | 9925.32 | 0 |  | 9925.32
19:00 | 10950.74 | 0 |  | 10950.74
19:30 | 10579.07 | 0 |  | 10579.07
20:00 | 10408.07 | 0 |  | 10408.07
21:00 | 10358.62 | 0 |  | 10358.62
22:00 | 10217.57 | 0 |  | 10217.57
23:00 | 10232.75 | 0 |  | 10232.75
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 25-03-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5528 | 4348 | 9876 | DAILY GENERATION CURVE
00:30 | 5383.5 | 4263 | 9646.5
01:00 | 5239 | 4178 | 9417 | 25-03-2026
01:30 | 5060 | 4099.5 | 9159.5
02:00 | 4881 | 4021 | 8902
02:30 | 4781 | 3975 | 8756
03:00 | 4681 | 3929 | 8610
03:30 | 4606 | 3919 | 8525
04:00 | 4531 | 3909 | 8440
04:30 | 4426.5 | 3892 | 8318.5
05:00 | 4322 | 3875 | 8197
05:30 | 4279.505 | 3875 | 8154.505
06:00 | 4237.01 | 3875 | 8112.01
06:30 | 4416.96 | 3941.92 | 8358.88
07:00 | 4596.91 | 4008.84 | 8605.75
07:30 | 4744.99 | 4073.655 | 8818.645
08:00 | 4893.07 | 4138.47 | 9031.54
08:30 | 4944.495 | 4185.89 | 9130.385
09:00 | 4995.92 | 4233.31 | 9229.23
09:30 | 5032.35 | 4284.655 | 9317.005
10:00 | 5068.78 | 4336 | 9404.78
10:30 | 5137.955 | 4423.47 | 9561.425
11:00 | 5207.13 | 4510.94 | 9718.07
11:30 | 5287.735 | 4627.385 | 9915.12
12:00 | 5368.34 | 4743.83 | 10112.17
12:30 | 5609.115 | 4976.275 | 10585.39
13:00 | 5849.89 | 5208.72 | 11058.61
13:30 | 5888.33 | 5281.935 | 11170.265
14:00 | 5926.77 | 5355.15 | 11281.92
14:30 | 5899.085 | 5240.675 | 11139.76
15:00 | 5871.4 | 5126.2 | 10997.6
15:30 | 5739.345 | 4972.08 | 10711.425
16:00 | 5607.29 | 4817.96 | 10425.25
16:30 | 5459.035 | 4752.74 | 10211.775
17:00 | 5310.78 | 4687.52 | 9998.3
17:30 | 5310.55 | 4651.26 | 9961.81
18:00 | 5310.32 | 4615 | 9925.32
18:30 | 5438.66 | 4999.37 | 10438.03
19:00 | 5567 | 5383.74 | 10950.74
19:30 | 5335 | 5244.07 | 10579.07
20:00 | 5193 | 5215.07 | 10408.07
20:30 | 5206 | 5177.345 | 10383.345 |  | Executive Engineer
21:00 | 5219 | 5139.62 | 10358.62 |  | Network Operation Division
21:30 | 5200 | 5088.095 | 10288.095
22:00 | 5181 | 5036.57 | 10217.57
22:30 | 5198 | 5027.16 | 10225.16
23:00 | 5215 | 5017.75 | 10232.75

## En-Curve
QF-LDC-12
Date | 25-03-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3900 | 2178 | 898 | 0 | 114 | 831 | 80 | 1875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3842.5 | 2115.5 | 898 | 0 | 112 | 830 | 80 | 1768.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25-03-2026
01:00 | 3785 | 2053 | 898 | 0 | 110 | 829 | 80 | 1662 | 0 | 0 | 0 | 0 | 0 | 0 | 0
01:30 | 3694.5 | 1968 | 898 | 0 | 108 | 828.5 | 60 | 1602.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Generated | 236.646 |  | MKWHr
02:00 | 3604 | 1883 | 898 | 0 | 106 | 828 | 40 | 1543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3507 | 1842.5 | 898 | 0 | 105 | 828 | 40 | 1535.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total Energy Requirement | 236.646 |  | MKWHr
03:00 | 3410 | 1802 | 898 | 0 | 104 | 828 | 40 | 1528 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 3367 | 1762.5 | 898 | 0 | 102 | 829 | 40 | 1521 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0
04:00 | 3324 | 1723 | 898 | 0 | 100 | 830 | 40 | 1514 | 0 | 0 | 0 | 0 | 0 | 11 | 0
04:30 | 3228 | 1706.5 | 892 | 0 | 99 | 830.5 | 40 | 1515.5 | 0 | 0 | 0 | 0 | 0 | 7 | 0
05:00 | 3132 | 1690 | 886 | 0 | 98 | 831 | 40 | 1517 | 0 | 0 | 0 | 0 | 0 | 3 | 0
05:30 | 3135.5 | 1642 | 886 | 0 | 97 | 831.5 | 40 | 1519 | 0.005 | 0 | 0 | 0 | 0 | 3.5 | 0
06:00 | 3139 | 1594 | 886 | 0 | 96 | 832 | 40 | 1521 | 0.01 | 0 | 0 | 0 | 0 | 4 | 0
06:30 | 3282.5 | 1656.5 | 886 | 0 | 94 | 832.5 | 40 | 1531 | 34.38 | 0 | 0 | 0 | 0 | 2 | 0
07:00 | 3426 | 1719 | 886 | 0 | 92 | 833 | 40 | 1541 | 68.75 | 0 | 0 | 0 | 0 | 0 | 0
07:30 | 3535.5 | 1777 | 886 | 0 | 79 | 831.5 | 40 | 1534 | 135.645 | 0 | 0 | 0 | 0 | 0 | 0
08:00 | 3645 | 1835 | 886 | 0 | 66 | 830 | 40 | 1527 | 202.54 | 0 | 0 | 0 | 0 | 0 | 0
08:30 | 3659 | 1842 | 886 | 0 | 68 | 827.6 | 40 | 1525 | 270.785 | 0 | 12 | 0 | 0 | 0 | 0
09:00 | 3673 | 1849 | 886 | 0 | 70 | 825.2 | 40 | 1523 | 339.03 | 0 | 24 | 0 | 0 | 0 | 0
09:30 | 3689.5 | 1846 | 886 | 0 | 85 | 827.32 | 40 | 1523.5 | 395.685 | 0 | 24 | 0 | 0 | 0 | 0
10:00 | 3706 | 1843 | 886 | 0 | 100 | 829.44 | 40 | 1524 | 452.34 | 0 | 24 | 0 | 0 | 0 | 0
10:30 | 3735.5 | 1872 | 886 | 0 | 94 | 833.98 | 40 | 1526.5 | 549.445 | 0 | 24 | 0 | 0 | 0 | 0
11:00 | 3765 | 1901 | 886 | 0 | 88 | 838.52 | 40 | 1529 | 646.55 | 0 | 24 | 0 | 0 | 0 | 0
11:30 | 3708 | 2037 | 886 | 0 | 94 | 848.685 | 40 | 1621 | 656.435 | 0 | 24 | 0 | 0 | 0 | 0
12:00 | 3651 | 2173 | 886 | 0 | 100 | 858.85 | 40 | 1713 | 666.32 | 0 | 24 | 0 | 0 | 0 | 0
12:30 | 3710.5 | 2275 | 886 | 0 | 103 | 918.925 | 40 | 1956.5 | 665.465 | 0 | 24 | 0 | 0 | 6 | 0
13:00 | 3770 | 2377 | 886 | 0 | 106 | 979 | 40 | 2200 | 664.61 | 0 | 24 | 0 | 0 | 12 | 0
13:30 | 3721.5 | 2391 | 886 | 0 | 109 | 969.2 | 40 | 2365 | 649.065 | 0 | 30 | 0 | 0 | 9.5 | 0
14:00 | 3673 | 2405 | 886 | 0 | 112 | 959.4 | 40 | 2530 | 633.52 | 0 | 36 | 0 | 0 | 7 | 0
14:30 | 3594.5 | 2416.5 | 886.5 | 0 | 118 | 953.755 | 40 | 2520 | 567.005 | 0 | 38 | 0 | 0 | 5.5 | 0
15:00 | 3516 | 2428 | 887 | 0 | 124 | 948.11 | 40 | 2510 | 500.49 | 0 | 40 | 0 | 0 | 4 | 0
15:30 | 3555 | 2329 | 886.5 | 0 | 121 | 910.895 | 40 | 2445.5 | 377.53 | 0 | 40 | 0 | 0 | 6 | 0
16:00 | 3594 | 2230 | 886 | 0 | 118 | 873.68 | 40 | 2381 | 254.57 | 0 | 40 | 0 | 0 | 8 | 0
16:30 | 3571.5 | 2115.5 | 886 | 0 | 117 | 870.46 | 40 | 2379 | 186.315 | 0 | 40 | 0 | 0 | 6 | 0
17:00 | 3549 | 2001 | 886 | 0 | 116 | 867.24 | 40 | 2377 | 118.06 | 0 | 40 | 0 | 0 | 4 | 0
17:30 | 3586 | 1970 | 886 | 0 | 119 | 868.395 | 40 | 2378.5 | 62.915 | 8.5 | 40 | 0 | 0 | 2.5 | 0
18:00 | 3623 | 1939 | 886 | 0 | 122 | 869.55 | 40 | 2380 | 7.77 | 17 | 40 | 0 | 0 | 1 | 0
18:30 | 3641.5 | 1931.5 | 886 | 0 | 127 | 1045.645 | 40 | 2690 | 3.885 | 17 | 55 | 0 | 0 | 0.5 | 0
19:00 | 3660 | 1924 | 886 | 0 | 132 | 1221.74 | 40 | 3000 | 0 | 17 | 70 | 0 | 0 | 0 | 0
19:30 | 3493 | 1763 | 886 | 0 | 128 | 1215.07 | 40 | 3006 | 0 | 0 | 48 | 0 | 0 | 0 | 0
20:00 | 3452 | 1712 | 886 | 0 | 128 | 1214.07 | 40 | 2944 | 0 | 0 | 32 | 0 | 0 | 0 | 0
20:30 | 3470.5 | 1728.5 | 886 | 0 | 124 | 1168.345 | 40 | 2938 | 0 | 0 | 28 | 0 | 0 | 0 | 0
21:00 | 3489 | 1745 | 886 | 0 | 120 | 1122.62 | 40 | 2932 | 0 | 0 | 24 | 0 | 0 | 0 | 0
21:30 | 3483.5 | 1738.5 | 886 | 0 | 105 | 1070.595 | 40 | 2940.5 | 0 | 0 | 24 | 0 | 0 | 0 | 0
22:00 | 3478 | 1732 | 886 | 0 | 90 | 1018.57 | 40 | 2949 | 0 | 0 | 24 | 0 | 0 | 0 | 0
22:30 | 3553 | 1732.5 | 886 | 0 | 100 | 998.16 | 40 | 2891.5 | 0 | 0 | 24 | 0 | 0 | 0 | 0
23:00 | 3628 | 1733 | 886 | 0 | 110 | 977.75 | 40 | 2834 | 0 | 0 | 24 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 25-03-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 414 | 05:00 | 402 | 13:00 | Madunaghat | 405 | 06:00 | 399 | 14:00
Amtali | 421 | 04:00 | 412 | 19:00 | Meghnaghat | 415 | 05:00 | 406 | 13:00
Ashuganj | 412 | 6:00 | 400 | 13:00 | Payra | 421 | 04:00 | 414 | 13:00
Bhulta | 407 | 05:00 | 395 | 13:00 | Rahanpur | 416 | 05:00 | 397 | 19:00
Bibiana | 416 | 06:00 | 409 | 13:00 | Rampal | 410 | 05:00 | 396 | 13:00
BIPTC | 399 | 03:00 | 389 | 19:30
Bogura | 411 | 05:00 | 388 | 19:00
Gopalganj | 415 | 05:00 | 402 | 13:00
Kaliakoir | 411 | 05:00 | 397 | 13:00
Korerhat | 412 | 05:00 | 403 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 236 | 04:00 | 228 | 13:00 | Jhenaidah | 230 | 05:00 | 218 | 13:00
AKSML | 236 | 05:00 | 228 | 13:00 | Kachua | 234 | 06:00 | 227 | 13:00
Aminbazar | 237 | 04:00 | 229 | 13:00 | Kaliakoir | 239 | 05:00 | 230 | 13:00
Ashuganj | 237 | 05:00 | 228 | 13:00 | Keranigonj | 236 | 06:00 | 227 | 13:00
Ashuganj-400 | 237 | 05:00 | 228 | 13:00 | Khulna(S) | 235 | 06:00 | 220 | 19:00
Baghabari | 236 | 05:00 | 227 | 19:00 | Korerhat | 237 | 04:00 | 228 | 13:00
Barapukuria | 232 | 05:00 | 212 | 19:00 | Madunaghat | 235 | 05:00 | 229 | 18:30
Barapukuria-230 | 232 | 05:00 | 212 | 19:00 | Madunaghat-400 | 235 | 05:00 | 230 | 20:00
Barishal | 233 | 03:00 | 226 | 19:00 | Maniknagar | 236 | 02:00 | 229 | 13:00
Bheramara | 232 | 05:00 | 222 | 13:00 | Meghnaghat | 241 | 07:00 | 234 | 13:00
Bhulta | 237 | 04:00 | 229 | 13:00 | Meghnaghat-400 | 236 | 05:00 | 229 | 13:00
Bibiana | 243 | 04:00 | 234 | 13:00 | Mirsorai | 240 | 07:00 | 234 | 19:30
BIPTC | 235 | 06:00 | 222 | 13:00 | Purbasadipur | 230 | 05:00 | 204 | 19:00
Bogura | 238 | 05:00 | 222 | 19:00 | Rajshahi | 232 | 06:00 | 218 | 19:00
Bogura-400 | 237 | 06:00 | 222 | 19:00 | Rampal | 234 | 06:00 | 222 | 19:00
Borhanuddin | 239 | 18:00 | 231 | 13:00 | Rampur | N/A | N/A | N/A | N/A
BSRM | 235 | 06:00 | 228 | 13:00 | Rampura | 237 | 06:00 | 229 | 13:00
Chowmuhani | 234 | 06:00 | 227 | 13:00 | Shikalbaha | 233 | 06:00 | 227 | 13:00
Cumilla(N) | 233 | 03:00 | 228 | 13:00 | Shyampur | 235 | 04:00 | 228 | 13:00
Faridpur | 232 | 04:00 | 224 | 13:00 | Siddhirganj | 238 | 05:00 | 231 | 13:00
Fenchuganj | 241 | 02:00 | 237 | 13:00 | Sirajgonj | 242 | 04:00 | 233 | 19:00
Feni | 235 | 06:00 | 228 | 13:00 | Sreepur | 232 | 04:00 | 224 | 13:00
Ghorashal | 240 | 04:00 | 230 | 00:00 | Tongi | 238 | 04:00 | 230 | 11:00
Ghorashal-230 | 236 | 06:00 | 227 | 13:00
Gopalganj | 232 | 06:00 | 223 | 13:00
GPH | 236 | 06:00 | 229 | 13:00
Haripur | 237 | 05:00 | 230 | 13:00
Hasnabad | 236 | 05:00 | 228 | 13:00
Hathazari | 233 | 03:00 | 224 | 19:00
Ishurdi | 236 | 06:00 | 225 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 06:00 | 129 | 13:00 | Madunaghat | 136 | 05:00 | 132 | 13:00
Agargaon | 136 | 05:00 | 129 | 13:00 | Magura | 130 | 05:00 | 120 | 12:00
Agrabad | 135 | 07:00 | 130 | 19:00 | Mahasthangarh | 135 | 04:00 | 122 | 19:00
AKS | 133 | 08:00 | 130 | 10:00 | Maijdee | 130 | 04:00 | 125 | 19:00
Aminbazar | 137 | 04:00 | 132 | 13:00 | Manikganj | 136 | 18:30 | 126 | 14:00
Amnura | 137 | 02:00 | 126 | 13:00 | Maniknagar | 134 | 04:00 | 129 | 13:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 119 | 09:00 | 106 | 19:00
Ashuganj-230 | 144 | 05:00 | 137 | 12:00 | Matuail | 137 | 20:00 | 132 | 13:00
Bagerhat | 130 | 05:00 | 116 | 19:00 | Metrorail_Motijheel | 134 | 07:00 | 129 | 13:00
Bajitpur | 136 | 05:00 | 126 | 18:00 | Metrorail_Uttara | 137 | 06:00 | 131 | 13:00
Bakerganj | 136 | 06:00 | 131 | 13:00 | Millgate | 137 | 04:00 | 130 | 13:00
Bakulia | 134 | 10:00 | 129 | 19:00 | Mirpur | 137 | 05:00 | 131 | 13:00
Banani | 137 | 04:00 | 130 | 13:00 | Mirzapur | 132 | 00:00 | 125 | 13:00
Bangabhaban | 133 | 04:00 | 129 | 13:00 | Mithapukur | 134 | 05:00 | 118 | 19:00
Barapukuria | 133 | 05:00 | 119 | 19:00 | MI_Cement | 137 | 06:00 | 131 | 13:00
Barguna | 136 | 05:00 | 130 | 19:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 135 | 06:00 | 130 | 13:00 | Mogbazar | 135 | 01:00 | 125 | 12:00
Barishal-230 | 136 | 02:00 | 130 | 19:00 | Mongla | 128 | 04:00 | 115 | 19:00
Baroaulia | 135 | 06:00 | 132 | 00:00 | Motijheel | 133 | 04:00 | 129 | 13:00
Baroirhat | 134 | 03:00 | 130 | 13:00 | Muktagacha | 133 | 16:00 | 125 | 13:00
Bashundhara | 136 | 02:00 | 129 | 13:00 | Munshiganj | 135 | 20:00 | 129 | 13:00
BashundharaCement | 136 | 20:00 | 132 | 16:00 | Muradnagar | 136 | 21:00 | 128 | 13:00
Beanibazar | 133 | 02:00 | 128 | 13:00 | Mymensingh | 135 | 05:00 | 123 | 08:00
Benapole | 127 | 03:00 | 114 | 19:00 | Nabinagar | 134 | 19:00 | 128 | 13:00
Bhaluka | 137 | 06:00 | 129 | 12:00 | Naogaon | 138 | 03:00 | 122 | 19:00
Bhandaria | 135 | 05:00 | 125 | 18:30 | Narail | 131 | 17:00 | 120 | 19:00
Bhangura | 134 | 03:00 | 129 | 14:00 | Narinda | 134 | 04:00 | 129 | 13:00
Bheramara | 135 | 04:00 | 130 | 13:00 | Narshingdi | 135 | 20:00 | 129 | 13:00
Bheramara(GK) | 135 | 04:00 | 130 | 13:00 | Natore | 134 | 05:00 | 125 | 19:00
Bhulta | 132 | 20:00 | 128 | 13:00 | Nawabganj | 134 | 04:00 | 128 | 13:00
Bog-Sherpur | 137 | 05:00 | 126 | 19:00 | Netrakona | 133 | 02:00 | 123 | 10:00
Bogura | 137 | 04:00 | 129 | 13:00 | New | 136 | 03:00 | 132 | 13:00
Bogura-230 | 137 | 04:00 | 127 | 19:00 | Niamatpur | 139 | 02:00 | 133 | 13:00
Brahmanbaria | 136 | 18:00 | 129 | 13:00 | Noapara | 131 | 06:00 | 121 | 13:00
Cantonment | 135 | 03:00 | 129 | 13:00 | Pabna | 135 | 04:00 | 129 | 13:00
Chandina | 136 | 04:00 | 131 | 13:00 | Palashbari | 132 | 05:00 | 119 | 19:00
Chandpur | 132 | 22:00 | 127 | 13:00 | Panchagarh | 138 | 04:00 | 122 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 136 | 04:00 | 132 | 12:00 | Patiya | 133 | 07:00 | 126 | 19:00
Chapai | 139 | 04:00 | 132 | 19:30 | Patuakhali | 136 | 04:00 | 130 | 19:00
Charsaidpur | 135 | 05:00 | 130 | 13:00 | Payra | 138 | 06:00 | 135 | 13:00
Chauddagram | 133 | 05:00 | 129 | 13:00 | PHP | 133 | 03:00 | 129 | 14:00
Chhatak | 133 | 03:00 | 126 | 14:00 | Postogola | 137 | 06:00 | 132 | 13:00
Chowmuhani | 131 | 07:00 | 126 | 15:00 | Pubail | 142 | 04:00 | 135 | 14:00
Chuadanga | 129 | 05:00 | 117 | 19:00 | Purbachal | 136 | 03:00 | 130 | 13:00
Coxsbazar | 119 | 08:00 | 107 | 20:00 | Purbasadipur | 133 | 05:00 | 116 | 19:00
Cumilla(N) | 136 | 06:00 | 131 | 13:00 | Rahanpur | 139 | 05:00 | 133 | 19:00
Cumilla(S) | 136 | 05:00 | 123 | 15:00 | Rahanpur-400 | 139 | 03:00 | 133 | 19:00
Daganbhuiyan | 132 | 06:00 | 128 | 13:00 | Rahim | 136 | 21:00 | 132 | 12:00
Daudkandi | 136 | 21:00 | 126 | 13:00 | Rajbari | 134 | 04:00 | 128 | 13:00
DhakaUniversity | 134 | 02:00 | 129 | 13:00 | Rajendrapur | 138 | 17:00 | 130 | 13:00
Dhamrai | 134 | 02:00 | 128 | 13:00 | Rajshahi | 134 | 03:00 | 125 | 13:00
Dhanmondi | 138 | 06:00 | 133 | 13:00 | Rajshahi-230 | 134 | 05:00 | 125 | 13:00
Dohazari | 129 | 05:00 | 121 | 19:00 | Ramganj | 130 | 05:00 | 124 | 13:00
Faridpur | 135 | 04:00 | 130 | 13:00 | Rampur | 134 | 03:00 | 130 | 19:00
Fatullah | 137 | 03:00 | 132 | 13:00 | Rampura | 134 | 04:00 | 129 | 13:00
Fenchuganj | 137 | 01:00 | 133 | 12:00 | Rangamati | 136 | 06:00 | 130 | 19:00
Feni | 130 | 03:00 | 127 | 15:00 | Rangpur | 132 | 05:00 | 118 | 19:00
Feni-230 | 132 | 04:00 | 128 | 13:00 | Ruppur | 136 | 05:00 | 130 | 18:30
Ghatail | 131 | 17:00 | 122 | 08:00 | Saidpur | 133 | 05:00 | 116 | 19:00
Ghorashal | 141 | 04:00 | 135 | 15:00 | Satkhira | 130 | 06:00 | 117 | 19:00
Goalpara | 133 | 05:00 | 123 | 19:00 | Satmasjid | 135 | 04:00 | 130 | 15:00
Gollamari | 134 | 05:00 | 125 | 13:00 | Savar | 136 | 19:00 | 130 | 13:00
Gopalganj | 135 | 04:00 | 127 | 19:00 | SevenRings | 142 | 03:00 | 136 | 13:00
Gopalganj-400 | 138 | 06:00 | 132 | 13:00 | ShahCement | 135 | 05:00 | 130 | 13:00
Gulshan | 133 | 02:00 | 128 | 13:00 | Shahjadpur | 138 | 04:00 | 133 | 13:00
Halishahar | 135 | 04:00 | 130 | 19:00 | Shahjibazar | 137 | 05:00 | 129 | 13:00
Haripur | 136 | 06:00 | 132 | 12:00 | Shahmirpur | 134 | 07:00 | 130 | 14:00
HaripurSBU | 136 | 21:00 | 132 | 14:00 | Shariatpur | 136 | 04:00 | 129 | 13:00
Hasnabad | 137 | 02:00 | 133 | 11:00 | Sherpur | 126 | 03:00 | 114 | 08:00
Hathazari | 136 | 07:00 | 132 | 19:00 | Shikalbaha | 126 | 06:00 | 119 | 18:30
Hatirjheel | 134 | 02:00 | 129 | 13:00 | Shikalbaha-230 | 135 | 05:00 | 131 | 19:00
Ishurdi | 137 | 03:00 | 131 | 19:00 | Shitalakhya | 137 | 06:00 | 131 | 13:00
Jaldhaka | 132 | 05:00 | 113 | 19:00 | Sholosohor | 135 | 04:00 | 131 | 19:00
Jamalpur | 129 | 02:00 | 117 | 08:00 | Shyampur | 136 | 04:00 | 132 | 13:00
Jashore | 130 | 04:00 | 123 | 13:00 | Shyampur-230 | 137 | 04:00 | 132 | 13:00
Jhenaidah | 131 | 05:00 | 122 | 14:00 | Siddhirganj | 137 | 05:00 | 133 | 12:00
Jhenaidah-230 | 132 | 06:00 | 122 | 20:00 | Sirajganj | 135 | 04:00 | 126 | 13:00
Joydebpur | 138 | 05:00 | 131 | 13:00 | Sonargaon | 137 | 20:00 | 131 | 12:00
Joypurhat | 133 | 04:00 | 121 | 19:00 | Sreemongol | 136 | 02:00 | 129 | 13:00
Juldah | 134 | 07:00 | 130 | 19:00 | Sreepur | 139 | 03:00 | 132 | 13:00
Kabirpur | 137 | 04:00 | 127 | 13:00 | Srinagar | 135 | 05:00 | 128 | 13:00
Kachua | 132 | 03:00 | 128 | 13:00 | SSM | 138 | 22:00 | 136 | 00:00
Kaliakoir | 137 | 03:00 | 126 | 01:00 | Sunamganj | 132 | 02:00 | 124 | 13:00
Kaliganj | 131 | 06:00 | 120 | 19:00 | Sylhet | 134 | 04:00 | 129 | 13:00
Kallyanpur | 137 | 19:00 | 131 | 13:00 | Sylhet-132 | 133 | 02:00 | 129 | 12:00
Kalurghat | 136 | 04:00 | 131 | 19:00 | Tangail | 130 | 16:00 | 123 | 13:00
Kamrangirchar | 136 | 05:00 | 129 | 13:00 | Taraganj | 133 | 05:00 | 115 | 18:30
Kaptai | N/A | N/A | N/A | N/A | Tasnim | 137 | 20:00 | 131 | 12:00
Kasba | 136 | 21:00 | 127 | 13:00 | Thakurgaon | 136 | 05:00 | 118 | 19:00
Kazla | 134 | 06:00 | 128 | 14:00 | TK | 137 | 04:00 | 132 | 18:30
Keranigonj | 135 | 05:00 | 129 | 13:00 | Tongi | 137 | 04:00 | 132 | 11:00
Khagrachori | 135 | 07:00 | 129 | 19:00 | Ullahpara | 137 | 04:00 | 128 | 19:00
Khulna | 132 | 05:00 | 124 | 13:00 | Ullon | 136 | 03:00 | 129 | 13:00
Khulna(S) | 135 | 06:00 | 125 | 13:00 | Uttara | 137 | 03:00 | 131 | 13:00
Khulshi | 134 | 07:00 | 129 | 19:00 | UttaraNew | 136 | 03:00 | 131 | 13:00
Kishoreganj | 136 | 17:00 | 126 | 13:00 | Zigatola | 135 | 06:00 | 129 | 13:00
Kodda | 137 | 04:00 | 126 | 13:00
Korerhat | 138 | 04:00 | 132 | 13:00
KSRM | 136 | 02:00 | 131 | 18:30
Kulaura | 138 | 05:00 | 132 | 13:00
Kurigram | 131 | 04:00 | 110 | 19:00
Kushtia | 134 | 06:00 | 126 | 13:00
Laksam | 138 | 19:30 | 128 | 13:00
Lakshmipur | 130 | 04:00 | 126 | 13:00
Lalbag | 135 | 05:00 | 128 | 13:00
Lalmonirhat | 130 | 03:00 | 119 | 21:00
Madanganj | 136 | 20:00 | 132 | 16:00
Madaripur | 136 | 05:00 | 130 | 19:00
Madartek | 134 | 04:00 | 129 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division